## 1 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-01-03 19:00 | 0 | 32.14 | 0 | 0 | 2243.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 2276.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 2268.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 1692.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 1654.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 1663.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 1573.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 98.4%
2026-01-03 18:50 | 0 | 33 | 0 | 0 | 2243.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 2276.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 2236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 2268.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 1692.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 1654.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 1663.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 1573.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 18:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 98.44%
2026-01-03 18:40 | 0 | 34.73 | 0 | 0 | 2243.6 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 |  | 2026-01-03 18:40 | 0 | 0 | 2276.3 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 |  | 2026-01-03 18:40 | 0 | 0 | 2236 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 |  | 2026-01-03 18:40 | 0 | 0 | 2268.2 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 |  | 2026-01-03 18:40 | 0 | 0 | 1692.1 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 |  | 2026-01-03 18:40 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 |  | 2026-01-03 18:40 | 0 | 0 | 1654.4 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 2026-01-03 18:40 | 0 | 0 | 1663.6 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 |  | 2026-01-03 18:40 | 0 | 0 | 1573.7 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 |  | 2026-01-03 18:40 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 3 | 97.44%
2026-01-03 18:30 | 6 | 37.31 | 4.3 | 4.078 | 2243.3 | 0.67967 | 0.37294 | 0.30673 | 2.2376 | 1 | 0.36761 | 0.63239 |  | 2026-01-03 18:30 | 4.594 | 4.431 | 2276 | 0.7385 | 0.37294 | 0.36556 | 2.2376 | 1.1 | 0.36761 | 0.73239 |  | 2026-01-03 18:30 | 3.956 | 4.156 | 2235.8 | 0.69267 | 0.37294 | 0.31973 | 2.2376 | 1 | 0.36761 | 0.63239 |  | 2026-01-03 18:30 | 4.052 | 4.461 | 2267.9 | 0.7435 | 0.37294 | 0.37056 | 2.2376 | 1.1 | 0.36761 | 0.73239 |  | 2026-01-03 18:30 | 2.678 | 2.937 | 1691.9 | 0.4895 | 0.27625 | 0.21325 | 1.6575 | 0.7 | 0.2723 | 0.4277 |  | 2026-01-03 18:30 | 2.782 | 2.925 | 1666.3 | 0.4875 | 0.27625 | 0.21125 | 1.6575 | 0.7 | 0.2723 | 0.4277 |  | 2026-01-03 18:30 | 2.754 | 2.901 | 1654.3 | 0.4835 | 0.27625 | 0.20725 | 1.6575 | 0.8 | 0.2723 | 0.5277 |  | 2026-01-03 18:30 | 2.632 | 3.066 | 1663.4 | 0.511 | 0.27625 | 0.23475 | 1.6575 | 0.7 | 0.2723 | 0.4277 |  | 2026-01-03 18:30 | 2.555 | 2.686 | 1573.5 | 0.44767 | 0.26282 | 0.18485 | 1.5769 | 0.7 | 0.25906 | 0.44094 |  | 2026-01-03 18:30 | 5.2735 | 2.8596 | 2.4139 | 17.1574 | 7.8 | 2.8187 | 4.9813 | 4 | 98.37%
2026-01-03 18:20 | 20 | 39.89 | 8.659 | 9.011 | 2242.3 | 1.5018 | 1.2314 | 0.27044 | 7.3884 | 1.9 | 1.2138 | 0.68621 |  | 2026-01-03 18:20 | 9.413 | 9.788 | 2274.9 | 1.6313 | 1.2314 | 0.39994 | 7.3884 | 2 | 1.2138 | 0.78621 |  | 2026-01-03 18:20 | 8.7 | 9.058 | 2234.8 | 1.5097 | 1.2314 | 0.27827 | 7.3884 | 2 | 1.2138 | 0.78621 |  | 2026-01-03 18:20 | 8.907 | 9.268 | 2266.8 | 1.5447 | 1.2314 | 0.31327 | 7.3884 | 2 | 1.2138 | 0.78621 |  | 2026-01-03 18:20 | 6.382 | 6.669 | 1691.2 | 1.1115 | 0.91215 | 0.19935 | 5.4729 | 1.5 | 0.8991 | 0.6009 |  | 2026-01-03 18:20 | 6.226 | 6.504 | 1665.6 | 1.084 | 0.91215 | 0.17185 | 5.4729 | 1.4 | 0.8991 | 0.5009 |  | 2026-01-03 18:20 | 6.259 | 6.54 | 1653.5 | 1.09 | 0.91215 | 0.17785 | 5.4729 | 1.4 | 0.8991 | 0.5009 |  | 2026-01-03 18:20 | 6.152 | 6.649 | 1662.7 | 1.1082 | 0.91215 | 0.19602 | 5.4729 | 1.4 | 0.8991 | 0.5009 |  | 2026-01-03 18:20 | 5.794 | 6.065 | 1572.8 | 1.0108 | 0.86779 | 0.14304 | 5.2068 | 1.3 | 0.85538 | 0.44462 |  | 2026-01-03 18:20 | 11.592 | 9.442 | 2.15 | 56.6518 | 14.9 | 9.3069 | 5.5931 | 5 | 98.52%
2026-01-03 18:10 | 37 | 41.9 | 15.279 | 15.697 | 2240.4 | 2.6162 | 2.2612 | 0.35499 | 13.5671 | 3.3 | 2.2288 | 1.0712 |  | 2026-01-03 18:10 | 16.644 | 16.505 | 2272.9 | 2.7508 | 2.2612 | 0.48966 | 13.5671 | 3.4 | 2.2288 | 1.1712 |  | 2026-01-03 18:10 | 15.602 | 16.03 | 2232.8 | 2.6717 | 2.2612 | 0.41049 | 13.5671 | 3.4 | 2.2288 | 1.1712 |  | 2026-01-03 18:10 | 15.756 | 16.241 | 2264.8 | 2.7068 | 2.2612 | 0.44566 | 13.5671 | 3.3 | 2.2288 | 1.0712 |  | 2026-01-03 18:10 | 11.669 | 12.07 | 1689.7 | 2.0117 | 1.6749 | 0.33672 | 10.0497 | 2.5 | 1.651 | 0.84901 |  | 2026-01-03 18:10 | 11.294 | 11.719 | 1664.2 | 1.9532 | 1.6749 | 0.27822 | 10.0497 | 2.4 | 1.651 | 0.74901 |  | 2026-01-03 18:10 | 11.343 | 11.741 | 1652.1 | 1.9568 | 1.6749 | 0.28189 | 10.0497 | 2.4 | 1.651 | 0.74901 |  | 2026-01-03 18:10 | 10.723 | 11.466 | 1661.3 | 1.911 | 1.6749 | 0.23605 | 10.0497 | 2.3 | 1.651 | 0.64901 |  | 2026-01-03 18:10 | 10.451 | 10.832 | 1571.5 | 1.8053 | 1.5935 | 0.21183 | 9.561 | 2.2 | 1.5707 | 0.62928 |  | 2026-01-03 18:10 | 20.3835 | 17.338 | 3.0455 | 104.0279 | 25.2 | 17.0901 | 8.1099 | 6 | 98.34%
2026-01-03 18:00 | 54 | 43.91 | 24.719 | 24.955 | 2237.1 | 4.1592 | 3.2754 | 0.88375 | 19.6525 | 4.8 | 3.2286 | 1.5714 |  | 2026-01-03 18:00 | 25.297 | 25.863 | 2269.5 | 4.3105 | 3.2754 | 1.0351 | 19.6525 | 5 | 3.2286 | 1.7714 |  | 2026-01-03 18:00 | 24.924 | 25.479 | 2229.4 | 4.2465 | 3.2754 | 0.97108 | 19.6525 | 5 | 3.2286 | 1.7714 |  | 2026-01-03 18:00 | 25.095 | 25.652 | 2261.5 | 4.2753 | 3.2754 | 0.99991 | 19.6525 | 5.1 | 3.2286 | 1.8714 |  | 2026-01-03 18:00 | 18.601 | 19.072 | 1687.2 | 3.1787 | 2.4262 | 0.75243 | 14.5574 | 3.8 | 2.3915 | 1.4085 |  | 2026-01-03 18:00 | 17.876 | 18.331 | 1661.8 | 3.0552 | 2.4262 | 0.62893 | 14.5574 | 3.7 | 2.3915 | 1.3085 |  | 2026-01-03 18:00 | 18.024 | 18.48 | 1649.7 | 3.08 | 2.4262 | 0.65376 | 14.5574 | 3.7 | 2.3915 | 1.3085 |  | 2026-01-03 18:00 | 17.348 | 18.026 | 1659 | 3.0043 | 2.4262 | 0.5781 | 14.5574 | 3.6 | 2.3915 | 1.2085 |  | 2026-01-03 18:00 | 16.599 | 17.037 | 1569.3 | 2.8395 | 2.3083 | 0.53124 | 13.8496 | 3.4 | 2.2753 | 1.1247 |  | 2026-01-03 18:00 | 32.1492 | 25.1149 | 7.0343 | 150.6893 | 38.1 | 24.7557 | 13.3443 | 7 | 98.27%
2026-01-03 17:50 | 103 | 45.92 | 34.628 | 35.252 | 2232.3 | 5.8753 | 6.2005 | -0.32516 | 37.203 | 6.8 | 6.1118 | 0.68818 |  | 2026-01-03 17:50 | 36.083 | 36.741 | 2264.5 | 6.1235 | 6.2005 | -0.076992 | 37.203 | 7.4 | 6.1118 | 1.2882 |  | 2026-01-03 17:50 | 35.402 | 36.04 | 2224.4 | 6.0067 | 6.2005 | -0.19383 | 37.203 | 6.8 | 6.1118 | 0.68818 |  | 2026-01-03 17:50 | 35.578 | 36.282 | 2256.4 | 6.047 | 6.2005 | -0.15349 | 37.203 | 6.8 | 6.1118 | 0.68818 |  | 2026-01-03 17:50 | 26.697 | 27.256 | 1683.4 | 4.5427 | 4.593 | -0.05029 | 27.5577 | 5.2 | 4.5273 | 0.67272 |  | 2026-01-03 17:50 | 25.686 | 26.224 | 1658.1 | 4.3707 | 4.593 | -0.22229 | 27.5577 | 5 | 4.5273 | 0.47272 |  | 2026-01-03 17:50 | 25.621 | 26.165 | 1646 | 4.3608 | 4.593 | -0.23212 | 27.5577 | 5 | 4.5273 | 0.47272 |  | 2026-01-03 17:50 | 25.332 | 26.139 | 1655.4 | 4.3565 | 4.593 | -0.23646 | 27.5577 | 4.9 | 4.5273 | 0.37272 |  | 2026-01-03 17:50 | 23.84 | 24.371 | 1565.9 | 4.0618 | 4.3696 | -0.3078 | 26.2178 | 4.7 | 4.3071 | 0.39286 |  | 2026-01-03 17:50 | 45.745 | 47.5434 | -1.7984 | 285.2606 | 52.6 | 46.8636 | 5.7364 | 8 | 97.17%
2026-01-03 17:40 | 141 | 47.07 | 46.713 | 47.468 | 2225.5 | 7.9113 | 8.4512 | -0.53986 | 50.7071 | 9.4 | 8.3303 | 1.0697 |  | 2026-01-03 17:40 | 49.183 | 49.316 | 2257.1 | 8.2193 | 8.4512 | -0.23186 | 50.7071 | 8.7 | 8.3303 | 0.36966 |  | 2026-01-03 17:40 | 47.413 | 48.184 | 2217.6 | 8.0307 | 8.4512 | -0.42052 | 50.7071 | 9.1 | 8.3303 | 0.76966 |  | 2026-01-03 17:40 | 47.662 | 48.442 | 2249.6 | 8.0737 | 8.4512 | -0.37752 | 50.7071 | 9.2 | 8.3303 | 0.86966 |  | 2026-01-03 17:40 | 35.961 | 36.609 | 1678.2 | 6.1015 | 6.2601 | -0.15864 | 37.5608 | 6.9 | 6.1706 | 0.72938 |  | 2026-01-03 17:40 | 34.58 | 35.189 | 1653.1 | 5.8648 | 6.2601 | -0.39531 | 37.5608 | 6.6 | 6.1706 | 0.42938 |  | 2026-01-03 17:40 | 34.699 | 35.321 | 1641 | 5.8868 | 6.2601 | -0.37331 | 37.5608 | 6.6 | 6.1706 | 0.42938 |  | 2026-01-03 17:40 | 34.185 | 35.181 | 1650.5 | 5.8635 | 6.2601 | -0.39664 | 37.5608 | 6.6 | 6.1706 | 0.42938 |  | 2026-01-03 17:40 | 32.194 | 32.784 | 1561.2 | 5.464 | 5.9557 | -0.49175 | 35.7345 | 6.2 | 5.8706 | 0.32942 |  | 2026-01-03 17:40 | 61.4157 | 64.8011 | -3.3854 | 388.8064 | 69.3 | 63.8744 | 5.4256 | 9 | 98.54%
2026-01-03 17:30 | 186 | 47.35 | 62.331 | 63.19 | 2216.1 | 10.5317 | 11.1365 | -0.60487 | 66.8192 | 11.2 | 10.9773 | 0.22272 |  | 2026-01-03 17:30 | 63.617 | 64.514 | 2248.4 | 10.7523 | 11.1365 | -0.3842 | 66.8192 | 12 | 10.9773 | 1.0227 |  | 2026-01-03 17:30 | 62.671 | 63.555 | 2208.5 | 10.5925 | 11.1365 | -0.54404 | 66.8192 | 11.7 | 10.9773 | 0.72272 |  | 2026-01-03 17:30 | 63.263 | 64.148 | 2240.4 | 10.6913 | 11.1365 | -0.4452 | 66.8192 | 11.7 | 10.9773 | 0.72272 |  | 2026-01-03 17:30 | 47.44 | 48.216 | 1671.3 | 8.036 | 8.2493 | -0.21329 | 49.4957 | 8.7 | 8.1313 | 0.56868 |  | 2026-01-03 17:30 | 45.785 | 46.52 | 1646.5 | 7.7533 | 8.2493 | -0.49595 | 49.4957 | 8.4 | 8.1313 | 0.26868 |  | 2026-01-03 17:30 | 45.837 | 46.597 | 1634.4 | 7.7662 | 8.2493 | -0.48312 | 49.4957 | 8.4 | 8.1313 | 0.26868 |  | 2026-01-03 17:30 | 45.299 | 46.672 | 1643.9 | 7.7787 | 8.2493 | -0.47062 | 49.4957 | 8.3 | 8.1313 | 0.16868 |  | 2026-01-03 17:30 | 42.912 | 43.636 | 1555 | 7.2727 | 7.8482 | -0.57551 | 47.089 | 7.8 | 7.7359 | 0.064055 |  | 2026-01-03 17:30 | 81.1747 | 85.3915 | -4.2168 | 512.3488 | 88.2 | 84.1704 | 4.0296
2026-01-03 17:20 | 227 | 47.35 | 75.868 | 76.886 | 2204.9 | 12.8143 | 13.5914 | -0.77703 | 81.5482 | 14.2 | 13.397 | 0.80299 |  | 2026-01-03 17:20 | 78.346 | 78.906 | 2236.4 | 13.151 | 13.5914 | -0.44036 | 81.5482 | 14.1 | 13.397 | 0.70299 |  | 2026-01-03 17:20 | 76.607 | 78.07 | 2196.8 | 13.0117 | 13.5914 | -0.5797 | 81.5482 | 13.9 | 13.397 | 0.50299 |  | 2026-01-03 17:20 | 77.333 | 78.367 | 2228.7 | 13.0612 | 13.5914 | -0.5302 | 81.5482 | 14.3 | 13.397 | 0.90299 |  | 2026-01-03 17:20 | 57.63 | 58.532 | 1662.6 | 9.7553 | 10.0677 | -0.31234 | 60.4061 | 10.7 | 9.9237 | 0.77629 |  | 2026-01-03 17:20 | 56.021 | 56.857 | 1638.1 | 9.4762 | 10.0677 | -0.59151 | 60.4061 | 10.4 | 9.9237 | 0.47629 |  | 2026-01-03 17:20 | 55.655 | 56.485 | 1626 | 9.4142 | 10.0677 | -0.65351 | 60.4061 | 10.4 | 9.9237 | 0.47629 |  | 2026-01-03 17:20 | 55.378 | 56.937 | 1635.6 | 9.4895 | 10.0677 | -0.57818 | 60.4061 | 10.2 | 9.9237 | 0.27629 |  | 2026-01-03 17:20 | 52.296 | 53.125 | 1547.2 | 8.8542 | 9.5781 | -0.72398 | 57.4689 | 9.7 | 9.4412 | 0.25882 |  | 2026-01-03 17:20 | 99.0275 | 104.2143 | -5.1868 | 625.2859 | 107.9 | 102.724 | 5.176
2026-01-03 17:10 | 272 | 47.35 | 92.077 | 93.235 | 2190.7 | 15.5392 | 16.2857 | -0.74652 | 97.7141 | 16.7 | 16.0528 | 0.6472 |  | 2026-01-03 17:10 | 93.77 | 94.967 | 2222.3 | 15.8278 | 16.2857 | -0.45785 | 97.7141 | 17.3 | 16.0528 | 1.2472 |  | 2026-01-03 17:10 | 92.561 | 93.876 | 2182.9 | 15.646 | 16.2857 | -0.63969 | 97.7141 | 17 | 16.0528 | 0.9472 |  | 2026-01-03 17:10 | 93.523 | 94.697 | 2214.4 | 15.7828 | 16.2857 | -0.50285 | 97.7141 | 17.2 | 16.0528 | 1.1472 |  | 2026-01-03 17:10 | 69.925 | 70.896 | 1651.9 | 11.816 | 12.0635 | -0.24747 | 72.3808 | 12.7 | 11.891 | 0.80904 |  | 2026-01-03 17:10 | 67.898 | 68.813 | 1627.7 | 11.4688 | 12.0635 | -0.59464 | 72.3808 | 12.3 | 11.891 | 0.40904 |  | 2026-01-03 17:10 | 67.71 | 68.637 | 1615.6 | 11.4395 | 12.0635 | -0.62397 | 72.3808 | 12.3 | 11.891 | 0.40904 |  | 2026-01-03 17:10 | 67.101 | 69.055 | 1625.4 | 11.5092 | 12.0635 | -0.55431 | 72.3808 | 12.3 | 11.891 | 0.40904 |  | 2026-01-03 17:10 | 63.379 | 64.266 | 1537.5 | 10.711 | 11.4769 | -0.7659 | 68.8614 | 11.5 | 11.3128 | 0.18722 |  | 2026-01-03 17:10 | 119.7403 | 124.8735 | -5.1332 | 749.2412 | 129.3 | 123.0878 | 6.2122
2026-01-03 17:00 | 319 | 47.35 | 109.107 | 110.498 | 2174 | 18.4163 | 19.0998 | -0.68343 | 114.5986 | 19 | 18.8266 | 0.17337 |  | 2026-01-03 17:00 | 110.886 | 112.301 | 2205 | 18.7168 | 19.0998 | -0.38293 | 114.5986 | 19.9 | 18.8266 | 1.0734 |  | 2026-01-03 17:00 | 109.42 | 111.344 | 2165.9 | 18.5573 | 19.0998 | -0.54243 | 114.5986 | 19.7 | 18.8266 | 0.87337 |  | 2026-01-03 17:00 | 110.801 | 112.226 | 2197.2 | 18.7043 | 19.0998 | -0.39543 | 114.5986 | 19.7 | 18.8266 | 0.87337 |  | 2026-01-03 17:00 | 82.748 | 83.846 | 1639.2 | 13.9743 | 14.148 | -0.17364 | 84.8878 | 14.8 | 13.9457 | 0.85435 |  | 2026-01-03 17:00 | 80.409 | 81.468 | 1615.4 | 13.578 | 14.148 | -0.56997 | 84.8878 | 14.5 | 13.9457 | 0.55435 |  | 2026-01-03 17:00 | 80.095 | 81.15 | 1603.3 | 13.525 | 14.148 | -0.62297 | 84.8878 | 14.4 | 13.9457 | 0.45435 |  | 2026-01-03 17:00 | 79.742 | 81.983 | 1613.1 | 13.6638 | 14.148 | -0.48414 | 84.8878 | 14.3 | 13.9457 | 0.35435 |  | 2026-01-03 17:00 | 75.204 | 76.218 | 1526 | 12.703 | 13.46 | -0.75704 | 80.7602 | 13.5 | 13.2676 | 0.23244 |  | 2026-01-03 17:00 | 141.839 | 146.451 | -4.612 | 878.7057 | 149.8 | 144.3567 | 5.4433
2026-01-03 16:50 | 365 | 47.64 | 124.967 | 126.562 | 2155 | 21.0937 | 21.8299 | -0.73623 | 130.9794 | 45.4 | 21.5177 | 23.8823 |  | 2026-01-03 16:50 | 129.518 | 129.086 | 2185.1 | 21.5143 | 21.8299 | -0.31556 | 130.9794 | 22.2 | 21.5177 | 0.68228 |  | 2026-01-03 16:50 | 125.734 | 128.089 | 2146.2 | 21.3482 | 21.8299 | -0.48173 | 130.9794 | 22.1 | 21.5177 | 0.58228 |  | 2026-01-03 16:50 | 127.269 | 128.919 | 2177.5 | 21.4865 | 21.8299 | -0.34339 | 130.9794 | 22.2 | 21.5177 | 0.68228 |  | 2026-01-03 16:50 | 95.151 | 96.346 | 1624.4 | 16.0577 | 16.1703 | -0.11262 | 97.0217 | 16.7 | 15.9391 | 0.76094 |  | 2026-01-03 16:50 | 92.758 | 93.913 | 1600.9 | 15.6522 | 16.1703 | -0.51812 | 97.0217 | 16.2 | 15.9391 | 0.26094 |  | 2026-01-03 16:50 | 92.41 | 93.551 | 1588.9 | 15.5918 | 16.1703 | -0.57846 | 97.0217 | 16.2 | 15.9391 | 0.26094 |  | 2026-01-03 16:50 | 92.118 | 94.509 | 1598.8 | 15.7515 | 16.1703 | -0.41879 | 97.0217 | 16.2 | 15.9391 | 0.26094 |  | 2026-01-03 16:50 | 86.944 | 88.089 | 1512.5 | 14.6815 | 15.384 | -0.70253 | 92.3042 | 15.3 | 15.164 | 0.13596 |  | 2026-01-03 16:50 | 163.1773 | 167.3848 | -4.2074 | 1004.3085 | 192.5 | 164.9912 | 27.5088
2026-01-03 16:40 | 389 | 48.22 | 134.137 | 135.849 | 2132.6 | 22.6415 | 23.214 | -0.57249 | 139.2839 | 0 | 22.882 | -22.882 |  | 2026-01-03 16:40 | 136.158 | 137.965 | 2162.9 | 22.9942 | 23.214 | -0.21982 | 139.2839 | 23.4 | 22.882 | 0.51797 |  | 2026-01-03 16:40 | 134.541 | 137.089 | 2124.1 | 22.8482 | 23.214 | -0.36582 | 139.2839 | 23.7 | 22.882 | 0.81797 |  | 2026-01-03 16:40 | 135.436 | 137.22 | 2155.3 | 22.87 | 23.214 | -0.34399 | 139.2839 | 24 | 22.882 | 1.118 |  | 2026-01-03 16:40 | 101.877 | 103.198 | 1607.7 | 17.1997 | 17.1955 | 0.0041193 | 103.1733 | 17.9 | 16.9497 | 0.95035 |  | 2026-01-03 16:40 | 98.853 | 100.114 | 1584.7 | 16.6857 | 17.1955 | -0.50988 | 103.1733 | 17.5 | 16.9497 | 0.55035 |  | 2026-01-03 16:40 | 99.085 | 100.306 | 1572.7 | 16.7177 | 17.1955 | -0.47788 | 103.1733 | 17.3 | 16.9497 | 0.35035 |  | 2026-01-03 16:40 | 99.609 | 102.16 | 1582.6 | 17.0267 | 17.1955 | -0.16888 | 103.1733 | 17.3 | 16.9497 | 0.35035 |  | 2026-01-03 16:40 | 93.469 | 94.681 | 1497.2 | 15.7802 | 16.3594 | -0.57927 | 98.1566 | 16.4 | 16.1255 | 0.27451 |  | 2026-01-03 16:40 | 174.7637 | 177.9976 | -3.2339 | 1067.9855 | 157.5 | 175.4522 | -17.9522
2026-01-03 16:30 | 449 | 48.22 | 154.492 | 156.527 | 2109.6 | 26.0878 | 26.7946 | -0.70672 | 160.7673 | 27.4 | 26.4114 | 0.98861 |  | 2026-01-03 16:30 | 156.794 | 158.982 | 2139.5 | 26.497 | 26.7946 | -0.29755 | 160.7673 | 27.5 | 26.4114 | 1.0886 |  | 2026-01-03 16:30 | 154.51 | 157.598 | 2100.4 | 26.2663 | 26.7946 | -0.52822 | 160.7673 | 27.1 | 26.4114 | 0.68861 |  | 2026-01-03 16:30 | 156.813 | 158.911 | 2131.3 | 26.4852 | 26.7946 | -0.30939 | 160.7673 | 27.4 | 26.4114 | 0.98861 |  | 2026-01-03 16:30 | 116.159 | 117.677 | 1589.8 | 19.6128 | 19.8478 | -0.23498 | 119.0869 | 20.6 | 19.564 | 1.036 |  | 2026-01-03 16:30 | 114.17 | 115.65 | 1567.2 | 19.275 | 19.8478 | -0.57282 | 119.0869 | 20 | 19.564 | 0.43601 |  | 2026-01-03 16:30 | 112.018 | 113.459 | 1555.4 | 18.9098 | 19.8478 | -0.93798 | 119.0869 | 19.9 | 19.564 | 0.33601 |  | 2026-01-03 16:30 | 112.207 | 114.986 | 1565.3 | 19.1643 | 19.8478 | -0.68348 | 119.0869 | 20.2 | 19.564 | 0.63601 |  | 2026-01-03 16:30 | 107.114 | 108.514 | 1480.8 | 18.0857 | 18.8827 | -0.79707 | 113.2964 | 18.8 | 18.6127 | 0.18728 |  | 2026-01-03 16:30 | 200.384 | 205.4522 | -5.0682 | 1232.7133 | 208.9 | 202.5143 | 6.3857
2026-01-03 16:20 | 497 | 48.5 | 171.24 | 173.583 | 2082.2 | 28.9305 | 29.6274 | -0.69687 | 177.7642 | 29.4 | 29.2037 | 0.1963 |  | 2026-01-03 16:20 | 174.44 | 176.315 | 2112 | 29.3858 | 29.6274 | -0.24153 | 177.7642 | 30.3 | 29.2037 | 1.0963 |  | 2026-01-03 16:20 | 171.298 | 175.163 | 2073.3 | 29.1938 | 29.6274 | -0.43353 | 177.7642 | 29.9 | 29.2037 | 0.6963 |  | 2026-01-03 16:20 | 173.233 | 175.639 | 2103.9 | 29.2732 | 29.6274 | -0.3542 | 177.7642 | 30.3 | 29.2037 | 1.0963 |  | 2026-01-03 16:20 | 129.552 | 131.285 | 1569.2 | 21.8808 | 21.9462 | -0.065364 | 131.6772 | 22.6 | 21.6324 | 0.96763 |  | 2026-01-03 16:20 | 126.474 | 128.153 | 1547.2 | 21.3588 | 21.9462 | -0.58736 | 131.6772 | 22.1 | 21.6324 | 0.46763 |  | 2026-01-03 16:20 | 125.295 | 126.958 | 1535.5 | 21.1597 | 21.9462 | -0.78653 | 131.6772 | 21.9 | 21.6324 | 0.26763 |  | 2026-01-03 16:20 | 125.633 | 129.032 | 1545.1 | 21.5053 | 21.9462 | -0.44086 | 131.6772 | 21.9 | 21.6324 | 0.26763 |  | 2026-01-03 16:20 | 118.535 | 120.108 | 1462 | 20.018 | 20.8791 | -0.86109 | 125.2745 | 20.7 | 20.5805 | 0.11948 |  | 2026-01-03 16:20 | 222.706 | 227.1733 | -4.4673 | 1363.0401 | 229.1 | 223.9248 | 5.1752
2026-01-03 16:10 | 537 | 48.5 | 184.186 | 186.744 | 2052.8 | 31.124 | 32.0119 | -0.88786 | 192.0712 | 32.5 | 31.5541 | 0.94591 |  | 2026-01-03 16:10 | 188.084 | 190.105 | 2081.7 | 31.6842 | 32.0119 | -0.3277 | 192.0712 | 33 | 31.5541 | 1.4459 |  | 2026-01-03 16:10 | 184.917 | 189.016 | 2043.4 | 31.5027 | 32.0119 | -0.5092 | 192.0712 | 31.5 | 31.5541 | -0.054094 |  | 2026-01-03 16:10 | 186.914 | 189.587 | 2073.6 | 31.5978 | 32.0119 | -0.41403 | 192.0712 | 32.3 | 31.5541 | 0.74591 |  | 2026-01-03 16:10 | 139.968 | 141.869 | 1546.6 | 23.6448 | 23.7125 | -0.067658 | 142.2749 | 23.9 | 23.3734 | 0.5266 |  | 2026-01-03 16:10 | 136.77 | 138.614 | 1525.1 | 23.1023 | 23.7125 | -0.61016 | 142.2749 | 23.4 | 23.3734 | 0.026597 |  | 2026-01-03 16:10 | 135.647 | 137.462 | 1513.6 | 22.9103 | 23.7125 | -0.80216 | 142.2749 | 23.1 | 23.3734 | -0.2734 |  | 2026-01-03 16:10 | 136.08 | 139.708 | 1523.2 | 23.2847 | 23.7125 | -0.42782 | 142.2749 | 23.2 | 23.3734 | -0.1734 |  | 2026-01-03 16:10 | 128.437 | 130.181 | 1441.3 | 21.6968 | 22.5595 | -0.86267 | 135.357 | 22.2 | 22.2369 | -0.036898 |  | 2026-01-03 16:10 | 240.5477 | 245.4569 | -4.9092 | 1472.7415 | 245.1 | 241.9469 | 3.1531
2026-01-03 16:00 | 577 | 48.5 | 200.308 | 203.132 | 2020.3 | 33.8553 | 34.3964 | -0.54103 | 206.3782 | 35 | 33.9045 | 1.0955 |  | 2026-01-03 16:00 | 201.699 | 204.625 | 2048.7 | 34.1042 | 34.3964 | -0.29219 | 206.3782 | 34.2 | 33.9045 | 0.29551 |  | 2026-01-03 16:00 | 198.969 | 203.456 | 2011.9 | 33.9093 | 34.3964 | -0.48703 | 206.3782 | 34.3 | 33.9045 | 0.39551 |  | 2026-01-03 16:00 | 200.836 | 203.75 | 2041.3 | 33.9583 | 34.3964 | -0.43803 | 206.3782 | 34.1 | 33.9045 | 0.19551 |  | 2026-01-03 16:00 | 150.593 | 152.654 | 1522.7 | 25.4423 | 25.4788 | -0.036451 | 152.8727 | 25.8 | 25.1144 | 0.68556 |  | 2026-01-03 16:00 | 146.972 | 149.112 | 1501.7 | 24.852 | 25.4788 | -0.62678 | 152.8727 | 25.6 | 25.1144 | 0.48556 |  | 2026-01-03 16:00 | 145.9 | 148.352 | 1490.5 | 24.7253 | 25.4788 | -0.75345 | 152.8727 | 25.4 | 25.1144 | 0.28556 |  | 2026-01-03 16:00 | 146.391 | 150.658 | 1500 | 25.1097 | 25.4788 | -0.36912 | 152.8727 | 25.2 | 25.1144 | 0.085562 |  | 2026-01-03 16:00 | 138.248 | 140.126 | 1419.1 | 23.3543 | 24.2399 | -0.88557 | 145.4394 | 23.8 | 23.8933 | -0.093277 |  | 2026-01-03 16:00 | 259.3108 | 263.7405 | -4.4297 | 1582.4429 | 263.4 | 259.969 | 3.431
2026-01-03 15:50 | 615 | 48.22 | 211.277 | 214.32 | 1985.3 | 35.72 | 36.7008 | -0.98078 | 220.2047 | 34.6 | 36.176 | -1.576 |  | 2026-01-03 15:50 | 214.335 | 217.444 | 2014.5 | 36.2407 | 36.7008 | -0.46011 | 220.2047 | 36.4 | 36.176 | 0.22404 |  | 2026-01-03 15:50 | 211.201 | 216.219 | 1977.6 | 36.0365 | 36.7008 | -0.66428 | 220.2047 | 36.4 | 36.176 | 0.22404 |  | 2026-01-03 15:50 | 213.527 | 216.669 | 2007.2 | 36.1115 | 36.7008 | -0.58928 | 220.2047 | 36.8 | 36.176 | 0.62404 |  | 2026-01-03 15:50 | 159.773 | 161.992 | 1496.9 | 26.9987 | 27.1858 | -0.1871 | 163.1146 | 27.6 | 26.797 | 0.80299 |  | 2026-01-03 15:50 | 156.286 | 158.441 | 1476.1 | 26.4068 | 27.1858 | -0.77893 | 163.1146 | 26.5 | 26.797 | -0.29701 |  | 2026-01-03 15:50 | 154.769 | 156.919 | 1465.1 | 26.1532 | 27.1858 | -1.0326 | 163.1146 | 26.3 | 26.797 | -0.49701 |  | 2026-01-03 15:50 | 155.092 | 159.084 | 1474.8 | 26.514 | 27.1858 | -0.67176 | 163.1146 | 26.4 | 26.797 | -0.39701 |  | 2026-01-03 15:50 | 146.807 | 148.831 | 1395.3 | 24.8052 | 25.8639 | -1.0587 | 155.1833 | 25 | 25.494 | -0.49403 |  | 2026-01-03 15:50 | 274.9865 | 281.4101 | -6.4236 | 1688.4603 | 276 | 277.3859 | -1.3859
2026-01-03 15:40 | 651 | 48.5 | 223.303 | 226.543 | 1950.7 | 37.7572 | 38.8077 | -1.0505 | 232.8461 | 38 | 38.2527 | -0.25273 |  | 2026-01-03 15:40 | 225.736 | 229.127 | 1978.1 | 38.1878 | 38.8077 | -0.61984 | 232.8461 | 39.3 | 38.2527 | 1.0473 |  | 2026-01-03 15:40 | 221.957 | 226.965 | 1941.2 | 37.8275 | 38.8077 | -0.98018 | 232.8461 | 37.9 | 38.2527 | -0.35273 |  | 2026-01-03 15:40 | 224.869 | 228.178 | 1970.4 | 38.0297 | 38.8077 | -0.77801 | 232.8461 | 38.5 | 38.2527 | 0.24727 |  | 2026-01-03 15:40 | 167.405 | 169.782 | 1469.3 | 28.297 | 28.7464 | -0.44943 | 172.4786 | 28.7 | 28.3354 | 0.36465 |  | 2026-01-03 15:40 | 164.078 | 166.658 | 1449.6 | 27.7763 | 28.7464 | -0.97009 | 172.4786 | 28.2 | 28.3354 | -0.13535 |  | 2026-01-03 15:40 | 161.86 | 164.156 | 1438.8 | 27.3593 | 28.7464 | -1.3871 | 172.4786 | 27.9 | 28.3354 | -0.43535 |  | 2026-01-03 15:40 | 162.417 | 166.835 | 1448.4 | 27.8058 | 28.7464 | -0.94059 | 172.4786 | 28 | 28.3354 | -0.33535 |  | 2026-01-03 15:40 | 154.232 | 156.39 | 1370.3 | 26.065 | 27.3487 | -1.2837 | 164.092 | 26.4 | 26.9576 | -0.55758 |  | 2026-01-03 15:40 | 289.1057 | 297.5651 | -8.4594 | 1785.3905 | 292.9 | 293.3099 | -0.40991
2026-01-03 15:30 | 684 | 48.5 | 232.99 | 236.534 | 1912.7 | 39.4223 | 40.7749 | -1.3526 | 244.6493 | 40.6 | 40.1918 | 0.40819 |  | 2026-01-03 15:30 | 236.624 | 240.277 | 1938.8 | 40.0462 | 40.7749 | -0.72872 | 244.6493 | 40.1 | 40.1918 | -0.091806 |  | 2026-01-03 15:30 | 232.833 | 238.585 | 1903.3 | 39.7642 | 40.7749 | -1.0107 | 244.6493 | 39.4 | 40.1918 | -0.79181 |  | 2026-01-03 15:30 | 235.222 | 238.828 | 1931.9 | 39.8047 | 40.7749 | -0.97022 | 244.6493 | 39.9 | 40.1918 | -0.29181 |  | 2026-01-03 15:30 | 176.069 | 178.605 | 1440.6 | 29.7675 | 30.2036 | -0.43612 | 181.2217 | 29.8 | 29.7717 | 0.028292 |  | 2026-01-03 15:30 | 172.34 | 174.913 | 1421.4 | 29.1522 | 30.2036 | -1.0515 | 181.2217 | 29.2 | 29.7717 | -0.57171 |  | 2026-01-03 15:30 | 171.119 | 173.531 | 1410.9 | 28.9218 | 30.2036 | -1.2818 | 181.2217 | 29.5 | 29.7717 | -0.27171 |  | 2026-01-03 15:30 | 171.675 | 176.491 | 1420.4 | 29.4152 | 30.2036 | -0.78845 | 181.2217 | 29.6 | 29.7717 | -0.17171 |  | 2026-01-03 15:30 | 162.268 | 164.555 | 1343.9 | 27.4258 | 28.735 | -1.3092 | 172.41 | 28.1 | 28.3241 | -0.22409 |  | 2026-01-03 15:30 | 303.7198 | 312.649 | -8.9292 | 1875.8942 | 306.2 | 308.1782 | -1.9782
2026-01-03 15:20 | 729 | 48.5 | 246.573 | 250.379 | 1872.1 | 41.7298 | 43.4574 | -1.7276 | 260.7447 | 41.7 | 42.836 | -1.136 |  | 2026-01-03 15:20 | 250.515 | 254.459 | 1898.7 | 42.4098 | 43.4574 | -1.0476 | 260.7447 | 42.6 | 42.836 | -0.236 |  | 2026-01-03 15:20 | 245.542 | 251.704 | 1863.9 | 41.9507 | 43.4574 | -1.5068 | 260.7447 | 41.8 | 42.836 | -1.036 |  | 2026-01-03 15:20 | 248.775 | 252.692 | 1892 | 42.1153 | 43.4574 | -1.3421 | 260.7447 | 42.4 | 42.836 | -0.436 |  | 2026-01-03 15:20 | 185.816 | 188.539 | 1410.8 | 31.4232 | 32.1907 | -0.76753 | 193.1442 | 31.7 | 31.7304 | -0.030373 |  | 2026-01-03 15:20 | 182.344 | 185.417 | 1392.2 | 30.9028 | 32.1907 | -1.2879 | 193.1442 | 31.1 | 31.7304 | -0.63037 |  | 2026-01-03 15:20 | 180.858 | 183.812 | 1381.4 | 30.6353 | 32.1907 | -1.5554 | 193.1442 | 30.4 | 31.7304 | -1.3304 |  | 2026-01-03 15:20 | 181.455 | 186.281 | 1390.8 | 31.0468 | 32.1907 | -1.1439 | 193.1442 | 30.6 | 31.7304 | -1.1304 |  | 2026-01-03 15:20 | 172.163 | 174.625 | 1315.8 | 29.1042 | 30.6255 | -1.5213 | 183.7528 | 29.4 | 30.1875 | -0.78752 |  | 2026-01-03 15:20 | 321.318 | 333.218 | -11.9 | 1999.3083 | 321.7 | 328.453 | -6.753
2026-01-03 15:10 | 750 | 48.79 | 251.302 | 256.154 | 1830.4 | 42.6923 | 44.6599 | -1.9675 | 267.9592 | 42.8 | 44.0212 | -1.2212 |  | 2026-01-03 15:10 | 255.825 | 261.304 | 1856.1 | 43.5507 | 44.6599 | -1.1092 | 267.9592 | 44.6 | 44.0212 | 0.57878 |  | 2026-01-03 15:10 | 251.61 | 258.246 | 1822.1 | 43.041 | 44.6599 | -1.6189 | 267.9592 | 42.6 | 44.0212 | -1.4212 |  | 2026-01-03 15:10 | 255.832 | 259.913 | 1849.6 | 43.3188 | 44.6599 | -1.341 | 267.9592 | 43.2 | 44.0212 | -0.82122 |  | 2026-01-03 15:10 | 190.29 | 193.09 | 1379.1 | 32.1817 | 33.0814 | -0.89971 | 198.4883 | 32.3 | 32.6083 | -0.30831 |  | 2026-01-03 15:10 | 187.377 | 190.194 | 1361.1 | 31.699 | 33.0814 | -1.3824 | 198.4883 | 31.7 | 32.6083 | -0.90831 |  | 2026-01-03 15:10 | 185.051 | 188.08 | 1351 | 31.3467 | 33.0814 | -1.7347 | 198.4883 | 31.9 | 32.6083 | -0.70831 |  | 2026-01-03 15:10 | 185.442 | 190.815 | 1360.2 | 31.8025 | 33.0814 | -1.2789 | 198.4883 | 32 | 32.6083 | -0.60831 |  | 2026-01-03 15:10 | 176.34 | 178.88 | 1286.4 | 29.8133 | 31.4728 | -1.6595 | 188.837 | 29.8 | 31.0228 | -1.2228 |  | 2026-01-03 15:10 | 329.446 | 342.4378 | -12.9918 | 2054.6267 | 330.9 | 337.5409 | -6.6409
2026-01-03 15:00 | 776 | 49.08 | 262.987 | 267.1 | 1787.6 | 44.5167 | 46.1569 | -1.6402 | 276.9414 | 44.5 | 45.4969 | -0.99686 | 0.9846 | 2026-01-03 15:00 | 0 | 0 | 1811.5 | 0 | 46.1569 | -46.1569 | 276.9414 | 44.5 | 45.4969 | -0.99686 |  | 2026-01-03 15:00 | 262.458 | 269.38 | 1779.5 | 44.8967 | 46.1569 | -1.2602 | 276.9414 | 44.3 | 45.4969 | -1.1969 | 0.9743 | 2026-01-03 15:00 | 264.818 | 269.381 | 1806.4 | 44.8968 | 46.1569 | -1.2601 | 276.9414 | 44.8 | 45.4969 | -0.69686 | 0.98306 | 2026-01-03 15:00 | 199.365 | 202.278 | 1346.8 | 33.713 | 34.1903 | -0.4773 | 205.1418 | 33.7 | 33.7014 | -0.0013798 | 0.9856 | 2026-01-03 15:00 | 195.343 | 198.609 | 1329.4 | 33.1015 | 34.1903 | -1.0888 | 205.1418 | 33 | 33.7014 | -0.70138 | 0.98356 | 2026-01-03 15:00 | 194.501 | 197.684 | 1319.1 | 32.9473 | 34.1903 | -1.243 | 205.1418 | 32.4 | 33.7014 | -1.3014 | 0.9839 | 2026-01-03 15:00 | 195.271 | 200.999 | 1328.2 | 33.4998 | 34.1903 | -0.69047 | 205.1418 | 32.6 | 33.7014 | -1.1014 | 0.9715 | 2026-01-03 15:00 | 183.766 | 186.47 | 1256.6 | 31.0783 | 32.5278 | -1.4495 | 195.167 | 31 | 32.0627 | -1.0627 | 0.9855 | 2026-01-03 15:00 | 298.6502 | 353.9167 | -55.2665 | 2123.5 | 340.8 | 348.8557 | -8.0557
2026-01-03 14:50 | 788 | 48.79 | 269.301 | 273.569 | 1743.1 | 45.5948 | 46.9226 | -1.3278 | 281.5358 | 45.9 | 46.2516 | -0.35163 | 0.9844 | 2026-01-03 14:50 | 271.086 | 275.466 | 1767 | 45.911 | 46.9226 | -1.0116 | 281.5358 | 45.5 | 46.2516 | -0.75163 | 0.9841 | 2026-01-03 14:50 | 270.327 | 277.262 | 1735.2 | 46.2103 | 46.9226 | -0.71229 | 281.5358 | 45 | 46.2516 | -1.2516 | 0.97499 | 2026-01-03 14:50 | 271.083 | 275.491 | 1761.6 | 45.9152 | 46.9226 | -1.0075 | 281.5358 | 45.7 | 46.2516 | -0.55163 | 0.984 | 2026-01-03 14:50 | 204.963 | 208.021 | 1313.1 | 34.6702 | 34.7575 | -0.087334 | 208.545 | 34.5 | 34.2605 | 0.23953 | 0.9853 | 2026-01-03 14:50 | 200.215 | 203.599 | 1296.4 | 33.9332 | 34.7575 | -0.82433 | 208.545 | 33.5 | 34.2605 | -0.76047 | 0.98338 | 2026-01-03 14:50 | 199.159 | 202.631 | 1286.7 | 33.7718 | 34.7575 | -0.98567 | 208.545 | 33.2 | 34.2605 | -1.0605 | 0.98287 | 2026-01-03 14:50 | 200.429 | 206.09 | 1295.6 | 34.3483 | 34.7575 | -0.40917 | 208.545 | 33.6 | 34.2605 | -0.66047 | 0.97253 | 2026-01-03 14:50 | 189.134 | 191.936 | 1225.6 | 31.9893 | 33.0675 | -1.0781 | 198.4047 | 32 | 32.5946 | -0.59459 | 0.9854 | 2026-01-03 14:50 | 352.3442 | 359.788 | -7.4438 | 2158.7278 | 348.9 | 354.643 | -5.743
2026-01-03 14:40 | 824 | 48.79 | 273.511 | 277.958 | 1697.2 | 46.3263 | 49.0663 | -2.74 | 294.3978 | 47.4 | 48.3647 | -0.96465 | 0.984 | 2026-01-03 14:40 | 282.686 | 281.649 | 1721.5 | 46.9415 | 49.0663 | -2.1248 | 294.3978 | 50.7 | 48.3647 | 2.3353 | 1.0037 | 2026-01-03 14:40 | 273.372 | 280.934 | 1690.2 | 46.8223 | 49.0663 | -2.244 | 294.3978 | 47.9 | 48.3647 | -0.46465 | 0.97308 | 2026-01-03 14:40 | 278.167 | 282.776 | 1715.9 | 47.1293 | 49.0663 | -1.937 | 294.3978 | 48.5 | 48.3647 | 0.13535 | 0.9837 | 2026-01-03 14:40 | 206.737 | 209.864 | 1278.6 | 34.9773 | 36.3454 | -1.3681 | 218.0724 | 35.8 | 35.8257 | -0.025667 | 0.9851 | 2026-01-03 14:40 | 204.003 | 207.426 | 1262.9 | 34.571 | 36.3454 | -1.7744 | 218.0724 | 35.4 | 35.8257 | -0.42567 | 0.9835 | 2026-01-03 14:40 | 202.96 | 206.58 | 1253.5 | 34.43 | 36.3454 | -1.9154 | 218.0724 | 35.1 | 35.8257 | -0.72567 | 0.98248 | 2026-01-03 14:40 | 203.571 | 209.547 | 1262 | 34.9245 | 36.3454 | -1.4209 | 218.0724 | 34.9 | 35.8257 | -0.92567 | 0.97148 | 2026-01-03 14:40 | 191.565 | 194.443 | 1193.6 | 32.4072 | 34.5782 | -2.171 | 207.4689 | 32.5 | 34.0837 | -1.5837 | 0.9852 | 2026-01-03 14:40 | 358.5295 | 376.225 | -17.6955 | 2257.3498 | 368.2 | 370.845 | -2.645
2026-01-03 14:30 | 896 | 48.79 | 297.497 | 302.457 | 1649.8 | 50.4095 | 53.3536 | -2.9441 | 320.1219 | 48.9 | 52.5907 | -3.6907 | 0.9836 | 2026-01-03 14:30 | 302.604 | 307.707 | 1670.8 | 51.2845 | 53.3536 | -2.0691 | 320.1219 | 99.3 | 52.5907 | 46.7093 | 0.98342 | 2026-01-03 14:30 | 296.318 | 304.493 | 1642.3 | 50.7488 | 53.3536 | -2.6048 | 320.1219 | 50.1 | 52.5907 | -2.4907 | 0.97315 | 2026-01-03 14:30 | 302.239 | 307.33 | 1667.4 | 51.2217 | 53.3536 | -2.132 | 320.1219 | 50.9 | 52.5907 | -1.6907 | 0.98343 | 2026-01-03 14:30 | 223.882 | 227.314 | 1242.8 | 37.8857 | 39.5212 | -1.6356 | 237.1273 | 38 | 38.9561 | -0.95607 | 0.9849 | 2026-01-03 14:30 | 221.343 | 225.427 | 1227.5 | 37.5712 | 39.5212 | -1.9501 | 237.1273 | 37.3 | 38.9561 | -1.6561 | 0.98188 | 2026-01-03 14:30 | 216.954 | 221.029 | 1218.4 | 36.8382 | 39.5212 | -2.6831 | 237.1273 | 37.1 | 38.9561 | -1.8561 | 0.98156 | 2026-01-03 14:30 | 218.192 | 224.741 | 1227.1 | 37.4568 | 39.5212 | -2.0644 | 237.1273 | 37.2 | 38.9561 | -1.7561 | 0.97086 | 2026-01-03 14:30 | 207.892 | 211.058 | 1161.1 | 35.1763 | 37.5995 | -2.4232 | 225.5973 | 35.2 | 37.0619 | -1.8619 | 0.985 | 2026-01-03 14:30 | 388.5927 | 409.099 | -20.5063 | 2454.594 | 434 | 403.2489 | 30.7511
2026-01-03 14:20 | 896 | 48.79 | 300.145 | 305.544 | 1600.9 | 50.924 | 53.3536 | -2.4296 | 320.1219 | 51.8 | 52.5907 | -0.79069 | 0.98233 |  |  |  |  | 0 | 53.3536 | -53.3536 | 320.1219 | 0 | 52.5907 | -52.5907 |  | 2026-01-03 14:20 | 298.914 | 307.225 | 1592.2 | 51.2042 | 53.3536 | -2.1495 | 320.1219 | 49.1 | 52.5907 | -3.4907 | 0.97295 | 2026-01-03 14:20 | 303.142 | 308.259 | 1616.5 | 51.3765 | 53.3536 | -1.9771 | 320.1219 | 49.6 | 52.5907 | -2.9907 | 0.9834 | 2026-01-03 14:20 | 226.92 | 230.422 | 1204.8 | 38.4037 | 39.5212 | -1.1176 | 237.1273 | 37.2 | 38.9561 | -1.7561 | 0.9848 | 2026-01-03 14:20 | 222.806 | 227.047 | 1190.2 | 37.8412 | 39.5212 | -1.6801 | 237.1273 | 37 | 38.9561 | -1.9561 | 0.98132 | 2026-01-03 14:20 | 221.421 | 225.515 | 1181.3 | 37.5858 | 39.5212 | -1.9354 | 237.1273 | 36.8 | 38.9561 | -2.1561 | 0.98185 | 2026-01-03 14:20 | 222.401 | 229.205 | 1189.9 | 38.2008 | 39.5212 | -1.3204 | 237.1273 | 37 | 38.9561 | -1.9561 | 0.97031 | 2026-01-03 14:20 | 210.116 | 213.316 | 1125.9 | 35.5527 | 37.5995 | -2.0469 | 225.5973 | 34.9 | 37.0619 | -2.1619 | 0.985 | 2026-01-03 14:20 | 341.0888 | 409.099 | -68.0102 | 2454.594 | 333.4 | 403.2489 | -69.8489
2026-01-03 14:10 | 890 | 48.5 | 298.436 | 303.35 | 1549.1 | 50.5583 | 53.055 | -2.4967 | 318.3303 | 48.8 | 52.2964 | -3.4964 | 0.9838 | 2026-01-03 14:10 | 302.946 | 307.997 | 1571.5 | 51.3328 | 53.055 | -1.7222 | 318.3303 | 51.4 | 52.2964 | -0.89636 | 0.9836 | 2026-01-03 14:10 | 298.23 | 306.254 | 1543.1 | 51.0423 | 53.055 | -2.0127 | 318.3303 | 49.8 | 52.2964 | -2.4964 | 0.9738 | 2026-01-03 14:10 | 301.53 | 306.558 | 1566.9 | 51.093 | 53.055 | -1.962 | 318.3303 | 50.6 | 52.2964 | -1.6964 | 0.9836 | 2026-01-03 14:10 | 226.397 | 229.868 | 1167.6 | 38.3113 | 39.3 | -0.9887 | 235.8002 | 37.9 | 38.738 | -0.83804 | 0.9849 | 2026-01-03 14:10 | 221.264 | 225.18 | 1153.2 | 37.53 | 39.3 | -1.77 | 235.8002 | 36.7 | 38.738 | -2.038 | 0.98261 | 2026-01-03 14:10 | 220.566 | 224.828 | 1144.5 | 37.4713 | 39.3 | -1.8287 | 235.8002 | 36.4 | 38.738 | -2.338 | 0.98104 | 2026-01-03 14:10 | 221.027 | 227.489 | 1152.9 | 37.9148 | 39.3 | -1.3852 | 235.8002 | 36.7 | 38.738 | -2.038 | 0.97159 | 2026-01-03 14:10 | 208.617 | 211.751 | 1091 | 35.2918 | 37.3891 | -2.0973 | 224.3347 | 34.7 | 36.8544 | -2.1544 | 0.9852 | 2026-01-03 14:10 | 390.5458 | 406.8094 | -16.2636 | 2440.8565 | 383 | 400.992 | -17.992
2026-01-03 14:00 | 877 | 48.5 | 294.13 | 298.943 | 1500.3 | 49.8238 | 52.2801 | -2.4562 | 313.6805 | 100.9 | 51.5325 | 49.3675 | 0.9839 | 2026-01-03 14:00 | 298.915 | 303.868 | 1520.1 | 50.6447 | 52.2801 | -1.6354 | 313.6805 | 51.8 | 51.5325 | 0.26752 | 0.9837 | 2026-01-03 14:00 | 292.389 | 300.294 | 1493.3 | 50.049 | 52.2801 | -2.2311 | 313.6805 | 49.8 | 51.5325 | -1.7325 | 0.97368 | 2026-01-03 14:00 | 295.656 | 300.586 | 1516.3 | 50.0977 | 52.2801 | -2.1824 | 313.6805 | 50.7 | 51.5325 | -0.83248 | 0.9836 | 2026-01-03 14:00 | 221.845 | 225.2 | 1129.7 | 37.5333 | 38.726 | -1.1927 | 232.3559 | 37.7 | 38.1722 | -0.4722 | 0.9851 | 2026-01-03 14:00 | 217.338 | 221.248 | 1116.5 | 36.8747 | 38.726 | -1.8513 | 232.3559 | 37.3 | 38.1722 | -0.8722 | 0.98233 | 2026-01-03 14:00 | 215.844 | 219.876 | 1108.1 | 36.646 | 38.726 | -2.08 | 232.3559 | 36.9 | 38.1722 | -1.2722 | 0.98166 | 2026-01-03 14:00 | 216.562 | 222.803 | 1116.2 | 37.1338 | 38.726 | -1.5922 | 232.3559 | 37.2 | 38.1722 | -0.9722 | 0.97199 | 2026-01-03 14:00 | 204.8 | 207.898 | 1056.3 | 34.6497 | 36.843 | -2.1933 | 221.0579 | 35.3 | 36.3161 | -1.0161 | 0.9851 | 2026-01-03 14:00 | 383.4527 | 400.8673 | -17.4146 | 2405.2035 | 437.6 | 395.1349 | 42.4651
2026-01-03 13:50 | 935 | 48.5 |  |  |  | 0 | 55.7376 | -55.7376 | 334.4256 | 0 | 54.9406 | -54.9406 |  | 2026-01-03 13:50 | 316.131 | 321.598 | 1468.3 | 53.5997 | 55.7376 | -2.1379 | 334.4256 | 53.1 | 54.9406 | -1.8406 | 0.983 | 2026-01-03 13:50 | 309.926 | 318.563 | 1443.5 | 53.0938 | 55.7376 | -2.6438 | 334.4256 | 52.2 | 54.9406 | -2.7406 | 0.97289 | 2026-01-03 13:50 | 314.272 | 319.69 | 1465.6 | 53.2817 | 55.7376 | -2.4559 | 334.4256 | 52.9 | 54.9406 | -2.0406 | 0.98305 | 2026-01-03 13:50 | 235.388 | 239.094 | 1092 | 39.849 | 41.2871 | -1.4381 | 247.7227 | 39.7 | 40.6967 | -0.99671 | 0.9845 | 2026-01-03 13:50 | 231.388 | 235.749 | 1079.2 | 39.2915 | 41.2871 | -1.9956 | 247.7227 | 38.9 | 40.6967 | -1.7967 | 0.9815 | 2026-01-03 13:50 | 229.985 | 234.443 | 1071.2 | 39.0738 | 41.2871 | -2.2133 | 247.7227 | 38.7 | 40.6967 | -1.9967 | 0.98098 | 2026-01-03 13:50 | 231.551 | 238.562 | 1079 | 39.7603 | 41.2871 | -1.5268 | 247.7227 | 39 | 40.6967 | -1.6967 | 0.97061 | 2026-01-03 13:50 | 218.915 | 222.294 | 1021 | 37.049 | 39.2796 | -2.2306 | 235.6774 | 36.8 | 38.7179 | -1.9179 | 0.9848 | 2026-01-03 13:50 | 354.9988 | 427.3784 | -72.3796 | 2564.2706 | 351.3 | 421.2669 | -69.9669
2026-01-03 13:40 | 951 | 48.5 | 316.045 | 321.413 | 1399.4 | 53.5688 | 56.6914 | -3.1226 | 340.1484 | 53 | 55.8807 | -2.8807 | 0.9833 | 2026-01-03 13:40 | 320.72 | 326.267 | 1415.2 | 54.3778 | 56.6914 | -2.3136 | 340.1484 | 52.6 | 55.8807 | -3.2807 | 0.983 | 2026-01-03 13:40 | 314.217 | 322.979 | 1391.3 | 53.8298 | 56.6914 | -2.8616 | 340.1484 | 52.1 | 55.8807 | -3.7807 | 0.97287 | 2026-01-03 13:40 | 318.331 | 323.836 | 1412.7 | 53.9727 | 56.6914 | -2.7187 | 340.1484 | 52.7 | 55.8807 | -3.1807 | 0.983 | 2026-01-03 13:40 | 238.659 | 242.441 | 1052.3 | 40.4068 | 41.9936 | -1.5868 | 251.9618 | 40.2 | 41.3931 | -1.1931 | 0.9844 | 2026-01-03 13:40 | 234.431 | 238.874 | 1040.3 | 39.8123 | 41.9936 | -2.1813 | 251.9618 | 39.4 | 41.3931 | -1.9931 | 0.9814 | 2026-01-03 13:40 | 232.962 | 237.246 | 1032.5 | 39.541 | 41.9936 | -2.4526 | 251.9618 | 39.2 | 41.3931 | -2.1931 | 0.98194 | 2026-01-03 13:40 | 234.337 | 241.05 | 1040 | 40.175 | 41.9936 | -1.8186 | 251.9618 | 39.4 | 41.3931 | -1.9931 | 0.97215 | 2026-01-03 13:40 | 221.321 | 224.758 | 984.2 | 37.4597 | 39.9517 | -2.4921 | 239.7104 | 37.2 | 39.3804 | -2.1804 | 0.98471 | 2026-01-03 13:40 | 413.144 | 434.6919 | -21.5479 | 2608.1511 | 405.8 | 428.4758 | -22.6758
2026-01-03 13:30 | 949 | 48.79 | 314.609 | 319.985 | 1346.4 | 53.3308 | 56.5096 | -3.1788 | 339.0577 | 54 | 55.7015 | -1.7015 | 0.9832 | 2026-01-03 13:30 | 319.732 | 325.295 | 1362.6 | 54.2158 | 56.5096 | -2.2938 | 339.0577 | 53.2 | 55.7015 | -2.5015 | 0.9829 | 2026-01-03 13:30 | 313.286 | 321.892 | 1339.2 | 53.6487 | 56.5096 | -2.8609 | 339.0577 | 53 | 55.7015 | -2.7015 | 0.97326 | 2026-01-03 13:30 | 317.594 | 323.119 | 1360 | 53.8532 | 56.5096 | -2.6564 | 339.0577 | 53.8 | 55.7015 | -1.9015 | 0.9829 | 2026-01-03 13:30 | 237.814 | 241.558 | 1012.1 | 40.2597 | 41.859 | -1.5993 | 251.1538 | 39.7 | 41.2604 | -1.5604 | 0.9845 | 2026-01-03 13:30 | 233.53 | 237.839 | 1000.9 | 39.6398 | 41.859 | -2.2191 | 251.1538 | 39 | 41.2604 | -2.2604 | 0.98188 | 2026-01-03 13:30 | 232.66 | 236.982 | 993.3 | 39.497 | 41.859 | -2.362 | 251.1538 | 38.8 | 41.2604 | -2.4604 | 0.98176 | 2026-01-03 13:30 | 233.866 | 240.691 | 1000.6 | 40.1152 | 41.859 | -1.7438 | 251.1538 | 39.1 | 41.2604 | -2.1604 | 0.97164 | 2026-01-03 13:30 | 220.845 | 224.254 | 947 | 37.3757 | 39.8236 | -2.448 | 238.9417 | 36.8 | 39.2541 | -2.4541 | 0.9848 | 2026-01-03 13:30 | 411.9358 | 433.2979 | -21.3621 | 2599.7876 | 407.4 | 427.1018 | -19.7018
2026-01-03 13:20 | 962 | 48.5 | 319.088 | 324.573 | 1292.4 | 54.0955 | 57.3471 | -3.2516 | 344.0828 | 53.5 | 56.5271 | -3.0271 | 0.9831 | 2026-01-03 13:20 | 324.25 | 329.925 | 1309.4 | 54.9875 | 57.3471 | -2.3596 | 344.0828 | 55 | 56.5271 | -1.5271 | 0.9828 | 2026-01-03 13:20 | 317.64 | 326.375 | 1286.2 | 54.3958 | 57.3471 | -2.9513 | 344.0828 | 53.3 | 56.5271 | -3.2271 | 0.97324 | 2026-01-03 13:20 | 322.01 | 327.612 | 1306.2 | 54.602 | 57.3471 | -2.7451 | 344.0828 | 54 | 56.5271 | -2.5271 | 0.9829 | 2026-01-03 13:20 | 241.548 | 245.376 | 972.4 | 40.896 | 42.4794 | -1.5834 | 254.8762 | 40.5 | 41.8719 | -1.3719 | 0.9844 | 2026-01-03 13:20 | 236.976 | 241.34 | 961.9 | 40.2233 | 42.4794 | -2.256 | 254.8762 | 39.8 | 41.8719 | -2.0719 | 0.98192 | 2026-01-03 13:20 | 236.056 | 240.476 | 954.5 | 40.0793 | 42.4794 | -2.4 | 254.8762 | 39.7 | 41.8719 | -2.1719 | 0.98162 | 2026-01-03 13:20 | 237.103 | 244.283 | 961.5 | 40.7138 | 42.4794 | -1.7655 | 254.8762 | 39.7 | 41.8719 | -2.1719 | 0.97061 | 2026-01-03 13:20 | 223.586 | 227.06 | 910.2 | 37.8433 | 40.4139 | -2.5705 | 242.4831 | 37.6 | 39.8359 | -2.2359 | 0.9847 | 2026-01-03 13:20 | 417.8367 | 439.7198 | -21.8832 | 2638.319 | 413.1 | 433.4318 | -20.3318
2026-01-03 13:10 | 970 | 48.5 | 321.852 | 327.122 | 1238.9 | 54.5203 | 57.824 | -3.3037 | 346.9442 | 53.7 | 56.9972 | -3.2972 | 0.98389 | 2026-01-03 13:10 | 327.388 | 333.084 | 1254.4 | 55.514 | 57.824 | -2.31 | 346.9442 | 54.5 | 56.9972 | -2.4972 | 0.9829 | 2026-01-03 13:10 | 320.959 | 329.72 | 1232.9 | 54.9533 | 57.824 | -2.8707 | 346.9442 | 53.5 | 56.9972 | -3.4972 | 0.97343 | 2026-01-03 13:10 | 325.31 | 330.97 | 1252.2 | 55.1617 | 57.824 | -2.6624 | 346.9442 | 54.2 | 56.9972 | -2.7972 | 0.9829 | 2026-01-03 13:10 | 244.093 | 247.961 | 931.9 | 41.3268 | 42.8326 | -1.5058 | 256.9957 | 40.6 | 42.2201 | -1.6201 | 0.9844 | 2026-01-03 13:10 | 239.403 | 243.916 | 922.1 | 40.6527 | 42.8326 | -2.18 | 256.9957 | 39.9 | 42.2201 | -2.3201 | 0.9815 | 2026-01-03 13:10 | 238.48 | 242.924 | 914.8 | 40.4873 | 42.8326 | -2.3453 | 256.9957 | 40.1 | 42.2201 | -2.1201 | 0.98171 | 2026-01-03 13:10 | 239.868 | 246.669 | 921.8 | 41.1115 | 42.8326 | -1.7211 | 256.9957 | 40.5 | 42.2201 | -1.7201 | 0.97243 | 2026-01-03 13:10 | 226.083 | 229.596 | 872.6 | 38.266 | 40.7499 | -2.4839 | 244.4996 | 38.1 | 40.1672 | -2.0672 | 0.9847 | 2026-01-03 13:10 | 421.9937 | 443.3766 | -21.3829 | 2660.2593 | 415.1 | 437.0363 | -21.9363
2026-01-03 13:00 | 977 | 48.5 | 325.785 | 331.352 | 1185.2 | 55.2253 | 58.2413 | -3.016 | 349.4479 | 53.8 | 57.4085 | -3.6085 | 0.9832 | 2026-01-03 13:00 | 330.199 | 335.909 | 1199.9 | 55.9848 | 58.2413 | -2.2565 | 349.4479 | 54.6 | 57.4085 | -2.8085 | 0.983 | 2026-01-03 13:00 | 323.837 | 332.784 | 1179.4 | 55.464 | 58.2413 | -2.7773 | 349.4479 | 54.1 | 57.4085 | -3.3085 | 0.97311 | 2026-01-03 13:00 | 327.925 | 333.664 | 1198 | 55.6107 | 58.2413 | -2.6307 | 349.4479 | 54.8 | 57.4085 | -2.6085 | 0.9828 | 2026-01-03 13:00 | 246.068 | 249.917 | 891.3 | 41.6528 | 43.1417 | -1.4889 | 258.8503 | 41.1 | 42.5248 | -1.4248 | 0.9846 | 2026-01-03 13:00 | 241.462 | 246.08 | 882.2 | 41.0133 | 43.1417 | -2.1284 | 258.8503 | 40.3 | 42.5248 | -2.2248 | 0.98123 | 2026-01-03 13:00 | 240.641 | 245.53 | 874.7 | 40.9217 | 43.1417 | -2.2201 | 258.8503 | 39.7 | 42.5248 | -2.8248 | 0.98009 | 2026-01-03 13:00 | 242.061 | 249.121 | 881.3 | 41.5202 | 43.1417 | -1.6216 | 258.8503 | 39.9 | 42.5248 | -2.6248 | 0.97166 | 2026-01-03 13:00 | 228.376 | 231.948 | 834.5 | 38.658 | 41.044 | -2.386 | 246.264 | 37.8 | 40.4571 | -2.6571 | 0.9846 | 2026-01-03 13:00 | 426.0508 | 446.5762 | -20.5253 | 2679.4571 | 416.1 | 440.1901 | -24.0901
2026-01-03 12:50 | 975 | 48.79 | 323.926 | 329.461 | 1131.4 | 54.9102 | 58.0578 | -3.1477 | 348.3469 | 54.6 | 57.2276 | -2.6276 | 0.9832 | 2026-01-03 12:50 | 328.87 | 334.626 | 1145.3 | 55.771 | 58.0578 | -2.2868 | 348.3469 | 54.8 | 57.2276 | -2.4276 | 0.9828 | 2026-01-03 12:50 | 323.251 | 332.099 | 1125.3 | 55.3498 | 58.0578 | -2.708 | 348.3469 | 53.7 | 57.2276 | -3.5276 | 0.97336 | 2026-01-03 12:50 | 327.236 | 332.963 | 1143.2 | 55.4938 | 58.0578 | -2.564 | 348.3469 | 54.5 | 57.2276 | -2.7276 | 0.9828 | 2026-01-03 12:50 | 245.254 | 249.166 | 850.2 | 41.5277 | 43.0058 | -1.4781 | 258.0347 | 40.7 | 42.3908 | -1.6908 | 0.9843 | 2026-01-03 12:50 | 241.022 | 245.504 | 841.9 | 40.9173 | 43.0058 | -2.0885 | 258.0347 | 40.1 | 42.3908 | -2.2908 | 0.98174 | 2026-01-03 12:50 | 239.819 | 244.685 | 835 | 40.7808 | 43.0058 | -2.225 | 258.0347 | 39.8 | 42.3908 | -2.5908 | 0.98011 | 2026-01-03 12:50 | 241.409 | 248.107 | 841.4 | 41.3512 | 43.0058 | -1.6546 | 258.0347 | 40.1 | 42.3908 | -2.2908 | 0.973 | 2026-01-03 12:50 | 227.501 | 231.059 | 796.7 | 38.5098 | 40.9147 | -2.4048 | 245.4881 | 37.8 | 40.3296 | -2.5296 | 0.9846 | 2026-01-03 12:50 | 424.6117 | 445.1691 | -20.5574 | 2671.0147 | 416.1 | 438.8032 | -22.7032
2026-01-03 12:40 | 970 | 48.5 | 323.624 | 329.12 | 1076.8 | 54.8533 | 57.824 | -2.9707 | 346.9442 | 160.9 | 56.9972 | 103.9028 | 0.9833 | 2026-01-03 12:40 | 328.937 | 334.592 | 1090.5 | 55.7653 | 57.824 | -2.0587 | 346.9442 | 55.9 | 56.9972 | -1.0972 | 0.9831 | 2026-01-03 12:40 | 322.014 | 330.658 | 1071.6 | 55.1097 | 57.824 | -2.7144 | 346.9442 | 53.3 | 56.9972 | -3.6972 | 0.97386 | 2026-01-03 12:40 | 326.526 | 332.207 | 1088.7 | 55.3678 | 57.824 | -2.4562 | 346.9442 | 54.1 | 56.9972 | -2.8972 | 0.9829 | 2026-01-03 12:40 | 243.995 | 247.811 | 809.5 | 41.3018 | 42.8326 | -1.5308 | 256.9957 | 40.4 | 42.2201 | -1.8201 | 0.9846 | 2026-01-03 12:40 | 239.985 | 244.354 | 801.8 | 40.7257 | 42.8326 | -2.107 | 256.9957 | 40.4 | 42.2201 | -1.8201 | 0.98212 | 2026-01-03 12:40 | 238.743 | 243.503 | 795.2 | 40.5838 | 42.8326 | -2.2488 | 256.9957 | 40.1 | 42.2201 | -2.1201 | 0.98045 | 2026-01-03 12:40 | 240.131 | 247.52 | 801.3 | 41.2533 | 42.8326 | -1.5793 | 256.9957 | 40.3 | 42.2201 | -1.9201 | 0.97015 | 2026-01-03 12:40 | 226.767 | 230.314 | 758.9 | 38.3857 | 40.7499 | -2.3643 | 244.4996 | 38.2 | 40.1672 | -1.9672 | 0.9846 | 2026-01-03 12:40 | 423.3465 | 443.3766 | -20.0301 | 2660.2593 | 523.6 | 437.0363 | 86.5637
2026-01-03 12:30 | 966 | 48.5 |  |  |  | 0 | 57.5856 | -57.5856 | 345.5135 | 0 | 56.7621 | -56.7621 |  | 2026-01-03 12:30 | 327.753 | 333.571 | 1034.6 | 55.5952 | 57.5856 | -1.9904 | 345.5135 | 53.2 | 56.7621 | -3.5621 | 0.98256 | 2026-01-03 12:30 | 321.493 | 330.734 | 1018.3 | 55.1223 | 57.5856 | -2.4633 | 345.5135 | 53.6 | 56.7621 | -3.1621 | 0.97206 | 2026-01-03 12:30 | 326.38 | 331.991 | 1034.6 | 55.3318 | 57.5856 | -2.2538 | 345.5135 | 54.4 | 56.7621 | -2.3621 | 0.9831 | 2026-01-03 12:30 | 244.024 | 247.816 | 769.1 | 41.3027 | 42.656 | -1.3533 | 255.9359 | 40.8 | 42.046 | -1.246 | 0.9847 | 2026-01-03 12:30 | 240.731 | 244.963 | 761.4 | 40.8272 | 42.656 | -1.8288 | 255.9359 | 39.5 | 42.046 | -2.546 | 0.98272 | 2026-01-03 12:30 | 238.827 | 243.675 | 755.1 | 40.6125 | 42.656 | -2.0435 | 255.9359 | 39.3 | 42.046 | -2.746 | 0.9801 | 2026-01-03 12:30 | 240.679 | 247.544 | 761 | 41.2573 | 42.656 | -1.3987 | 255.9359 | 40.3 | 42.046 | -1.746 | 0.97227 | 2026-01-03 12:30 | 227.607 | 231.12 | 720.7 | 38.52 | 40.5819 | -2.0619 | 243.4913 | 38 | 40.0016 | -2.0016 | 0.9848 | 2026-01-03 12:30 | 368.569 | 441.5482 | -72.9792 | 2649.2892 | 359.1 | 435.2341 | -76.1341
2026-01-03 12:20 | 958 | 48.5 |  |  |  | 0 | 57.1087 | -57.1087 | 342.6521 | 0 | 56.292 | -56.292 |  | 2026-01-03 12:20 | 324.958 | 330.544 | 981.4 | 55.0907 | 57.1087 | -2.018 | 342.6521 | 54.1 | 56.292 | -2.192 | 0.9831 | 2026-01-03 12:20 | 318.818 | 327.418 | 964.7 | 54.5697 | 57.1087 | -2.539 | 342.6521 | 53.1 | 56.292 | -3.192 | 0.97373 | 2026-01-03 12:20 | 323.351 | 328.989 | 980.2 | 54.8315 | 57.1087 | -2.2772 | 342.6521 | 53.9 | 56.292 | -2.392 | 0.98286 | 2026-01-03 12:20 | 242.03 | 245.816 | 728.3 | 40.9693 | 42.3027 | -1.3334 | 253.8164 | 40.3 | 41.6978 | -1.3978 | 0.9846 | 2026-01-03 12:20 | 238.266 | 242.49 | 721.9 | 40.415 | 42.3027 | -1.8877 | 253.8164 | 39.8 | 41.6978 | -1.8978 | 0.98258 | 2026-01-03 12:20 | 237.326 | 242.043 | 715.8 | 40.3405 | 42.3027 | -1.9622 | 253.8164 | 40.1 | 41.6978 | -1.5978 | 0.98051 | 2026-01-03 12:20 | 239.286 | 246.752 | 720.7 | 41.1253 | 42.3027 | -1.1774 | 253.8164 | 39.2 | 41.6978 | -2.4978 | 0.96974 | 2026-01-03 12:20 | 226.085 | 229.554 | 682.7 | 38.259 | 40.2458 | -1.9868 | 241.4749 | 37.6 | 39.6703 | -2.0703 | 0.98489 | 2026-01-03 12:20 | 365.601 | 437.8915 | -72.2905 | 2627.3489 | 358.1 | 431.6296 | -73.5296
2026-01-03 12:10 | 951 | 48.79 | 319.199 | 324.499 | 915.9 | 54.0832 | 56.6287 | -2.5455 | 339.7722 | 52.6 | 55.8189 | -3.2189 | 0.98367 | 2026-01-03 12:10 | 323.785 | 329.351 | 927.3 | 54.8918 | 56.6287 | -1.7369 | 339.7722 | 53.3 | 55.8189 | -2.5189 | 0.9831 | 2026-01-03 12:10 | 318.216 | 326.916 | 911.6 | 54.486 | 56.6287 | -2.1427 | 339.7722 | 52.4 | 55.8189 | -3.4189 | 0.97339 | 2026-01-03 12:10 | 322.975 | 328.494 | 926.3 | 54.749 | 56.6287 | -1.8797 | 339.7722 | 53.2 | 55.8189 | -2.6189 | 0.9832 | 2026-01-03 12:10 | 241.898 | 245.632 | 688 | 40.9387 | 41.9472 | -1.0085 | 251.6831 | 40.2 | 41.3473 | -1.1473 | 0.9848 | 2026-01-03 12:10 | 238.039 | 242.276 | 682.1 | 40.3793 | 41.9472 | -1.5679 | 251.6831 | 39.7 | 41.3473 | -1.6473 | 0.98251 | 2026-01-03 12:10 | 236.297 | 240.81 | 675.7 | 40.135 | 41.9472 | -1.8122 | 251.6831 | 38.8 | 41.3473 | -2.5473 | 0.98126 | 2026-01-03 12:10 | 238.576 | 245.721 | 681.5 | 40.9535 | 41.9472 | -0.99369 | 251.6831 | 39.7 | 41.3473 | -1.6473 | 0.97092 | 2026-01-03 12:10 | 225.81 | 229.225 | 645.1 | 38.2042 | 39.9076 | -1.7034 | 239.4453 | 37.1 | 39.3369 | -2.2369 | 0.9851 | 2026-01-03 12:10 | 418.8207 | 434.2111 | -15.3904 | 2605.2666 | 407 | 428.0019 | -21.0019
2026-01-03 12:00 | 937 | 48.79 | 315.592 | 320.821 | 863.3 | 53.4702 | 55.7951 | -2.3249 | 334.7703 | 51.5 | 54.9972 | -3.4972 | 0.9837 | 2026-01-03 12:00 | 319.869 | 325.268 | 874 | 54.2113 | 55.7951 | -1.5837 | 334.7703 | 54.4 | 54.9972 | -0.59718 | 0.9834 | 2026-01-03 12:00 | 314.324 | 322.776 | 859.2 | 53.796 | 55.7951 | -1.9991 | 334.7703 | 52.7 | 54.9972 | -2.2972 | 0.97381 | 2026-01-03 12:00 | 318.553 | 323.996 | 873.1 | 53.9993 | 55.7951 | -1.7957 | 334.7703 | 53.5 | 54.9972 | -1.4972 | 0.9832 | 2026-01-03 12:00 | 238.136 | 241.836 | 647.8 | 40.306 | 41.3297 | -1.0237 | 247.978 | 39.4 | 40.7387 | -1.3387 | 0.9847 | 2026-01-03 12:00 | 234.345 | 238.501 | 642.4 | 39.7502 | 41.3297 | -1.5795 | 247.978 | 38.9 | 40.7387 | -1.8387 | 0.98257 | 2026-01-03 12:00 | 232.922 | 236.92 | 636.9 | 39.4867 | 41.3297 | -1.843 | 247.978 | 38.6 | 40.7387 | -2.1387 | 0.98313 | 2026-01-03 12:00 | 234.139 | 240.915 | 641.8 | 40.1525 | 41.3297 | -1.1772 | 247.978 | 38.7 | 40.7387 | -2.0387 | 0.97187 | 2026-01-03 12:00 | 221.805 | 225.183 | 608 | 37.5305 | 39.3201 | -1.7896 | 235.9204 | 36.7 | 38.7578 | -2.0578 | 0.985 | 2026-01-03 12:00 | 412.7027 | 427.8189 | -15.1163 | 2566.9136 | 404.4 | 421.7011 | -17.3011
2026-01-03 11:50 | 926 | 48.5 | 312.197 | 317.402 | 811.8 | 52.9003 | 55.2011 | -2.3008 | 331.2065 | 52.7 | 54.4117 | -1.7117 | 0.9836 | 2026-01-03 11:50 | 316.505 | 321.818 | 819.6 | 53.6363 | 55.2011 | -1.5648 | 331.2065 | 51.8 | 54.4117 | -2.6117 | 0.98349 | 2026-01-03 11:50 | 310.325 | 318.982 | 806.5 | 53.1637 | 55.2011 | -2.0374 | 331.2065 | 51.5 | 54.4117 | -2.9117 | 0.97286 | 2026-01-03 11:50 | 315.702 | 321.031 | 819.6 | 53.5052 | 55.2011 | -1.6959 | 331.2065 | 51.9 | 54.4117 | -2.5117 | 0.9834 | 2026-01-03 11:50 | 235.653 | 239.29 | 608.4 | 39.8817 | 40.8897 | -1.008 | 245.3382 | 39.2 | 40.305 | -1.105 | 0.9848 | 2026-01-03 11:50 | 232.66 | 236.717 | 603.5 | 39.4528 | 40.8897 | -1.4369 | 245.3382 | 38.6 | 40.305 | -1.705 | 0.98286 | 2026-01-03 11:50 | 230.856 | 234.935 | 598.3 | 39.1558 | 40.8897 | -1.7339 | 245.3382 | 38.3 | 40.305 | -2.005 | 0.98264 | 2026-01-03 11:50 | 231.947 | 238.976 | 603.1 | 39.8293 | 40.8897 | -1.0604 | 245.3382 | 38.6 | 40.305 | -1.705 | 0.97059 | 2026-01-03 11:50 | 219.704 | 223.05 | 571.3 | 37.175 | 38.9015 | -1.7265 | 233.4089 | 36.5 | 38.3452 | -1.8452 | 0.985 | 2026-01-03 11:50 | 408.7002 | 423.2646 | -14.5645 | 2539.5878 | 399.1 | 417.2119 | -18.1119
2026-01-03 11:40 | 908 | 48.79 | 309.037 | 314.114 | 759.1 | 52.3523 | 54.0682 | -1.7159 | 324.4092 | 50.5 | 53.295 | -2.795 | 0.98384 | 2026-01-03 11:40 | 312.865 | 318.082 | 767.8 | 53.0137 | 54.0682 | -1.0545 | 324.4092 | 53.3 | 53.295 | 0.0049725 | 0.9836 | 2026-01-03 11:40 | 307.017 | 315.077 | 755 | 52.5128 | 54.0682 | -1.5554 | 324.4092 | 51 | 53.295 | -2.295 | 0.97442 | 2026-01-03 11:40 | 311.814 | 317.045 | 767.7 | 52.8408 | 54.0682 | -1.2274 | 324.4092 | 52.2 | 53.295 | -1.095 | 0.9835 | 2026-01-03 11:40 | 232.89 | 236.413 | 569.2 | 39.4022 | 40.0505 | -0.64835 | 240.3031 | 38.7 | 39.4778 | -0.7778 | 0.9851 | 2026-01-03 11:40 | 229.932 | 234.096 | 564.9 | 39.016 | 40.0505 | -1.0345 | 240.3031 | 38.2 | 39.4778 | -1.2778 | 0.98221 | 2026-01-03 11:40 | 228.204 | 232.116 | 560 | 38.686 | 40.0505 | -1.3645 | 240.3031 | 38.6 | 39.4778 | -0.8778 | 0.98315 | 2026-01-03 11:40 | 230.094 | 236.642 | 564.5 | 39.4403 | 40.0505 | -0.61019 | 240.3031 | 38.2 | 39.4778 | -1.2778 | 0.97233 | 2026-01-03 11:40 | 217.798 | 221.07 | 534.8 | 36.845 | 38.1031 | -1.2581 | 228.6187 | 36.2 | 37.5582 | -1.3582 | 0.9852 | 2026-01-03 11:40 | 404.1092 | 414.578 | -10.4688 | 2487.468 | 396.9 | 408.6495 | -11.7495
2026-01-03 11:30 | 895 | 48.79 | 305.644 | 310.582 | 708.6 | 51.7637 | 53.2941 | -1.5304 | 319.7646 | 52.4 | 52.532 | -0.13199 | 0.9841 | 2026-01-03 11:30 | 309.072 | 314.116 | 714.5 | 52.3527 | 53.2941 | -0.94143 | 319.7646 | 49.5 | 52.532 | -3.032 | 0.98394 | 2026-01-03 11:30 | 303.329 | 311.369 | 704 | 51.8948 | 53.2941 | -1.3993 | 319.7646 | 50 | 52.532 | -2.532 | 0.97418 | 2026-01-03 11:30 | 308.663 | 313.746 | 715.5 | 52.291 | 53.2941 | -1.0031 | 319.7646 | 50.7 | 52.532 | -1.832 | 0.9838 | 2026-01-03 11:30 | 230.508 | 233.947 | 530.5 | 38.9912 | 39.4771 | -0.48594 | 236.8627 | 37.8 | 38.9126 | -1.1126 | 0.9853 | 2026-01-03 11:30 | 227.843 | 231.701 | 526.7 | 38.6168 | 39.4771 | -0.86028 | 236.8627 | 37.3 | 38.9126 | -1.6126 | 0.98335 | 2026-01-03 11:30 | 225.904 | 229.982 | 521.4 | 38.3303 | 39.4771 | -1.1468 | 236.8627 | 36.4 | 38.9126 | -2.5126 | 0.98227 | 2026-01-03 11:30 | 227.424 | 234.196 | 526.3 | 39.0327 | 39.4771 | -0.44444 | 236.8627 | 37.3 | 38.9126 | -1.6126 | 0.97108 | 2026-01-03 11:30 | 215.17 | 218.358 | 498.6 | 36.393 | 37.5576 | -1.1646 | 225.3455 | 35.8 | 37.0205 | -1.2205 | 0.9854 | 2026-01-03 11:30 | 399.6662 | 408.6424 | -8.9762 | 2451.8545 | 387.2 | 402.7988 | -15.5988
2026-01-03 11:20 | 873 | 48.5 | 300.068 | 304.854 | 656.2 | 50.809 | 52.0416 | -1.2326 | 312.2498 | 49.8 | 51.2974 | -1.4974 | 0.9843 | 2026-01-03 11:20 | 303.813 | 308.722 | 665 | 51.4537 | 52.0416 | -0.58797 | 312.2498 | 50.4 | 51.2974 | -0.89744 | 0.9841 | 2026-01-03 11:20 | 298.526 | 306.256 | 654 | 51.0427 | 52.0416 | -0.99897 | 312.2498 | 48.9 | 51.2974 | -2.3974 | 0.97476 | 2026-01-03 11:20 | 302.42 | 307.369 | 664.8 | 51.2282 | 52.0416 | -0.81347 | 312.2498 | 50.1 | 51.2974 | -1.1974 | 0.9839 | 2026-01-03 11:20 | 225.672 | 229.039 | 492.7 | 38.1732 | 38.5494 | -0.37619 | 231.2961 | 37.5 | 37.9981 | -0.4981 | 0.9853 | 2026-01-03 11:20 | 222.707 | 226.221 | 489.4 | 37.7035 | 38.5494 | -0.84586 | 231.2961 | 36.9 | 37.9981 | -1.0981 | 0.98447 | 2026-01-03 11:20 | 220.943 | 224.728 | 485 | 37.4547 | 38.5494 | -1.0947 | 231.2961 | 36.6 | 37.9981 | -1.3981 | 0.98316 | 2026-01-03 11:20 | 222.512 | 229.176 | 489 | 38.196 | 38.5494 | -0.35336 | 231.2961 | 36.8 | 37.9981 | -1.1981 | 0.97092 | 2026-01-03 11:20 | 210.382 | 213.456 | 462.8 | 35.576 | 36.6749 | -1.0989 | 220.0496 | 34.3 | 36.1505 | -1.8505 | 0.9856 | 2026-01-03 11:20 | 391.6368 | 399.0389 | -7.4021 | 2394.2334 | 381.3 | 393.3326 | -12.0326
2026-01-03 11:10 | 851 | 48.5 | 292.843 | 297.434 | 606.4 | 49.5723 | 50.7302 | -1.1578 | 304.381 | 48.5 | 50.0047 | -1.5047 | 0.98456 | 2026-01-03 11:10 | 296.513 | 301.273 | 614.6 | 50.2122 | 50.7302 | -0.51799 | 304.381 | 50.5 | 50.0047 | 0.49528 | 0.9842 | 2026-01-03 11:10 | 291.477 | 298.772 | 605.1 | 49.7953 | 50.7302 | -0.93483 | 304.381 | 48.4 | 50.0047 | -1.6047 | 0.97558 | 2026-01-03 11:10 | 295.322 | 300.094 | 614.7 | 50.0157 | 50.7302 | -0.71449 | 304.381 | 48.5 | 50.0047 | -1.5047 | 0.9841 | 2026-01-03 11:10 | 220.47 | 223.668 | 455.2 | 37.278 | 37.5779 | -0.2999 | 225.4674 | 36.2 | 37.0405 | -0.84053 | 0.9857 | 2026-01-03 11:10 | 217.415 | 220.705 | 452.5 | 36.7842 | 37.5779 | -0.79373 | 225.4674 | 35.8 | 37.0405 | -1.2405 | 0.98509 | 2026-01-03 11:10 | 215.817 | 219.622 | 448.4 | 36.6037 | 37.5779 | -0.97423 | 225.4674 | 35.5 | 37.0405 | -1.5405 | 0.98267 | 2026-01-03 11:10 | 217.222 | 223.516 | 452.2 | 37.2527 | 37.5779 | -0.32523 | 225.4674 | 35.8 | 37.0405 | -1.2405 | 0.97184 | 2026-01-03 11:10 | 205.665 | 208.67 | 428.5 | 34.7783 | 35.7507 | -0.97238 | 214.5043 | 33.8 | 35.2395 | -1.4395 | 0.9856 | 2026-01-03 11:10 | 382.2923 | 388.9829 | -6.6906 | 2333.8976 | 373 | 383.4205 | -10.4205
2026-01-03 11:00 | 828 | 48.79 | 286.344 | 290.795 | 557.9 | 48.4658 | 49.3045 | -0.83865 | 295.8269 | 47.8 | 48.5994 | -0.79943 | 0.98469 | 2026-01-03 11:00 | 289.593 | 294.152 | 564.1 | 49.0253 | 49.3045 | -0.27915 | 295.8269 | 45.9 | 48.5994 | -2.6994 | 0.9845 | 2026-01-03 11:00 | 284.399 | 291.87 | 556.7 | 48.645 | 49.3045 | -0.65948 | 295.8269 | 46.9 | 48.5994 | -1.6994 | 0.9744 | 2026-01-03 11:00 | 288.798 | 293.404 | 566.2 | 48.9007 | 49.3045 | -0.40382 | 295.8269 | 47.5 | 48.5994 | -1.0994 | 0.9843 | 2026-01-03 11:00 | 215.178 | 218.3 | 419 | 36.3833 | 36.5218 | -0.13851 | 219.131 | 35.4 | 35.9996 | -0.59958 | 0.9857 | 2026-01-03 11:00 | 212.958 | 216.288 | 416.7 | 36.048 | 36.5218 | -0.47384 | 219.131 | 35 | 35.9996 | -0.99958 | 0.9846 | 2026-01-03 11:00 | 211.17 | 214.444 | 412.9 | 35.7407 | 36.5218 | -0.78117 | 219.131 | 34.8 | 35.9996 | -1.1996 | 0.98473 | 2026-01-03 11:00 | 212.481 | 218.444 | 416.4 | 36.4073 | 36.5218 | -0.11451 | 219.131 | 34.9 | 35.9996 | -1.0996 | 0.9727 | 2026-01-03 11:00 | 201.396 | 204.256 | 394.7 | 34.0427 | 34.746 | -0.70334 | 208.476 | 33.6 | 34.2491 | -0.64914 | 0.986 | 2026-01-03 11:00 | 373.6588 | 378.0513 | -4.3925 | 2268.3078 | 361.8 | 372.6452 | -10.8452
2026-01-03 10:50 | 803 | 48.79 | 278.839 | 283.012 | 510.1 | 47.1687 | 47.8158 | -0.64716 | 286.8949 | 44.7 | 47.1321 | -2.4321 | 0.98526 | 2026-01-03 10:50 | 282.594 | 286.956 | 518.2 | 47.826 | 47.8158 | 0.010177 | 286.8949 | 45.9 | 47.1321 | -1.2321 | 0.9848 | 2026-01-03 10:50 | 277.656 | 284.739 | 509.8 | 47.4565 | 47.8158 | -0.35932 | 286.8949 | 45.8 | 47.1321 | -1.3321 | 0.97512 | 2026-01-03 10:50 | 281.821 | 286.2 | 518.7 | 47.7 | 47.8158 | -0.11582 | 286.8949 | 46.4 | 47.1321 | -0.73206 | 0.9847 | 2026-01-03 10:50 | 210.196 | 213.159 | 383.6 | 35.5265 | 35.4191 | 0.10737 | 212.5148 | 34.6 | 34.9126 | -0.31263 | 0.9861 | 2026-01-03 10:50 | 207.886 | 210.816 | 381.7 | 35.136 | 35.4191 | -0.28313 | 212.5148 | 34.2 | 34.9126 | -0.71263 | 0.9861 | 2026-01-03 10:50 | 206.274 | 209.605 | 378.1 | 34.9342 | 35.4191 | -0.48496 | 212.5148 | 33.9 | 34.9126 | -1.0126 | 0.98411 | 2026-01-03 10:50 | 207.444 | 213.475 | 381.5 | 35.5792 | 35.4191 | 0.16004 | 212.5148 | 34.2 | 34.9126 | -0.71263 | 0.97175 | 2026-01-03 10:50 | 196.077 | 198.841 | 361.1 | 33.1402 | 33.6969 | -0.55675 | 202.1815 | 31.8 | 33.215 | -1.415 | 0.9861 | 2026-01-03 10:50 | 364.4672 | 366.6367 | -2.1695 | 2199.8203 | 351.5 | 361.3938 | -9.8938
2026-01-03 10:40 | 776 | 48.79 | 271.289 | 275.309 | 465.4 | 45.8848 | 46.2081 | -0.32323 | 277.2484 | 43.6 | 45.5473 | -1.9473 | 0.9854 | 2026-01-03 10:40 | 274.803 | 278.96 | 472.3 | 46.4933 | 46.2081 | 0.28527 | 277.2484 | 45.5 | 45.5473 | -0.047292 | 0.9851 | 2026-01-03 10:40 | 270.233 | 276.684 | 464 | 46.114 | 46.2081 | -0.094068 | 277.2484 | 44 | 45.5473 | -1.5473 | 0.97668 | 2026-01-03 10:40 | 274.101 | 278.275 | 472.3 | 46.3792 | 46.2081 | 0.1711 | 277.2484 | 44.8 | 45.5473 | -0.74729 | 0.985 | 2026-01-03 10:40 | 204.054 | 206.888 | 349 | 34.4813 | 34.2282 | 0.25314 | 205.3692 | 33.3 | 33.7387 | -0.43873 | 0.9863 | 2026-01-03 10:40 | 202.155 | 204.963 | 347.5 | 34.1605 | 34.2282 | -0.067698 | 205.3692 | 33 | 33.7387 | -0.73873 | 0.9863 | 2026-01-03 10:40 | 200.069 | 203.097 | 344.2 | 33.8495 | 34.2282 | -0.3787 | 205.3692 | 32.7 | 33.7387 | -1.0387 | 0.98509 | 2026-01-03 10:40 | 201.43 | 207.361 | 347.3 | 34.5602 | 34.2282 | 0.33197 | 205.3692 | 33.3 | 33.7387 | -0.43873 | 0.9714 | 2026-01-03 10:40 | 190.879 | 193.55 | 329.3 | 32.2583 | 32.5639 | -0.30556 | 195.3833 | 31.6 | 32.0982 | -0.49823 | 0.9862 | 2026-01-03 10:40 | 354.1812 | 354.309 | -0.12779 | 2125.8537 | 341.8 | 349.2423 | -7.4423
2026-01-03 10:30 | 746 | 48.5 | 260.985 | 264.798 | 421.8 | 44.133 | 44.4709 | -0.33786 | 266.8251 | 43.5 | 43.8349 | -0.33492 | 0.9856 | 2026-01-03 10:30 | 264.412 | 268.951 | 426.8 | 44.8252 | 44.4709 | 0.35431 | 266.8251 | 43.5 | 43.8349 | -0.33492 | 0.98312 | 2026-01-03 10:30 | 260.696 | 266.458 | 420 | 44.4097 | 44.4709 | -0.06119 | 266.8251 | 42.4 | 43.8349 | -1.4349 | 0.97838 | 2026-01-03 10:30 | 264.667 | 268.616 | 427.5 | 44.7693 | 44.4709 | 0.29848 | 266.8251 | 43.4 | 43.8349 | -0.43492 | 0.9853 | 2026-01-03 10:30 | 196.991 | 199.687 | 315.7 | 33.2812 | 32.9414 | 0.33979 | 197.6483 | 32.3 | 32.4703 | -0.17031 | 0.9865 | 2026-01-03 10:30 | 195.076 | 197.726 | 314.5 | 32.9543 | 32.9414 | 0.012958 | 197.6483 | 32 | 32.4703 | -0.47031 | 0.9866 | 2026-01-03 10:30 | 193.18 | 195.804 | 311.5 | 32.634 | 32.9414 | -0.30738 | 197.6483 | 31.7 | 32.4703 | -0.77031 | 0.9866 | 2026-01-03 10:30 | 193.759 | 199.251 | 314 | 33.2085 | 32.9414 | 0.26712 | 197.6483 | 31.4 | 32.4703 | -1.0703 | 0.97244 | 2026-01-03 10:30 | 183.746 | 186.279 | 297.7 | 31.0465 | 31.3396 | -0.29314 | 188.0378 | 29.8 | 30.8915 | -1.0915 | 0.9864 | 2026-01-03 10:30 | 341.2617 | 340.9886 | 0.2731 | 2045.9314 | 330 | 336.1124 | -6.1124
2026-01-03 10:20 | 712 | 48.5 | 250.134 | 254.562 | 378.3 | 42.427 | 42.444 | -0.017035 | 254.6642 | 39.7 | 41.8371 | -2.1371 | 0.98261 | 2026-01-03 10:20 | 254.059 | 257.745 | 383.3 | 42.9575 | 42.444 | 0.51347 | 254.6642 | 80.5 | 41.8371 | 38.6629 | 0.9857 | 2026-01-03 10:20 | 250.282 | 256.159 | 377.6 | 42.6932 | 42.444 | 0.24913 | 254.6642 | 41.3 | 41.8371 | -0.53708 | 0.97706 | 2026-01-03 10:20 | 254.074 | 257.812 | 384.1 | 42.9687 | 42.444 | 0.52463 | 254.6642 | 41.6 | 41.8371 | -0.23708 | 0.9855 | 2026-01-03 10:20 | 189.009 | 191.557 | 283.4 | 31.9262 | 31.44 | 0.48614 | 188.6402 | 30.9 | 30.9904 | -0.090433 | 0.9867 | 2026-01-03 10:20 | 187.221 | 189.725 | 282.5 | 31.6208 | 31.44 | 0.18081 | 188.6402 | 30.6 | 30.9904 | -0.39043 | 0.9868 | 2026-01-03 10:20 | 185.169 | 187.646 | 279.8 | 31.2743 | 31.44 | -0.16569 | 188.6402 | 30.3 | 30.9904 | -0.69043 | 0.9868 | 2026-01-03 10:20 | 186.214 | 191.323 | 282.6 | 31.8872 | 31.44 | 0.44714 | 188.6402 | 30.5 | 30.9904 | -0.49043 | 0.9733 | 2026-01-03 10:20 | 176.595 | 178.975 | 267.9 | 29.8292 | 29.9113 | -0.082124 | 179.4677 | 28.8 | 29.4836 | -0.68356 | 0.9867 | 2026-01-03 10:20 | 327.584 | 325.4475 | 2.1365 | 1952.6852 | 354.2 | 320.7936 | 33.4064
2026-01-03 10:10 | 679 | 48.5 | 240.378 | 243.766 | 338.6 | 40.6277 | 40.4768 | 0.15084 | 242.861 | 39.1 | 39.898 | -0.79801 | 0.9861 |  |  |  |  | 0 | 40.4768 | -40.4768 | 242.861 | 0 | 39.898 | -39.898 |  | 2026-01-03 10:10 | 239.484 | 244.544 | 336.3 | 40.7573 | 40.4768 | 0.28051 | 242.861 | 38.9 | 39.898 | -0.99801 | 0.97931 | 2026-01-03 10:10 | 243.445 | 246.927 | 342.5 | 41.1545 | 40.4768 | 0.67767 | 242.861 | 39.5 | 39.898 | -0.39801 | 0.9859 | 2026-01-03 10:10 | 181.19 | 183.577 | 252.5 | 30.5962 | 29.9828 | 0.61333 | 179.897 | 29.4 | 29.5541 | -0.15408 | 0.987 | 2026-01-03 10:10 | 179.424 | 181.787 | 251.9 | 30.2978 | 29.9828 | 0.315 | 179.897 | 29.2 | 29.5541 | -0.35408 | 0.987 | 2026-01-03 10:10 | 177.988 | 180.332 | 249.5 | 30.0553 | 29.9828 | 0.0725 | 179.897 | 28.9 | 29.5541 | -0.65408 | 0.987 | 2026-01-03 10:10 | 178.669 | 183.582 | 252.1 | 30.597 | 29.9828 | 0.61417 | 179.897 | 29 | 29.5541 | -0.55408 | 0.97324 | 2026-01-03 10:10 | 169.499 | 171.732 | 239.1 | 28.622 | 28.525 | 0.097047 | 171.1497 | 27.6 | 28.117 | -0.51705 | 0.987 | 2026-01-03 10:10 | 272.7078 | 310.3636 | -37.6558 | 1862.1815 | 261.6 | 305.9254 | -44.3254
2026-01-03 10:00 | 643 | 48.5 | 227.549 | 230.826 | 299.5 | 38.471 | 38.3308 | 0.14022 | 229.9847 | 36.7 | 37.7826 | -1.0826 | 0.9858 | 2026-01-03 10:00 | 230.84 | 234.094 | 302.8 | 39.0157 | 38.3308 | 0.68489 | 229.9847 | 38.1 | 37.7826 | 0.31735 | 0.9861 | 2026-01-03 10:00 | 227.016 | 231.842 | 297.4 | 38.6403 | 38.3308 | 0.30955 | 229.9847 | 36.6 | 37.7826 | -1.1826 | 0.97918 | 2026-01-03 10:00 | 230.83 | 234.084 | 303 | 39.014 | 38.3308 | 0.68322 | 229.9847 | 37.2 | 37.7826 | -0.58265 | 0.9861 | 2026-01-03 10:00 | 171.023 | 173.24 | 223.1 | 28.8733 | 28.3932 | 0.48016 | 170.359 | 27.6 | 27.9871 | -0.38715 | 0.9872 | 2026-01-03 10:00 | 170.132 | 172.355 | 222.7 | 28.7258 | 28.3932 | 0.33266 | 170.359 | 27.4 | 27.9871 | -0.58715 | 0.9871 | 2026-01-03 10:00 | 168.262 | 170.639 | 220.6 | 28.4398 | 28.3932 | 0.046664 | 170.359 | 27.1 | 27.9871 | -0.88715 | 0.98607 | 2026-01-03 10:00 | 169.316 | 173.754 | 223.1 | 28.959 | 28.3932 | 0.56583 | 170.359 | 27.6 | 27.9871 | -0.38715 | 0.97446 | 2026-01-03 10:00 | 160.647 | 162.746 | 211.5 | 27.1243 | 27.0126 | 0.11175 | 162.0755 | 26.2 | 26.6263 | -0.4263 | 0.9871 | 2026-01-03 10:00 | 297.2633 | 293.9084 | 3.355 | 1763.4502 | 284.5 | 289.7055 | -5.2055
2026-01-03 09:50 | 604 | 48.5 | 215.086 | 217.919 | 262.8 | 36.3198 | 36.0059 | 0.31394 | 216.0354 | 35 | 35.491 | -0.49101 |  | 2026-01-03 09:50 | 217.056 | 219.953 | 264.7 | 36.6588 | 36.0059 | 0.65294 | 216.0354 | 34.5 | 35.491 | -0.99101 |  | 2026-01-03 09:50 | 214.269 | 218.881 | 260.8 | 36.4802 | 36.0059 | 0.47427 | 216.0354 | 34.8 | 35.491 | -0.69101 |  | 2026-01-03 09:50 | 217.862 | 220.843 | 265.8 | 36.8072 | 36.0059 | 0.80127 | 216.0354 | 35.4 | 35.491 | -0.09101 |  | 2026-01-03 09:50 | 161.707 | 163.771 | 195.5 | 27.2952 | 26.671 | 0.62413 | 160.0262 | 26.2 | 26.2896 | -0.089637 |  | 2026-01-03 09:50 | 161.045 | 163.066 | 195.3 | 27.1777 | 26.671 | 0.50663 | 160.0262 | 26.2 | 26.2896 | -0.089637 |  | 2026-01-03 09:50 | 158.956 | 160.984 | 193.5 | 26.8307 | 26.671 | 0.15963 | 160.0262 | 25.8 | 26.2896 | -0.48964 |  | 2026-01-03 09:50 | 160.018 | 164.248 | 195.5 | 27.3747 | 26.671 | 0.70363 | 160.0262 | 25.7 | 26.2896 | -0.58964 |  | 2026-01-03 09:50 | 151.639 | 153.605 | 185.3 | 25.6008 | 25.3742 | 0.22665 | 152.2451 | 24.4 | 25.0113 | -0.61133 |  | 2026-01-03 09:50 | 280.545 | 276.0819 | 4.4631 | 1656.4914 | 268 | 272.1339 | -4.1339
2026-01-03 09:40 | 568 | 48.5 | 202.169 | 205.253 | 227.8 | 34.2088 | 33.8598 | 0.34899 | 203.1591 | 32.6 | 33.3757 | -0.77565 |  | 2026-01-03 09:40 | 203.312 | 206.726 | 230.2 | 34.4543 | 33.8598 | 0.59449 | 203.1591 | 33 | 33.3757 | -0.37565 |  | 2026-01-03 09:40 | 201.859 | 205.634 | 226 | 34.2723 | 33.8598 | 0.41249 | 203.1591 | 32.4 | 33.3757 | -0.97565 |  | 2026-01-03 09:40 | 205.408 | 208.135 | 230.4 | 34.6892 | 33.8598 | 0.82932 | 203.1591 | 33 | 33.3757 | -0.37565 |  | 2026-01-03 09:40 | 152.332 | 154.245 | 169.3 | 25.7075 | 25.0814 | 0.62613 | 150.4882 | 24.5 | 24.7227 | -0.22271 |  | 2026-01-03 09:40 | 151.899 | 153.744 | 169.1 | 25.624 | 25.0814 | 0.54263 | 150.4882 | 24.3 | 24.7227 | -0.42271 |  | 2026-01-03 09:40 | 149.831 | 151.697 | 167.7 | 25.2828 | 25.0814 | 0.20146 | 150.4882 | 24.1 | 24.7227 | -0.62271 |  | 2026-01-03 09:40 | 150.914 | 155.151 | 169.8 | 25.8585 | 25.0814 | 0.77713 | 150.4882 | 24.2 | 24.7227 | -0.52271 |  | 2026-01-03 09:40 | 143.162 | 144.866 | 160.9 | 24.1443 | 23.8618 | 0.28252 | 143.1709 | 22.9 | 23.5206 | -0.62059 |  | 2026-01-03 09:40 | 264.2418 | 259.6267 | 4.6152 | 1557.7601 | 251 | 255.914 | -4.914
2026-01-03 09:30 | 528 | 48.5 | 188.448 | 190.853 | 195.2 | 31.8088 | 31.4754 | 0.33348 | 188.8521 | 29.8 | 31.0253 | -1.2253 |  | 2026-01-03 09:30 | 188.604 | 192.244 | 197.2 | 32.0407 | 31.4754 | 0.56532 | 188.8521 | 31.8 | 31.0253 | 0.77475 |  | 2026-01-03 09:30 | 187.491 | 191.1 | 193.6 | 31.85 | 31.4754 | 0.37465 | 188.8521 | 30.1 | 31.0253 | -0.92525 |  | 2026-01-03 09:30 | 190.956 | 193.432 | 197.4 | 32.2387 | 31.4754 | 0.76332 | 188.8521 | 30.7 | 31.0253 | -0.32525 |  | 2026-01-03 09:30 | 141.241 | 142.956 | 144.8 | 23.826 | 23.3151 | 0.51092 | 139.8905 | 22.6 | 22.9817 | -0.38167 |  | 2026-01-03 09:30 | 140.425 | 142.145 | 144.8 | 23.6908 | 23.3151 | 0.37576 | 139.8905 | 22.6 | 22.9817 | -0.38167 |  | 2026-01-03 09:30 | 138.825 | 140.54 | 143.6 | 23.4233 | 23.3151 | 0.10826 | 139.8905 | 22.3 | 22.9817 | -0.68167 |  | 2026-01-03 09:30 | 140.016 | 143.468 | 145.6 | 23.9113 | 23.3151 | 0.59626 | 139.8905 | 22.6 | 22.9817 | -0.38167 |  | 2026-01-03 09:30 | 132.937 | 134.598 | 138 | 22.433 | 22.1814 | 0.25159 | 133.0884 | 21.4 | 21.8642 | -0.46421 |  | 2026-01-03 09:30 | 245.2227 | 241.3431 | 3.8796 | 1448.0587 | 233.9 | 237.8919 | -3.9919
2026-01-03 09:20 | 487 | 47.64 | 174.087 | 176.255 | 165.4 | 29.3758 | 29.1265 | 0.24938 | 174.7587 | 27.9 | 28.7099 | -0.80995 |  | 2026-01-03 09:20 | 175.674 | 177.88 | 165.4 | 29.6467 | 29.1265 | 0.52021 | 174.7587 | 28.4 | 28.7099 | -0.30995 |  | 2026-01-03 09:20 | 173.148 | 176.205 | 163.5 | 29.3675 | 29.1265 | 0.24104 | 174.7587 | 27.3 | 28.7099 | -1.4099 |  | 2026-01-03 09:20 | 176.319 | 178.569 | 166.7 | 29.7615 | 29.1265 | 0.63504 | 174.7587 | 27.8 | 28.7099 | -0.90995 |  | 2026-01-03 09:20 | 130.452 | 132.01 | 122.2 | 22.0017 | 21.5752 | 0.42651 | 129.4509 | 20.6 | 21.2666 | -0.66663 |  | 2026-01-03 09:20 | 129.561 | 131.044 | 122.2 | 21.8407 | 21.5752 | 0.26551 | 129.4509 | 21 | 21.2666 | -0.26663 |  | 2026-01-03 09:20 | 128.526 | 130.1 | 121.3 | 21.6833 | 21.5752 | 0.10818 | 129.4509 | 20.5 | 21.2666 | -0.76663 |  | 2026-01-03 09:20 | 129.838 | 133.324 | 123 | 22.2207 | 21.5752 | 0.64551 | 129.4509 | 20.7 | 21.2666 | -0.56663 |  | 2026-01-03 09:20 | 123.154 | 124.675 | 116.6 | 20.7792 | 20.5261 | 0.25308 | 123.1565 | 19.7 | 20.2326 | -0.53256 |  | 2026-01-03 09:20 | 226.677 | 223.3325 | 3.3445 | 1339.9952 | 213.9 | 220.1389 | -6.2389
2026-01-03 09:10 | 445 | 45.92 | 158.782 | 160.727 | 137.5 | 26.7878 | 26.7885 | -0.00070001 | 160.7312 | 25.1 | 26.4055 | -1.3055 |  | 2026-01-03 09:10 | 158.353 | 160.325 | 137 | 26.7208 | 26.7885 | -0.0677 | 160.7312 | 23.8 | 26.4055 | -2.6055 |  | 2026-01-03 09:10 | 157.998 | 160.609 | 136.2 | 26.7682 | 26.7885 | -0.020367 | 160.7312 | 25.3 | 26.4055 | -1.1055 |  | 2026-01-03 09:10 | 161.013 | 163.01 | 138.9 | 27.1683 | 26.7885 | 0.3798 | 160.7312 | 25.8 | 26.4055 | -0.60546 |  | 2026-01-03 09:10 | 118.897 | 120.305 | 101.6 | 20.0508 | 19.8434 | 0.20748 | 119.0601 | 19 | 19.5596 | -0.5596 |  | 2026-01-03 09:10 | 118.212 | 119.599 | 101.2 | 19.9332 | 19.8434 | 0.089809 | 119.0601 | 18.4 | 19.5596 | -1.1596 |  | 2026-01-03 09:10 | 117.041 | 118.451 | 100.8 | 19.7418 | 19.8434 | -0.10152 | 119.0601 | 18.5 | 19.5596 | -1.0596 |  | 2026-01-03 09:10 | 118.349 | 121.178 | 102.3 | 20.1963 | 19.8434 | 0.35298 | 119.0601 | 18.7 | 19.5596 | -0.8596 |  | 2026-01-03 09:10 | 112.186 | 113.537 | 96.9 | 18.9228 | 18.8785 | 0.044336 | 113.271 | 17.7 | 18.6085 | -0.90853 |  | 2026-01-03 09:10 | 206.2902 | 205.4061 | 0.8841 | 1232.4364 | 192.3 | 202.4688 | -10.1688
2026-01-03 09:00 | 402 | 43.62 | 143.114 | 144.823 | 112.4 | 24.1372 | 24.4102 | -0.27301 | 146.4611 | 22.5 | 24.0611 | -1.5611 |  | 2026-01-03 09:00 | 144.616 | 146.366 | 113.2 | 24.3943 | 24.4102 | -0.015846 | 146.4611 | 23.4 | 24.0611 | -0.66111 |  | 2026-01-03 09:00 | 142.056 | 144.178 | 110.9 | 24.0297 | 24.4102 | -0.38051 | 146.4611 | 22.3 | 24.0611 | -1.7611 |  | 2026-01-03 09:00 | 144.519 | 146.274 | 113.1 | 24.379 | 24.4102 | -0.031179 | 146.4611 | 22.7 | 24.0611 | -1.3611 |  | 2026-01-03 09:00 | 106.604 | 107.877 | 82.6 | 17.9795 | 18.0816 | -0.10211 | 108.4897 | 16.8 | 17.823 | -1.023 |  | 2026-01-03 09:00 | 106.185 | 107.431 | 82.8 | 17.9052 | 18.0816 | -0.17645 | 108.4897 | 16.7 | 17.823 | -1.123 |  | 2026-01-03 09:00 | 105.432 | 106.633 | 82.3 | 17.7722 | 18.0816 | -0.30945 | 108.4897 | 16.6 | 17.823 | -1.223 |  | 2026-01-03 09:00 | 106.671 | 109.276 | 83.6 | 18.2127 | 18.0816 | 0.13105 | 108.4897 | 16.8 | 17.823 | -1.023 |  | 2026-01-03 09:00 | 101.143 | 102.34 | 79.2 | 17.0567 | 17.2024 | -0.14575 | 103.2145 | 16 | 16.9564 | -0.95642 |  | 2026-01-03 09:00 | 185.8663 | 187.1696 | -1.3033 | 1123.0175 | 173.8 | 184.4931 | -10.6931
2026-01-03 08:50 | 359 | 41.04 | 127.095 | 128.587 | 89.9 | 21.4312 | 22.0097 | -0.57854 | 132.0583 | 19.9 | 21.695 | -1.795 |  | 2026-01-03 08:50 | 127.058 | 128.575 | 89.8 | 21.4292 | 22.0097 | -0.58054 | 132.0583 | 19.8 | 21.695 | -1.895 |  | 2026-01-03 08:50 | 125.766 | 127.777 | 88.6 | 21.2962 | 22.0097 | -0.71354 | 132.0583 | 19.5 | 21.695 | -2.195 |  | 2026-01-03 08:50 | 128.44 | 129.934 | 90.4 | 21.6557 | 22.0097 | -0.35404 | 132.0583 | 19.8 | 21.695 | -1.895 |  | 2026-01-03 08:50 | 94.491 | 95.571 | 65.8 | 15.9285 | 16.3035 | -0.37499 | 97.8209 | 14.7 | 16.0703 | -1.3703 |  | 2026-01-03 08:50 | 93.713 | 94.784 | 66.1 | 15.7973 | 16.3035 | -0.50615 | 97.8209 | 14.7 | 16.0703 | -1.3703 |  | 2026-01-03 08:50 | 93.403 | 94.413 | 65.7 | 15.7355 | 16.3035 | -0.56799 | 97.8209 | 14.6 | 16.0703 | -1.4703 |  | 2026-01-03 08:50 | 94.687 | 96.933 | 66.8 | 16.1555 | 16.3035 | -0.14799 | 97.8209 | 14.8 | 16.0703 | -1.2703 |  | 2026-01-03 08:50 | 89.818 | 90.872 | 63.2 | 15.1453 | 15.5107 | -0.36542 | 93.0645 | 14 | 15.2889 | -1.2889 |  | 2026-01-03 08:50 | 164.5743 | 168.7635 | -4.1892 | 1012.5812 | 151.8 | 166.3502 | -14.5502
2026-01-03 08:40 | 316 | 39.03 | 110.668 | 111.922 | 70 | 18.6537 | 19.5178 | -0.86418 | 117.1071 | 17.5 | 19.2387 | -1.7387 |  | 2026-01-03 08:40 | 111.492 | 112.8 | 70 | 18.8 | 19.5178 | -0.71785 | 117.1071 | 17.2 | 19.2387 | -2.0387 |  | 2026-01-03 08:40 | 109.894 | 111.531 | 69.1 | 18.5885 | 19.5178 | -0.92935 | 117.1071 | 16.9 | 19.2387 | -2.3387 |  | 2026-01-03 08:40 | 111.925 | 113.216 | 70.6 | 18.8693 | 19.5178 | -0.64851 | 117.1071 | 17.3 | 19.2387 | -1.9387 |  | 2026-01-03 08:40 | 82.046 | 82.995 | 51.1 | 13.8325 | 14.4577 | -0.62516 | 86.746 | 12.5 | 14.2509 | -1.7509 |  | 2026-01-03 08:40 | 82.295 | 83.269 | 51.4 | 13.8782 | 14.4577 | -0.5795 | 86.746 | 12.7 | 14.2509 | -1.5509 |  | 2026-01-03 08:40 | 81.453 | 82.417 | 51.1 | 13.7362 | 14.4577 | -0.7215 | 86.746 | 12.6 | 14.2509 | -1.6509 |  | 2026-01-03 08:40 | 82.678 | 84.834 | 52 | 14.139 | 14.4577 | -0.31866 | 86.746 | 12.8 | 14.2509 | -1.4509 |  | 2026-01-03 08:40 | 78.45 | 79.387 | 49.2 | 13.2312 | 13.7547 | -0.52351 | 82.5281 | 12.1 | 13.558 | -1.458 |  | 2026-01-03 08:40 | 143.7285 | 149.6567 | -5.9282 | 897.9404 | 131.6 | 147.5166 | -15.9166
2026-01-03 08:30 | 273 | 36.74 | 93.698 | 94.74 | 52.5 | 15.79 | 17.0041 | -1.2141 | 102.0244 | 14.2 | 16.7609 | -2.5609 |  | 2026-01-03 08:30 | 95.18 | 96.241 | 52.8 | 16.0402 | 17.0041 | -0.9639 | 102.0244 | 14.9 | 16.7609 | -1.8609 |  | 2026-01-03 08:30 | 93.671 | 95.088 | 52.2 | 15.848 | 17.0041 | -1.1561 | 102.0244 | 14.4 | 16.7609 | -2.3609 |  | 2026-01-03 08:30 | 95.475 | 96.385 | 53.3 | 16.0642 | 17.0041 | -0.9399 | 102.0244 | 14.7 | 16.7609 | -2.0609 |  | 2026-01-03 08:30 | 69.983 | 70.847 | 38.6 | 11.8078 | 12.5956 | -0.78777 | 75.5736 | 10.7 | 12.4155 | -1.7155 |  | 2026-01-03 08:30 | 70.183 | 71.035 | 38.7 | 11.8392 | 12.5956 | -0.75644 | 75.5736 | 10.6 | 12.4155 | -1.8155 |  | 2026-01-03 08:30 | 69.443 | 70.301 | 38.5 | 11.7168 | 12.5956 | -0.87877 | 75.5736 | 10.5 | 12.4155 | -1.9155 |  | 2026-01-03 08:30 | 70.59 | 72.66 | 39.2 | 12.11 | 12.5956 | -0.4856 | 75.5736 | 10.7 | 12.4155 | -1.7155 |  | 2026-01-03 08:30 | 66.909 | 67.749 | 37.1 | 11.2915 | 11.9832 | -0.69166 | 71.8989 | 10.3 | 11.8118 | -1.5118 |  | 2026-01-03 08:30 | 122.5077 | 130.3818 | -7.8742 | 782.291 | 111 | 128.5174 | -17.5174
2026-01-03 08:20 | 230 | 34.44 | 78.416 | 79.312 | 38.3 | 13.2187 | 14.446 | -1.2274 | 86.6762 | 11.6 | 14.2395 | -2.6395 |  | 2026-01-03 08:20 | 78.434 | 79.379 | 37.9 | 13.2298 | 14.446 | -1.2162 | 86.6762 | 11.4 | 14.2395 | -2.8395 |  | 2026-01-03 08:20 | 78.042 | 78.958 | 37.8 | 13.1597 | 14.446 | -1.2864 | 86.6762 | 11.6 | 14.2395 | -2.6395 |  | 2026-01-03 08:20 | 79.605 | 80.531 | 38.6 | 13.4218 | 14.446 | -1.0242 | 86.6762 | 12 | 14.2395 | -2.2395 |  | 2026-01-03 08:20 | 58.029 | 58.793 | 27.9 | 9.7988 | 10.7008 | -0.90193 | 64.2046 | 8.8 | 10.5477 | -1.7477 |  | 2026-01-03 08:20 | 58.093 | 58.84 | 28.1 | 9.8067 | 10.7008 | -0.8941 | 64.2046 | 8.8 | 10.5477 | -1.7477 |  | 2026-01-03 08:20 | 57.95 | 58.725 | 28 | 9.7875 | 10.7008 | -0.91327 | 64.2046 | 8.8 | 10.5477 | -1.7477 |  | 2026-01-03 08:20 | 58.838 | 60.547 | 28.5 | 10.0912 | 10.7008 | -0.6096 | 64.2046 | 8.9 | 10.5477 | -1.6477 |  | 2026-01-03 08:20 | 55.827 | 56.573 | 26.8 | 9.4288 | 10.1805 | -0.75162 | 61.0827 | 8.3 | 10.0349 | -1.7349 |  | 2026-01-03 08:20 | 101.943 | 110.7676 | -8.8246 | 664.6059 | 90.2 | 109.1837 | -18.9837
2026-01-03 08:10 | 188 | 31 | 63.498 | 64.263 | 26.7 | 10.7105 | 11.9551 | -1.2446 | 71.7305 | 9.4 | 11.7841 | -2.3841 |  | 2026-01-03 08:10 | 63.702 | 64.502 | 26.5 | 10.7503 | 11.9551 | -1.2048 | 71.7305 | 9.3 | 11.7841 | -2.4841 |  | 2026-01-03 08:10 | 62.885 | 63.662 | 26.2 | 10.6103 | 11.9551 | -1.3448 | 71.7305 | 9.2 | 11.7841 | -2.5841 |  | 2026-01-03 08:10 | 63.989 | 64.786 | 26.6 | 10.7977 | 11.9551 | -1.1574 | 71.7305 | 9.3 | 11.7841 | -2.4841 |  | 2026-01-03 08:10 | 46.543 | 47.213 | 19.1 | 7.8688 | 8.8556 | -0.98679 | 53.1337 | 6.8 | 8.729 | -1.929 |  | 2026-01-03 08:10 | 46.867 | 47.537 | 19.3 | 7.9228 | 8.8556 | -0.93279 | 53.1337 | 6.8 | 8.729 | -1.929 |  | 2026-01-03 08:10 | 46.492 | 47.171 | 19.2 | 7.8618 | 8.8556 | -0.99379 | 53.1337 | 6.8 | 8.729 | -1.929 |  | 2026-01-03 08:10 | 47.336 | 48.631 | 19.6 | 8.1052 | 8.8556 | -0.75045 | 53.1337 | 6.9 | 8.729 | -1.829 |  | 2026-01-03 08:10 | 44.891 | 45.57 | 18.5 | 7.595 | 8.425 | -0.83003 | 50.5502 | 6.7 | 8.3045 | -1.6045 |  | 2026-01-03 08:10 | 82.2225 | 91.6679 | -9.4454 | 550.0072 | 71.2 | 90.357 | -19.157
2026-01-03 08:00 | 147 | 27.84 | 48.053 | 49.054 | 17.3 | 8.1757 | 9.4535 | -1.2778 | 56.7208 | 6.9 | 9.3183 | -2.4183 |  | 2026-01-03 08:00 | 48.551 | 49.25 | 17.2 | 8.2083 | 9.4535 | -1.2451 | 56.7208 | 7 | 9.3183 | -2.3183 |  | 2026-01-03 08:00 | 48.094 | 48.767 | 17 | 8.1278 | 9.4535 | -1.3256 | 56.7208 | 7 | 9.3183 | -2.3183 |  | 2026-01-03 08:00 | 48.978 | 49.609 | 17.3 | 8.2682 | 9.4535 | -1.1853 | 56.7208 | 7 | 9.3183 | -2.3183 |  | 2026-01-03 08:00 | 35.615 | 36.183 | 12.3 | 6.0305 | 7.0026 | -0.97207 | 42.0154 | 5.1 | 6.9024 | -1.8024 |  | 2026-01-03 08:00 | 35.817 | 36.388 | 12.5 | 6.0647 | 7.0026 | -0.9379 | 42.0154 | 5.1 | 6.9024 | -1.8024 |  | 2026-01-03 08:00 | 35.698 | 36.286 | 12.4 | 6.0477 | 7.0026 | -0.9549 | 42.0154 | 5 | 6.9024 | -1.9024 |  | 2026-01-03 08:00 | 36.337 | 37.437 | 12.7 | 6.2395 | 7.0026 | -0.76307 | 42.0154 | 5.3 | 6.9024 | -1.6024 |  | 2026-01-03 08:00 | 34.285 | 34.853 | 11.8 | 5.8088 | 6.6621 | -0.85324 | 39.9725 | 4.8 | 6.5668 | -1.7668 |  | 2026-01-03 08:00 | 62.9712 | 72.4862 | -9.5151 | 434.9173 | 53.2 | 71.4497 | -18.2497
2026-01-03 07:50 | 108 | 25.26 | 35.045 | 35.611 | 10.4 | 5.9352 | 7.0088 | -1.0736 | 42.0525 | 4.9 | 6.9085 | -2.0085 |  | 2026-01-03 07:50 | 34.406 | 34.98 | 10.2 | 5.83 | 7.0088 | -1.1788 | 42.0525 | 4.7 | 6.9085 | -2.2085 |  | 2026-01-03 07:50 | 34.61 | 35.176 | 10 | 5.8627 | 7.0088 | -1.1461 | 42.0525 | 4.8 | 6.9085 | -2.1085 |  | 2026-01-03 07:50 | 35.125 | 35.7 | 10.3 | 5.95 | 7.0088 | -1.0588 | 42.0525 | 4.8 | 6.9085 | -2.1085 |  | 2026-01-03 07:50 | 25.523 | 26.177 | 7.2 | 4.3628 | 5.1917 | -0.82883 | 31.15 | 3.5 | 5.1174 | -1.6174 |  | 2026-01-03 07:50 | 25.9 | 26.396 | 7.4 | 4.3993 | 5.1917 | -0.79233 | 31.15 | 3.6 | 5.1174 | -1.5174 |  | 2026-01-03 07:50 | 25.655 | 26.299 | 7.4 | 4.3832 | 5.1917 | -0.8085 | 31.15 | 3.6 | 5.1174 | -1.5174 |  | 2026-01-03 07:50 | 26.123 | 27.016 | 7.4 | 4.5027 | 5.1917 | -0.689 | 31.15 | 3.6 | 5.1174 | -1.5174 |  | 2026-01-03 07:50 | 24.721 | 25.215 | 7 | 4.2025 | 4.9392 | -0.73673 | 29.6354 | 3.4 | 4.8686 | -1.4686 |  | 2026-01-03 07:50 | 45.4283 | 53.7409 | -8.3126 | 322.4454 | 36.9 | 52.9724 | -16.0724
2026-01-03 07:40 | 73 | 23.25 | 23.138 | 23.62 | 5.5 | 3.9367 | 4.7708 | -0.83409 | 28.6245 | 3 | 4.7025 | -1.7025 |  | 2026-01-03 07:40 | 22.965 | 23.56 | 5.5 | 3.9267 | 4.7708 | -0.84409 | 28.6245 | 3 | 4.7025 | -1.7025 |  | 2026-01-03 07:40 | 23.111 | 23.592 | 5.2 | 3.932 | 4.7708 | -0.83875 | 28.6245 | 3 | 4.7025 | -1.7025 |  | 2026-01-03 07:40 | 23.103 | 23.589 | 5.5 | 3.9315 | 4.7708 | -0.83925 | 28.6245 | 3 | 4.7025 | -1.7025 |  | 2026-01-03 07:40 | 16.859 | 17.33 | 3.7 | 2.8883 | 3.5339 | -0.64556 | 21.2034 | 2.2 | 3.4834 | -1.2834 |  | 2026-01-03 07:40 | 17.108 | 17.513 | 3.8 | 2.9188 | 3.5339 | -0.61506 | 21.2034 | 2.3 | 3.4834 | -1.1834 |  | 2026-01-03 07:40 | 17.071 | 17.482 | 3.8 | 2.9137 | 3.5339 | -0.62023 | 21.2034 | 2.3 | 3.4834 | -1.1834 |  | 2026-01-03 07:40 | 17.38 | 18.224 | 3.8 | 3.0373 | 3.5339 | -0.49656 | 21.2034 | 2.2 | 3.4834 | -1.2834 |  | 2026-01-03 07:40 | 16.254 | 16.657 | 3.6 | 2.7762 | 3.3621 | -0.58589 | 20.1724 | 2.1 | 3.314 | -1.214 |  | 2026-01-03 07:40 | 30.2612 | 36.5806 | -6.3195 | 219.4839 | 23.1 | 36.0575 | -12.9575
2026-01-03 07:30 | 40 | 22.39 | 13.657 | 14.042 | 2.5 | 2.3403 | 2.6219 | -0.2816 | 15.7316 | 1.7 | 2.5844 | -0.88444 |  | 2026-01-03 07:30 | 13.406 | 14.133 | 2.5 | 2.3555 | 2.6219 | -0.26643 | 15.7316 | 1.7 | 2.5844 | -0.88444 |  | 2026-01-03 07:30 | 13.52 | 13.961 | 2.2 | 2.3268 | 2.6219 | -0.2951 | 15.7316 | 1.6 | 2.5844 | -0.98444 |  | 2026-01-03 07:30 | 13.362 | 14.209 | 2.5 | 2.3682 | 2.6219 | -0.25377 | 15.7316 | 1.7 | 2.5844 | -0.88444 |  | 2026-01-03 07:30 | 9.835 | 10.564 | 1.5 | 1.7607 | 1.9422 | -0.18151 | 11.653 | 1.2 | 1.9144 | -0.7144 |  | 2026-01-03 07:30 | 9.895 | 10.243 | 1.5 | 1.7072 | 1.9422 | -0.23501 | 11.653 | 1.1 | 1.9144 | -0.8144 |  | 2026-01-03 07:30 | 9.928 | 10.281 | 1.5 | 1.7135 | 1.9422 | -0.22867 | 11.653 | 1.2 | 1.9144 | -0.7144 |  | 2026-01-03 07:30 | 10.138 | 10.725 | 1.6 | 1.7875 | 1.9422 | -0.15467 | 11.653 | 1.2 | 1.9144 | -0.7144 |  | 2026-01-03 07:30 | 9.383 | 9.724 | 1.5 | 1.6207 | 1.8477 | -0.22707 | 11.0864 | 1.2 | 1.8213 | -0.62131 |  | 2026-01-03 07:30 | 17.9803 | 20.1042 | -2.1238 | 120.6249 | 12.6 | 19.8167 | -7.2167
2026-01-03 07:20 | 18 | 21.52 | 6.402 | 6.9 | 0.8 | 1.15 | 1.1834 | -0.03343 | 7.1006 | 0.7 | 1.1665 | -0.46651 |  | 2026-01-03 07:20 | 6.707 | 7.312 | 0.8 | 1.2187 | 1.1834 | 0.035237 | 7.1006 | 0.7 | 1.1665 | -0.46651 |  | 2026-01-03 07:20 | 6.596 | 6.877 | 0.6 | 1.1462 | 1.1834 | -0.037263 | 7.1006 | 0.6 | 1.1665 | -0.56651 |  | 2026-01-03 07:20 | 6.637 | 7.296 | 0.8 | 1.216 | 1.1834 | 0.03257 | 7.1006 | 0.7 | 1.1665 | -0.46651 |  | 2026-01-03 07:20 | 4.763 | 5.406 | 0.3 | 0.901 | 0.87661 | 0.024385 | 5.2597 | 0.3 | 0.86408 | -0.56408 |  | 2026-01-03 07:20 | 4.729 | 4.948 | 0.4 | 0.82467 | 0.87661 | -0.051948 | 5.2597 | 0.4 | 0.86408 | -0.46408 |  | 2026-01-03 07:20 | 4.795 | 4.998 | 0.3 | 0.833 | 0.87661 | -0.043615 | 5.2597 | 0.3 | 0.86408 | -0.56408 |  | 2026-01-03 07:20 | 4.865 | 5.479 | 0.4 | 0.91317 | 0.87661 | 0.036552 | 5.2597 | 0.4 | 0.86408 | -0.46408 |  | 2026-01-03 07:20 | 4.503 | 4.712 | 0.3 | 0.78533 | 0.83399 | -0.048657 | 5.0039 | 0.3 | 0.82206 | -0.52206 |  | 2026-01-03 07:20 | 8.988 | 9.0742 | -0.086169 | 54.445 | 4.4 | 8.9444 | -4.5444
2026-01-03 07:10 | 5 | 20.95 | 2.102 | 2.21 | 0.1 | 0.36833 | 0.32938 | 0.038955 | 1.9763 | 0.1 | 0.32467 | -0.22467 |  | 2026-01-03 07:10 | 2.333 | 2.85 | 0.1 | 0.475 | 0.32938 | 0.14562 | 1.9763 | 0.1 | 0.32467 | -0.22467 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.32938 | -0.32938 | 1.9763 | 0 | 0.32467 | -0.32467 |  | 2026-01-03 07:10 | 2.216 | 3.035 | 0.1 | 0.50583 | 0.32938 | 0.17645 | 1.9763 | 0.1 | 0.32467 | -0.22467 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.24398 | -0.24398 | 1.4639 | 0 | 0.2405 | -0.2405 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.24398 | -0.24398 | 1.4639 | 0 | 0.2405 | -0.2405 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.24398 | -0.24398 | 1.4639 | 0 | 0.2405 | -0.2405 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.24398 | -0.24398 | 1.4639 | 0 | 0.2405 | -0.2405 |  | 2026-01-03 07:10 | 0 | 0 | 0 | 0 | 0.23212 | -0.23212 | 1.3927 | 0 | 0.2288 | -0.2288 |  | 2026-01-03 07:10 | 1.3492 | 2.5256 | -1.1764 | 15.1534 | 0.3 | 2.4895 | -2.1895
2026-01-03 07:00 | 0 | 21.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-01-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[110 empty] | Total: - | 17278.9468 | 18096.296 | -817.3491 |  | 17274.4 | 17837.5189 | -563.1189
Sum:- | 39487 |  | 12502.948 |  | 80947.6 |  |  |  |  | 2243.6 | 2326.3236 | -82.7236 | 0.98404 |  | 12835.308 |  | 83567.3 |  |  |  |  | 2276.3 | 2326.3236 | -50.0236 | 0.98439 |  | 13413.807 |  | 84029.6 |  |  |  |  | 2236 | 2326.3236 | -90.3236 | 0.97442 |  | 13604.383 |  | 85303 |  |  |  |  | 2268.2 | 2326.3236 | -58.1236 | 0.98374 |  | 10149.154 |  | 63534.1 |  |  |  |  | 1692.1 | 1723.2027 | -31.1027 | 0.98522 |  | 9996.205 |  | 62736.8 |  |  |  |  | 1666.5 | 1723.2027 | -56.7027 | 0.98338 |  | 9922.467 |  | 62256 |  |  |  |  | 1654.4 | 1723.2027 | -68.8027 | 0.98269 |  | 9975.76 |  | 62678.4 |  |  |  |  | 1663.6 | 1723.2027 | -59.6027 | 0.97172 |  | 9437.192 |  | 59310.5 |  |  |  |  | 1573.7 | 1639.4139 | -65.7139 | 0.98535
Formulas:
Time = [Time]

## 2 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-02-03 19:00 | POA & WMS not working right now | POA & WMS not working right now | 0.091 | 0.096 | 2242.7 | 0.016 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.092 | 0.097 | 2278 | 0.016167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.063 | 0.097 | 2234.6 | 0.016167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.075 | 0.079 | 2267.8 | 0.013167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.087 | 0.091 | 1690.8 | 0.015167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.053 | 0.076 | 1682.2 | 0.012667 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.09 | 0.095 | 1681.4 | 0.015833 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.073 | 0.086 | 1665.4 | 0.014333 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.065 | 0.089 | 1576 | 0.014833 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-02-03 19:00 | 0.13433 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 1 | 98.38%
2026-02-03 18:50 |  |  | 0.005 | 0.07 | 2242.7 | 0.011667 | 0 | 0.011667 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.048 | 0.526 | 2278 | 0.087667 | 0 | 0.087667 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.002 | 0.103 | 2234.6 | 0.017167 | 0 | 0.017167 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.004 | 0.569 | 2267.8 | 0.094833 | 0 | 0.094833 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.003 | 0.087 | 1690.8 | 0.0145 | 0 | 0.0145 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.072 | 0.091 | 1682.2 | 0.015167 | 0 | 0.015167 | 0 | 0 | 0 | 0 |  | 2026-02-03 18:50 | 0.097 | 0.102 | 1681.4 | 0.017 | 0 | 0.017 | 0 | 0 | 0 | 0 |  | 2026-02-03 18:50 | 0.083 | 0.273 | 1665.4 | 0.0455 | 0 | 0.0455 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.076 | 0.082 | 1576 | 0.013667 | 0 | 0.013667 | 0 | 0.1 | 0 | 0.1 |  | 2026-02-03 18:50 | 0.31717 | 0 | 0.31717 | 0 | 0.7 | 0 | 0.7 | 2 | 91.54%
2026-02-03 18:40 |  |  | 1.275 | 1.341 | 2242.6 | 0.2235 | 0 | 0.2235 | 0 | 0.4 | 0 | 0.4 |  | 2026-02-03 18:40 | 1.48 | 1.859 | 2277.9 | 0.30983 | 0 | 0.30983 | 0 | 0.5 | 0 | 0.5 |  | 2026-02-03 18:40 | 1.19 | 1.263 | 2234.5 | 0.2105 | 0 | 0.2105 | 0 | 0.4 | 0 | 0.4 |  | 2026-02-03 18:40 | 1.275 | 1.739 | 2267.7 | 0.28983 | 0 | 0.28983 | 0 | 0.4 | 0 | 0.4 |  | 2026-02-03 18:40 | 0.756 | 0.816 | 1690.7 | 0.136 | 0 | 0.136 | 0 | 0.3 | 0 | 0.3 |  | 2026-02-03 18:40 | 0.756 | 0.795 | 1682.2 | 0.1325 | 0 | 0.1325 | 0 | 0.3 | 0 | 0.3 |  | 2026-02-03 18:40 | 0.703 | 0.739 | 1681.4 | 0.12317 | 0 | 0.12317 | 0 | 0.3 | 0 | 0.3 |  | 2026-02-03 18:40 | 0.816 | 0.991 | 1665.3 | 0.16517 | 0 | 0.16517 | 0 | 0.3 | 0 | 0.3 |  | 2026-02-03 18:40 | 0.648 | 0.681 | 1575.9 | 0.1135 | 0 | 0.1135 | 0 | 0.2 | 0 | 0.2 |  | 2026-02-03 18:40 | 1.704 | 0 | 1.704 | 0 | 3.1 | 0 | 3.1 | 3 | 97.38%
2026-02-03 18:30 |  |  | 4.39 | 4.607 | 2242.2 | 0.76783 | 0 | 0.76783 | 0 | 1.2 | 0 | 1.2 |  | 2026-02-03 18:30 | 5.036 | 5.207 | 2277.4 | 0.86783 | 0 | 0.86783 | 0 | 1.2 | 0 | 1.2 |  | 2026-02-03 18:30 | 4.416 | 4.634 | 2234.1 | 0.77233 | 0 | 0.77233 | 0 | 1.1 | 0 | 1.1 |  | 2026-02-03 18:30 | 4.506 | 4.784 | 2267.3 | 0.79733 | 0 | 0.79733 | 0 | 1.2 | 0 | 1.2 |  | 2026-02-03 18:30 | 3.208 | 3.373 | 1690.4 | 0.56217 | 0 | 0.56217 | 0 | 0.8 | 0 | 0.8 |  | 2026-02-03 18:30 | 3.042 | 3.198 | 1681.9 | 0.533 | 0 | 0.533 | 0 | 0.9 | 0 | 0.9 |  | 2026-02-03 18:30 | 3.182 | 3.346 | 1681.1 | 0.55767 | 0 | 0.55767 | 0 | 0.9 | 0 | 0.9 |  | 2026-02-03 18:30 | 3.144 | 3.619 | 1665 | 0.60317 | 0 | 0.60317 | 0 | 0.8 | 0 | 0.8 |  | 2026-02-03 18:30 | 2.93 | 3.081 | 1575.7 | 0.5135 | 0 | 0.5135 | 0 | 0.8 | 0 | 0.8 |  | 2026-02-03 18:30 | 5.9748 | 0 | 5.9748 | 0 | 8.9 | 0 | 8.9 | 4 | 98.34%
2026-02-03 18:20 |  |  | 9.314 | 9.678 | 2241 | 1.613 | 0 | 1.613 | 0 | 2.1 | 0 | 2.1 |  | 2026-02-03 18:20 | 10.158 | 10.815 | 2276.2 | 1.8025 | 0 | 1.8025 | 0 | 2.3 | 0 | 2.3 |  | 2026-02-03 18:20 | 9.653 | 10.041 | 2233 | 1.6735 | 0 | 1.6735 | 0 | 2.3 | 0 | 2.3 |  | 2026-02-03 18:20 | 9.804 | 10.183 | 2266.1 | 1.6972 | 0 | 1.6972 | 0 | 2.2 | 0 | 2.2 |  | 2026-02-03 18:20 | 7.148 | 7.458 | 1689.6 | 1.243 | 0 | 1.243 | 0 | 1.7 | 0 | 1.7 |  | 2026-02-03 18:20 | 6.974 | 7.277 | 1681 | 1.2128 | 0 | 1.2128 | 0 | 1.5 | 0 | 1.5 |  | 2026-02-03 18:20 | 7.012 | 7.317 | 1680.2 | 1.2195 | 0 | 1.2195 | 0 | 1.6 | 0 | 1.6 |  | 2026-02-03 18:20 | 6.55 | 6.867 | 1664.2 | 1.1445 | 0 | 1.1445 | 0 | 1.5 | 0 | 1.5 |  | 2026-02-03 18:20 | 6.351 | 6.636 | 1574.9 | 1.106 | 0 | 1.106 | 0 | 1.5 | 0 | 1.5 |  | 2026-02-03 18:20 | 12.712 | 0 | 12.712 | 0 | 16.7 | 0 | 16.7 | 5 | 98.49%
|  |  | 16.688 | 17.118 | 2238.9 | 2.853 | 0 | 2.853 | 0 | 3.6 | 0 | 3.6 |  | 2026-02-03 18:10 | 17.814 | 18.284 | 2273.9 | 3.0473 | 0 | 3.0473 | 0 | 3.6 | 0 | 3.6 |  | 2026-02-03 18:10 | 17.226 | 17.68 | 2230.7 | 2.9467 | 0 | 2.9467 | 0 | 3.6 | 0 | 3.6 |  | 2026-02-03 18:10 | 17.365 | 17.823 | 2263.9 | 2.9705 | 0 | 2.9705 | 0 | 3.7 | 0 | 3.7 |  | 2026-02-03 18:10 | 12.849 | 13.263 | 1687.9 | 2.2105 | 0 | 2.2105 | 0 | 2.7 | 0 | 2.7 |  | 2026-02-03 18:10 | 12.468 | 12.878 | 1679.5 | 2.1463 | 0 | 2.1463 | 0 | 2.7 | 0 | 2.7 |  | 2026-02-03 18:10 | 12.59 | 13.002 | 1678.6 | 2.167 | 0 | 2.167 | 0 | 2.6 | 0 | 2.6 |  | 2026-02-03 18:10 | 11.337 | 11.963 | 1662.7 | 1.9938 | 0 | 1.9938 | 0 | 2.4 | 0 | 2.4 |  | 2026-02-03 18:10 | 11.609 | 12.005 | 1573.4 | 2.0008 | 0 | 2.0008 | 0 | 2.5 | 0 | 2.5 |  | 0 | 22.336 | 0 | 22.336 | 0 | 27.4 | 0 | 27.4 | 6 | 98.29%
|  |  | 26.323 | 26.879 | 2235.3 | 4.4798 | 0 | 4.4798 | 0 | 5.4 | 0 | 5.4 |  | 2026-02-03 18:00 | 27.258 | 27.828 | 2270.3 | 4.638 | 0 | 4.638 | 0 | 6 | 0 | 6 |  | 2026-02-03 18:00 | 26.916 | 27.495 | 2227.1 | 4.5825 | 0 | 4.5825 | 0 | 5.5 | 0 | 5.5 |  | 2026-02-03 18:00 | 27.015 | 27.583 | 2260.2 | 4.5972 | 0 | 4.5972 | 0 | 5.5 | 0 | 5.5 |  | 2026-02-03 18:00 | 20.139 | 20.63 | 1685.2 | 3.4383 | 0 | 3.4383 | 0 | 4.2 | 0 | 4.2 |  | 2026-02-03 18:00 | 19.514 | 19.988 | 1676.8 | 3.3313 | 0 | 3.3313 | 0 | 4 | 0 | 4 |  | 2026-02-03 18:00 | 19.638 | 20.123 | 1676 | 3.3538 | 0 | 3.3538 | 0 | 4.1 | 0 | 4.1 |  | 2026-02-03 18:00 | 18.625 | 19.441 | 1660.3 | 3.2402 | 0 | 3.2402 | 0 | 3.9 | 0 | 3.9 |  | 2026-02-03 18:00 | 18.238 | 18.69 | 1570.9 | 3.115 | 0 | 3.115 | 0 | 3.7 | 0 | 3.7 |  | 0 | 34.7762 | 0 | 34.7762 | 0 | 42.3 | 0 | 42.3 | 7 | 98.21%
|  |  | 38.874 | 39.538 | 2229.9 | 6.5897 | 0 | 6.5897 | 0 | 7.6 | 0 | 7.6 |  | 2026-02-03 17:50 | 42.859 | 43.587 | 2264.3 | 7.2645 | 0 | 7.2645 | 0 | 7.3 | 0 | 7.3 |  | 2026-02-03 17:50 | 39.648 | 40.33 | 2221.6 | 6.7217 | 0 | 6.7217 | 0 | 7.7 | 0 | 7.7 |  | 2026-02-03 17:50 | 39.735 | 40.426 | 2254.7 | 6.7377 | 0 | 6.7377 | 0 | 7.7 | 0 | 7.7 |  | 2026-02-03 17:50 | 29.888 | 30.464 | 1681 | 5.0773 | 0 | 5.0773 | 0 | 5.8 | 0 | 5.8 |  | 2026-02-03 17:50 | 28.964 | 29.525 | 1672.8 | 4.9208 | 0 | 4.9208 | 0 | 5.7 | 0 | 5.7 |  | 2026-02-03 17:50 | 29.198 | 29.76 | 1671.9 | 4.96 | 0 | 4.96 | 0 | 5.7 | 0 | 5.7 |  | 2026-02-03 17:50 | 28.28 | 29.062 | 1656.4 | 4.8437 | 0 | 4.8437 | 0 | 5.5 | 0 | 5.5 |  | 2026-02-03 17:50 | 27.077 | 27.627 | 1567.2 | 4.6045 | 0 | 4.6045 | 0 | 5.2 | 0 | 5.2 |  | 0 | 51.7198 | 0 | 51.7198 | 0 | 58.2 | 0 | 58.2 | 8 | 97.16%
|  |  | 52.645 | 53.436 | 2222.3 | 8.906 | 0 | 8.906 | 0 | 9.5 | 0 | 9.5 |  | 2026-02-03 17:40 | 53.337 | 54.177 | 2257 | 9.0295 | 0 | 9.0295 | 0 | 22.7 | 0 | 22.7 |  | 2026-02-03 17:40 | 52.983 | 53.795 | 2213.9 | 8.9658 | 0 | 8.9658 | 0 | 10 | 0 | 10 |  | 2026-02-03 17:40 | 53.19 | 54.016 | 2247 | 9.0027 | 0 | 9.0027 | 0 | 10 | 0 | 10 |  | 2026-02-03 17:40 | 40.144 | 40.85 | 1675.2 | 6.8083 | 0 | 6.8083 | 0 | 7.5 | 0 | 7.5 |  | 2026-02-03 17:40 | 38.998 | 39.715 | 1667.1 | 6.6192 | 0 | 6.6192 | 0 | 7.3 | 0 | 7.3 |  | 2026-02-03 17:40 | 39.232 | 39.906 | 1666.2 | 6.651 | 0 | 6.651 | 0 | 7.3 | 0 | 7.3 |  | 2026-02-03 17:40 | 38.073 | 39.009 | 1650.9 | 6.5015 | 0 | 6.5015 | 0 | 7.1 | 0 | 7.1 |  | 2026-02-03 17:40 | 36.125 | 36.739 | 1562 | 6.1232 | 0 | 6.1232 | 0 | 6.7 | 0 | 6.7 |  | 0 | 68.6072 | 0 | 68.6072 | 0 | 88.1 | 0 | 88.1 | 9 | 98.51%
|  |  | 65.601 | 66.479 | 2212.8 | 11.0798 | 0 | 11.0798 | 0 | 12.3 | 0 | 12.3 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 17:30 | 66.516 | 67.433 | 2203.9 | 11.2388 | 0 | 11.2388 | 0 | 12.1 | 0 | 12.1 |  | 2026-02-03 17:30 | 66.832 | 67.74 | 2237 | 11.29 | 0 | 11.29 | 0 | 12.2 | 0 | 12.2 |  | 2026-02-03 17:30 | 50.17 | 50.965 | 1667.7 | 8.4942 | 0 | 8.4942 | 0 | 9.1 | 0 | 9.1 |  | 2026-02-03 17:30 | 48.867 | 49.626 | 1659.8 | 8.271 | 0 | 8.271 | 0 | 9 | 0 | 9 |  | 2026-02-03 17:30 | 49.259 | 50.04 | 1658.9 | 8.34 | 0 | 8.34 | 0 | 9.1 | 0 | 9.1 |  | 2026-02-03 17:30 | 47.833 | 49.238 | 1643.8 | 8.2063 | 0 | 8.2063 | 0 | 8.9 | 0 | 8.9 |  | 2026-02-03 17:30 | 45.275 | 46.011 | 1555.3 | 7.6685 | 0 | 7.6685 | 0 | 8.4 | 0 | 8.4 |  | 0 | 74.5887 | 0 | 74.5887 | 0 | 81.1 | 0 | 81.1
2026-02-03 17:20 |  |  | 79.78 | 80.819 | 2200.5 | 13.4698 | 0 | 13.4698 | 0 | 14.4 | 0 | 14.4 |  | 2026-02-03 17:20 | 81.294 | 82.373 | 2234.3 | 13.7288 | 0 | 13.7288 | 0 | 14.7 | 0 | 14.7 |  | 2026-02-03 17:20 | 80.127 | 81.46 | 2191.8 | 13.5767 | 0 | 13.5767 | 0 | 14.7 | 0 | 14.7 |  | 2026-02-03 17:20 | 80.495 | 81.555 | 2224.8 | 13.5925 | 0 | 13.5925 | 0 | 14.8 | 0 | 14.8 |  | 2026-02-03 17:20 | 60.529 | 61.233 | 1658.6 | 10.2055 | 0 | 10.2055 | 0 | 11.1 | 0 | 11.1 |  | 2026-02-03 17:20 | 59.243 | 60.096 | 1650.8 | 10.016 | 0 | 10.016 | 0 | 10.8 | 0 | 10.8 |  | 2026-02-03 17:20 | 59.514 | 60.377 | 1649.8 | 10.0628 | 0 | 10.0628 | 0 | 11 | 0 | 11 |  | 2026-02-03 17:20 | 58.026 | 59.736 | 1634.9 | 9.956 | 0 | 9.956 | 0 | 10.7 | 0 | 10.7 |  | 2026-02-03 17:20 | 54.912 | 55.754 | 1546.9 | 9.2923 | 0 | 9.2923 | 0 | 10.1 | 0 | 10.1 |  | 2026-02-03 17:20 | 103.9005 | 0 | 103.9005 | 0 | 112.3 | 0 | 112.3
2026-02-03 17:10 |  |  | 94.541 | 95.709 | 2186.1 | 15.9515 | 0 | 15.9515 | 0 | 16.9 | 0 | 16.9 |  | 2026-02-03 17:10 | 97.501 | 98.542 | 2219.6 | 16.4237 | 0 | 16.4237 | 0 | 17.5 | 0 | 17.5 |  | 2026-02-03 17:10 | 95.454 | 97.21 | 2177.1 | 16.2017 | 0 | 16.2017 | 0 | 17.3 | 0 | 17.3 |  | 2026-02-03 17:10 | 96.377 | 97.587 | 2210 | 16.2645 | 0 | 16.2645 | 0 | 17.5 | 0 | 17.5 |  | 2026-02-03 17:10 | 71.982 | 72.974 | 1647.5 | 12.1623 | 0 | 12.1623 | 0 | 13.1 | 0 | 13.1 |  | 2026-02-03 17:10 | 70.8 | 71.762 | 1640 | 11.9603 | 0 | 11.9603 | 0 | 12.8 | 0 | 12.8 |  | 2026-02-03 17:10 | 71.018 | 71.99 | 1638.8 | 11.9983 | 0 | 11.9983 | 0 | 12.7 | 0 | 12.7 |  | 2026-02-03 17:10 | 69.388 | 71.414 | 1624.2 | 11.9023 | 0 | 11.9023 | 0 | 12.4 | 0 | 12.4 |  | 2026-02-03 17:10 | 65.757 | 66.699 | 1536.8 | 11.1165 | 0 | 11.1165 | 0 | 11.8 | 0 | 11.8 |  | 2026-02-03 17:10 | 123.9812 | 0 | 123.9812 | 0 | 132 | 0 | 132
2026-02-03 17:00 |  |  | 110.341 | 111.715 | 2169.2 | 18.6192 | 0 | 18.6192 | 0 | 19.8 | 0 | 19.8 |  | 2026-02-03 17:00 | 113.126 | 114.265 | 2202.1 | 19.0442 | 0 | 19.0442 | 0 | 43.9 | 0 | 43.9 |  | 2026-02-03 17:00 | 111.491 | 113.402 | 2159.8 | 18.9003 | 0 | 18.9003 | 0 | 19.8 | 0 | 19.8 |  | 2026-02-03 17:00 | 112.241 | 113.673 | 2192.5 | 18.9455 | 0 | 18.9455 | 0 | 19.9 | 0 | 19.9 |  | 2026-02-03 17:00 | 84.171 | 85.28 | 1634.4 | 14.2133 | 0 | 14.2133 | 0 | 14.9 | 0 | 14.9 |  | 2026-02-03 17:00 | 82.482 | 83.56 | 1627.2 | 13.9267 | 0 | 13.9267 | 0 | 14.7 | 0 | 14.7 |  | 2026-02-03 17:00 | 82.775 | 83.848 | 1626.1 | 13.9747 | 0 | 13.9747 | 0 | 14.7 | 0 | 14.7 |  | 2026-02-03 17:00 | 80.834 | 82.973 | 1611.8 | 13.8288 | 0 | 13.8288 | 0 | 14.3 | 0 | 14.3 |  | 2026-02-03 17:00 | 76.437 | 77.459 | 1525 | 12.9098 | 0 | 12.9098 | 0 | 13.8 | 0 | 13.8 |  | 2026-02-03 17:00 | 144.3625 | 0 | 144.3625 | 0 | 175.8 | 0 | 175.8
2026-02-03 16:50 |  |  | 126.827 | 128.445 | 2149.4 | 21.4075 | 0 | 21.4075 | 0 | 47.5 | 0 | 47.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 16:50 | 127.598 | 130.045 | 2140 | 21.6742 | 0 | 21.6742 | 0 | 22.6 | 0 | 22.6 |  | 2026-02-03 16:50 | 128.503 | 130.156 | 2172.6 | 21.6927 | 0 | 21.6927 | 0 | 22.8 | 0 | 22.8 |  | 2026-02-03 16:50 | 96.292 | 97.531 | 1619.5 | 16.2552 | 0 | 16.2552 | 0 | 17 | 0 | 17 |  | 2026-02-03 16:50 | 94.543 | 95.74 | 1612.5 | 15.9567 | 0 | 15.9567 | 0 | 16.7 | 0 | 16.7 |  | 2026-02-03 16:50 | 94.955 | 96.157 | 1611.4 | 16.0262 | 0 | 16.0262 | 0 | 17.1 | 0 | 17.1 |  | 2026-02-03 16:50 | 92.799 | 95.098 | 1597.5 | 15.8497 | 0 | 15.8497 | 0 | 16.8 | 0 | 16.8 |  | 2026-02-03 16:50 | 87.636 | 88.727 | 1511.2 | 14.7878 | 0 | 14.7878 | 0 | 15.6 | 0 | 15.6 |  | 2026-02-03 16:50 | 143.6498 | 0 | 143.6498 | 0 | 176.1 | 0 | 176.1
2026-02-03 16:40 |  |  | 142.663 | 144.097 | 2126.9 | 24.0162 | 0 | 24.0162 | 0 | 0 | 0 | 0 |  | 2026-02-03 16:40 | 147.542 | 148.628 | 2158.2 | 24.7713 | 0 | 24.7713 | 0 | 24.6 | 0 | 24.6 |  | 2026-02-03 16:40 | 142.847 | 145.335 | 2117.4 | 24.2225 | 0 | 24.2225 | 0 | 25 | 0 | 25 |  | 2026-02-03 16:40 | 144.077 | 145.989 | 2149.8 | 24.3315 | 0 | 24.3315 | 0 | 25.3 | 0 | 25.3 |  | 2026-02-03 16:40 | 108.173 | 109.564 | 1602.5 | 18.2607 | 0 | 18.2607 | 0 | 19 | 0 | 19 |  | 2026-02-03 16:40 | 106.402 | 107.76 | 1595.8 | 17.96 | 0 | 17.96 | 0 | 19 | 0 | 19 |  | 2026-02-03 16:40 | 106.87 | 108.245 | 1594.3 | 18.0408 | 0 | 18.0408 | 0 | 18.6 | 0 | 18.6 |  | 2026-02-03 16:40 | 104.787 | 107.699 | 1580.7 | 17.9498 | 0 | 17.9498 | 0 | 18.3 | 0 | 18.3 |  | 2026-02-03 16:40 | 99.258 | 100.525 | 1495.6 | 16.7542 | 0 | 16.7542 | 0 | 17.4 | 0 | 17.4 |  | 2026-02-03 16:40 | 186.307 | 0 | 186.307 | 0 | 167.2 | 0 | 167.2
2026-02-03 16:30 |  |  | 159.063 | 161.142 | 2101.9 | 26.857 | 0 | 26.857 | 0 | 27.2 | 0 | 27.2 |  | 2026-02-03 16:30 | 161.67 | 163.849 | 2133.6 | 27.3082 | 0 | 27.3082 | 0 | 27.2 | 0 | 27.2 |  | 2026-02-03 16:30 | 158.938 | 162.374 | 2092.4 | 27.0623 | 0 | 27.0623 | 0 | 27.7 | 0 | 27.7 |  | 2026-02-03 16:30 | 160.661 | 162.827 | 2124.5 | 27.1378 | 0 | 27.1378 | 0 | 28 | 0 | 28 |  | 2026-02-03 16:30 | 119.889 | 121.468 | 1583.5 | 20.2447 | 0 | 20.2447 | 0 | 21 | 0 | 21 |  | 2026-02-03 16:30 | 118.328 | 119.85 | 1576.8 | 19.975 | 0 | 19.975 | 0 | 20.3 | 0 | 20.3 |  | 2026-02-03 16:30 | 118.209 | 119.754 | 1575.7 | 19.959 | 0 | 19.959 | 0 | 20.5 | 0 | 20.5 |  | 2026-02-03 16:30 | 115.87 | 119.004 | 1562.4 | 19.834 | 0 | 19.834 | 0 | 20.1 | 0 | 20.1 |  | 2026-02-03 16:30 | 109.759 | 111.137 | 1478.2 | 18.5228 | 0 | 18.5228 | 0 | 18.9 | 0 | 18.9 |  | 2026-02-03 16:30 | 206.9008 | 0 | 206.9008 | 0 | 210.9 | 0 | 210.9
2026-02-03 16:20 |  |  | 170.764 | 173.031 | 2074.7 | 28.8385 | 0 | 28.8385 | 0 | 29.5 | 0 | 29.5 |  | 2026-02-03 16:20 | 173.775 | 176.171 | 2106.4 | 29.3618 | 0 | 29.3618 | 0 | 30.5 | 0 | 30.5 |  | 2026-02-03 16:20 | 171.669 | 175.394 | 2064.7 | 29.2323 | 0 | 29.2323 | 0 | 29.2 | 0 | 29.2 |  | 2026-02-03 16:20 | 173.221 | 175.574 | 2096.5 | 29.2623 | 0 | 29.2623 | 0 | 29.4 | 0 | 29.4 |  | 2026-02-03 16:20 | 129.888 | 131.572 | 1562.5 | 21.9287 | 0 | 21.9287 | 0 | 22 | 0 | 22 |  | 2026-02-03 16:20 | 127.903 | 129.603 | 1556.5 | 21.6005 | 0 | 21.6005 | 0 | 21.8 | 0 | 21.8 |  | 2026-02-03 16:20 | 128.327 | 130.004 | 1555.2 | 21.6673 | 0 | 21.6673 | 0 | 21.8 | 0 | 21.8 |  | 2026-02-03 16:20 | 126.151 | 129.447 | 1542.3 | 21.5745 | 0 | 21.5745 | 0 | 21.7 | 0 | 21.7 |  | 2026-02-03 16:20 | 118.92 | 120.489 | 1459.3 | 20.0815 | 0 | 20.0815 | 0 | 20.5 | 0 | 20.5 |  | 2026-02-03 16:20 | 223.5475 | 0 | 223.5475 | 0 | 226.4 | 0 | 226.4
2026-02-03 16:10 |  |  | 184.93 | 187.48 | 2045.2 | 31.2467 | 0 | 31.2467 | 0 | 32.3 | 0 | 32.3 |  | 2026-02-03 16:10 | 188.006 | 190.675 | 2075.9 | 31.7792 | 0 | 31.7792 | 0 | 33.3 | 0 | 33.3 |  | 2026-02-03 16:10 | 184.196 | 188.424 | 2035.5 | 31.404 | 0 | 31.404 | 0 | 31.9 | 0 | 31.9 |  | 2026-02-03 16:10 | 186.268 | 188.874 | 2067.1 | 31.479 | 0 | 31.479 | 0 | 32.3 | 0 | 32.3 |  | 2026-02-03 16:10 | 139.217 | 141.079 | 1540.5 | 23.5132 | 0 | 23.5132 | 0 | 24.1 | 0 | 24.1 |  | 2026-02-03 16:10 | 137.502 | 139.341 | 1534.7 | 23.2235 | 0 | 23.2235 | 0 | 23.8 | 0 | 23.8 |  | 2026-02-03 16:10 | 137.511 | 139.354 | 1533.4 | 23.2257 | 0 | 23.2257 | 0 | 24 | 0 | 24 |  | 2026-02-03 16:10 | 135.416 | 138.993 | 1520.6 | 23.1655 | 0 | 23.1655 | 0 | 23.2 | 0 | 23.2 |  | 2026-02-03 16:10 | 127.996 | 129.708 | 1438.8 | 21.618 | 0 | 21.618 | 0 | 21.9 | 0 | 21.9 |  | 2026-02-03 16:10 | 240.6547 | 0 | 240.6547 | 0 | 246.8 | 0 | 246.8
2026-02-03 16:00 |  |  | 198.92 | 201.663 | 2012.9 | 33.6105 | 0 | 33.6105 | 0 | 34.8 | 0 | 34.8 |  | 2026-02-03 16:00 | 202.926 | 205.856 | 2042.6 | 34.3093 | 0 | 34.3093 | 0 | 34 | 0 | 34 |  | 2026-02-03 16:00 | 199.066 | 203.563 | 2003.6 | 33.9272 | 0 | 33.9272 | 0 | 34.3 | 0 | 34.3 |  | 2026-02-03 16:00 | 200.923 | 203.776 | 2034.8 | 33.9627 | 0 | 33.9627 | 0 | 34.7 | 0 | 34.7 |  | 2026-02-03 16:00 | 150.626 | 152.656 | 1516.4 | 25.4427 | 0 | 25.4427 | 0 | 26 | 0 | 26 |  | 2026-02-03 16:00 | 148.595 | 150.621 | 1510.9 | 25.1035 | 0 | 25.1035 | 0 | 25.7 | 0 | 25.7 |  | 2026-02-03 16:00 | 148.887 | 150.879 | 1509.4 | 25.1465 | 0 | 25.1465 | 0 | 25.4 | 0 | 25.4 |  | 2026-02-03 16:00 | 146.588 | 150.492 | 1497.4 | 25.082 | 0 | 25.082 | 0 | 25.2 | 0 | 25.2 |  | 2026-02-03 16:00 | 138.311 | 140.147 | 1416.9 | 23.3578 | 0 | 23.3578 | 0 | 23.8 | 0 | 23.8 |  | 2026-02-03 16:00 | 259.9422 | 0 | 259.9422 | 0 | 263.9 | 0 | 263.9
2026-02-03 15:50 |  |  | 211.228 | 214.227 | 1978.1 | 35.7045 | 0 | 35.7045 | 0 | 35.7 | 0 | 35.7 |  | 2026-02-03 15:50 | 215.172 | 218.294 | 2008.6 | 36.3823 | 0 | 36.3823 | 0 | 37.4 | 0 | 37.4 |  | 2026-02-03 15:50 | 211.105 | 215.658 | 1969.3 | 35.943 | 0 | 35.943 | 0 | 36.2 | 0 | 36.2 |  | 2026-02-03 15:50 | 213.614 | 216.735 | 2000.1 | 36.1225 | 0 | 36.1225 | 0 | 36.5 | 0 | 36.5 |  | 2026-02-03 15:50 | 159.82 | 162.056 | 1490.4 | 27.0093 | 0 | 27.0093 | 0 | 27.4 | 0 | 27.4 |  | 2026-02-03 15:50 | 157.938 | 160.116 | 1485.2 | 26.686 | 0 | 26.686 | 0 | 27 | 0 | 27 |  | 2026-02-03 15:50 | 157.908 | 160.101 | 1484 | 26.6835 | 0 | 26.6835 | 0 | 27 | 0 | 27 |  | 2026-02-03 15:50 | 155.797 | 160.15 | 1472.2 | 26.6917 | 0 | 26.6917 | 0 | 26.7 | 0 | 26.7 |  | 2026-02-03 15:50 | 147.187 | 149.186 | 1393.1 | 24.8643 | 0 | 24.8643 | 0 | 25.2 | 0 | 25.2 |  | 2026-02-03 15:50 | 276.0872 | 0 | 276.0872 | 0 | 279.1 | 0 | 279.1
2026-02-03 15:40 |  |  | 222.751 | 225.983 | 1942.4 | 37.6638 | 0 | 37.6638 | 0 | 38.1 | 0 | 38.1 |  | 2026-02-03 15:40 | 227.551 | 230.993 | 1971.2 | 38.4988 | 0 | 38.4988 | 0 | 37.8 | 0 | 37.8 |  | 2026-02-03 15:40 | 222.803 | 227.878 | 1933.1 | 37.9797 | 0 | 37.9797 | 0 | 37.6 | 0 | 37.6 |  | 2026-02-03 15:40 | 225.734 | 229.125 | 1963.6 | 38.1875 | 0 | 38.1875 | 0 | 38.2 | 0 | 38.2 |  | 2026-02-03 15:40 | 168.639 | 171.033 | 1463 | 28.5055 | 0 | 28.5055 | 0 | 28.5 | 0 | 28.5 |  | 2026-02-03 15:40 | 166.788 | 169.175 | 1458.2 | 28.1958 | 0 | 28.1958 | 0 | 28.2 | 0 | 28.2 |  | 2026-02-03 15:40 | 166.691 | 169.054 | 1457 | 28.1757 | 0 | 28.1757 | 0 | 28.3 | 0 | 28.3 |  | 2026-02-03 15:40 | 164.66 | 169.096 | 1445.5 | 28.1827 | 0 | 28.1827 | 0 | 28.3 | 0 | 28.3 |  | 2026-02-03 15:40 | 155.717 | 157.88 | 1367.9 | 26.3133 | 0 | 26.3133 | 0 | 26.7 | 0 | 26.7 |  | 2026-02-03 15:40 | 291.7028 | 0 | 291.7028 | 0 | 291.7 | 0 | 291.7
2026-02-03 15:30 |  |  | 232.654 | 235.72 | 1904.3 | 39.2867 | 0 | 39.2867 | 0 | 38.9 | 0 | 38.9 |  | 2026-02-03 15:30 | 236.589 | 240.216 | 1933.4 | 40.036 | 0 | 40.036 | 0 | 40.8 | 0 | 40.8 |  | 2026-02-03 15:30 | 231.424 | 237.016 | 1895.5 | 39.5027 | 0 | 39.5027 | 0 | 39.3 | 0 | 39.3 |  | 2026-02-03 15:30 | 235.06 | 238.664 | 1925.4 | 39.7773 | 0 | 39.7773 | 0 | 39.9 | 0 | 39.9 |  | 2026-02-03 15:30 | 175.161 | 177.702 | 1434.5 | 29.617 | 0 | 29.617 | 0 | 30.1 | 0 | 30.1 |  | 2026-02-03 15:30 | 173.968 | 176.456 | 1430 | 29.4093 | 0 | 29.4093 | 0 | 29.9 | 0 | 29.9 |  | 2026-02-03 15:30 | 173.703 | 176.274 | 1428.7 | 29.379 | 0 | 29.379 | 0 | 29.8 | 0 | 29.8 |  | 2026-02-03 15:30 | 171.975 | 176.656 | 1417.2 | 29.4427 | 0 | 29.4427 | 0 | 29.1 | 0 | 29.1 |  | 2026-02-03 15:30 | 162.687 | 165.014 | 1341.2 | 27.5023 | 0 | 27.5023 | 0 | 27.6 | 0 | 27.6 |  | 2026-02-03 15:30 | 303.953 | 0 | 303.953 | 0 | 305.4 | 0 | 305.4
2026-02-03 15:20 |  |  | 241.897 | 245.581 | 1865.4 | 40.9302 | 0 | 40.9302 | 0 | 41 | 0 | 41 |  | 2026-02-03 15:20 | 246.535 | 250.391 | 1892.6 | 41.7318 | 0 | 41.7318 | 0 | 41.8 | 0 | 41.8 |  | 2026-02-03 15:20 | 241.338 | 247.292 | 1856.2 | 41.2153 | 0 | 41.2153 | 0 | 41.6 | 0 | 41.6 |  | 2026-02-03 15:20 | 245.061 | 248.869 | 1885.5 | 41.4782 | 0 | 41.4782 | 0 | 42.1 | 0 | 42.1 |  | 2026-02-03 15:20 | 182.858 | 185.511 | 1404.4 | 30.9185 | 0 | 30.9185 | 0 | 31.1 | 0 | 31.1 |  | 2026-02-03 15:20 | 181.357 | 184.058 | 1400.1 | 30.6763 | 0 | 30.6763 | 0 | 30.7 | 0 | 30.7 |  | 2026-02-03 15:20 | 180.982 | 183.596 | 1398.9 | 30.5993 | 0 | 30.5993 | 0 | 30.7 | 0 | 30.7 |  | 2026-02-03 15:20 | 178.79 | 183.879 | 1388.1 | 30.6465 | 0 | 30.6465 | 0 | 30.2 | 0 | 30.2 |  | 2026-02-03 15:20 | 169.334 | 171.773 | 1313.6 | 28.6288 | 0 | 28.6288 | 0 | 28.7 | 0 | 28.7 |  | 2026-02-03 15:20 | 316.825 | 0 | 316.825 | 0 | 317.9 | 0 | 317.9
2026-02-03 15:10 |  |  | 252.934 | 256.89 | 1824.4 | 42.815 | 0 | 42.815 | 0 | 42.5 | 0 | 42.5 |  | 2026-02-03 15:10 | 258.352 | 261.504 | 1850.8 | 43.584 | 0 | 43.584 | 0 | 43.2 | 0 | 43.2 |  | 2026-02-03 15:10 | 252.711 | 259.407 | 1814.6 | 43.2345 | 0 | 43.2345 | 0 | 42.4 | 0 | 42.4 |  | 2026-02-03 15:10 | 255.522 | 259.571 | 1843.4 | 43.2618 | 0 | 43.2618 | 0 | 42.9 | 0 | 42.9 |  | 2026-02-03 15:10 | 191.372 | 194.188 | 1373.3 | 32.3647 | 0 | 32.3647 | 0 | 32.1 | 0 | 32.1 |  | 2026-02-03 15:10 | 188.683 | 191.778 | 1369.4 | 31.963 | 0 | 31.963 | 0 | 31.7 | 0 | 31.7 |  | 2026-02-03 15:10 | 189.143 | 192.251 | 1368.2 | 32.0418 | 0 | 32.0418 | 0 | 32.3 | 0 | 32.3 |  | 2026-02-03 15:10 | 186.295 | 191.294 | 1357.9 | 31.8823 | 0 | 31.8823 | 0 | 31.9 | 0 | 31.9 |  | 2026-02-03 15:10 | 176.328 | 178.937 | 1284.9 | 29.8228 | 0 | 29.8228 | 0 | 30.1 | 0 | 30.1 |  | 2026-02-03 15:10 | 330.97 | 0 | 330.97 | 0 | 329.1 | 0 | 329.1
2026-02-03 15:00 |  |  | 261.106 | 265.325 | 1781.9 | 44.2208 | 0 | 44.2208 | 0 | 44.7 | 0 | 44.7 | 0.9841 | 2026-02-03 15:00 | 265.241 | 269.581 | 1807.6 | 44.9302 | 0 | 44.9302 | 0 | 45.8 | 0 | 45.8 | 0.9839 | 2026-02-03 15:00 | 259.672 | 266.267 | 1772.2 | 44.3778 | 0 | 44.3778 | 0 | 44.4 | 0 | 44.4 | 0.97523 | 2026-02-03 15:00 | 263.191 | 267.525 | 1800.5 | 44.5875 | 0 | 44.5875 | 0 | 44.9 | 0 | 44.9 | 0.9838 | 2026-02-03 15:00 | 196.836 | 199.813 | 1341.2 | 33.3022 | 0 | 33.3022 | 0 | 33.7 | 0 | 33.7 | 0.9851 | 2026-02-03 15:00 | 194.792 | 197.996 | 1337.7 | 32.9993 | 0 | 32.9993 | 0 | 33.3 | 0 | 33.3 | 0.98382 | 2026-02-03 15:00 | 195.577 | 198.917 | 1335.9 | 33.1528 | 0 | 33.1528 | 0 | 32.8 | 0 | 32.8 | 0.98321 | 2026-02-03 15:00 | 193.44 | 198.855 | 1326 | 33.1425 | 0 | 33.1425 | 0 | 32.4 | 0 | 32.4 | 0.97277 | 2026-02-03 15:00 | 182.718 | 185.425 | 1254.8 | 30.9042 | 0 | 30.9042 | 0 | 31.2 | 0 | 31.2 | 0.9854 | 2026-02-03 15:00 | 341.6173 | 0 | 341.6173 | 0 | 343.2 | 0 | 343.2
2026-02-03 14:50 |  |  | 271.298 | 275.709 | 1737.2 | 45.9515 | 0 | 45.9515 | 0 | 46.1 | 0 | 46.1 | 0.984 | 2026-02-03 14:50 | 275.608 | 280.724 | 1761.8 | 46.7873 | 0 | 46.7873 | 0 | 45.5 | 0 | 45.5 | 0.98178 | 2026-02-03 14:50 | 270.724 | 278.118 | 1727.8 | 46.353 | 0 | 46.353 | 0 | 45.3 | 0 | 45.3 | 0.97341 | 2026-02-03 14:50 | 274.533 | 279.054 | 1755.6 | 46.509 | 0 | 46.509 | 0 | 46 | 0 | 46 | 0.9838 | 2026-02-03 14:50 | 205.409 | 208.495 | 1307.5 | 34.7492 | 0 | 34.7492 | 0 | 34.4 | 0 | 34.4 | 0.9852 | 2026-02-03 14:50 | 203.465 | 207.46 | 1304.4 | 34.5767 | 0 | 34.5767 | 0 | 34.1 | 0 | 34.1 | 0.98074 | 2026-02-03 14:50 | 203.314 | 206.984 | 1303.1 | 34.4973 | 0 | 34.4973 | 0 | 34.5 | 0 | 34.5 | 0.98227 | 2026-02-03 14:50 | 201.014 | 206.74 | 1293.6 | 34.4567 | 0 | 34.4567 | 0 | 34.1 | 0 | 34.1 | 0.9723 | 2026-02-03 14:50 | 190.938 | 193.806 | 1223.6 | 32.301 | 0 | 32.301 | 0 | 31.8 | 0 | 31.8 | 0.9852 | 2026-02-03 14:50 | 356.1817 | 0 | 356.1817 | 0 | 351.8 | 0 | 351.8
2026-02-03 14:40 |  |  | 279.13 | 283.669 | 1691.1 | 47.2782 | 0 | 47.2782 | 0 | 45.9 | 0 | 45.9 | 0.984 | 2026-02-03 14:40 | 283.283 | 287.948 | 1716.3 | 47.9913 | 0 | 47.9913 | 0 | 47.4 | 0 | 47.4 | 0.9838 | 2026-02-03 14:40 | 277.518 | 285.017 | 1682.5 | 47.5028 | 0 | 47.5028 | 0 | 46.9 | 0 | 46.9 | 0.97369 | 2026-02-03 14:40 | 281.52 | 286.185 | 1709.6 | 47.6975 | 0 | 47.6975 | 0 | 47.6 | 0 | 47.6 | 0.9837 | 2026-02-03 14:40 | 210.561 | 213.746 | 1273.1 | 35.6243 | 0 | 35.6243 | 0 | 35.6 | 0 | 35.6 | 0.9851 | 2026-02-03 14:40 | 208.935 | 212.312 | 1270.3 | 35.3853 | 0 | 35.3853 | 0 | 35.3 | 0 | 35.3 | 0.98409 | 2026-02-03 14:40 | 208.791 | 212.658 | 1268.6 | 35.443 | 0 | 35.443 | 0 | 34.8 | 0 | 34.8 | 0.98182 | 2026-02-03 14:40 | 206.644 | 212.658 | 1259.5 | 35.443 | 0 | 35.443 | 0 | 35.1 | 0 | 35.1 | 0.97172 | 2026-02-03 14:40 | 195.89 | 198.813 | 1191.8 | 33.1355 | 0 | 33.1355 | 0 | 32.8 | 0 | 32.8 | 0.9853 | 2026-02-03 14:40 | 365.501 | 0 | 365.501 | 0 | 361.4 | 0 | 361.4
2026-02-03 14:30 |  |  | 283.752 | 288.424 | 1645.2 | 48.0707 | 0 | 48.0707 | 0 | 48.1 | 0 | 48.1 | 0.9838 | 2026-02-03 14:30 | 288.376 | 293.214 | 1668.9 | 48.869 | 0 | 48.869 | 0 | 49 | 0 | 49 | 0.9835 | 2026-02-03 14:30 | 282.227 | 290.032 | 1635.6 | 48.3387 | 0 | 48.3387 | 0 | 47.3 | 0 | 47.3 | 0.97309 | 2026-02-03 14:30 | 286.084 | 290.913 | 1662 | 48.4855 | 0 | 48.4855 | 0 | 48 | 0 | 48 | 0.9834 | 2026-02-03 14:30 | 213.963 | 217.288 | 1237.5 | 36.2147 | 0 | 36.2147 | 0 | 35.8 | 0 | 35.8 | 0.9847 | 2026-02-03 14:30 | 212.234 | 215.984 | 1235 | 35.9973 | 0 | 35.9973 | 0 | 36 | 0 | 36 | 0.98264 | 2026-02-03 14:30 | 212.133 | 216.307 | 1233.8 | 36.0512 | 0 | 36.0512 | 0 | 36 | 0 | 36 | 0.9807 | 2026-02-03 14:30 | 210.445 | 216.355 | 1224.4 | 36.0592 | 0 | 36.0592 | 0 | 35.1 | 0 | 35.1 | 0.97268 | 2026-02-03 14:30 | 199.182 | 202.226 | 1159 | 33.7043 | 0 | 33.7043 | 0 | 33.8 | 0 | 33.8 | 0.98495 | 2026-02-03 14:30 | 371.7905 | 0 | 371.7905 | 0 | 369.1 | 0 | 369.1
2026-02-03 14:20 |  |  | 289.407 | 294.093 | 1597.1 | 49.0155 | 0 | 49.0155 | 0 | 48.6 | 0 | 48.6 | 0.98407 | 2026-02-03 14:20 | 295.087 | 300.099 | 1619.9 | 50.0165 | 0 | 50.0165 | 0 | 49.5 | 0 | 49.5 | 0.9833 | 2026-02-03 14:20 | 287.721 | 295.41 | 1588.3 | 49.235 | 0 | 49.235 | 0 | 49 | 0 | 49 | 0.97397 | 2026-02-03 14:20 | 292.545 | 297.513 | 1614 | 49.5855 | 0 | 49.5855 | 0 | 49.7 | 0 | 49.7 | 0.9833 | 2026-02-03 14:20 | 217.964 | 221.351 | 1201.7 | 36.8918 | 0 | 36.8918 | 0 | 37.2 | 0 | 37.2 | 0.9847 | 2026-02-03 14:20 | 216.368 | 220.533 | 1199 | 36.7555 | 0 | 36.7555 | 0 | 36.4 | 0 | 36.4 | 0.98111 | 2026-02-03 14:20 | 215.623 | 219.317 | 1197.8 | 36.5528 | 0 | 36.5528 | 0 | 36.3 | 0 | 36.3 | 0.98316 | 2026-02-03 14:20 | 213.584 | 219.74 | 1189.3 | 36.6233 | 0 | 36.6233 | 0 | 35.9 | 0 | 35.9 | 0.97199 | 2026-02-03 14:20 | 202.663 | 205.778 | 1125.2 | 34.2963 | 0 | 34.2963 | 0 | 34 | 0 | 34 | 0.98486 | 2026-02-03 14:20 | 378.9723 | 0 | 378.9723 | 0 | 376.6 | 0 | 376.6
2026-02-03 14:10 |  |  | 295.894 | 300.437 | 1548.5 | 50.0728 | 0 | 50.0728 | 0 | 50.3 | 0 | 50.3 | 0.98488 | 2026-02-03 14:10 | 300.622 | 305.759 | 1570.4 | 50.9598 | 0 | 50.9598 | 0 | 52.9 | 0 | 52.9 | 0.9832 | 2026-02-03 14:10 | 293.826 | 301.866 | 1539.3 | 50.311 | 0 | 50.311 | 0 | 49.3 | 0 | 49.3 | 0.97337 | 2026-02-03 14:10 | 298.639 | 303.766 | 1564.3 | 50.6277 | 0 | 50.6277 | 0 | 50 | 0 | 50 | 0.98312 | 2026-02-03 14:10 | 222.743 | 226.227 | 1164.5 | 37.7045 | 0 | 37.7045 | 0 | 37.4 | 0 | 37.4 | 0.9846 | 2026-02-03 14:10 | 220.947 | 224.794 | 1162.6 | 37.4657 | 0 | 37.4657 | 0 | 37 | 0 | 37 | 0.98289 | 2026-02-03 14:10 | 220.766 | 224.739 | 1161.5 | 37.4565 | 0 | 37.4565 | 0 | 37 | 0 | 37 | 0.98232 | 2026-02-03 14:10 | 218.598 | 224.976 | 1153.4 | 37.496 | 0 | 37.496 | 0 | 36.7 | 0 | 36.7 | 0.97165 | 2026-02-03 14:10 | 207.112 | 210.287 | 1091.2 | 35.0478 | 0 | 35.0478 | 0 | 35.2 | 0 | 35.2 | 0.9849 | 2026-02-03 14:10 | 387.1418 | 0 | 387.1418 | 0 | 385.8 | 0 | 385.8
2026-02-03 14:00 |  |  | 300.113 | 304.94 | 1498.2 | 50.8233 | 0 | 50.8233 | 0 | 50.4 | 0 | 50.4 | 0.98417 | 2026-02-03 14:00 | 304.848 | 310.12 | 1517.5 | 51.6867 | 0 | 51.6867 | 0 | 51 | 0 | 51 | 0.983 | 2026-02-03 14:00 | 298.722 | 306.925 | 1490 | 51.1542 | 0 | 51.1542 | 0 | 50.4 | 0 | 50.4 | 0.97327 | 2026-02-03 14:00 | 301.793 | 307.012 | 1514.3 | 51.1687 | 0 | 51.1687 | 0 | 51.1 | 0 | 51.1 | 0.983 | 2026-02-03 14:00 | 227.157 | 230.757 | 1127.1 | 38.4595 | 0 | 38.4595 | 0 | 38.3 | 0 | 38.3 | 0.9844 | 2026-02-03 14:00 | 223.424 | 227.709 | 1125.6 | 37.9515 | 0 | 37.9515 | 0 | 38.9 | 0 | 38.9 | 0.98118 | 2026-02-03 14:00 | 225.253 | 229.457 | 1124.5 | 38.2428 | 0 | 38.2428 | 0 | 38.1 | 0 | 38.1 | 0.98168 | 2026-02-03 14:00 | 222.38 | 228.585 | 1116.7 | 38.0975 | 0 | 38.0975 | 0 | 37.7 | 0 | 37.7 | 0.97285 | 2026-02-03 14:00 | 209.404 | 212.674 | 1056 | 35.4457 | 0 | 35.4457 | 0 | 35.6 | 0 | 35.6 | 0.98462 | 2026-02-03 14:00 | 393.0298 | 0 | 393.0298 | 0 | 391.5 | 0 | 391.5
2026-02-03 13:50 |  |  | 311.188 | 316.537 | 1447.8 | 52.7562 | 0 | 52.7562 | 0 | 52.2 | 0 | 52.2 | 0.9831 | 2026-02-03 13:50 | 316.384 | 321.921 | 1466.5 | 53.6535 | 0 | 53.6535 | 0 | 51.6 | 0 | 51.6 | 0.9828 | 2026-02-03 13:50 | 308.125 | 317.129 | 1439.6 | 52.8548 | 0 | 52.8548 | 0 | 52 | 0 | 52 | 0.97161 | 2026-02-03 13:50 | 312.743 | 318.184 | 1463.2 | 53.0307 | 0 | 53.0307 | 0 | 52.6 | 0 | 52.6 | 0.9829 | 2026-02-03 13:50 | 234.572 | 238.365 | 1088.8 | 39.7275 | 0 | 39.7275 | 0 | 39.4 | 0 | 39.4 | 0.98409 | 2026-02-03 13:50 | 232.252 | 236.548 | 1086.7 | 39.4247 | 0 | 39.4247 | 0 | 38 | 0 | 38 | 0.98184 | 2026-02-03 13:50 | 232.426 | 236.818 | 1086.4 | 39.4697 | 0 | 39.4697 | 0 | 39 | 0 | 39 | 0.98145 | 2026-02-03 13:50 | 230.339 | 237.086 | 1079 | 39.5143 | 0 | 39.5143 | 0 | 39.2 | 0 | 39.2 | 0.97154 | 2026-02-03 13:50 | 217.65 | 221.009 | 1020.4 | 36.8348 | 0 | 36.8348 | 0 | 36.6 | 0 | 36.6 | 0.9848 | 2026-02-03 13:50 | 407.2662 | 0 | 407.2662 | 0 | 400.6 | 0 | 400.6
2026-02-03 13:40 |  |  | 316.136 | 321.571 | 1395.6 | 53.5952 | 0 | 53.5952 | 0 | 52.7 | 0 | 52.7 | 0.9831 | 2026-02-03 13:40 | 322.575 | 327.435 | 1414.9 | 54.5725 | 0 | 54.5725 | 0 | 54.1 | 0 | 54.1 | 0.98516 | 2026-02-03 13:40 | 314.527 | 323.192 | 1387.6 | 53.8653 | 0 | 53.8653 | 0 | 53.2 | 0 | 53.2 | 0.97319 | 2026-02-03 13:40 | 317.573 | 323.131 | 1410.6 | 53.8552 | 0 | 53.8552 | 0 | 53.8 | 0 | 53.8 | 0.9828 | 2026-02-03 13:40 | 238.736 | 242.495 | 1049.4 | 40.4158 | 0 | 40.4158 | 0 | 40.5 | 0 | 40.5 | 0.9845 | 2026-02-03 13:40 | 235.643 | 240.263 | 1048.7 | 40.0438 | 0 | 40.0438 | 0 | 40 | 0 | 40 | 0.98077 | 2026-02-03 13:40 | 236.376 | 241.248 | 1047.4 | 40.208 | 0 | 40.208 | 0 | 40.1 | 0 | 40.1 | 0.97981 | 2026-02-03 13:40 | 234.122 | 241.091 | 1039.8 | 40.1818 | 0 | 40.1818 | 0 | 39.2 | 0 | 39.2 | 0.97109 | 2026-02-03 13:40 | 221.146 | 224.582 | 983.8 | 37.4303 | 0 | 37.4303 | 0 | 37 | 0 | 37 | 0.9847 | 2026-02-03 13:40 | 414.168 | 0 | 414.168 | 0 | 410.6 | 0 | 410.6
2026-02-03 13:30 |  |  | 318.498 | 324.039 | 1342.9 | 54.0065 | 0 | 54.0065 | 0 | 52.8 | 0 | 52.8 | 0.9829 | 2026-02-03 13:30 | 322.885 | 328.806 | 1360.8 | 54.801 | 0 | 54.801 | 0 | 53.1 | 0 | 53.1 | 0.98199 | 2026-02-03 13:30 | 317.085 | 326.325 | 1334.4 | 54.3875 | 0 | 54.3875 | 0 | 52.6 | 0 | 52.6 | 0.97168 | 2026-02-03 13:30 | 321.018 | 326.703 | 1356.8 | 54.4505 | 0 | 54.4505 | 0 | 53.4 | 0 | 53.4 | 0.9826 | 2026-02-03 13:30 | 240.663 | 244.576 | 1008.9 | 40.7627 | 0 | 40.7627 | 0 | 39.9 | 0 | 39.9 | 0.984 | 2026-02-03 13:30 | 237.871 | 242.559 | 1008.7 | 40.4265 | 0 | 40.4265 | 0 | 39.6 | 0 | 39.6 | 0.98067 | 2026-02-03 13:30 | 238.618 | 243.226 | 1007.3 | 40.5377 | 0 | 40.5377 | 0 | 39.6 | 0 | 39.6 | 0.98105 | 2026-02-03 13:30 | 236.856 | 243.926 | 1000.6 | 40.6543 | 0 | 40.6543 | 0 | 39.3 | 0 | 39.3 | 0.97102 | 2026-02-03 13:30 | 223.864 | 227.342 | 946.8 | 37.8903 | 0 | 37.8903 | 0 | 37.3 | 0 | 37.3 | 0.9847 | 2026-02-03 13:30 | 417.917 | 0 | 417.917 | 0 | 407.6 | 0 | 407.6
2026-02-03 13:20 |  |  | 316.651 | 322.127 | 1290.1 | 53.6878 | 0 | 53.6878 | 0 | 53.7 | 0 | 53.7 | 0.983 | 2026-02-03 13:20 | 322.493 | 328.204 | 1307.7 | 54.7007 | 0 | 54.7007 | 0 | 53.8 | 0 | 53.8 | 0.9826 | 2026-02-03 13:20 | 314.931 | 323.85 | 1281.8 | 53.975 | 0 | 53.975 | 0 | 52.4 | 0 | 52.4 | 0.97246 | 2026-02-03 13:20 | 320.988 | 326.672 | 1303.4 | 54.4453 | 0 | 54.4453 | 0 | 53.4 | 0 | 53.4 | 0.9826 | 2026-02-03 13:20 | 238.875 | 242.759 | 969 | 40.4598 | 0 | 40.4598 | 0 | 39.9 | 0 | 39.9 | 0.984 | 2026-02-03 13:20 | 238.112 | 242.465 | 969.1 | 40.4108 | 0 | 40.4108 | 0 | 39.6 | 0 | 39.6 | 0.98205 | 2026-02-03 13:20 | 237 | 241.501 | 967.7 | 40.2502 | 0 | 40.2502 | 0 | 39.5 | 0 | 39.5 | 0.98136 | 2026-02-03 13:20 | 235.828 | 242.702 | 961.3 | 40.4503 | 0 | 40.4503 | 0 | 39.3 | 0 | 39.3 | 0.97168 | 2026-02-03 13:20 | 223.761 | 227.232 | 909.5 | 37.872 | 0 | 37.872 | 0 | 37.2 | 0 | 37.2 | 0.98472 | 2026-02-03 13:20 | 416.252 | 0 | 416.252 | 0 | 408.8 | 0 | 408.8
2026-02-03 13:10 |  |  | 320.583 | 326.194 | 1236.4 | 54.3657 | 0 | 54.3657 | 0 | 53.6 | 0 | 53.6 | 0.9828 | 2026-02-03 13:10 | 0 | 330.955 | 1253.9 | 55.1592 | 0 | 55.1592 | 0 | 55.3 | 0 | 55.3 | 0 | 2026-02-03 13:10 | 317.911 | 327.069 | 1229.4 | 54.5115 | 0 | 54.5115 | 0 | 52.7 | 0 | 52.7 | 0.972 | 2026-02-03 13:10 | 322.468 | 328.245 | 1250 | 54.7075 | 0 | 54.7075 | 0 | 53.4 | 0 | 53.4 | 0.9824 | 2026-02-03 13:10 | 241.062 | 244.982 | 929.1 | 40.8303 | 0 | 40.8303 | 0 | 40.4 | 0 | 40.4 | 0.984 | 2026-02-03 13:10 | 238.757 | 243.171 | 929.5 | 40.5285 | 0 | 40.5285 | 0 | 40.1 | 0 | 40.1 | 0.98185 | 2026-02-03 13:10 | 238.928 | 243.995 | 928.2 | 40.6658 | 0 | 40.6658 | 0 | 40.1 | 0 | 40.1 | 0.97923 | 2026-02-03 13:10 | 237.309 | 244.497 | 922 | 40.7495 | 0 | 40.7495 | 0 | 39.9 | 0 | 39.9 | 0.9706 | 2026-02-03 13:10 | 224.656 | 228.239 | 872.3 | 38.0398 | 0 | 38.0398 | 0 | 37.7 | 0 | 37.7 | 0.9843 | 2026-02-03 13:10 | 419.5578 | 0 | 419.5578 | 0 | 413.2 | 0 | 413.2
2026-02-03 13:00 |  |  | 320.111 | 325.945 | 1182.8 | 54.3242 | 0 | 54.3242 | 0 | 52.7 | 0 | 52.7 | 0.9821 | 2026-02-03 13:00 | 325.048 | 330.767 | 1198.6 | 55.1278 | 0 | 55.1278 | 0 | 54.2 | 0 | 54.2 | 0.98271 | 2026-02-03 13:00 | 318.586 | 327.886 | 1176.7 | 54.6477 | 0 | 54.6477 | 0 | 53 | 0 | 53 | 0.97164 | 2026-02-03 13:00 | 322.73 | 328.512 | 1196.6 | 54.752 | 0 | 54.752 | 0 | 53.9 | 0 | 53.9 | 0.9824 | 2026-02-03 13:00 | 241.951 | 245.868 | 888.7 | 40.978 | 0 | 40.978 | 0 | 39.7 | 0 | 39.7 | 0.98407 | 2026-02-03 13:00 | 239.614 | 244.089 | 889.4 | 40.6815 | 0 | 40.6815 | 0 | 40.1 | 0 | 40.1 | 0.98167 | 2026-02-03 13:00 | 239.789 | 244.632 | 888.1 | 40.772 | 0 | 40.772 | 0 | 40 | 0 | 40 | 0.9802 | 2026-02-03 13:00 | 238.408 | 245.429 | 882.1 | 40.9048 | 0 | 40.9048 | 0 | 39.7 | 0 | 39.7 | 0.97139 | 2026-02-03 13:00 | 225.519 | 229.116 | 834.6 | 38.186 | 0 | 38.186 | 0 | 37.7 | 0 | 37.7 | 0.9843 | 2026-02-03 13:00 | 420.374 | 0 | 420.374 | 0 | 411 | 0 | 411
2026-02-03 12:50 |  |  | 320.025 | 325.626 | 1130.1 | 54.271 | 0 | 54.271 | 0 | 53.2 | 0 | 53.2 | 0.9828 | 2026-02-03 12:50 | 326.23 | 331.574 | 1144.4 | 55.2623 | 0 | 55.2623 | 0 | 53.9 | 0 | 53.9 | 0.98388 | 2026-02-03 12:50 | 317.677 | 326.462 | 1123.7 | 54.4103 | 0 | 54.4103 | 0 | 53.5 | 0 | 53.5 | 0.97309 | 2026-02-03 12:50 | 323.578 | 329.342 | 1142.7 | 54.8903 | 0 | 54.8903 | 0 | 54.3 | 0 | 54.3 | 0.9825 | 2026-02-03 12:50 | 240.814 | 244.768 | 849 | 40.7947 | 0 | 40.7947 | 0 | 41 | 0 | 41 | 0.98385 | 2026-02-03 12:50 | 239.98 | 244.482 | 849.3 | 40.747 | 0 | 40.747 | 0 | 39.7 | 0 | 39.7 | 0.98159 | 2026-02-03 12:50 | 238.922 | 243.754 | 848.1 | 40.6257 | 0 | 40.6257 | 0 | 39.7 | 0 | 39.7 | 0.98018 | 2026-02-03 12:50 | 237.588 | 244.583 | 842.4 | 40.7638 | 0 | 40.7638 | 0 | 39.5 | 0 | 39.5 | 0.9714 | 2026-02-03 12:50 | 225.607 | 229.182 | 796.9 | 38.197 | 0 | 38.197 | 0 | 37.4 | 0 | 37.4 | 0.9844 | 2026-02-03 12:50 | 419.9622 | 0 | 419.9622 | 0 | 412.2 | 0 | 412.2
2026-02-03 12:40 |  |  | 322.003 | 327.638 | 1076.9 | 54.6063 | 0 | 54.6063 | 0 | 53.9 | 0 | 53.9 | 0.9828 | 2026-02-03 12:40 | 327.064 | 332.917 | 1090.5 | 55.4862 | 0 | 55.4862 | 0 | 109.5 | 0 | 109.5 | 0.98242 | 2026-02-03 12:40 | 319.452 | 328.934 | 1070.2 | 54.8223 | 0 | 54.8223 | 0 | 52.9 | 0 | 52.9 | 0.97117 | 2026-02-03 12:40 | 324.427 | 330.206 | 1088.4 | 55.0343 | 0 | 55.0343 | 0 | 53.5 | 0 | 53.5 | 0.9825 | 2026-02-03 12:40 | 242.033 | 245.97 | 808 | 40.995 | 0 | 40.995 | 0 | 40.2 | 0 | 40.2 | 0.98399 | 2026-02-03 12:40 | 241.011 | 245.452 | 809.6 | 40.9087 | 0 | 40.9087 | 0 | 40.4 | 0 | 40.4 | 0.98191 | 2026-02-03 12:40 | 240.547 | 245.429 | 808.4 | 40.9048 | 0 | 40.9048 | 0 | 40.4 | 0 | 40.4 | 0.98011 | 2026-02-03 12:40 | 239.065 | 246.204 | 802.9 | 41.034 | 0 | 41.034 | 0 | 40.1 | 0 | 40.1 | 0.971 | 2026-02-03 12:40 | 226.702 | 230.318 | 759.5 | 38.3863 | 0 | 38.3863 | 0 | 38 | 0 | 38 | 0.9843 | 2026-02-03 12:40 | 422.178 | 0 | 422.178 | 0 | 468.9 | 0 | 468.9
2026-02-03 12:30 |  |  | 321.279 | 326.986 | 1023 | 54.4977 | 0 | 54.4977 | 0 | 53.9 | 0 | 53.9 | 0.98255 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 12:30 | 319.652 | 328.885 | 1017.3 | 54.8142 | 0 | 54.8142 | 0 | 53.5 | 0 | 53.5 | 0.97193 | 2026-02-03 12:30 | 322.957 | 328.799 | 1034.9 | 54.7998 | 0 | 54.7998 | 0 | 54.2 | 0 | 54.2 | 0.98223 | 2026-02-03 12:30 | 242.172 | 246.085 | 767.8 | 41.0142 | 0 | 41.0142 | 0 | 39.9 | 0 | 39.9 | 0.9841 | 2026-02-03 12:30 | 239.92 | 244.318 | 769.2 | 40.7197 | 0 | 40.7197 | 0 | 39.5 | 0 | 39.5 | 0.982 | 2026-02-03 12:30 | 240.683 | 245.326 | 768 | 40.8877 | 0 | 40.8877 | 0 | 39.6 | 0 | 39.6 | 0.98107 | 2026-02-03 12:30 | 238.399 | 245.553 | 762.8 | 40.9255 | 0 | 40.9255 | 0 | 39.3 | 0 | 39.3 | 0.97087 | 2026-02-03 12:30 | 225.567 | 229.165 | 721.5 | 38.1942 | 0 | 38.1942 | 0 | 37.1 | 0 | 37.1 | 0.9843 | 2026-02-03 12:30 | 365.8528 | 0 | 365.8528 | 0 | 357 | 0 | 357
2026-02-03 12:20 |  |  | 319.245 | 324.733 | 969.1 | 54.1222 | 0 | 54.1222 | 0 | 54.6 | 0 | 54.6 | 0.9831 | 2026-02-03 12:20 | 324.495 | 330.05 | 981 | 55.0083 | 0 | 55.0083 | 0 | 54 | 0 | 54 | 0.98317 | 2026-02-03 12:20 | 317.434 | 326.428 | 963.8 | 54.4047 | 0 | 54.4047 | 0 | 52.3 | 0 | 52.3 | 0.97245 | 2026-02-03 12:20 | 321.896 | 327.563 | 980.7 | 54.5938 | 0 | 54.5938 | 0 | 53.7 | 0 | 53.7 | 0.9827 | 2026-02-03 12:20 | 240.423 | 244.283 | 727.9 | 40.7138 | 0 | 40.7138 | 0 | 40.1 | 0 | 40.1 | 0.9842 | 2026-02-03 12:20 | 238.371 | 242.781 | 729.7 | 40.4635 | 0 | 40.4635 | 0 | 39.8 | 0 | 39.8 | 0.98184 | 2026-02-03 12:20 | 239.011 | 243.709 | 728.4 | 40.6182 | 0 | 40.6182 | 0 | 40 | 0 | 40 | 0.98072 | 2026-02-03 12:20 | 236.882 | 243.995 | 723.5 | 40.6658 | 0 | 40.6658 | 0 | 39.5 | 0 | 39.5 | 0.97085 | 2026-02-03 12:20 | 223.448 | 226.966 | 684.4 | 37.8277 | 0 | 37.8277 | 0 | 37.3 | 0 | 37.3 | 0.9845 | 2026-02-03 12:20 | 418.418 | 0 | 418.418 | 0 | 411.3 | 0 | 411.3
2026-02-03 12:10 |  |  | 316.106 | 321.605 | 914.5 | 53.6008 | 0 | 53.6008 | 0 | 50.7 | 0 | 50.7 | 0.9829 | 2026-02-03 12:10 | 321.873 | 327.539 | 927 | 54.5898 | 0 | 54.5898 | 0 | 52.5 | 0 | 52.5 | 0.9827 | 2026-02-03 12:10 | 315.304 | 324.245 | 911.5 | 54.0408 | 0 | 54.0408 | 0 | 52.7 | 0 | 52.7 | 0.97243 | 2026-02-03 12:10 | 320.031 | 325.665 | 927 | 54.2775 | 0 | 54.2775 | 0 | 52.9 | 0 | 52.9 | 0.9827 | 2026-02-03 12:10 | 239.064 | 242.902 | 687.8 | 40.4837 | 0 | 40.4837 | 0 | 39.6 | 0 | 39.6 | 0.9842 | 2026-02-03 12:10 | 237.248 | 241.825 | 689.9 | 40.3042 | 0 | 40.3042 | 0 | 39.3 | 0 | 39.3 | 0.98107 | 2026-02-03 12:10 | 237.982 | 242.575 | 688.4 | 40.4292 | 0 | 40.4292 | 0 | 39.3 | 0 | 39.3 | 0.98107 | 2026-02-03 12:10 | 236.102 | 243.301 | 684 | 40.5502 | 0 | 40.5502 | 0 | 39.1 | 0 | 39.1 | 0.97041 | 2026-02-03 12:10 | 222.744 | 226.251 | 647.1 | 37.7085 | 0 | 37.7085 | 0 | 37.4 | 0 | 37.4 | 0.9845 | 2026-02-03 12:10 | 415.9847 | 0 | 415.9847 | 0 | 403.5 | 0 | 403.5
2026-02-03 12:00 |  |  | 314.495 | 319.836 | 863.8 | 53.306 | 0 | 53.306 | 0 | 52.7 | 0 | 52.7 | 0.9833 | 2026-02-03 12:00 | 319.036 | 325.161 | 874.5 | 54.1935 | 0 | 54.1935 | 0 | 52.7 | 0 | 52.7 | 0.98116 | 2026-02-03 12:00 | 312.531 | 321.187 | 858.8 | 53.5312 | 0 | 53.5312 | 0 | 51.7 | 0 | 51.7 | 0.97305 | 2026-02-03 12:00 | 317.86 | 323.423 | 874.1 | 53.9038 | 0 | 53.9038 | 0 | 52.6 | 0 | 52.6 | 0.9828 | 2026-02-03 12:00 | 237.375 | 241.161 | 648.2 | 40.1935 | 0 | 40.1935 | 0 | 39.7 | 0 | 39.7 | 0.9843 | 2026-02-03 12:00 | 235.771 | 240.251 | 650.6 | 40.0418 | 0 | 40.0418 | 0 | 39.4 | 0 | 39.4 | 0.98135 | 2026-02-03 12:00 | 236.535 | 241.238 | 649.1 | 40.2063 | 0 | 40.2063 | 0 | 39.5 | 0 | 39.5 | 0.9805 | 2026-02-03 12:00 | 234.897 | 242.058 | 644.9 | 40.343 | 0 | 40.343 | 0 | 39.2 | 0 | 39.2 | 0.97042 | 2026-02-03 12:00 | 221.32 | 224.759 | 609.7 | 37.4598 | 0 | 37.4598 | 0 | 36.5 | 0 | 36.5 | 0.9847 | 2026-02-03 12:00 | 413.179 | 0 | 413.179 | 0 | 404 | 0 | 404
2026-02-03 11:50 |  |  | 313.042 | 318.537 | 811.1 | 53.0895 | 0 | 53.0895 | 0 | 52.4 | 0 | 52.4 | 0.98275 | 2026-02-03 11:50 | 318.437 | 323.878 | 821.8 | 53.9797 | 0 | 53.9797 | 0 | 52.1 | 0 | 52.1 | 0.9832 | 2026-02-03 11:50 | 311.089 | 319.634 | 807.1 | 53.2723 | 0 | 53.2723 | 0 | 51.5 | 0 | 51.5 | 0.97327 | 2026-02-03 11:50 | 316.075 | 321.476 | 821.5 | 53.5793 | 0 | 53.5793 | 0 | 53.2 | 0 | 53.2 | 0.9832 | 2026-02-03 11:50 | 235.621 | 239.331 | 608.5 | 39.8885 | 0 | 39.8885 | 0 | 39.1 | 0 | 39.1 | 0.9845 | 2026-02-03 11:50 | 234.374 | 238.292 | 611.2 | 39.7153 | 0 | 39.7153 | 0 | 39 | 0 | 39 | 0.98356 | 2026-02-03 11:50 | 234.274 | 238.695 | 609.6 | 39.7825 | 0 | 39.7825 | 0 | 39 | 0 | 39 | 0.98148 | 2026-02-03 11:50 | 232.442 | 239.386 | 605.7 | 39.8977 | 0 | 39.8977 | 0 | 38.7 | 0 | 38.7 | 0.97099 | 2026-02-03 11:50 | 220.107 | 223.482 | 573.2 | 37.247 | 0 | 37.247 | 0 | 36.6 | 0 | 36.6 | 0.9849 | 2026-02-03 11:50 | 410.4518 | 0 | 410.4518 | 0 | 401.6 | 0 | 401.6
2026-02-03 11:40 |  |  | 308.27 | 313.378 | 758.7 | 52.2297 | 0 | 52.2297 | 0 | 53.3 | 0 | 53.3 | 0.9837 | 2026-02-03 11:40 | 314.426 | 319.701 | 769.7 | 53.2835 | 0 | 53.2835 | 0 | 52.1 | 0 | 52.1 | 0.9835 | 2026-02-03 11:40 | 307.369 | 315.883 | 755.6 | 52.6472 | 0 | 52.6472 | 0 | 50.9 | 0 | 50.9 | 0.97305 | 2026-02-03 11:40 | 312.91 | 318.224 | 768.3 | 53.0373 | 0 | 53.0373 | 0 | 50.9 | 0 | 50.9 | 0.9833 | 2026-02-03 11:40 | 232.833 | 236.451 | 569.4 | 39.4085 | 0 | 39.4085 | 0 | 38.6 | 0 | 38.6 | 0.9847 | 2026-02-03 11:40 | 232.311 | 236.6 | 572.2 | 39.4333 | 0 | 39.4333 | 0 | 38.5 | 0 | 38.5 | 0.98187 | 2026-02-03 11:40 | 231.736 | 236.03 | 570.6 | 39.3383 | 0 | 39.3383 | 0 | 38.4 | 0 | 38.4 | 0.98181 | 2026-02-03 11:40 | 230.38 | 237.3 | 567 | 39.55 | 0 | 39.55 | 0 | 38.2 | 0 | 38.2 | 0.97084 | 2026-02-03 11:40 | 218.608 | 221.869 | 536.6 | 36.9782 | 0 | 36.9782 | 0 | 36.2 | 0 | 36.2 | 0.9853 | 2026-02-03 11:40 | 405.906 | 0 | 405.906 | 0 | 397.1 | 0 | 397.1
2026-02-03 11:30 |  |  | 301.237 | 306.26 | 705.4 | 51.0433 | 0 | 51.0433 | 0 | 46.8 | 0 | 46.8 | 0.9836 | 2026-02-03 11:30 | 307.788 | 312.952 | 717.6 | 52.1587 | 0 | 52.1587 | 0 | 50.9 | 0 | 50.9 | 0.9835 | 2026-02-03 11:30 | 301.64 | 309.696 | 704.7 | 51.616 | 0 | 51.616 | 0 | 49.9 | 0 | 49.9 | 0.97399 | 2026-02-03 11:30 | 306.802 | 312.013 | 717.4 | 52.0022 | 0 | 52.0022 | 0 | 50.9 | 0 | 50.9 | 0.9833 | 2026-02-03 11:30 | 228.749 | 232.28 | 530.8 | 38.7133 | 0 | 38.7133 | 0 | 37.3 | 0 | 37.3 | 0.9848 | 2026-02-03 11:30 | 228.28 | 232.142 | 533.7 | 38.6903 | 0 | 38.6903 | 0 | 37.2 | 0 | 37.2 | 0.98336 | 2026-02-03 11:30 | 227.994 | 231.905 | 532.2 | 38.6508 | 0 | 38.6508 | 0 | 37.2 | 0 | 37.2 | 0.98314 | 2026-02-03 11:30 | 227.01 | 233.586 | 528.8 | 38.931 | 0 | 38.931 | 0 | 37 | 0 | 37 | 0.97185 | 2026-02-03 11:30 | 214.845 | 218.05 | 500.4 | 36.3417 | 0 | 36.3417 | 0 | 35.6 | 0 | 35.6 | 0.9853 | 2026-02-03 11:30 | 398.1473 | 0 | 398.1473 | 0 | 382.8 | 0 | 382.8
2026-02-03 11:20 |  |  | 296.462 | 301.34 | 658.6 | 50.2233 | 0 | 50.2233 | 0 | 48.6 | 0 | 48.6 | 0.98381 | 2026-02-03 11:20 | 301.724 | 306.755 | 666.7 | 51.1258 | 0 | 51.1258 | 0 | 49.6 | 0 | 49.6 | 0.9836 | 2026-02-03 11:20 | 294.593 | 302.427 | 654.8 | 50.4045 | 0 | 50.4045 | 0 | 48.4 | 0 | 48.4 | 0.9741 | 2026-02-03 11:20 | 300.309 | 305.347 | 666.5 | 50.8912 | 0 | 50.8912 | 0 | 49.3 | 0 | 49.3 | 0.9835 | 2026-02-03 11:20 | 223.727 | 227.111 | 493.5 | 37.8518 | 0 | 37.8518 | 0 | 37.3 | 0 | 37.3 | 0.9851 | 2026-02-03 11:20 | 223.262 | 227.131 | 496.5 | 37.8552 | 0 | 37.8552 | 0 | 36.7 | 0 | 36.7 | 0.98297 | 2026-02-03 11:20 | 223.268 | 227.404 | 495 | 37.9007 | 0 | 37.9007 | 0 | 37.1 | 0 | 37.1 | 0.98181 | 2026-02-03 11:20 | 222.34 | 228.802 | 491.8 | 38.1337 | 0 | 38.1337 | 0 | 36.9 | 0 | 36.9 | 0.97176 | 2026-02-03 11:20 | 210.02 | 213.175 | 464.8 | 35.5292 | 0 | 35.5292 | 0 | 34.4 | 0 | 34.4 | 0.9852 | 2026-02-03 11:20 | 389.9153 | 0 | 389.9153 | 0 | 378.3 | 0 | 378.3
2026-02-03 11:10 |  |  | 290.058 | 294.744 | 610 | 49.124 | 0 | 49.124 | 0 | 47.9 | 0 | 47.9 | 0.9841 | 2026-02-03 11:10 | 295.233 | 300.064 | 617.1 | 50.0107 | 0 | 50.0107 | 0 | 49.5 | 0 | 49.5 | 0.9839 | 2026-02-03 11:10 | 287.799 | 295.225 | 606.4 | 49.2042 | 0 | 49.2042 | 0 | 47.7 | 0 | 47.7 | 0.97485 | 2026-02-03 11:10 | 293.752 | 298.559 | 617.2 | 49.7598 | 0 | 49.7598 | 0 | 48.6 | 0 | 48.6 | 0.9839 | 2026-02-03 11:10 | 217.679 | 220.927 | 456.2 | 36.8212 | 0 | 36.8212 | 0 | 35.5 | 0 | 35.5 | 0.9853 | 2026-02-03 11:10 | 218.196 | 221.748 | 459.8 | 36.958 | 0 | 36.958 | 0 | 36.1 | 0 | 36.1 | 0.98398 | 2026-02-03 11:10 | 217.42 | 221.021 | 457.9 | 36.8368 | 0 | 36.8368 | 0 | 35.5 | 0 | 35.5 | 0.98371 | 2026-02-03 11:10 | 215.493 | 221.971 | 454.9 | 36.9952 | 0 | 36.9952 | 0 | 35.6 | 0 | 35.6 | 0.97082 | 2026-02-03 11:10 | 204.596 | 207.627 | 430.4 | 34.6045 | 0 | 34.6045 | 0 | 33.8 | 0 | 33.8 | 0.9854 | 2026-02-03 11:10 | 380.3143 | 0 | 380.3143 | 0 | 370.2 | 0 | 370.2
2026-02-03 11:00 |  |  | 283.965 | 288.494 | 562.1 | 48.0823 | 0 | 48.0823 | 0 | 47.4 | 0 | 47.4 | 0.9843 | 2026-02-03 11:00 | 287.522 | 292.167 | 567.6 | 48.6945 | 0 | 48.6945 | 0 | 46.8 | 0 | 46.8 | 0.9841 | 2026-02-03 11:00 | 282.553 | 289.761 | 558.7 | 48.2935 | 0 | 48.2935 | 0 | 46.6 | 0 | 46.6 | 0.97512 | 2026-02-03 11:00 | 286.608 | 291.239 | 568.6 | 48.5398 | 0 | 48.5398 | 0 | 47.2 | 0 | 47.2 | 0.9841 | 2026-02-03 11:00 | 213.356 | 216.495 | 420.7 | 36.0825 | 0 | 36.0825 | 0 | 35.2 | 0 | 35.2 | 0.9855 | 2026-02-03 11:00 | 213.119 | 216.643 | 423.7 | 36.1072 | 0 | 36.1072 | 0 | 35.2 | 0 | 35.2 | 0.98373 | 2026-02-03 11:00 | 212.885 | 216.696 | 422.4 | 36.116 | 0 | 36.116 | 0 | 35.2 | 0 | 35.2 | 0.98241 | 2026-02-03 11:00 | 210.789 | 217.284 | 419.3 | 36.214 | 0 | 36.214 | 0 | 34.4 | 0 | 34.4 | 0.97011 | 2026-02-03 11:00 | 199.72 | 202.659 | 396.6 | 33.7765 | 0 | 33.7765 | 0 | 33 | 0 | 33 | 0.9855 | 2026-02-03 11:00 | 371.9063 | 0 | 371.9063 | 0 | 361 | 0 | 361
2026-02-03 10:50 |  |  | 277.102 | 281.436 | 514.7 | 46.906 | 0 | 46.906 | 0 | 44.6 | 0 | 44.6 | 0.9846 | 2026-02-03 10:50 | 0 | 285.386 | 520.8 | 47.5643 | 0 | 47.5643 | 0 | 47.1 | 0 | 47.1 | 0 | 2026-02-03 10:50 | 275.831 | 282.887 | 512.1 | 47.1478 | 0 | 47.1478 | 0 | 44.9 | 0 | 44.9 | 0.97506 | 2026-02-03 10:50 | 279.792 | 284.255 | 521.4 | 47.3758 | 0 | 47.3758 | 0 | 46.4 | 0 | 46.4 | 0.9843 | 2026-02-03 10:50 | 208.793 | 211.801 | 385.5 | 35.3002 | 0 | 35.3002 | 0 | 34.5 | 0 | 34.5 | 0.9858 | 2026-02-03 10:50 | 208.292 | 211.351 | 388.5 | 35.2252 | 0 | 35.2252 | 0 | 34.5 | 0 | 34.5 | 0.98553 | 2026-02-03 10:50 | 208.888 | 212.369 | 387.2 | 35.3948 | 0 | 35.3948 | 0 | 34.6 | 0 | 34.6 | 0.98361 | 2026-02-03 10:50 | 206.825 | 212.763 | 384.9 | 35.4605 | 0 | 35.4605 | 0 | 34.3 | 0 | 34.3 | 0.97209 | 2026-02-03 10:50 | 195.409 | 198.256 | 363.6 | 33.0427 | 0 | 33.0427 | 0 | 31.9 | 0 | 31.9 | 0.98564 | 2026-02-03 10:50 | 363.4173 | 0 | 363.4173 | 0 | 352.8 | 0 | 352.8
2026-02-03 10:40 |  |  | 268.576 | 272.749 | 470.1 | 45.4582 | 0 | 45.4582 | 0 | 44.4 | 0 | 44.4 | 0.9847 | 2026-02-03 10:40 | 272.297 | 276.584 | 473.7 | 46.0973 | 0 | 46.0973 | 0 | 86.8 | 0 | 86.8 | 0.9845 | 2026-02-03 10:40 | 266.903 | 273.31 | 467.2 | 45.5517 | 0 | 45.5517 | 0 | 44.2 | 0 | 44.2 | 0.97656 | 2026-02-03 10:40 | 271.688 | 275.937 | 475 | 45.9895 | 0 | 45.9895 | 0 | 44.2 | 0 | 44.2 | 0.9846 | 2026-02-03 10:40 | 201.887 | 204.795 | 351 | 34.1325 | 0 | 34.1325 | 0 | 32.9 | 0 | 32.9 | 0.9858 | 2026-02-03 10:40 | 202.31 | 205.212 | 354 | 34.202 | 0 | 34.202 | 0 | 32.9 | 0 | 32.9 | 0.98586 | 2026-02-03 10:40 | 202.363 | 205.492 | 352.6 | 34.2487 | 0 | 34.2487 | 0 | 32.9 | 0 | 32.9 | 0.98477 | 2026-02-03 10:40 | 201.196 | 206.848 | 350.6 | 34.4747 | 0 | 34.4747 | 0 | 33.2 | 0 | 33.2 | 0.97268 | 2026-02-03 10:40 | 190.145 | 192.845 | 331.7 | 32.1408 | 0 | 32.1408 | 0 | 31.4 | 0 | 31.4 | 0.986 | 2026-02-03 10:40 | 352.2953 | 0 | 352.2953 | 0 | 382.9 | 0 | 382.9
2026-02-03 10:30 |  |  | 260.125 | 264.033 | 425.7 | 44.0055 | 0 | 44.0055 | 0 | 42.5 | 0 | 42.5 | 0.9852 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 10:30 | 258.924 | 265.018 | 423 | 44.1697 | 0 | 44.1697 | 0 | 42.2 | 0 | 42.2 | 0.97701 | 2026-02-03 10:30 | 264.107 | 268.156 | 430.8 | 44.6927 | 0 | 44.6927 | 0 | 43.1 | 0 | 43.1 | 0.9849 | 2026-02-03 10:30 | 195.758 | 198.538 | 318.1 | 33.0897 | 0 | 33.0897 | 0 | 31.9 | 0 | 31.9 | 0.986 | 2026-02-03 10:30 | 196.337 | 199.223 | 321.1 | 33.2038 | 0 | 33.2038 | 0 | 32 | 0 | 32 | 0.98551 | 2026-02-03 10:30 | 195.913 | 199.097 | 319.7 | 33.1828 | 0 | 33.1828 | 0 | 32 | 0 | 32 | 0.98401 | 2026-02-03 10:30 | 194.365 | 199.986 | 317.4 | 33.331 | 0 | 33.331 | 0 | 31.2 | 0 | 31.2 | 0.97189 | 2026-02-03 10:30 | 184.109 | 186.685 | 300.3 | 31.1142 | 0 | 31.1142 | 0 | 30.1 | 0 | 30.1 | 0.9862 | 2026-02-03 10:30 | 296.7893 | 0 | 296.7893 | 0 | 285 | 0 | 285
2026-02-03 10:20 |  |  | 249.902 | 253.605 | 383.2 | 42.2675 | 0 | 42.2675 | 0 | 40.8 | 0 | 40.8 | 0.9854 | 2026-02-03 10:20 | 253.251 | 257.082 | 386.9 | 42.847 | 0 | 42.847 | 0 | 42 | 0 | 42 | 0.9851 | 2026-02-03 10:20 | 248.719 | 254.431 | 380.8 | 42.4052 | 0 | 42.4052 | 0 | 40.7 | 0 | 40.7 | 0.97755 | 2026-02-03 10:20 | 253.375 | 257.181 | 387.7 | 42.8635 | 0 | 42.8635 | 0 | 41.4 | 0 | 41.4 | 0.9852 | 2026-02-03 10:20 | 187.805 | 190.414 | 286.2 | 31.7357 | 0 | 31.7357 | 0 | 30.7 | 0 | 30.7 | 0.9863 | 2026-02-03 10:20 | 188.395 | 191.012 | 289.1 | 31.8353 | 0 | 31.8353 | 0 | 30.8 | 0 | 30.8 | 0.9863 | 2026-02-03 10:20 | 188.127 | 190.891 | 287.7 | 31.8152 | 0 | 31.8152 | 0 | 30.8 | 0 | 30.8 | 0.98552 | 2026-02-03 10:20 | 186.306 | 191.529 | 286.2 | 31.9215 | 0 | 31.9215 | 0 | 30.5 | 0 | 30.5 | 0.97273 | 2026-02-03 10:20 | 176.258 | 178.724 | 270.2 | 29.7873 | 0 | 29.7873 | 0 | 28.3 | 0 | 28.3 | 0.9862 | 2026-02-03 10:20 | 327.4782 | 0 | 327.4782 | 0 | 316 | 0 | 316
2026-02-03 10:10 |  |  | 238.741 | 242.229 | 342.4 | 40.3715 | 0 | 40.3715 | 0 | 38.6 | 0 | 38.6 | 0.9856 | 2026-02-03 10:10 | 240.045 | 244.91 | 344.9 | 40.8183 | 0 | 40.8183 | 0 | 39.1 | 0 | 39.1 | 0.98014 | 2026-02-03 10:10 | 237.405 | 243 | 340.1 | 40.5 | 0 | 40.5 | 0 | 38.5 | 0 | 38.5 | 0.97698 | 2026-02-03 10:10 | 241.388 | 244.989 | 346.3 | 40.8315 | 0 | 40.8315 | 0 | 39.1 | 0 | 39.1 | 0.9853 | 2026-02-03 10:10 | 179.147 | 181.617 | 255.5 | 30.2695 | 0 | 30.2695 | 0 | 29.1 | 0 | 29.1 | 0.9864 | 2026-02-03 10:10 | 179.701 | 182.179 | 258.3 | 30.3632 | 0 | 30.3632 | 0 | 29.5 | 0 | 29.5 | 0.9864 | 2026-02-03 10:10 | 179.635 | 182.301 | 256.9 | 30.3835 | 0 | 30.3835 | 0 | 29.4 | 0 | 29.4 | 0.98538 | 2026-02-03 10:10 | 178.107 | 183.069 | 255.7 | 30.5115 | 0 | 30.5115 | 0 | 29.3 | 0 | 29.3 | 0.9729 | 2026-02-03 10:10 | 168.469 | 170.809 | 241.9 | 28.4682 | 0 | 28.4682 | 0 | 27.7 | 0 | 27.7 | 0.9863 | 2026-02-03 10:10 | 312.5172 | 0 | 312.5172 | 0 | 300.3 | 0 | 300.3
2026-02-03 10:00 |  |  | 228.233 | 231.437 | 303.8 | 38.5728 | 0 | 38.5728 | 0 | 37.6 | 0 | 37.6 | 0.98616 | 2026-02-03 10:00 | 230.013 | 233.751 | 305.8 | 38.9585 | 0 | 38.9585 | 0 | 37.3 | 0 | 37.3 | 0.98401 | 2026-02-03 10:00 | 226.758 | 231.618 | 301.6 | 38.603 | 0 | 38.603 | 0 | 36.8 | 0 | 36.8 | 0.97902 | 2026-02-03 10:00 | 230.718 | 234.103 | 307.2 | 39.0172 | 0 | 39.0172 | 0 | 37.5 | 0 | 37.5 | 0.98554 | 2026-02-03 10:00 | 171.145 | 173.383 | 226.4 | 28.8972 | 0 | 28.8972 | 0 | 27.7 | 0 | 27.7 | 0.98709 | 2026-02-03 10:00 | 171.669 | 173.983 | 228.8 | 28.9972 | 0 | 28.9972 | 0 | 27.5 | 0 | 27.5 | 0.9867 | 2026-02-03 10:00 | 171.558 | 173.853 | 227.5 | 28.9755 | 0 | 28.9755 | 0 | 27.8 | 0 | 27.8 | 0.9868 | 2026-02-03 10:00 | 170.011 | 174.806 | 226.4 | 29.1343 | 0 | 29.1343 | 0 | 27.5 | 0 | 27.5 | 0.97257 | 2026-02-03 10:00 | 160.837 | 163.022 | 214.2 | 27.1703 | 0 | 27.1703 | 0 | 26 | 0 | 26 | 0.9866 | 2026-02-03 10:00 | 298.326 | 0 | 298.326 | 0 | 285.7 | 0 | 285.7
2026-02-03 09:50 |  |  | 215.994 | 218.95 | 266.2 | 36.4917 | 0 | 36.4917 | 0 | 34.6 | 0 | 34.6 |  | 2026-02-03 09:50 | 218.171 | 221.474 | 268.5 | 36.9123 | 0 | 36.9123 | 0 | 35.6 | 0 | 35.6 |  | 2026-02-03 09:50 | 215.01 | 219.542 | 264.8 | 36.5903 | 0 | 36.5903 | 0 | 35 | 0 | 35 |  | 2026-02-03 09:50 | 218.477 | 221.534 | 269.7 | 36.9223 | 0 | 36.9223 | 0 | 35.5 | 0 | 35.5 |  | 2026-02-03 09:50 | 161.963 | 164.08 | 198.7 | 27.3467 | 0 | 27.3467 | 0 | 26.4 | 0 | 26.4 |  | 2026-02-03 09:50 | 162.818 | 164.946 | 201.3 | 27.491 | 0 | 27.491 | 0 | 26.5 | 0 | 26.5 |  | 2026-02-03 09:50 | 162.471 | 164.675 | 199.7 | 27.4458 | 0 | 27.4458 | 0 | 26.1 | 0 | 26.1 |  | 2026-02-03 09:50 | 160.843 | 165.278 | 198.9 | 27.5463 | 0 | 27.5463 | 0 | 25.9 | 0 | 25.9 |  | 2026-02-03 09:50 | 152.189 | 154.194 | 188.2 | 25.699 | 0 | 25.699 | 0 | 24.5 | 0 | 24.5 |  | 2026-02-03 09:50 | 282.4455 | 0 | 282.4455 | 0 | 270.1 | 0 | 270.1
2026-02-03 09:40 |  |  | 202.543 | 205.232 | 231.6 | 34.2053 | 0 | 34.2053 | 0 | 32.9 | 0 | 32.9 |  | 2026-02-03 09:40 | 203.877 | 207.355 | 232.9 | 34.5592 | 0 | 34.5592 | 0 | 32.3 | 0 | 32.3 |  | 2026-02-03 09:40 | 201.39 | 205.598 | 229.8 | 34.2663 | 0 | 34.2663 | 0 | 32.2 | 0 | 32.2 |  | 2026-02-03 09:40 | 204.836 | 207.618 | 234.2 | 34.603 | 0 | 34.603 | 0 | 32.8 | 0 | 32.8 |  | 2026-02-03 09:40 | 151.543 | 153.477 | 172.3 | 25.5795 | 0 | 25.5795 | 0 | 24.6 | 0 | 24.6 |  | 2026-02-03 09:40 | 152.503 | 154.465 | 174.8 | 25.7442 | 0 | 25.7442 | 0 | 24.8 | 0 | 24.8 |  | 2026-02-03 09:40 | 152.383 | 154.328 | 173.6 | 25.7213 | 0 | 25.7213 | 0 | 24.8 | 0 | 24.8 |  | 2026-02-03 09:40 | 150.733 | 154.874 | 173 | 25.8123 | 0 | 25.8123 | 0 | 24.5 | 0 | 24.5 |  | 2026-02-03 09:40 | 142.683 | 144.548 | 163.7 | 24.0913 | 0 | 24.0913 | 0 | 23.1 | 0 | 23.1 |  | 2026-02-03 09:40 | 264.5825 | 0 | 264.5825 | 0 | 252 | 0 | 252
2026-02-03 09:30 |  |  | 188.489 | 191.528 | 198.7 | 31.9213 | 0 | 31.9213 | 0 | 30.5 | 0 | 30.5 |  | 2026-02-03 09:30 | 191.087 | 194.069 | 200.6 | 32.3448 | 0 | 32.3448 | 0 | 31.2 | 0 | 31.2 |  | 2026-02-03 09:30 | 188.443 | 191.993 | 197.6 | 31.9988 | 0 | 31.9988 | 0 | 30.4 | 0 | 30.4 |  | 2026-02-03 09:30 | 191.63 | 194.174 | 201.4 | 32.3623 | 0 | 32.3623 | 0 | 30.9 | 0 | 30.9 |  | 2026-02-03 09:30 | 141.644 | 143.437 | 147.7 | 23.9062 | 0 | 23.9062 | 0 | 22.5 | 0 | 22.5 |  | 2026-02-03 09:30 | 142.889 | 144.698 | 150 | 24.1163 | 0 | 24.1163 | 0 | 22.7 | 0 | 22.7 |  | 2026-02-03 09:30 | 142.801 | 144.522 | 148.8 | 24.087 | 0 | 24.087 | 0 | 22.7 | 0 | 22.7 |  | 2026-02-03 09:30 | 141.29 | 145.036 | 148.5 | 24.1727 | 0 | 24.1727 | 0 | 22.4 | 0 | 22.4 |  | 2026-02-03 09:30 | 133.6 | 135.305 | 140.6 | 22.5508 | 0 | 22.5508 | 0 | 21.5 | 0 | 21.5 |  | 2026-02-03 09:30 | 247.4603 | 0 | 247.4603 | 0 | 234.8 | 0 | 234.8
2026-02-03 09:20 |  |  | 175.041 | 177.257 | 168.2 | 29.5428 | 0 | 29.5428 | 0 | 27.4 | 0 | 27.4 |  | 2026-02-03 09:20 | 175.217 | 177.471 | 169.4 | 29.5785 | 0 | 29.5785 | 0 | 28.4 | 0 | 28.4 |  | 2026-02-03 09:20 | 174.091 | 177.311 | 167.2 | 29.5518 | 0 | 29.5518 | 0 | 27.9 | 0 | 27.9 |  | 2026-02-03 09:20 | 177.242 | 179.54 | 170.5 | 29.9233 | 0 | 29.9233 | 0 | 28.4 | 0 | 28.4 |  | 2026-02-03 09:20 | 130.932 | 132.536 | 125.2 | 22.0893 | 0 | 22.0893 | 0 | 21 | 0 | 21 |  | 2026-02-03 09:20 | 132.06 | 133.705 | 127.3 | 22.2842 | 0 | 22.2842 | 0 | 21.3 | 0 | 21.3 |  | 2026-02-03 09:20 | 131.821 | 133.449 | 126.1 | 22.2415 | 0 | 22.2415 | 0 | 21.1 | 0 | 21.1 |  | 2026-02-03 09:20 | 130.652 | 134.157 | 126.1 | 22.3595 | 0 | 22.3595 | 0 | 21 | 0 | 21 |  | 2026-02-03 09:20 | 123.592 | 125.131 | 119.1 | 20.8552 | 0 | 20.8552 | 0 | 19.7 | 0 | 19.7 |  | 2026-02-03 09:20 | 228.4262 | 0 | 228.4262 | 0 | 216.2 | 0 | 216.2
2026-02-03 09:10 |  |  | 159.535 | 161.511 | 140.8 | 26.9185 | 0 | 26.9185 | 0 | 26 | 0 | 26 |  | 2026-02-03 09:10 | 160.324 | 162.417 | 141 | 27.0695 | 0 | 27.0695 | 0 | 25.2 | 0 | 25.2 |  | 2026-02-03 09:10 | 158.747 | 161.462 | 139.3 | 26.9103 | 0 | 26.9103 | 0 | 25.1 | 0 | 25.1 |  | 2026-02-03 09:10 | 161.701 | 163.748 | 142.1 | 27.2913 | 0 | 27.2913 | 0 | 25.7 | 0 | 25.7 |  | 2026-02-03 09:10 | 119.315 | 120.752 | 104.2 | 20.1253 | 0 | 20.1253 | 0 | 18.9 | 0 | 18.9 |  | 2026-02-03 09:10 | 120.763 | 122.217 | 106 | 20.3695 | 0 | 20.3695 | 0 | 19.1 | 0 | 19.1 |  | 2026-02-03 09:10 | 119.802 | 121.245 | 105 | 20.2075 | 0 | 20.2075 | 0 | 19 | 0 | 19 |  | 2026-02-03 09:10 | 119.379 | 122.752 | 105.1 | 20.4587 | 0 | 20.4587 | 0 | 18.9 | 0 | 18.9 |  | 2026-02-03 09:10 | 112.91 | 114.293 | 99.4 | 19.0488 | 0 | 19.0488 | 0 | 18.1 | 0 | 18.1 |  | 2026-02-03 09:10 | 208.3995 | 0 | 208.3995 | 0 | 196 | 0 | 196
2026-02-03 09:00 |  |  | 143.044 | 145.752 | 114.8 | 24.292 | 0 | 24.292 | 0 | 22.2 | 0 | 22.2 |  | 2026-02-03 09:00 | 145.738 | 147.497 | 115.8 | 24.5828 | 0 | 24.5828 | 0 | 23.3 | 0 | 23.3 |  | 2026-02-03 09:00 | 143.405 | 145.555 | 114.2 | 24.2592 | 0 | 24.2592 | 0 | 22.8 | 0 | 22.8 |  | 2026-02-03 09:00 | 145.827 | 147.613 | 116.4 | 24.6022 | 0 | 24.6022 | 0 | 23.1 | 0 | 23.1 |  | 2026-02-03 09:00 | 107.69 | 108.976 | 85.3 | 18.1627 | 0 | 18.1627 | 0 | 17 | 0 | 17 |  | 2026-02-03 09:00 | 109.226 | 110.519 | 86.9 | 18.4198 | 0 | 18.4198 | 0 | 17.3 | 0 | 17.3 |  | 2026-02-03 09:00 | 108.507 | 109.792 | 86 | 18.2987 | 0 | 18.2987 | 0 | 17.2 | 0 | 17.2 |  | 2026-02-03 09:00 | 107.802 | 110.864 | 86.2 | 18.4773 | 0 | 18.4773 | 0 | 17.1 | 0 | 17.1 |  | 2026-02-03 09:00 | 102.044 | 103.273 | 81.3 | 17.2122 | 0 | 17.2122 | 0 | 16 | 0 | 16 |  | 2026-02-03 09:00 | 188.3068 | 0 | 188.3068 | 0 | 176 | 0 | 176
2026-02-03 08:50 | 368 |  | 128.773 | 130.297 | 92.6 | 21.7162 | 25.995 | -4.2788 | 155.9698 | 20.7 | 25.6232 | -4.9232 |  | 2026-02-03 08:50 | 129.685 | 131.234 | 92.5 | 21.8723 | 25.995 | -4.1226 | 155.9698 | 19.8 | 25.6232 | -5.8232 |  | 2026-02-03 08:50 | 127.734 | 129.47 | 91.4 | 21.5783 | 25.995 | -4.4166 | 155.9698 | 19.9 | 25.6232 | -5.7232 |  | 2026-02-03 08:50 | 130.273 | 131.829 | 93.3 | 21.9715 | 25.995 | -4.0235 | 155.9698 | 20.4 | 25.6232 | -5.2232 |  | 2026-02-03 08:50 | 95.821 | 96.946 | 68.3 | 16.1577 | 19.2555 | -3.0979 | 115.5332 | 15 | 18.9802 | -3.9802 |  | 2026-02-03 08:50 | 96.074 | 97.172 | 69.6 | 16.1953 | 19.2555 | -3.0602 | 115.5332 | 15.2 | 18.9802 | -3.7802 |  | 2026-02-03 08:50 | 96.436 | 97.53 | 68.8 | 16.255 | 19.2555 | -3.0005 | 115.5332 | 15 | 18.9802 | -3.9802 |  | 2026-02-03 08:50 | 96.165 | 98.764 | 69.1 | 16.4607 | 19.2555 | -2.7949 | 115.5332 | 15.1 | 18.9802 | -3.8802 |  | 2026-02-03 08:50 | 91.063 | 92.122 | 65.3 | 15.3537 | 18.3193 | -2.9656 | 109.9155 | 14.2 | 18.0573 | -3.8573 |  | 2026-02-03 08:50 | 167.5607 | 199.3213 | -31.7606 | 1195.9277 | 155.3 | 196.471 | -41.171
2026-02-03 08:40 | 325 |  | 112.449 | 113.705 | 71.9 | 18.9508 | 22.9575 | -4.0067 | 137.7451 | 17.4 | 22.6292 | -5.2292 |  | 2026-02-03 08:40 | 113.167 | 114.44 | 72.7 | 19.0733 | 22.9575 | -3.8842 | 137.7451 | 17.9 | 22.6292 | -4.7292 |  | 2026-02-03 08:40 | 111.795 | 113.186 | 71.5 | 18.8643 | 22.9575 | -4.0932 | 137.7451 | 17.3 | 22.6292 | -5.3292 |  | 2026-02-03 08:40 | 114.239 | 115.568 | 72.9 | 19.2613 | 22.9575 | -3.6962 | 137.7451 | 17.7 | 22.6292 | -4.9292 |  | 2026-02-03 08:40 | 83.924 | 84.926 | 53.3 | 14.1543 | 17.0056 | -2.8512 | 102.0334 | 13 | 16.7624 | -3.7624 |  | 2026-02-03 08:40 | 85.39 | 86.366 | 54.4 | 14.3943 | 17.0056 | -2.6112 | 102.0334 | 13.2 | 16.7624 | -3.5624 |  | 2026-02-03 08:40 | 84.148 | 85.144 | 53.8 | 14.1907 | 17.0056 | -2.8149 | 102.0334 | 13.1 | 16.7624 | -3.6624 |  | 2026-02-03 08:40 | 84.349 | 86.571 | 54 | 14.4285 | 17.0056 | -2.5771 | 102.0334 | 13 | 16.7624 | -3.7624 |  | 2026-02-03 08:40 | 79.912 | 80.866 | 51.1 | 13.4777 | 16.1787 | -2.701 | 97.0721 | 12.4 | 15.9473 | -3.5473 |  | 2026-02-03 08:40 | 146.7953 | 176.031 | -29.2357 | 1056.1862 | 135 | 173.5138 | -38.5138
2026-02-03 08:30 | 281 |  | 96.247 | 97.317 | 54.5 | 16.2195 | 19.8494 | -3.6299 | 119.0965 | 14.3 | 19.5656 | -5.2656 |  | 2026-02-03 08:30 | 97.229 | 98.34 | 54.8 | 16.39 | 19.8494 | -3.4594 | 119.0965 | 14.8 | 19.5656 | -4.7656 |  | 2026-02-03 08:30 | 95.694 | 96.836 | 54.2 | 16.1393 | 19.8494 | -3.7101 | 119.0965 | 14.6 | 19.5656 | -4.9656 |  | 2026-02-03 08:30 | 97.898 | 99.017 | 55.2 | 16.5028 | 19.8494 | -3.3466 | 119.0965 | 14.9 | 19.5656 | -4.6656 |  | 2026-02-03 08:30 | 71.749 | 72.628 | 40.3 | 12.1047 | 14.7033 | -2.5986 | 88.2197 | 10.9 | 14.493 | -3.593 |  | 2026-02-03 08:30 | 73.041 | 73.875 | 41.2 | 12.3125 | 14.7033 | -2.3908 | 88.2197 | 11.2 | 14.493 | -3.293 |  | 2026-02-03 08:30 | 72.249 | 73.113 | 40.7 | 12.1855 | 14.7033 | -2.5178 | 88.2197 | 11 | 14.493 | -3.493 |  | 2026-02-03 08:30 | 72.415 | 74.219 | 41 | 12.3698 | 14.7033 | -2.3334 | 88.2197 | 11.1 | 14.493 | -3.393 |  | 2026-02-03 08:30 | 68.6 | 69.447 | 38.7 | 11.5745 | 13.9883 | -2.4138 | 83.9301 | 10.4 | 13.7883 | -3.3883 |  | 2026-02-03 08:30 | 125.7987 | 152.1991 | -26.4005 | 913.1948 | 113.2 | 150.0227 | -36.8227
2026-02-03 08:20 | 240 |  | 80.837 | 81.744 | 40.2 | 13.624 | 16.9532 | -3.3292 | 101.7195 | 12.4 | 16.7108 | -4.3108 |  | 2026-02-03 08:20 | 80.742 | 82.171 | 40 | 13.6952 | 16.9532 | -3.2581 | 101.7195 | 12.3 | 16.7108 | -4.4108 |  | 2026-02-03 08:20 | 79.862 | 80.791 | 39.6 | 13.4652 | 16.9532 | -3.4881 | 101.7195 | 12 | 16.7108 | -4.7108 |  | 2026-02-03 08:20 | 81.671 | 82.612 | 40.3 | 13.7687 | 16.9532 | -3.1846 | 101.7195 | 12.3 | 16.7108 | -4.4108 |  | 2026-02-03 08:20 | 59.711 | 60.47 | 29.4 | 10.0783 | 12.558 | -2.4796 | 75.3477 | 8.9 | 12.3784 | -3.4784 |  | 2026-02-03 08:20 | 60.939 | 61.692 | 30 | 10.282 | 12.558 | -2.276 | 75.3477 | 9.1 | 12.3784 | -3.2784 |  | 2026-02-03 08:20 | 60.304 | 61.049 | 29.7 | 10.1748 | 12.558 | -2.3831 | 75.3477 | 9.1 | 12.3784 | -3.2784 |  | 2026-02-03 08:20 | 60.412 | 62.157 | 29.9 | 10.3595 | 12.558 | -2.1985 | 75.3477 | 9.1 | 12.3784 | -3.2784 |  | 2026-02-03 08:20 | 57.251 | 58.017 | 28.3 | 9.6695 | 11.9473 | -2.2778 | 71.684 | 8.7 | 11.7765 | -3.0765 |  | 2026-02-03 08:20 | 105.1172 | 129.9921 | -24.875 | 779.9529 | 93.9 | 128.1333 | -34.2333
2026-02-03 08:10 | 196 |  | 64.015 | 64.773 | 27.8 | 10.7955 | 13.8451 | -3.0496 | 83.0709 | 9.4 | 13.6472 | -4.2472 |  | 2026-02-03 08:10 | 65.313 | 66.568 | 27.7 | 11.0947 | 13.8451 | -2.7505 | 83.0709 | 9.6 | 13.6472 | -4.0472 |  | 2026-02-03 08:10 | 64.952 | 65.741 | 27.6 | 10.9568 | 13.8451 | -2.8883 | 83.0709 | 9.6 | 13.6472 | -4.0472 |  | 2026-02-03 08:10 | 66.366 | 67.179 | 28 | 11.1965 | 13.8451 | -2.6486 | 83.0709 | 9.8 | 13.6472 | -3.8472 |  | 2026-02-03 08:10 | 48.443 | 49.121 | 20.5 | 8.1868 | 10.2557 | -2.0688 | 61.534 | 7.2 | 10.109 | -2.909 |  | 2026-02-03 08:10 | 49.371 | 50.18 | 20.9 | 8.3633 | 10.2557 | -1.8923 | 61.534 | 7.3 | 10.109 | -2.809 |  | 2026-02-03 08:10 | 48.793 | 49.486 | 20.6 | 8.2477 | 10.2557 | -2.008 | 61.534 | 7.1 | 10.109 | -3.009 |  | 2026-02-03 08:10 | 48.952 | 50.459 | 20.8 | 8.4098 | 10.2557 | -1.8458 | 61.534 | 7.2 | 10.109 | -2.909 |  | 2026-02-03 08:10 | 46.487 | 47.166 | 19.6 | 7.861 | 9.757 | -1.896 | 58.542 | 6.8 | 9.6175 | -2.8175 |  | 2026-02-03 08:10 | 85.1122 | 106.1602 | -21.0481 | 636.9615 | 74 | 104.6422 | -30.6422
2026-02-03 08:00 | 153 |  | 50.343 | 51.027 | 18.4 | 8.5045 | 10.8077 | -2.3032 | 64.8462 | 7.3 | 10.6531 | -3.3531 |  | 2026-02-03 08:00 | 47.751 | 50.755 | 18.1 | 8.4592 | 10.8077 | -2.3485 | 64.8462 | 7.3 | 10.6531 | -3.3531 |  | 2026-02-03 08:00 | 49.885 | 50.573 | 18 | 8.4288 | 10.8077 | -2.3789 | 64.8462 | 7.1 | 10.6531 | -3.5531 |  | 2026-02-03 08:00 | 50.988 | 51.681 | 18.2 | 8.6135 | 10.8077 | -2.1942 | 64.8462 | 7.3 | 10.6531 | -3.3531 |  | 2026-02-03 08:00 | 37.148 | 37.729 | 13.3 | 6.2882 | 8.0057 | -1.7175 | 48.0342 | 5.3 | 7.8912 | -2.5912 |  | 2026-02-03 08:00 | 38.074 | 38.646 | 13.6 | 6.441 | 8.0057 | -1.5647 | 48.0342 | 5.5 | 7.8912 | -2.3912 |  | 2026-02-03 08:00 | 37.318 | 37.882 | 13.5 | 6.3137 | 8.0057 | -1.692 | 48.0342 | 5.4 | 7.8912 | -2.4912 |  | 2026-02-03 08:00 | 37.867 | 38.808 | 13.6 | 6.468 | 8.0057 | -1.5377 | 48.0342 | 5.4 | 7.8912 | -2.4912 |  | 2026-02-03 08:00 | 35.839 | 36.411 | 12.8 | 6.0685 | 7.6164 | -1.5479 | 45.6986 | 5.2 | 7.5075 | -2.3075 |  | 2026-02-03 08:00 | 65.5853 | 82.87 | -17.2847 | 497.2199 | 55.8 | 81.685 | -25.885
2026-02-03 07:50 | 113 |  | 35.738 | 37.443 | 11.1 | 6.2405 | 7.9822 | -1.7417 | 47.8929 | 5.1 | 7.868 | -2.768 |  | 2026-02-03 07:50 | 35.686 | 36.252 | 10.8 | 6.042 | 7.9822 | -1.9402 | 47.8929 | 4.9 | 7.868 | -2.968 |  | 2026-02-03 07:50 | 36.244 | 36.815 | 10.9 | 6.1358 | 7.9822 | -1.8463 | 47.8929 | 5 | 7.868 | -2.868 |  | 2026-02-03 07:50 | 36.849 | 37.429 | 10.9 | 6.2382 | 7.9822 | -1.744 | 47.8929 | 5 | 7.868 | -2.868 |  | 2026-02-03 07:50 | 26.877 | 27.372 | 8 | 4.562 | 5.9127 | -1.3507 | 35.4762 | 3.7 | 5.8282 | -2.1282 |  | 2026-02-03 07:50 | 27.667 | 28.157 | 8.1 | 4.6928 | 5.9127 | -1.2199 | 35.4762 | 3.8 | 5.8282 | -2.0282 |  | 2026-02-03 07:50 | 27.281 | 27.781 | 8.1 | 4.6302 | 5.9127 | -1.2825 | 35.4762 | 3.8 | 5.8282 | -2.0282 |  | 2026-02-03 07:50 | 27.556 | 28.354 | 8.2 | 4.7257 | 5.9127 | -1.187 | 35.4762 | 3.8 | 5.8282 | -2.0282 |  | 2026-02-03 07:50 | 26.06 | 26.551 | 7.6 | 4.4252 | 5.6252 | -1.2 | 33.7512 | 3.5 | 5.5448 | -2.0448 |  | 2026-02-03 07:50 | 47.6923 | 61.2046 | -13.5123 | 367.2278 | 38.6 | 60.3294 | -21.7294
2026-02-03 07:40 | 76 |  | 24.669 | 25.144 | 6 | 4.1907 | 5.3685 | -1.1779 | 32.2112 | 3.3 | 5.2918 | -1.9918 |  | 2026-02-03 07:40 | 23.768 | 24.84 | 5.9 | 4.14 | 5.3685 | -1.2285 | 32.2112 | 3.2 | 5.2918 | -2.0918 |  | 2026-02-03 07:40 | 24.312 | 24.803 | 5.9 | 4.1338 | 5.3685 | -1.2347 | 32.2112 | 3.2 | 5.2918 | -2.0918 |  | 2026-02-03 07:40 | 24.169 | 24.676 | 5.9 | 4.1127 | 5.3685 | -1.2559 | 32.2112 | 3.2 | 5.2918 | -2.0918 |  | 2026-02-03 07:40 | 17.797 | 18.298 | 4.3 | 3.0497 | 3.9767 | -0.92702 | 23.8601 | 2.4 | 3.9198 | -1.5198 |  | 2026-02-03 07:40 | 18.217 | 18.629 | 4.3 | 3.1048 | 3.9767 | -0.87185 | 23.8601 | 2.3 | 3.9198 | -1.6198 |  | 2026-02-03 07:40 | 18.154 | 18.576 | 4.3 | 3.096 | 3.9767 | -0.88069 | 23.8601 | 2.3 | 3.9198 | -1.6198 |  | 2026-02-03 07:40 | 18.337 | 19.245 | 4.4 | 3.2075 | 3.9767 | -0.76919 | 23.8601 | 2.4 | 3.9198 | -1.5198 |  | 2026-02-03 07:40 | 17.144 | 17.542 | 4.1 | 2.9237 | 3.7833 | -0.85966 | 22.6999 | 2.3 | 3.7292 | -1.4292 |  | 2026-02-03 07:40 | 31.9588 | 41.1642 | -9.2053 | 246.9851 | 24.6 | 40.5755 | -15.9755
2026-02-03 07:30 | 43 |  | 14.436 | 14.8 | 2.7 | 2.4667 | 3.0375 | -0.57079 | 18.2247 | 1.8 | 2.994 | -1.194 |  | 2026-02-03 07:30 | 13.548 | 14.3 | 2.7 | 2.3833 | 3.0375 | -0.65412 | 18.2247 | 1.8 | 2.994 | -1.194 |  | 2026-02-03 07:30 | 14.485 | 14.875 | 2.7 | 2.4792 | 3.0375 | -0.55829 | 18.2247 | 1.8 | 2.994 | -1.194 |  | 2026-02-03 07:30 | 14.326 | 14.976 | 2.7 | 2.496 | 3.0375 | -0.54146 | 18.2247 | 1.8 | 2.994 | -1.194 |  | 2026-02-03 07:30 | 10.598 | 11.163 | 1.9 | 1.8605 | 2.25 | -0.38947 | 13.4998 | 1.3 | 2.2178 | -0.91779 |  | 2026-02-03 07:30 | 10.721 | 11.074 | 2 | 1.8457 | 2.25 | -0.4043 | 13.4998 | 1.4 | 2.2178 | -0.81779 |  | 2026-02-03 07:30 | 10.798 | 11.16 | 2 | 1.86 | 2.25 | -0.38997 | 13.4998 | 1.4 | 2.2178 | -0.81779 |  | 2026-02-03 07:30 | 10.914 | 11.517 | 2 | 1.9195 | 2.25 | -0.33047 | 13.4998 | 1.3 | 2.2178 | -0.91779 |  | 2026-02-03 07:30 | 10.095 | 10.443 | 1.8 | 1.7405 | 2.1406 | -0.40007 | 12.8434 | 1.2 | 2.11 | -0.90996 |  | 2026-02-03 07:30 | 19.0513 | 23.2903 | -4.2389 | 139.7416 | 13.8 | 22.9572 | -9.1572
2026-02-03 07:20 | 21 |  | 7.359 | 7.653 | 0.9 | 1.2755 | 1.4834 | -0.20791 | 8.9005 | 0.8 | 1.4622 | -0.6622 |  | 2026-02-03 07:20 | 7.382 | 7.997 | 0.9 | 1.3328 | 1.4834 | -0.15058 | 8.9005 | 0.8 | 1.4622 | -0.6622 |  | 2026-02-03 07:20 | 7.392 | 7.693 | 0.9 | 1.2822 | 1.4834 | -0.20124 | 8.9005 | 0.8 | 1.4622 | -0.6622 |  | 2026-02-03 07:20 | 7.429 | 8.138 | 0.9 | 1.3563 | 1.4834 | -0.12708 | 8.9005 | 0.8 | 1.4622 | -0.6622 |  | 2026-02-03 07:20 | 5.384 | 5.893 | 0.6 | 0.98217 | 1.0988 | -0.11665 | 6.5929 | 0.5 | 1.0831 | -0.58311 |  | 2026-02-03 07:20 | 5.386 | 5.612 | 0.6 | 0.93533 | 1.0988 | -0.16349 | 6.5929 | 0.5 | 1.0831 | -0.58311 |  | 2026-02-03 07:20 | 5.454 | 5.697 | 0.6 | 0.9495 | 1.0988 | -0.14932 | 6.5929 | 0.5 | 1.0831 | -0.58311 |  | 2026-02-03 07:20 | 5.402 | 5.793 | 0.7 | 0.9655 | 1.0988 | -0.13332 | 6.5929 | 0.6 | 1.0831 | -0.48311 |  | 2026-02-03 07:20 | 4.993 | 5.218 | 0.6 | 0.86967 | 1.0454 | -0.17573 | 6.2724 | 0.5 | 1.0304 | -0.53044 |  | 2026-02-03 07:20 | 9.949 | 11.3743 | -1.4253 | 68.2459 | 5.8 | 11.2117 | -5.4117
2026-02-03 07:10 | 7 |  | 2.643 | 2.779 | 0.1 | 0.46317 | 0.49447 | -0.031303 | 2.9668 | 0.1 | 0.4874 | -0.3874 |  | 2026-02-03 07:10 | 2.729 | 3.392 | 0.1 | 0.56533 | 0.49447 | 0.070864 | 2.9668 | 0.1 | 0.4874 | -0.3874 |  | 2026-02-03 07:10 | 2.662 | 2.797 | 0.1 | 0.46617 | 0.49447 | -0.028303 | 2.9668 | 0.1 | 0.4874 | -0.3874 |  | 2026-02-03 07:10 | 2.736 | 3.492 | 0.1 | 0.582 | 0.49447 | 0.08753 | 2.9668 | 0.1 | 0.4874 | -0.3874 |  | 2026-02-03 07:10 | 1.842 | 2.501 | 0.1 | 0.41683 | 0.36627 | 0.05056 | 2.1976 | 0.1 | 0.36104 | -0.26104 |  | 2026-02-03 07:10 | 1.839 | 1.934 | 0.1 | 0.32233 | 0.36627 | -0.04394 | 2.1976 | 0.1 | 0.36104 | -0.26104 |  | 2026-02-03 07:10 | 1.812 | 1.905 | 0.1 | 0.3175 | 0.36627 | -0.048774 | 2.1976 | 0.1 | 0.36104 | -0.26104 |  | 2026-02-03 07:10 | 1.898 | 2.194 | 0.1 | 0.36567 | 0.36627 | -0.0006071 | 2.1976 | 0.1 | 0.36104 | -0.26104 |  | 2026-02-03 07:10 | 1.664 | 1.75 | 0.1 | 0.29167 | 0.34846 | -0.056797 | 2.0908 | 0.1 | 0.34348 | -0.24348 |  | 2026-02-03 07:10 | 3.7907 | 3.7914 | -0.00077082 | 22.7486 | 0.9 | 3.7372 | -2.8372
2026-02-03 07:00 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-02-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[110 empty] | Total: - | 17506.4953 | #VALUE! | #VALUE! |  | 17318.9 | #VALUE! | #VALUE!
Sum:- | 1823 |  | 13459.387 |  | 84296.3 |  |  |  |  | 2242.7 | #VALUE! | #VALUE! | 0.98379 |  | 12281.419 |  | 79611.5 |  |  |  |  | 2278 | #VALUE! | #VALUE! | 0.9154 |  | 13408.691 |  | 83897.3 |  |  |  |  | 2234.6 | #VALUE! | #VALUE! | 0.97385 |  | 13608.313 |  | 85229.4 |  |  |  |  | 2267.8 | #VALUE! | #VALUE! | 0.98343 |  | 10144.263 |  | 63430.7 |  |  |  |  | 1690.8 | #VALUE! | #VALUE! | 0.98485 |  | 10092.179 |  | 63306.6 |  |  |  |  | 1682.2 | #VALUE! | #VALUE! | 0.98293 |  | 10090.361 |  | 63229.4 |  |  |  |  | 1681.4 | #VALUE! | #VALUE! | 0.98214 |  | 9994.32 |  | 62730.6 |  |  |  |  | 1665.4 | #VALUE! | #VALUE! | 0.9716 |  | 9457.773 |  | 59351 |  |  |  |  | 1576 | #VALUE! | #VALUE! | 0.9851
Formulas:
Time = [Time]

## 3 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
POA & WMS not working right now |  | POA & WMS not working right now | 0 | 0 | 2227.8 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 2261.4 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 2216.9 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 2248.2 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 1676.7 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 1666.5 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 1667 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 1676.2 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | 0 | 1585.7 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 2026-03-03 19:00 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 1 | 98.36%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 98.34%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 97.33%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 98.32%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 98.46%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 98.23%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 98.19%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 97.16%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 98.49%
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 17:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 2227.8 | 0 | 0 | 0 | 0 | 10.2 | 0 | 10.2 |  | 2026-03-03 17:10 | 0 | 0 | 2261.4 | 0 | 0 | 0 | 0 | 10.9 | 0 | 10.9 |  | 2026-03-03 17:10 | 0 | 0 | 2216.9 | 0 | 0 | 0 | 0 | 10.5 | 0 | 10.5 |  | 2026-03-03 17:10 | 0 | 0 | 2248.2 | 0 | 0 | 0 | 0 | 10.5 | 0 | 10.5 |  | 2026-03-03 17:10 | 0 | 0 | 1676.7 | 0 | 0 | 0 | 0 | 7.8 | 0 | 7.8 |  | 2026-03-03 17:10 | 0 | 0 | 1666.5 | 0 | 0 | 0 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 17:10 | 0 | 0 | 1667 | 0 | 0 | 0 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 17:10 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 17:10 | 0 | 0 | 1585.7 | 0 | 0 | 0 | 0 | 7.2 | 0 | 7.2 |  | 2026-03-03 17:10 | 0 | 0 | 0 | 0 | 80.2 | 0 | 80.2
|  |  | 113.174 | 114.37 | 2217.6 | 19.0617 | 0 | 19.0617 | 0 | 20.3 | 0 | 20.3 |  | 2026-03-03 17:00 | 115.889 | 117.404 | 2250.5 | 19.5673 | 0 | 19.5673 | 0 | 20.2 | 0 | 20.2 |  | 2026-03-03 17:00 | 114.219 | 116.558 | 2206.4 | 19.4263 | 0 | 19.4263 | 0 | 20.1 | 0 | 20.1 |  | 2026-03-03 17:00 | 114.922 | 116.394 | 2237.7 | 19.399 | 0 | 19.399 | 0 | 20.4 | 0 | 20.4 |  | 2026-03-03 17:00 | 86.216 | 87.36 | 1668.9 | 14.56 | 0 | 14.56 | 0 | 15.5 | 0 | 15.5 |  | 2026-03-03 17:00 | 84.448 | 85.552 | 1658.8 | 14.2587 | 0 | 14.2587 | 0 | 15.2 | 0 | 15.2 |  | 2026-03-03 17:00 | 84.597 | 85.711 | 1659.3 | 14.2852 | 0 | 14.2852 | 0 | 15.2 | 0 | 15.2 |  | 2026-03-03 17:00 | 85.001 | 87.302 | 1668.5 | 14.5503 | 0 | 14.5503 | 0 | 15.3 | 0 | 15.3 |  | 2026-03-03 17:00 | 79.259 | 80.311 | 1578.5 | 13.3852 | 0 | 13.3852 | 0 | 14.4 | 0 | 14.4 |  | 2026-03-03 17:00 | 148.4937 | 0 | 148.4937 | 0 | 156.6 | 0 | 156.6
|  |  | 128.7 | 130.356 | 2197.3 | 21.726 | 0 | 21.726 | 0 | 48.1 | 0 | 48.1 |  | 2026-03-03 16:50 | 131.109 | 132.836 | 2230.3 | 22.1393 | 0 | 22.1393 | 0 | 23 | 0 | 23 |  | 2026-03-03 16:50 | 129.479 | 132.029 | 2186.3 | 22.0048 | 0 | 22.0048 | 0 | 22.9 | 0 | 22.9 |  | 2026-03-03 16:50 | 130.607 | 132.3 | 2217.3 | 22.05 | 0 | 22.05 | 0 | 23.3 | 0 | 23.3 |  | 2026-03-03 16:50 | 97.916 | 99.186 | 1653.4 | 16.531 | 0 | 16.531 | 0 | 17.3 | 0 | 17.3 |  | 2026-03-03 16:50 | 96.339 | 97.558 | 1643.6 | 16.2597 | 0 | 16.2597 | 0 | 16.9 | 0 | 16.9 |  | 2026-03-03 16:50 | 96.326 | 97.555 | 1644.1 | 16.2592 | 0 | 16.2592 | 0 | 16.9 | 0 | 16.9 |  | 2026-03-03 16:50 | 96.779 | 99.293 | 1653.2 | 16.5488 | 0 | 16.5488 | 0 | 16.9 | 0 | 16.9 |  | 2026-03-03 16:50 | 91.166 | 92.329 | 1564.1 | 15.3882 | 0 | 15.3882 | 0 | 16 | 0 | 16 |  | 2026-03-03 16:50 | 168.907 | 0 | 168.907 | 0 | 201.3 | 0 | 201.3
|  |  | 143.774 | 145.682 | 2174.6 | 24.2803 | 0 | 24.2803 | 0 | 0 | 0 | 0 |  | 2026-03-03 16:40 | 147.716 | 149.78 | 2207.3 | 24.9633 | 0 | 24.9633 | 0 | 25.9 | 0 | 25.9 |  | 2026-03-03 16:40 | 144.487 | 147.634 | 2163.4 | 24.6057 | 0 | 24.6057 | 0 | 25.4 | 0 | 25.4 |  | 2026-03-03 16:40 | 145.743 | 147.722 | 2194 | 24.6203 | 0 | 24.6203 | 0 | 25.3 | 0 | 25.3 |  | 2026-03-03 16:40 | 109.354 | 110.806 | 1636.1 | 18.4677 | 0 | 18.4677 | 0 | 18.9 | 0 | 18.9 |  | 2026-03-03 16:40 | 107.405 | 108.809 | 1626.7 | 18.1348 | 0 | 18.1348 | 0 | 18.7 | 0 | 18.7 |  | 2026-03-03 16:40 | 107.477 | 108.893 | 1627.2 | 18.1488 | 0 | 18.1488 | 0 | 19 | 0 | 19 |  | 2026-03-03 16:40 | 107.582 | 110.597 | 1636.3 | 18.4328 | 0 | 18.4328 | 0 | 19 | 0 | 19 |  | 2026-03-03 16:40 | 101.483 | 102.809 | 1548.1 | 17.1348 | 0 | 17.1348 | 0 | 17.9 | 0 | 17.9 |  | 2026-03-03 16:40 | 188.7887 | 0 | 188.7887 | 0 | 170.1 | 0 | 170.1
|  |  | 160.04 | 162.197 | 2149.2 | 27.0328 | 0 | 27.0328 | 0 | 27.6 | 0 | 27.6 |  | 2026-03-03 16:30 | 163.218 | 165.17 | 2181.4 | 27.5283 | 0 | 27.5283 | 0 | 28.6 | 0 | 28.6 |  | 2026-03-03 16:30 | 160.079 | 163.589 | 2138 | 27.2648 | 0 | 27.2648 | 0 | 27.8 | 0 | 27.8 |  | 2026-03-03 16:30 | 161.713 | 163.926 | 2168.7 | 27.321 | 0 | 27.321 | 0 | 28 | 0 | 28 |  | 2026-03-03 16:30 | 120.707 | 122.325 | 1617.2 | 20.3875 | 0 | 20.3875 | 0 | 21 | 0 | 21 |  | 2026-03-03 16:30 | 118.853 | 120.431 | 1608 | 20.0718 | 0 | 20.0718 | 0 | 20.7 | 0 | 20.7 |  | 2026-03-03 16:30 | 118.806 | 120.395 | 1608.2 | 20.0658 | 0 | 20.0658 | 0 | 20.3 | 0 | 20.3 |  | 2026-03-03 16:30 | 118.696 | 121.73 | 1617.3 | 20.2883 | 0 | 20.2883 | 0 | 20.3 | 0 | 20.3 |  | 2026-03-03 16:30 | 112.278 | 113.809 | 1530.2 | 18.9682 | 0 | 18.9682 | 0 | 19.5 | 0 | 19.5 |  | 2026-03-03 16:30 | 208.9287 | 0 | 208.9287 | 0 | 213.8 | 0 | 213.8
|  |  | 172.403 | 174.798 | 2121.6 | 29.133 | 0 | 29.133 | 0 | 29.9 | 0 | 29.9 |  | 2026-03-03 16:20 | 177.319 | 178.172 | 2152.8 | 29.6953 | 0 | 29.6953 | 0 | 31.3 | 0 | 31.3 |  | 2026-03-03 16:20 | 172.929 | 176.873 | 2110.2 | 29.4788 | 0 | 29.4788 | 0 | 30 | 0 | 30 |  | 2026-03-03 16:20 | 174.798 | 177.262 | 2140.7 | 29.5437 | 0 | 29.5437 | 0 | 30.3 | 0 | 30.3 |  | 2026-03-03 16:20 | 130.804 | 132.567 | 1596.2 | 22.0945 | 0 | 22.0945 | 0 | 22.7 | 0 | 22.7 |  | 2026-03-03 16:20 | 129.084 | 130.824 | 1587.3 | 21.804 | 0 | 21.804 | 0 | 22.6 | 0 | 22.6 |  | 2026-03-03 16:20 | 128.937 | 130.688 | 1587.9 | 21.7813 | 0 | 21.7813 | 0 | 22.7 | 0 | 22.7 |  | 2026-03-03 16:20 | 128.999 | 132.673 | 1597 | 22.1122 | 0 | 22.1122 | 0 | 22.7 | 0 | 22.7 |  | 2026-03-03 16:20 | 122.329 | 123.965 | 1510.7 | 20.6608 | 0 | 20.6608 | 0 | 21.2 | 0 | 21.2 |  | 2026-03-03 16:20 | 226.3037 | 0 | 226.3037 | 0 | 233.4 | 0 | 233.4
|  |  | 186.885 | 189.519 | 2091.7 | 31.5865 | 0 | 31.5865 | 0 | 32.4 | 0 | 32.4 |  | 2026-03-03 16:10 | 189.97 | 192.687 | 2121.5 | 32.1145 | 0 | 32.1145 | 0 | 32.2 | 0 | 32.2 |  | 2026-03-03 16:10 | 186.65 | 191.229 | 2080.2 | 31.8715 | 0 | 31.8715 | 0 | 32.4 | 0 | 32.4 |  | 2026-03-03 16:10 | 188.483 | 191.179 | 2110.4 | 31.8632 | 0 | 31.8632 | 0 | 32.8 | 0 | 32.8 |  | 2026-03-03 16:10 | 141.058 | 142.988 | 1573.5 | 23.8313 | 0 | 23.8313 | 0 | 24.5 | 0 | 24.5 |  | 2026-03-03 16:10 | 139.224 | 141.687 | 1564.7 | 23.6145 | 0 | 23.6145 | 0 | 23.9 | 0 | 23.9 |  | 2026-03-03 16:10 | 139.266 | 141.276 | 1565.2 | 23.546 | 0 | 23.546 | 0 | 23.9 | 0 | 23.9 |  | 2026-03-03 16:10 | 139.421 | 143.588 | 1574.3 | 23.9313 | 0 | 23.9313 | 0 | 23.9 | 0 | 23.9 |  | 2026-03-03 16:10 | 131.936 | 133.728 | 1489.5 | 22.288 | 0 | 22.288 | 0 | 22.6 | 0 | 22.6 |  | 2026-03-03 16:10 | 244.6468 | 0 | 244.6468 | 0 | 248.6 | 0 | 248.6
|  |  | 201.094 | 203.991 | 2059.3 | 33.9985 | 0 | 33.9985 | 0 | 34.9 | 0 | 34.9 |  | 2026-03-03 16:00 | 204.069 | 207.072 | 2089.3 | 34.512 | 0 | 34.512 | 0 | 35.9 | 0 | 35.9 |  | 2026-03-03 16:00 | 200.721 | 205.549 | 2047.8 | 34.2582 | 0 | 34.2582 | 0 | 34.4 | 0 | 34.4 |  | 2026-03-03 16:00 | 202.733 | 205.695 | 2077.6 | 34.2825 | 0 | 34.2825 | 0 | 34.8 | 0 | 34.8 |  | 2026-03-03 16:00 | 151.887 | 153.981 | 1549 | 25.6635 | 0 | 25.6635 | 0 | 26 | 0 | 26 |  | 2026-03-03 16:00 | 149.665 | 151.82 | 1540.8 | 25.3033 | 0 | 25.3033 | 0 | 25.7 | 0 | 25.7 |  | 2026-03-03 16:00 | 149.766 | 152.028 | 1541.3 | 25.338 | 0 | 25.338 | 0 | 25.9 | 0 | 25.9 |  | 2026-03-03 16:00 | 149.936 | 154.039 | 1550.4 | 25.6732 | 0 | 25.6732 | 0 | 26 | 0 | 26 |  | 2026-03-03 16:00 | 141.64 | 143.593 | 1466.9 | 23.9322 | 0 | 23.9322 | 0 | 24.6 | 0 | 24.6 |  | 2026-03-03 16:00 | 262.9613 | 0 | 262.9613 | 0 | 268.2 | 0 | 268.2
|  |  | 214.546 | 216.798 | 2024.4 | 36.133 | 0 | 36.133 | 0 | 37.6 | 0 | 37.6 |  | 2026-03-03 15:50 | 217.495 | 220.717 | 2053.4 | 36.7862 | 0 | 36.7862 | 0 | 36.1 | 0 | 36.1 |  | 2026-03-03 15:50 | 213.469 | 218.486 | 2013.4 | 36.4143 | 0 | 36.4143 | 0 | 36.5 | 0 | 36.5 |  | 2026-03-03 15:50 | 215.838 | 219.036 | 2042.8 | 36.506 | 0 | 36.506 | 0 | 36.9 | 0 | 36.9 |  | 2026-03-03 15:50 | 161.305 | 163.595 | 1523 | 27.2658 | 0 | 27.2658 | 0 | 27.9 | 0 | 27.9 |  | 2026-03-03 15:50 | 159.474 | 161.745 | 1515.1 | 26.9575 | 0 | 26.9575 | 0 | 27.6 | 0 | 27.6 |  | 2026-03-03 15:50 | 159.173 | 161.532 | 1515.4 | 26.922 | 0 | 26.922 | 0 | 27.2 | 0 | 27.2 |  | 2026-03-03 15:50 | 159.557 | 164.116 | 1524.4 | 27.3527 | 0 | 27.3527 | 0 | 27.3 | 0 | 27.3 |  | 2026-03-03 15:50 | 150.911 | 153.007 | 1442.3 | 25.5012 | 0 | 25.5012 | 0 | 25.8 | 0 | 25.8 |  | 2026-03-03 15:50 | 279.8387 | 0 | 279.8387 | 0 | 282.9 | 0 | 282.9
|  |  | 228.046 | 230.864 | 1986.8 | 38.4773 | 0 | 38.4773 | 0 | 77.8 | 0 | 77.8 |  | 2026-03-03 15:40 | 232.31 | 235.456 | 2017.3 | 39.2427 | 0 | 39.2427 | 0 | 39.3 | 0 | 39.3 |  | 2026-03-03 15:40 | 226.297 | 232.083 | 1976.9 | 38.6805 | 0 | 38.6805 | 0 | 39 | 0 | 39 |  | 2026-03-03 15:40 | 228.515 | 231.995 | 2005.9 | 38.6658 | 0 | 38.6658 | 0 | 39.3 | 0 | 39.3 |  | 2026-03-03 15:40 | 171.398 | 173.849 | 1495.1 | 28.9748 | 0 | 28.9748 | 0 | 29.2 | 0 | 29.2 |  | 2026-03-03 15:40 | 168.812 | 171.557 | 1487.5 | 28.5928 | 0 | 28.5928 | 0 | 28.7 | 0 | 28.7 |  | 2026-03-03 15:40 | 168.892 | 171.717 | 1488.2 | 28.6195 | 0 | 28.6195 | 0 | 28.8 | 0 | 28.8 |  | 2026-03-03 15:40 | 169.357 | 174.094 | 1497.1 | 29.0157 | 0 | 29.0157 | 0 | 28.8 | 0 | 28.8 |  | 2026-03-03 15:40 | 159.962 | 162.217 | 1416.5 | 27.0362 | 0 | 27.0362 | 0 | 27.7 | 0 | 27.7 |  | 2026-03-03 15:40 | 297.3053 | 0 | 297.3053 | 0 | 338.6 | 0 | 338.6
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 15:30 | 238.209 | 241.91 | 1978 | 40.3183 | 0 | 40.3183 | 0 | 40.8 | 0 | 40.8 |  | 2026-03-03 15:30 | 234.095 | 240.289 | 1937.9 | 40.0482 | 0 | 40.0482 | 0 | 40.1 | 0 | 40.1 |  | 2026-03-03 15:30 | 236.998 | 240.68 | 1966.6 | 40.1133 | 0 | 40.1133 | 0 | 40.6 | 0 | 40.6 |  | 2026-03-03 15:30 | 176.551 | 179.112 | 1465.9 | 29.852 | 0 | 29.852 | 0 | 30.3 | 0 | 30.3 |  | 2026-03-03 15:30 | 174.982 | 177.684 | 1458.8 | 29.614 | 0 | 29.614 | 0 | 29.9 | 0 | 29.9 |  | 2026-03-03 15:30 | 174.715 | 177.434 | 1459.4 | 29.5723 | 0 | 29.5723 | 0 | 30.5 | 0 | 30.5 |  | 2026-03-03 15:30 | 175.501 | 180.433 | 1468.3 | 30.0722 | 0 | 30.0722 | 0 | 30.6 | 0 | 30.6 |  | 2026-03-03 15:30 | 166.155 | 168.531 | 1388.8 | 28.0885 | 0 | 28.0885 | 0 | 28.4 | 0 | 28.4 |  | 2026-03-03 15:30 | 267.6788 | 0 | 267.6788 | 0 | 271.2 | 0 | 271.2
|  |  | 247.23 | 251.097 | 1909 | 41.8495 | 0 | 41.8495 | 0 | 42 | 0 | 42 |  | 2026-03-03 15:20 | 251.682 | 255.696 | 1937.2 | 42.616 | 0 | 42.616 | 0 | 43.3 | 0 | 43.3 |  | 2026-03-03 15:20 | 246.568 | 252.684 | 1897.8 | 42.114 | 0 | 42.114 | 0 | 42 | 0 | 42 |  | 2026-03-03 15:20 | 249.087 | 253.118 | 1926 | 42.1863 | 0 | 42.1863 | 0 | 42.5 | 0 | 42.5 |  | 2026-03-03 15:20 | 186.669 | 189.452 | 1435.6 | 31.5753 | 0 | 31.5753 | 0 | 31.8 | 0 | 31.8 |  | 2026-03-03 15:20 | 183.924 | 187.225 | 1428.9 | 31.2042 | 0 | 31.2042 | 0 | 31.4 | 0 | 31.4 |  | 2026-03-03 15:20 | 184.518 | 187.511 | 1428.9 | 31.2518 | 0 | 31.2518 | 0 | 31 | 0 | 31 |  | 2026-03-03 15:20 | 184.979 | 190.151 | 1437.7 | 31.6918 | 0 | 31.6918 | 0 | 31.5 | 0 | 31.5 |  | 2026-03-03 15:20 | 174.94 | 177.496 | 1360.4 | 29.5827 | 0 | 29.5827 | 0 | 29.8 | 0 | 29.8 |  | 2026-03-03 15:20 | 324.0717 | 0 | 324.0717 | 0 | 325.3 | 0 | 325.3
|  |  | 257.298 | 261.375 | 1867 | 43.5625 | 0 | 43.5625 | 0 | 43.7 | 0 | 43.7 |  | 2026-03-03 15:10 | 261.33 | 265.552 | 1893.9 | 44.2587 | 0 | 44.2587 | 0 | 44.4 | 0 | 44.4 |  | 2026-03-03 15:10 | 256.31 | 262.795 | 1855.8 | 43.7992 | 0 | 43.7992 | 0 | 43.5 | 0 | 43.5 |  | 2026-03-03 15:10 | 259.865 | 264.037 | 1883.5 | 44.0062 | 0 | 44.0062 | 0 | 44 | 0 | 44 |  | 2026-03-03 15:10 | 193.988 | 196.862 | 1403.8 | 32.8103 | 0 | 32.8103 | 0 | 32.9 | 0 | 32.9 |  | 2026-03-03 15:10 | 192.019 | 195.163 | 1397.5 | 32.5272 | 0 | 32.5272 | 0 | 33 | 0 | 33 |  | 2026-03-03 15:10 | 191.894 | 194.98 | 1397.9 | 32.4967 | 0 | 32.4967 | 0 | 32.9 | 0 | 32.9 |  | 2026-03-03 15:10 | 192.583 | 198.126 | 1406.2 | 33.021 | 0 | 33.021 | 0 | 32.6 | 0 | 32.6 |  | 2026-03-03 15:10 | 182.604 | 185.291 | 1330.6 | 30.8818 | 0 | 30.8818 | 0 | 31.3 | 0 | 31.3 |  | 2026-03-03 15:10 | 337.3635 | 0 | 337.3635 | 0 | 338.3 | 0 | 338.3
|  |  | 267.797 | 271.286 | 1823.3 | 45.2143 | 0 | 45.2143 | 0 | 46.1 | 0 | 46.1 | 0.9839 | 2026-03-03 15:00 | 271.475 | 275.889 | 1849.5 | 45.9815 | 0 | 45.9815 | 0 | 45.5 | 0 | 45.5 | 0.984 | 2026-03-03 15:00 | 266.175 | 273.352 | 1812.3 | 45.5587 | 0 | 45.5587 | 0 | 45.3 | 0 | 45.3 | 0.97374 | 2026-03-03 15:00 | 269.34 | 273.72 | 1839.5 | 45.62 | 0 | 45.62 | 0 | 45.7 | 0 | 45.7 | 0.984 | 2026-03-03 15:00 | 201.506 | 204.533 | 1370.9 | 34.0888 | 0 | 34.0888 | 0 | 34.3 | 0 | 34.3 | 0.9852 | 2026-03-03 15:00 | 199.244 | 202.798 | 1364.5 | 33.7997 | 0 | 33.7997 | 0 | 33.3 | 0 | 33.3 | 0.98248 | 2026-03-03 15:00 | 199.25 | 203.05 | 1365 | 33.8417 | 0 | 33.8417 | 0 | 33.4 | 0 | 33.4 | 0.98129 | 2026-03-03 15:00 | 199.821 | 205.521 | 1373.6 | 34.2535 | 0 | 34.2535 | 0 | 33.4 | 0 | 33.4 | 0.97227 | 2026-03-03 15:00 | 189.224 | 192.047 | 1299.3 | 32.0078 | 0 | 32.0078 | 0 | 31.2 | 0 | 31.2 | 0.9853 | 2026-03-03 15:00 | 350.366 | 0 | 350.366 | 0 | 348.2 | 0 | 348.2
|  |  | 275.64 | 280.149 | 1777.2 | 46.6915 | 0 | 46.6915 | 0 | 45.7 | 0 | 45.7 | 0.98401 | 2026-03-03 14:50 | 279.282 | 283.91 | 1804 | 47.3183 | 0 | 47.3183 | 0 | 46.9 | 0 | 46.9 | 0.9837 | 2026-03-03 14:50 | 273.99 | 281.144 | 1767 | 46.8573 | 0 | 46.8573 | 0 | 45.9 | 0 | 45.9 | 0.97455 | 2026-03-03 14:50 | 276.119 | 280.723 | 1793.8 | 46.7872 | 0 | 46.7872 | 0 | 46.4 | 0 | 46.4 | 0.9836 | 2026-03-03 14:50 | 206.599 | 209.766 | 1336.6 | 34.961 | 0 | 34.961 | 0 | 34.7 | 0 | 34.7 | 0.9849 | 2026-03-03 14:50 | 203.477 | 206.988 | 1331.2 | 34.498 | 0 | 34.498 | 0 | 34.3 | 0 | 34.3 | 0.98304 | 2026-03-03 14:50 | 203.504 | 207.39 | 1331.6 | 34.565 | 0 | 34.565 | 0 | 34.3 | 0 | 34.3 | 0.98126 | 2026-03-03 14:50 | 203.948 | 209.617 | 1340.2 | 34.9362 | 0 | 34.9362 | 0 | 35 | 0 | 35 | 0.97296 | 2026-03-03 14:50 | 192.791 | 195.707 | 1268.1 | 32.6178 | 0 | 32.6178 | 0 | 33.1 | 0 | 33.1 | 0.9851 | 2026-03-03 14:50 | 359.2323 | 0 | 359.2323 | 0 | 356.3 | 0 | 356.3
|  |  | 284.003 | 288.619 | 1731.5 | 48.1032 | 0 | 48.1032 | 0 | 47.3 | 0 | 47.3 | 0.9836 | 2026-03-03 14:40 | 290.506 | 293.188 | 1757.1 | 48.8647 | 0 | 48.8647 | 0 | 49.5 | 0 | 49.5 | 0.99085 | 2026-03-03 14:40 | 281.576 | 289.177 | 1721.1 | 48.1962 | 0 | 48.1962 | 0 | 47.1 | 0 | 47.1 | 0.97372 | 2026-03-03 14:40 | 285.244 | 290.059 | 1747.4 | 48.3432 | 0 | 48.3432 | 0 | 47.7 | 0 | 47.7 | 0.9834 | 2026-03-03 14:40 | 213.256 | 216.57 | 1301.9 | 36.095 | 0 | 36.095 | 0 | 36.2 | 0 | 36.2 | 0.9847 | 2026-03-03 14:40 | 210.479 | 214.105 | 1296.9 | 35.6842 | 0 | 35.6842 | 0 | 35.7 | 0 | 35.7 | 0.98306 | 2026-03-03 14:40 | 211.184 | 215.206 | 1297.3 | 35.8677 | 0 | 35.8677 | 0 | 35.8 | 0 | 35.8 | 0.98131 | 2026-03-03 14:40 | 211.927 | 217.841 | 1305.2 | 36.3068 | 0 | 36.3068 | 0 | 35.3 | 0 | 35.3 | 0.97285 | 2026-03-03 14:40 | 200.209 | 203.238 | 1235 | 33.873 | 0 | 33.873 | 0 | 33.3 | 0 | 33.3 | 0.9851 | 2026-03-03 14:40 | 371.3338 | 0 | 371.3338 | 0 | 367.9 | 0 | 367.9
|  |  | 288.9 | 293.717 | 1684.2 | 48.9528 | 0 | 48.9528 | 0 | 49.9 | 0 | 49.9 | 0.9834 | 2026-03-03 14:30 | 294.166 | 299.162 | 1707.6 | 49.8603 | 0 | 49.8603 | 0 | 49.1 | 0 | 49.1 | 0.9833 | 2026-03-03 14:30 | 287.372 | 295.125 | 1674 | 49.1875 | 0 | 49.1875 | 0 | 48.9 | 0 | 48.9 | 0.97373 | 2026-03-03 14:30 | 291.031 | 296.004 | 1699.7 | 49.334 | 0 | 49.334 | 0 | 49.5 | 0 | 49.5 | 0.9832 | 2026-03-03 14:30 | 217.835 | 221.22 | 1265.7 | 36.87 | 0 | 36.87 | 0 | 36.5 | 0 | 36.5 | 0.9847 | 2026-03-03 14:30 | 215.237 | 219.24 | 1261.2 | 36.54 | 0 | 36.54 | 0 | 36 | 0 | 36 | 0.98174 | 2026-03-03 14:30 | 215.364 | 219.236 | 1261.5 | 36.5393 | 0 | 36.5393 | 0 | 36.1 | 0 | 36.1 | 0.98234 | 2026-03-03 14:30 | 216.086 | 222.187 | 1269.9 | 37.0312 | 0 | 37.0312 | 0 | 36.7 | 0 | 36.7 | 0.97254 | 2026-03-03 14:30 | 204.47 | 207.605 | 1201.7 | 34.6008 | 0 | 34.6008 | 0 | 34.7 | 0 | 34.7 | 0.9849 | 2026-03-03 14:30 | 378.916 | 0 | 378.916 | 0 | 377.4 | 0 | 377.4
|  |  | 296.603 | 301.61 | 1634.3 | 50.2683 | 0 | 50.2683 | 0 | 49.1 | 0 | 49.1 | 0.9832 | 2026-03-03 14:20 | 300.249 | 305.41 | 1658.5 | 50.9017 | 0 | 50.9017 | 0 | 50.6 | 0 | 50.6 | 0.9831 | 2026-03-03 14:20 | 295.341 | 303.855 | 1625.1 | 50.6425 | 0 | 50.6425 | 0 | 49.7 | 0 | 49.7 | 0.97198 | 2026-03-03 14:20 | 298.362 | 303.491 | 1650.2 | 50.5818 | 0 | 50.5818 | 0 | 50.2 | 0 | 50.2 | 0.9831 | 2026-03-03 14:20 | 223.577 | 227.105 | 1229.2 | 37.8508 | 0 | 37.8508 | 0 | 37.7 | 0 | 37.7 | 0.98447 | 2026-03-03 14:20 | 220.413 | 224.51 | 1225.2 | 37.4183 | 0 | 37.4183 | 0 | 37.2 | 0 | 37.2 | 0.98175 | 2026-03-03 14:20 | 220.745 | 225.209 | 1225.4 | 37.5348 | 0 | 37.5348 | 0 | 37.2 | 0 | 37.2 | 0.98018 | 2026-03-03 14:20 | 221.284 | 227.561 | 1233.2 | 37.9268 | 0 | 37.9268 | 0 | 38 | 0 | 38 | 0.97242 | 2026-03-03 14:20 | 209.464 | 212.719 | 1167 | 35.4532 | 0 | 35.4532 | 0 | 35.5 | 0 | 35.5 | 0.9847 | 2026-03-03 14:20 | 388.5783 | 0 | 388.5783 | 0 | 385.2 | 0 | 385.2
|  |  | 302.196 | 307.36 | 1585.2 | 51.2267 | 0 | 51.2267 | 0 | 52.1 | 0 | 52.1 | 0.983 | 2026-03-03 14:10 | 307.172 | 312.432 | 1607.9 | 52.072 | 0 | 52.072 | 0 | 53 | 0 | 53 | 0.98316 | 2026-03-03 14:10 | 301.042 | 309.216 | 1575.4 | 51.536 | 0 | 51.536 | 0 | 51 | 0 | 51 | 0.97357 | 2026-03-03 14:10 | 304.799 | 310.07 | 1600 | 51.6783 | 0 | 51.6783 | 0 | 51.8 | 0 | 51.8 | 0.983 | 2026-03-03 14:10 | 228.532 | 232.177 | 1191.5 | 38.6962 | 0 | 38.6962 | 0 | 38.7 | 0 | 38.7 | 0.9843 | 2026-03-03 14:10 | 226.037 | 230.284 | 1188 | 38.3807 | 0 | 38.3807 | 0 | 38.2 | 0 | 38.2 | 0.98156 | 2026-03-03 14:10 | 225.802 | 229.762 | 1188.2 | 38.2937 | 0 | 38.2937 | 0 | 38.1 | 0 | 38.1 | 0.98276 | 2026-03-03 14:10 | 227.469 | 234.087 | 1195.2 | 39.0145 | 0 | 39.0145 | 0 | 37.3 | 0 | 37.3 | 0.97173 | 2026-03-03 14:10 | 215.352 | 218.72 | 1131.5 | 36.4533 | 0 | 36.4533 | 0 | 35.8 | 0 | 35.8 | 0.9846 | 2026-03-03 14:10 | 397.3513 | 0 | 397.3513 | 0 | 396 | 0 | 396
|  |  | 312.386 | 317.788 | 1533.1 | 52.9647 | 0 | 52.9647 | 0 | 50.7 | 0 | 50.7 | 0.983 | 2026-03-03 14:00 | 317.859 | 323.449 | 1554.9 | 53.9082 | 0 | 53.9082 | 0 | 51.7 | 0 | 51.7 | 0.98272 | 2026-03-03 14:00 | 309.809 | 318.447 | 1524.4 | 53.0745 | 0 | 53.0745 | 0 | 51.2 | 0 | 51.2 | 0.97287 | 2026-03-03 14:00 | 314.824 | 320.334 | 1548.2 | 53.389 | 0 | 53.389 | 0 | 51.8 | 0 | 51.8 | 0.9828 | 2026-03-03 14:00 | 234.732 | 238.525 | 1152.8 | 39.7542 | 0 | 39.7542 | 0 | 38.7 | 0 | 38.7 | 0.9841 | 2026-03-03 14:00 | 232.647 | 237.154 | 1149.8 | 39.5257 | 0 | 39.5257 | 0 | 38.8 | 0 | 38.8 | 0.981 | 2026-03-03 14:00 | 231.73 | 236.047 | 1150.1 | 39.3412 | 0 | 39.3412 | 0 | 38.9 | 0 | 38.9 | 0.98171 | 2026-03-03 14:00 | 232.872 | 239.659 | 1157.9 | 39.9432 | 0 | 39.9432 | 0 | 39 | 0 | 39 | 0.97168 | 2026-03-03 14:00 | 221.634 | 225.078 | 1095.7 | 37.513 | 0 | 37.513 | 0 | 36.9 | 0 | 36.9 | 0.9847 | 2026-03-03 14:00 | 409.4135 | 0 | 409.4135 | 0 | 397.7 | 0 | 397.7
|  |  | 312.385 | 317.787 | 1482.4 | 52.9645 | 0 | 52.9645 | 0 | 52.8 | 0 | 52.8 | 0.98187 | 2026-03-03 13:50 | 319.324 | 324.938 | 1503.2 | 54.1563 | 0 | 54.1563 | 0 | 54 | 0 | 54 | 0.98272 | 2026-03-03 13:50 | 311.656 | 320.466 | 1473.2 | 53.411 | 0 | 53.411 | 0 | 53.2 | 0 | 53.2 | 0.97251 | 2026-03-03 13:50 | 316.049 | 321.646 | 1496.4 | 53.6077 | 0 | 53.6077 | 0 | 54.1 | 0 | 54.1 | 0.9826 | 2026-03-03 13:50 | 236.31 | 240.128 | 1114.1 | 40.0213 | 0 | 40.0213 | 0 | 40.4 | 0 | 40.4 | 0.9841 | 2026-03-03 13:50 | 233.337 | 237.819 | 1111 | 39.6365 | 0 | 39.6365 | 0 | 39.4 | 0 | 39.4 | 0.98115 | 2026-03-03 13:50 | 233.558 | 238.082 | 1111.2 | 39.6803 | 0 | 39.6803 | 0 | 39.3 | 0 | 39.3 | 0.981 | 2026-03-03 13:50 | 234.391 | 241.435 | 1118.9 | 40.2392 | 0 | 40.2392 | 0 | 39.6 | 0 | 39.6 | 0.97082 | 2026-03-03 13:50 | 221.674 | 225.141 | 1058.8 | 37.5235 | 0 | 37.5235 | 0 | 37.5 | 0 | 37.5 | 0.9846 | 2026-03-03 13:50 | 411.2403 | 0 | 411.2403 | 0 | 410.3 | 0 | 410.3
|  |  | 320.791 | 326.713 | 1429.6 | 54.4522 | 0 | 54.4522 | 0 | 54.1 | 0 | 54.1 | 0.9851 | 2026-03-03 13:40 | 328.917 | 334.574 | 1449.2 | 55.7623 | 0 | 55.7623 | 0 | 56.7 | 0 | 56.7 | 0.98309 | 2026-03-03 13:40 | 319.808 | 328.914 | 1420 | 54.819 | 0 | 54.819 | 0 | 53.2 | 0 | 53.2 | 0.97231 | 2026-03-03 13:40 | 326.527 | 332.343 | 1442.3 | 55.3905 | 0 | 55.3905 | 0 | 54 | 0 | 54 | 0.9825 | 2026-03-03 13:40 | 242.352 | 246.343 | 1073.7 | 41.0572 | 0 | 41.0572 | 0 | 40.3 | 0 | 40.3 | 0.9838 | 2026-03-03 13:40 | 241.383 | 246.018 | 1071.6 | 41.003 | 0 | 41.003 | 0 | 40.1 | 0 | 40.1 | 0.98116 | 2026-03-03 13:40 | 240.032 | 244.878 | 1071.9 | 40.813 | 0 | 40.813 | 0 | 40 | 0 | 40 | 0.98021 | 2026-03-03 13:40 | 241.611 | 248.362 | 1079.3 | 41.3937 | 0 | 41.3937 | 0 | 40.2 | 0 | 40.2 | 0.97282 | 2026-03-03 13:40 | 229.809 | 233.498 | 1021.3 | 38.9163 | 0 | 38.9163 | 0 | 38.1 | 0 | 38.1 | 0.9842 | 2026-03-03 13:40 | 423.6072 | 0 | 423.6072 | 0 | 416.7 | 0 | 416.7
|  |  | 322.942 | 327.826 | 1375.5 | 54.6377 | 0 | 54.6377 | 0 | 53.8 | 0 | 53.8 | 0.9829 | 2026-03-03 13:30 | 328.431 | 334.213 | 1392.5 | 55.7022 | 0 | 55.7022 | 0 | 54.7 | 0 | 54.7 | 0.9827 | 2026-03-03 13:30 | 321.031 | 330.091 | 1366.8 | 55.0152 | 0 | 55.0152 | 0 | 53.6 | 0 | 53.6 | 0.97255 | 2026-03-03 13:30 | 325.339 | 331.125 | 1388.3 | 55.1875 | 0 | 55.1875 | 0 | 54.4 | 0 | 54.4 | 0.98253 | 2026-03-03 13:30 | 243.542 | 247.502 | 1033.4 | 41.2503 | 0 | 41.2503 | 0 | 40.7 | 0 | 40.7 | 0.984 | 2026-03-03 13:30 | 241.087 | 245.705 | 1031.5 | 40.9508 | 0 | 40.9508 | 0 | 40.3 | 0 | 40.3 | 0.98121 | 2026-03-03 13:30 | 241.212 | 246.044 | 1031.9 | 41.0073 | 0 | 41.0073 | 0 | 40.3 | 0 | 40.3 | 0.98036 | 2026-03-03 13:30 | 242.843 | 249.947 | 1039.1 | 41.6578 | 0 | 41.6578 | 0 | 40.6 | 0 | 40.6 | 0.97158 | 2026-03-03 13:30 | 229.281 | 232.938 | 983.2 | 38.823 | 0 | 38.823 | 0 | 39.4 | 0 | 39.4 | 0.9843 | 2026-03-03 13:30 | 424.2318 | 0 | 424.2318 | 0 | 417.8 | 0 | 417.8
|  |  | 323.912 | 329.547 | 1321.7 | 54.9245 | 0 | 54.9245 | 0 | 54.5 | 0 | 54.5 | 0.9828 | 2026-03-03 13:20 | 330.257 | 334.88 | 1337.8 | 55.8133 | 0 | 55.8133 | 0 | 53.1 | 0 | 53.1 | 0.9862 | 2026-03-03 13:20 | 321.452 | 330.48 | 1313.2 | 55.08 | 0 | 55.08 | 0 | 54 | 0 | 54 | 0.97268 | 2026-03-03 13:20 | 326.803 | 332.556 | 1333.9 | 55.426 | 0 | 55.426 | 0 | 54.8 | 0 | 54.8 | 0.9827 | 2026-03-03 13:20 | 243.29 | 247.271 | 992.7 | 41.2118 | 0 | 41.2118 | 0 | 41 | 0 | 41 | 0.9839 | 2026-03-03 13:20 | 241.676 | 246.143 | 991.2 | 41.0238 | 0 | 41.0238 | 0 | 40.5 | 0 | 40.5 | 0.98185 | 2026-03-03 13:20 | 241.348 | 246.208 | 991.6 | 41.0347 | 0 | 41.0347 | 0 | 41.2 | 0 | 41.2 | 0.98026 | 2026-03-03 13:20 | 243.472 | 250.338 | 998.5 | 41.723 | 0 | 41.723 | 0 | 41.5 | 0 | 41.5 | 0.97257 | 2026-03-03 13:20 | 229.93 | 233.501 | 943.8 | 38.9168 | 0 | 38.9168 | 0 | 38.2 | 0 | 38.2 | 0.98471 | 2026-03-03 13:20 | 425.154 | 0 | 425.154 | 0 | 418.8 | 0 | 418.8
|  |  | 331.844 | 337.652 | 1267.2 | 56.2753 | 0 | 56.2753 | 0 | 56.2 | 0 | 56.2 | 0.9828 | 2026-03-03 13:10 | 337.448 | 343.319 | 1284.7 | 57.2198 | 0 | 57.2198 | 0 | 58.1 | 0 | 58.1 | 0.9829 | 2026-03-03 13:10 | 329.59 | 338.894 | 1259.2 | 56.4823 | 0 | 56.4823 | 0 | 54.6 | 0 | 54.6 | 0.97255 | 2026-03-03 13:10 | 333.779 | 339.655 | 1279.1 | 56.6092 | 0 | 56.6092 | 0 | 55.3 | 0 | 55.3 | 0.9827 | 2026-03-03 13:10 | 250.635 | 254.659 | 951.7 | 42.4432 | 0 | 42.4432 | 0 | 41.9 | 0 | 41.9 | 0.9842 | 2026-03-03 13:10 | 247.601 | 252.38 | 950.7 | 42.0633 | 0 | 42.0633 | 0 | 41.5 | 0 | 41.5 | 0.98106 | 2026-03-03 13:10 | 248.745 | 253.529 | 950.4 | 42.2548 | 0 | 42.2548 | 0 | 41 | 0 | 41 | 0.98113 | 2026-03-03 13:10 | 250.311 | 257.746 | 957 | 42.9577 | 0 | 42.9577 | 0 | 41.3 | 0 | 41.3 | 0.97115 | 2026-03-03 13:10 | 235.659 | 239.394 | 905.6 | 39.899 | 0 | 39.899 | 0 | 38.9 | 0 | 38.9 | 0.9844 | 2026-03-03 13:10 | 436.2047 | 0 | 436.2047 | 0 | 428.8 | 0 | 428.8
|  |  | 330.417 | 336.2 | 1211 | 56.0333 | 0 | 56.0333 | 0 | 54.2 | 0 | 54.2 | 0.9829 | 2026-03-03 13:00 | 336.094 | 342.024 | 1226.6 | 57.004 | 0 | 57.004 | 0 | 53.7 | 0 | 53.7 | 0.98266 | 2026-03-03 13:00 | 328.194 | 337.634 | 1204.6 | 56.2723 | 0 | 56.2723 | 0 | 55.4 | 0 | 55.4 | 0.97204 | 2026-03-03 13:00 | 332.773 | 338.666 | 1223.8 | 56.4443 | 0 | 56.4443 | 0 | 57 | 0 | 57 | 0.9826 | 2026-03-03 13:00 | 248.833 | 252.828 | 909.8 | 42.138 | 0 | 42.138 | 0 | 41.5 | 0 | 41.5 | 0.9842 | 2026-03-03 13:00 | 246.493 | 251.043 | 909.2 | 41.8405 | 0 | 41.8405 | 0 | 41.2 | 0 | 41.2 | 0.98188 | 2026-03-03 13:00 | 246.766 | 251.798 | 909.4 | 41.9663 | 0 | 41.9663 | 0 | 41.2 | 0 | 41.2 | 0.98002 | 2026-03-03 13:00 | 248.826 | 255.859 | 915.7 | 42.6432 | 0 | 42.6432 | 0 | 41.4 | 0 | 41.4 | 0.97251 | 2026-03-03 13:00 | 234.539 | 238.256 | 866.7 | 39.7093 | 0 | 39.7093 | 0 | 39.1 | 0 | 39.1 | 0.9844 | 2026-03-03 13:00 | 434.0513 | 0 | 434.0513 | 0 | 424.7 | 0 | 424.7
|  |  | 330.645 | 336.397 | 1156.8 | 56.0662 | 0 | 56.0662 | 0 | 55.5 | 0 | 55.5 | 0.9828 | 2026-03-03 12:50 | 335.651 | 341.56 | 1172.9 | 56.9267 | 0 | 56.9267 | 0 | 60.1 | 0 | 60.1 | 0.9827 | 2026-03-03 12:50 | 329.263 | 339.062 | 1149.2 | 56.5103 | 0 | 56.5103 | 0 | 54.3 | 0 | 54.3 | 0.9711 | 2026-03-03 12:50 | 332.771 | 338.664 | 1166.8 | 56.444 | 0 | 56.444 | 0 | 54.3 | 0 | 54.3 | 0.9826 | 2026-03-03 12:50 | 250.069 | 254.109 | 868.3 | 42.3515 | 0 | 42.3515 | 0 | 41.3 | 0 | 41.3 | 0.9841 | 2026-03-03 12:50 | 247.623 | 252.559 | 868 | 42.0932 | 0 | 42.0932 | 0 | 40.9 | 0 | 40.9 | 0.98046 | 2026-03-03 12:50 | 248.111 | 252.943 | 868.2 | 42.1572 | 0 | 42.1572 | 0 | 41.5 | 0 | 41.5 | 0.9809 | 2026-03-03 12:50 | 249.454 | 257.025 | 874.3 | 42.8375 | 0 | 42.8375 | 0 | 41.8 | 0 | 41.8 | 0.97054 | 2026-03-03 12:50 | 235.6 | 239.309 | 827.6 | 39.8848 | 0 | 39.8848 | 0 | 39.5 | 0 | 39.5 | 0.9845 | 2026-03-03 12:50 | 435.2713 | 0 | 435.2713 | 0 | 429.2 | 0 | 429.2
|  |  | 328.264 | 334.009 | 1101.3 | 55.6682 | 0 | 55.6682 | 0 | 56.4 | 0 | 56.4 | 0.98322 | 2026-03-03 12:40 | 333.419 | 339.263 | 1112.8 | 56.5438 | 0 | 56.5438 | 0 | 53.7 | 0 | 53.7 | 0.98277 | 2026-03-03 12:40 | 327.166 | 336.819 | 1094.9 | 56.1365 | 0 | 56.1365 | 0 | 54.9 | 0 | 54.9 | 0.97134 | 2026-03-03 12:40 | 330.82 | 336.766 | 1112.5 | 56.1277 | 0 | 56.1277 | 0 | 55.4 | 0 | 55.4 | 0.98234 | 2026-03-03 12:40 | 248.975 | 252.998 | 827 | 42.1663 | 0 | 42.1663 | 0 | 41.7 | 0 | 41.7 | 0.9841 | 2026-03-03 12:40 | 245.876 | 250.894 | 827.1 | 41.8157 | 0 | 41.8157 | 0 | 41.3 | 0 | 41.3 | 0.98 | 2026-03-03 12:40 | 247.312 | 252.237 | 826.7 | 42.0395 | 0 | 42.0395 | 0 | 40.9 | 0 | 40.9 | 0.98047 | 2026-03-03 12:40 | 249.155 | 256.692 | 832.5 | 42.782 | 0 | 42.782 | 0 | 41.3 | 0 | 41.3 | 0.97064 | 2026-03-03 12:40 | 233.9 | 237.58 | 788.1 | 39.5967 | 0 | 39.5967 | 0 | 38.7 | 0 | 38.7 | 0.98451 | 2026-03-03 12:40 | 432.8763 | 0 | 432.8763 | 0 | 424.3 | 0 | 424.3
|  |  | 327.09 | 332.672 | 1044.9 | 55.4453 | 0 | 55.4453 | 0 | 52.3 | 0 | 52.3 | 0.98027 | 2026-03-03 12:30 | 332.197 | 338.17 | 1059.1 | 56.3617 | 0 | 56.3617 | 0 | 53.8 | 0 | 53.8 | 0.98234 | 2026-03-03 12:30 | 326.655 | 336.333 | 1040 | 56.0555 | 0 | 56.0555 | 0 | 54.3 | 0 | 54.3 | 0.97122 | 2026-03-03 12:30 | 329.98 | 335.926 | 1057.1 | 55.9877 | 0 | 55.9877 | 0 | 54.5 | 0 | 54.5 | 0.9823 | 2026-03-03 12:30 | 248.784 | 252.804 | 785.3 | 42.134 | 0 | 42.134 | 0 | 40.9 | 0 | 40.9 | 0.9841 | 2026-03-03 12:30 | 246.189 | 251.119 | 785.8 | 41.8532 | 0 | 41.8532 | 0 | 40.9 | 0 | 40.9 | 0.98037 | 2026-03-03 12:30 | 248.42 | 253.186 | 785.8 | 42.1977 | 0 | 42.1977 | 0 | 41.1 | 0 | 41.1 | 0.98118 | 2026-03-03 12:30 | 250.53 | 257.751 | 791.2 | 42.9585 | 0 | 42.9585 | 0 | 41.5 | 0 | 41.5 | 0.97198 | 2026-03-03 12:30 | 234.247 | 238.008 | 749.4 | 39.668 | 0 | 39.668 | 0 | 39 | 0 | 39 | 0.9842 | 2026-03-03 12:30 | 432.6615 | 0 | 432.6615 | 0 | 418.3 | 0 | 418.3
|  |  | 322.424 | 328.913 | 992.6 | 54.8188 | 0 | 54.8188 | 0 | 53.4 | 0 | 53.4 | 0.9829 | 2026-03-03 12:20 | 327.873 | 333.784 | 1005.3 | 55.6307 | 0 | 55.6307 | 0 | 55.8 | 0 | 55.8 | 0.98229 | 2026-03-03 12:20 | 322.783 | 332.19 | 985.7 | 55.365 | 0 | 55.365 | 0 | 53.2 | 0 | 53.2 | 0.97168 | 2026-03-03 12:20 | 327.343 | 333.241 | 1002.6 | 55.5402 | 0 | 55.5402 | 0 | 54.7 | 0 | 54.7 | 0.9823 | 2026-03-03 12:20 | 245.262 | 249.301 | 744.4 | 41.5502 | 0 | 41.5502 | 0 | 40.8 | 0 | 40.8 | 0.9838 | 2026-03-03 12:20 | 243.118 | 247.834 | 744.9 | 41.3057 | 0 | 41.3057 | 0 | 40.1 | 0 | 40.1 | 0.98097 | 2026-03-03 12:20 | 243.548 | 248.398 | 744.7 | 41.3997 | 0 | 41.3997 | 0 | 40.8 | 0 | 40.8 | 0.98047 | 2026-03-03 12:20 | 245.031 | 252.607 | 749.7 | 42.1012 | 0 | 42.1012 | 0 | 41 | 0 | 41 | 0.97001 | 2026-03-03 12:20 | 231.567 | 235.304 | 710.4 | 39.2173 | 0 | 39.2173 | 0 | 38.7 | 0 | 38.7 | 0.98412 | 2026-03-03 12:20 | 426.9287 | 0 | 426.9287 | 0 | 418.5 | 0 | 418.5
|  |  | 324.426 | 330.07 | 939.2 | 55.0117 | 0 | 55.0117 | 0 | 54.3 | 0 | 54.3 | 0.98331 | 2026-03-03 12:10 | 328.261 | 334.074 | 949.5 | 55.679 | 0 | 55.679 | 0 | 53.5 | 0 | 53.5 | 0.9826 | 2026-03-03 12:10 | 321.708 | 331.166 | 932.5 | 55.1943 | 0 | 55.1943 | 0 | 53.3 | 0 | 53.3 | 0.97144 | 2026-03-03 12:10 | 326.34 | 332.119 | 947.9 | 55.3532 | 0 | 55.3532 | 0 | 53.9 | 0 | 53.9 | 0.9826 | 2026-03-03 12:10 | 243.453 | 247.437 | 703.6 | 41.2395 | 0 | 41.2395 | 0 | 40.4 | 0 | 40.4 | 0.9839 | 2026-03-03 12:10 | 241.614 | 246.44 | 704.8 | 41.0733 | 0 | 41.0733 | 0 | 40.4 | 0 | 40.4 | 0.98042 | 2026-03-03 12:10 | 241.955 | 246.455 | 703.9 | 41.0758 | 0 | 41.0758 | 0 | 40 | 0 | 40 | 0.98174 | 2026-03-03 12:10 | 243.352 | 250.757 | 708.7 | 41.7928 | 0 | 41.7928 | 0 | 40.3 | 0 | 40.3 | 0.97047 | 2026-03-03 12:10 | 229.923 | 233.614 | 671.7 | 38.9357 | 0 | 38.9357 | 0 | 38 | 0 | 38 | 0.9842 | 2026-03-03 12:10 | 425.3553 | 0 | 425.3553 | 0 | 414.1 | 0 | 414.1
|  |  | 321.8 | 327.261 | 884.9 | 54.5435 | 0 | 54.5435 | 0 | 54.4 | 0 | 54.4 | 0.9831 | 2026-03-03 12:00 | 326.685 | 332.369 | 896 | 55.3948 | 0 | 55.3948 | 0 | 55.3 | 0 | 55.3 | 0.9829 | 2026-03-03 12:00 | 319.786 | 328.912 | 879.2 | 54.8187 | 0 | 54.8187 | 0 | 53.3 | 0 | 53.3 | 0.97225 | 2026-03-03 12:00 | 324.707 | 330.423 | 894 | 55.0705 | 0 | 55.0705 | 0 | 54.2 | 0 | 54.2 | 0.9827 | 2026-03-03 12:00 | 242.52 | 246.413 | 663.2 | 41.0688 | 0 | 41.0688 | 0 | 40.4 | 0 | 40.4 | 0.9842 | 2026-03-03 12:00 | 241.039 | 245.796 | 664.4 | 40.966 | 0 | 40.966 | 0 | 39.8 | 0 | 39.8 | 0.98065 | 2026-03-03 12:00 | 241.311 | 246.09 | 663.9 | 41.015 | 0 | 41.015 | 0 | 40.4 | 0 | 40.4 | 0.98058 | 2026-03-03 12:00 | 243.017 | 250.109 | 668.4 | 41.6848 | 0 | 41.6848 | 0 | 40.7 | 0 | 40.7 | 0.97164 | 2026-03-03 12:00 | 229.566 | 233.142 | 633.7 | 38.857 | 0 | 38.857 | 0 | 38.5 | 0 | 38.5 | 0.98466 | 2026-03-03 12:00 | 423.4192 | 0 | 423.4192 | 0 | 417 | 0 | 417
|  |  | 317.856 | 323.32 | 830.5 | 53.8867 | 0 | 53.8867 | 0 | 50.6 | 0 | 50.6 | 0.98298 | 2026-03-03 11:50 | 323.525 | 329.187 | 840.7 | 54.8645 | 0 | 54.8645 | 0 | 51.4 | 0 | 51.4 | 0.9828 | 2026-03-03 11:50 | 316.483 | 325.253 | 825.9 | 54.2088 | 0 | 54.2088 | 0 | 54 | 0 | 54 | 0.97304 | 2026-03-03 11:50 | 322.152 | 327.79 | 839.8 | 54.6317 | 0 | 54.6317 | 0 | 53.4 | 0 | 53.4 | 0.9828 | 2026-03-03 11:50 | 240.176 | 244.007 | 622.8 | 40.6678 | 0 | 40.6678 | 0 | 39.9 | 0 | 39.9 | 0.9843 | 2026-03-03 11:50 | 239.127 | 243.578 | 624.6 | 40.5963 | 0 | 40.5963 | 0 | 39.7 | 0 | 39.7 | 0.98173 | 2026-03-03 11:50 | 239.062 | 243.878 | 623.5 | 40.6463 | 0 | 40.6463 | 0 | 39.1 | 0 | 39.1 | 0.98025 | 2026-03-03 11:50 | 240.903 | 247.963 | 627.7 | 41.3272 | 0 | 41.3272 | 0 | 39.5 | 0 | 39.5 | 0.97153 | 2026-03-03 11:50 | 228.215 | 231.735 | 595.2 | 38.6225 | 0 | 38.6225 | 0 | 37.3 | 0 | 37.3 | 0.98481 | 2026-03-03 11:50 | 419.4518 | 0 | 419.4518 | 0 | 404.9 | 0 | 404.9
|  |  | 313.57 | 318.998 | 779.9 | 53.1663 | 0 | 53.1663 | 0 | 52.9 | 0 | 52.9 | 0.98313 | 2026-03-03 11:40 | 318.532 | 324.008 | 789.3 | 54.0013 | 0 | 54.0013 | 0 | 53.8 | 0 | 53.8 |  | 2026-03-03 11:40 | 311.493 | 320.454 | 771.9 | 53.409 | 0 | 53.409 | 0 | 49.8 | 0 | 49.8 | 0.97204 | 2026-03-03 11:40 | 316.436 | 321.876 | 786.4 | 53.646 | 0 | 53.646 | 0 | 52 | 0 | 52 | 0.9831 | 2026-03-03 11:40 | 236.161 | 239.879 | 582.9 | 39.9798 | 0 | 39.9798 | 0 | 38.9 | 0 | 38.9 | 0.9845 | 2026-03-03 11:40 | 235.017 | 239.419 | 584.9 | 39.9032 | 0 | 39.9032 | 0 | 38.7 | 0 | 38.7 | 0.98161 | 2026-03-03 11:40 | 235.452 | 240.283 | 584.4 | 40.0472 | 0 | 40.0472 | 0 | 38.8 | 0 | 38.8 | 0.97989 | 2026-03-03 11:40 | 238.322 | 245.403 | 588.2 | 40.9005 | 0 | 40.9005 | 0 | 39.1 | 0 | 39.1 | 0.97115 | 2026-03-03 11:40 | 224.101 | 227.537 | 557.9 | 37.9228 | 0 | 37.9228 | 0 | 37.4 | 0 | 37.4 | 0.9849 | 2026-03-03 11:40 | 412.9762 | 0 | 412.9762 | 0 | 401.4 | 0 | 401.4
|  |  | 307.206 | 312.478 | 727 | 52.0797 | 0 | 52.0797 | 0 | 50.4 | 0 | 50.4 | 0.9836 | 2026-03-03 11:30 | 312.016 | 317.82 | 735.5 | 52.97 | 0 | 52.97 | 0 | 51.2 | 0 | 51.2 | 0.98174 | 2026-03-03 11:30 | 306.191 | 314.414 | 722.1 | 52.4023 | 0 | 52.4023 | 0 | 50.1 | 0 | 50.1 | 0.97385 | 2026-03-03 11:30 | 311.27 | 316.621 | 734.4 | 52.7702 | 0 | 52.7702 | 0 | 50.9 | 0 | 50.9 | 0.9831 | 2026-03-03 11:30 | 232.428 | 236.063 | 544 | 39.3438 | 0 | 39.3438 | 0 | 38 | 0 | 38 | 0.9846 | 2026-03-03 11:30 | 231.239 | 235.363 | 546.2 | 39.2272 | 0 | 39.2272 | 0 | 37.8 | 0 | 37.8 | 0.98248 | 2026-03-03 11:30 | 231.565 | 235.724 | 545.6 | 39.2873 | 0 | 39.2873 | 0 | 37.9 | 0 | 37.9 | 0.98236 | 2026-03-03 11:30 | 233.459 | 240.207 | 549.1 | 40.0345 | 0 | 40.0345 | 0 | 38.7 | 0 | 38.7 | 0.97191 | 2026-03-03 11:30 | 220.618 | 223.955 | 520.5 | 37.3258 | 0 | 37.3258 | 0 | 36.1 | 0 | 36.1 | 0.9851 | 2026-03-03 11:30 | 405.4408 | 0 | 405.4408 | 0 | 391.1 | 0 | 391.1
|  |  | 300.128 | 305.132 | 676.6 | 50.8553 | 0 | 50.8553 | 0 | 49.6 | 0 | 49.6 | 0.9837 | 2026-03-03 11:20 | 304.016 | 309.116 | 684.3 | 51.5193 | 0 | 51.5193 | 0 | 53 | 0 | 53 | 0.9835 | 2026-03-03 11:20 | 297.562 | 305.85 | 672 | 50.975 | 0 | 50.975 | 0 | 49.7 | 0 | 49.7 | 0.9729 | 2026-03-03 11:20 | 301.768 | 306.924 | 683.5 | 51.154 | 0 | 51.154 | 0 | 50.4 | 0 | 50.4 | 0.9832 | 2026-03-03 11:20 | 224.986 | 228.459 | 506 | 38.0765 | 0 | 38.0765 | 0 | 37.5 | 0 | 37.5 | 0.9848 | 2026-03-03 11:20 | 223.994 | 228.219 | 508.4 | 38.0365 | 0 | 38.0365 | 0 | 37.4 | 0 | 37.4 | 0.98149 | 2026-03-03 11:20 | 223.75 | 227.767 | 507.7 | 37.9612 | 0 | 37.9612 | 0 | 37.3 | 0 | 37.3 | 0.98236 | 2026-03-03 11:20 | 225.302 | 232.071 | 510.4 | 38.6785 | 0 | 38.6785 | 0 | 37.1 | 0 | 37.1 | 0.97083 | 2026-03-03 11:20 | 213.354 | 216.581 | 484.4 | 36.0968 | 0 | 36.0968 | 0 | 35.2 | 0 | 35.2 | 0.9851 | 2026-03-03 11:20 | 393.3532 | 0 | 393.3532 | 0 | 387.2 | 0 | 387.2
|  |  | 299.656 | 304.621 | 627 | 50.7702 | 0 | 50.7702 | 0 | 50.7 | 0 | 50.7 | 0.984 | 2026-03-03 11:10 | 304.062 | 309.163 | 631.3 | 51.5272 | 0 | 51.5272 | 0 | 47.3 | 0 | 47.3 | 0.9835 | 2026-03-03 11:10 | 297.534 | 305.789 | 622.3 | 50.9648 | 0 | 50.9648 | 0 | 48.5 | 0 | 48.5 | 0.973 | 2026-03-03 11:10 | 301.889 | 307.015 | 633.1 | 51.1692 | 0 | 51.1692 | 0 | 49.2 | 0 | 49.2 | 0.9833 | 2026-03-03 11:10 | 225.091 | 228.574 | 468.5 | 38.0957 | 0 | 38.0957 | 0 | 36.7 | 0 | 36.7 | 0.98476 | 2026-03-03 11:10 | 223.949 | 227.829 | 471 | 37.9715 | 0 | 37.9715 | 0 | 37 | 0 | 37 | 0.98297 | 2026-03-03 11:10 | 223.713 | 227.602 | 470.4 | 37.9337 | 0 | 37.9337 | 0 | 36.9 | 0 | 36.9 | 0.98291 | 2026-03-03 11:10 | 225.284 | 231.922 | 473.3 | 38.6537 | 0 | 38.6537 | 0 | 37.1 | 0 | 37.1 | 0.97138 | 2026-03-03 11:10 | 213.536 | 216.744 | 449.2 | 36.124 | 0 | 36.124 | 0 | 35.2 | 0 | 35.2 | 0.9852 | 2026-03-03 11:10 | 393.2098 | 0 | 393.2098 | 0 | 378.6 | 0 | 378.6
|  |  | 292.271 | 297.023 | 576.3 | 49.5038 | 0 | 49.5038 | 0 | 45.5 | 0 | 45.5 | 0.98465 | 2026-03-03 11:00 | 296.486 | 301.307 | 584 | 50.2178 | 0 | 50.2178 | 0 | 48.3 | 0 | 48.3 | 0.984 | 2026-03-03 11:00 | 291.173 | 298.727 | 573.8 | 49.7878 | 0 | 49.7878 | 0 | 47.2 | 0 | 47.2 | 0.97471 | 2026-03-03 11:00 | 294.652 | 299.534 | 583.9 | 49.9223 | 0 | 49.9223 | 0 | 48.6 | 0 | 48.6 | 0.9837 | 2026-03-03 11:00 | 220.007 | 223.312 | 431.8 | 37.2187 | 0 | 37.2187 | 0 | 36.2 | 0 | 36.2 | 0.9852 | 2026-03-03 11:00 | 218.848 | 222.422 | 434 | 37.0703 | 0 | 37.0703 | 0 | 35.6 | 0 | 35.6 | 0.98393 | 2026-03-03 11:00 | 218.872 | 222.63 | 433.5 | 37.105 | 0 | 37.105 | 0 | 35.6 | 0 | 35.6 | 0.98312 | 2026-03-03 11:00 | 220.097 | 226.62 | 436.2 | 37.77 | 0 | 37.77 | 0 | 35.9 | 0 | 35.9 | 0.97122 | 2026-03-03 11:00 | 208.572 | 211.7 | 414 | 35.2833 | 0 | 35.2833 | 0 | 34 | 0 | 34 | 0.98522 | 2026-03-03 11:00 | 383.8792 | 0 | 383.8792 | 0 | 366.9 | 0 | 366.9
|  |  | 282.125 | 286.524 | 530.8 | 47.754 | 0 | 47.754 | 0 | 46.4 | 0 | 46.4 | 0.9844 | 2026-03-03 10:50 | 286.179 | 290.832 | 535.7 | 48.472 | 0 | 48.472 | 0 | 46.4 | 0 | 46.4 | 0.984 | 2026-03-03 10:50 | 280.859 | 288.323 | 526.6 | 48.0538 | 0 | 48.0538 | 0 | 46.8 | 0 | 46.8 | 0.97411 | 2026-03-03 10:50 | 284.225 | 288.876 | 535.3 | 48.146 | 0 | 48.146 | 0 | 46.9 | 0 | 46.9 | 0.9839 | 2026-03-03 10:50 | 212.094 | 215.28 | 395.6 | 35.88 | 0 | 35.88 | 0 | 34.8 | 0 | 34.8 | 0.9852 | 2026-03-03 10:50 | 210.878 | 214.432 | 398.4 | 35.7387 | 0 | 35.7387 | 0 | 34.8 | 0 | 34.8 | 0.98343 | 2026-03-03 10:50 | 211.037 | 214.494 | 397.9 | 35.749 | 0 | 35.749 | 0 | 34.7 | 0 | 34.7 | 0.98388 | 2026-03-03 10:50 | 212.372 | 218.64 | 400.3 | 36.44 | 0 | 36.44 | 0 | 34.9 | 0 | 34.9 | 0.97133 | 2026-03-03 10:50 | 201.326 | 204.283 | 380 | 34.0472 | 0 | 34.0472 | 0 | 33.1 | 0 | 33.1 | 0.98552 | 2026-03-03 10:50 | 370.2807 | 0 | 370.2807 | 0 | 358.8 | 0 | 358.8
|  |  | 271.709 | 276.015 | 484.4 | 46.0025 | 0 | 46.0025 | 0 | 45.3 | 0 | 45.3 | 0.9848 | 2026-03-03 10:40 | 275.037 | 281.606 | 489.3 | 46.9343 | 0 | 46.9343 | 0 | 46.7 | 0 | 46.7 | 0.97667 | 2026-03-03 10:40 | 270.494 | 277.512 | 479.8 | 46.252 | 0 | 46.252 | 0 | 45 | 0 | 45 | 0.97471 | 2026-03-03 10:40 | 276.363 | 280.735 | 488.4 | 46.7892 | 0 | 46.7892 | 0 | 45.1 | 0 | 45.1 | 0.98443 | 2026-03-03 10:40 | 204.106 | 207.13 | 360.8 | 34.5217 | 0 | 34.5217 | 0 | 33.5 | 0 | 33.5 | 0.9854 | 2026-03-03 10:40 | 204.953 | 208.237 | 363.6 | 34.7062 | 0 | 34.7062 | 0 | 33.6 | 0 | 33.6 | 0.98423 | 2026-03-03 10:40 | 203.89 | 207.137 | 363.2 | 34.5228 | 0 | 34.5228 | 0 | 33.5 | 0 | 33.5 | 0.98432 | 2026-03-03 10:40 | 205.565 | 211.656 | 365.4 | 35.276 | 0 | 35.276 | 0 | 33.6 | 0 | 33.6 | 0.97122 | 2026-03-03 10:40 | 195.168 | 198.019 | 346.9 | 33.0032 | 0 | 33.0032 | 0 | 32 | 0 | 32 | 0.9856 | 2026-03-03 10:40 | 358.0078 | 0 | 358.0078 | 0 | 348.3 | 0 | 348.3
|  |  | 265.096 | 269.188 | 439.1 | 44.8647 | 0 | 44.8647 | 0 | 43.1 | 0 | 43.1 | 0.9851 | 2026-03-03 10:30 | 268.544 | 272.859 | 442.6 | 45.4765 | 0 | 45.4765 | 0 | 45.4 | 0 | 45.4 | 0.98419 | 2026-03-03 10:30 | 263.046 | 269.778 | 434.8 | 44.963 | 0 | 44.963 | 0 | 42.1 | 0 | 42.1 | 0.97505 | 2026-03-03 10:30 | 267.132 | 271.338 | 443.3 | 45.223 | 0 | 45.223 | 0 | 43.4 | 0 | 43.4 | 0.9845 | 2026-03-03 10:30 | 198.73 | 201.613 | 327.3 | 33.6022 | 0 | 33.6022 | 0 | 32.7 | 0 | 32.7 | 0.9857 | 2026-03-03 10:30 | 198.418 | 201.42 | 330 | 33.57 | 0 | 33.57 | 0 | 32.6 | 0 | 32.6 | 0.9851 | 2026-03-03 10:30 | 198.273 | 201.501 | 329.7 | 33.5835 | 0 | 33.5835 | 0 | 32.6 | 0 | 32.6 | 0.98398 | 2026-03-03 10:30 | 199.385 | 205.315 | 331.8 | 34.2192 | 0 | 34.2192 | 0 | 32.8 | 0 | 32.8 | 0.97112 | 2026-03-03 10:30 | 188.888 | 191.628 | 314.9 | 31.938 | 0 | 31.938 | 0 | 31.1 | 0 | 31.1 | 0.9857 | 2026-03-03 10:30 | 347.44 | 0 | 347.44 | 0 | 335.8 | 0 | 335.8
|  |  | 254.369 | 258.216 | 396 | 43.036 | 0 | 43.036 | 0 | 43.5 | 0 | 43.5 | 0.9854 | 2026-03-03 10:20 | 256.897 | 260.809 | 397.2 | 43.4682 | 0 | 43.4682 | 0 | 39.3 | 0 | 39.3 | 0.985 | 2026-03-03 10:20 | 252.617 | 258.529 | 392.7 | 43.0882 | 0 | 43.0882 | 0 | 41.5 | 0 | 41.5 | 0.97713 | 2026-03-03 10:20 | 257.281 | 261.279 | 399.9 | 43.5465 | 0 | 43.5465 | 0 | 42.2 | 0 | 42.2 | 0.9847 | 2026-03-03 10:20 | 190.303 | 193.025 | 294.6 | 32.1708 | 0 | 32.1708 | 0 | 30.8 | 0 | 30.8 | 0.9859 | 2026-03-03 10:20 | 191.148 | 193.912 | 297.4 | 32.3187 | 0 | 32.3187 | 0 | 31 | 0 | 31 | 0.98575 | 2026-03-03 10:20 | 190.383 | 193.221 | 297.1 | 32.2035 | 0 | 32.2035 | 0 | 30.9 | 0 | 30.9 | 0.98531 | 2026-03-03 10:20 | 191.814 | 197.144 | 299 | 32.8573 | 0 | 32.8573 | 0 | 31.1 | 0 | 31.1 | 0.97296 | 2026-03-03 10:20 | 181.942 | 184.516 | 283.8 | 30.7527 | 0 | 30.7527 | 0 | 29.5 | 0 | 29.5 | 0.98605 | 2026-03-03 10:20 | 333.4418 | 0 | 333.4418 | 0 | 319.8 | 0 | 319.8
|  |  | 242.987 | 246.587 | 352.5 | 41.0978 | 0 | 41.0978 | 0 | 38.2 | 0 | 38.2 | 0.9857 | 2026-03-03 10:10 | 245.52 | 249.244 | 357.9 | 41.5407 | 0 | 41.5407 | 0 | 42.6 | 0 | 42.6 | 0.98506 | 2026-03-03 10:10 | 241.545 | 247.347 | 351.2 | 41.2245 | 0 | 41.2245 | 0 | 39.1 | 0 | 39.1 | 0.97654 | 2026-03-03 10:10 | 244.492 | 248.215 | 357.7 | 41.3692 | 0 | 41.3692 | 0 | 39.7 | 0 | 39.7 | 0.985 | 2026-03-03 10:10 | 181.97 | 184.572 | 263.8 | 30.762 | 0 | 30.762 | 0 | 29.5 | 0 | 29.5 | 0.9859 | 2026-03-03 10:10 | 181.963 | 184.558 | 266.4 | 30.7597 | 0 | 30.7597 | 0 | 29.6 | 0 | 29.6 | 0.98594 | 2026-03-03 10:10 | 181.883 | 184.466 | 266.2 | 30.7443 | 0 | 30.7443 | 0 | 29.5 | 0 | 29.5 | 0.986 | 2026-03-03 10:10 | 182.954 | 188.172 | 267.9 | 31.362 | 0 | 31.362 | 0 | 29.7 | 0 | 29.7 | 0.97227 | 2026-03-03 10:10 | 173.535 | 175.999 | 254.3 | 29.3332 | 0 | 29.3332 | 0 | 28.2 | 0 | 28.2 | 0.986 | 2026-03-03 10:10 | 318.1933 | 0 | 318.1933 | 0 | 306.1 | 0 | 306.1
|  |  | 231.572 | 234.932 | 314.3 | 39.1553 | 0 | 39.1553 | 0 | 37.1 | 0 | 37.1 | 0.9861 | 2026-03-03 10:00 | 233.774 | 237.238 | 315.3 | 39.5397 | 0 | 39.5397 | 0 | 38.4 | 0 | 38.4 | 0.9854 | 2026-03-03 10:00 | 229.932 | 235.175 | 312.1 | 39.1958 | 0 | 39.1958 | 0 | 37.4 | 0 | 37.4 | 0.97771 | 2026-03-03 10:00 | 234.141 | 237.634 | 318 | 39.6057 | 0 | 39.6057 | 0 | 38 | 0 | 38 | 0.9853 | 2026-03-03 10:00 | 173.269 | 175.694 | 234.3 | 29.2823 | 0 | 29.2823 | 0 | 28.1 | 0 | 28.1 | 0.9862 | 2026-03-03 10:00 | 174.247 | 176.648 | 236.8 | 29.4413 | 0 | 29.4413 | 0 | 28.2 | 0 | 28.2 | 0.98641 | 2026-03-03 10:00 | 173.756 | 176.17 | 236.7 | 29.3617 | 0 | 29.3617 | 0 | 28.2 | 0 | 28.2 | 0.9863 | 2026-03-03 10:00 | 175.019 | 180.247 | 238.2 | 30.0412 | 0 | 30.0412 | 0 | 28.9 | 0 | 28.9 | 0.971 | 2026-03-03 10:00 | 166.076 | 168.394 | 226.1 | 28.0657 | 0 | 28.0657 | 0 | 27.3 | 0 | 27.3 | 0.98623 | 2026-03-03 10:00 | 303.6887 | 0 | 303.6887 | 0 | 291.6 | 0 | 291.6
|  |  | 220.079 | 223.181 | 277.2 | 37.1968 | 0 | 37.1968 | 0 | 35.5 | 0 | 35.5 |  | 2026-03-03 09:50 | 222.244 | 225.445 | 276.9 | 37.5742 | 0 | 37.5742 | 0 | 33.4 | 0 | 33.4 |  | 2026-03-03 09:50 | 218.446 | 222.983 | 274.7 | 37.1638 | 0 | 37.1638 | 0 | 35.1 | 0 | 35.1 |  | 2026-03-03 09:50 | 222.906 | 226.117 | 280 | 37.6862 | 0 | 37.6862 | 0 | 35.8 | 0 | 35.8 |  | 2026-03-03 09:50 | 164.791 | 167.046 | 206.2 | 27.841 | 0 | 27.841 | 0 | 26.5 | 0 | 26.5 |  | 2026-03-03 09:50 | 166.098 | 168.337 | 208.6 | 28.0562 | 0 | 28.0562 | 0 | 27.1 | 0 | 27.1 |  | 2026-03-03 09:50 | 165.532 | 167.78 | 208.5 | 27.9633 | 0 | 27.9633 | 0 | 27 | 0 | 27 |  | 2026-03-03 09:50 | 167.025 | 171.511 | 209.3 | 28.5852 | 0 | 28.5852 | 0 | 26.8 | 0 | 26.8 |  | 2026-03-03 09:50 | 158.076 | 160.223 | 198.8 | 26.7038 | 0 | 26.7038 | 0 | 25.4 | 0 | 25.4 |  | 2026-03-03 09:50 | 288.7705 | 0 | 288.7705 | 0 | 272.6 | 0 | 272.6
|  |  | 206.918 | 209.792 | 241.7 | 34.9653 | 0 | 34.9653 | 0 | 33.3 | 0 | 33.3 |  | 2026-03-03 09:40 | 208.694 | 211.71 | 243.5 | 35.285 | 0 | 35.285 | 0 | 33.7 | 0 | 33.7 |  | 2026-03-03 09:40 | 205.789 | 210.126 | 239.6 | 35.021 | 0 | 35.021 | 0 | 33.6 | 0 | 33.6 |  | 2026-03-03 09:40 | 209.381 | 212.332 | 244.2 | 35.3887 | 0 | 35.3887 | 0 | 34.2 | 0 | 34.2 |  | 2026-03-03 09:40 | 154.931 | 156.964 | 179.7 | 26.1607 | 0 | 26.1607 | 0 | 25.3 | 0 | 25.3 |  | 2026-03-03 09:40 | 155.892 | 157.945 | 181.5 | 26.3242 | 0 | 26.3242 | 0 | 25.1 | 0 | 25.1 |  | 2026-03-03 09:40 | 155.337 | 157.415 | 181.5 | 26.2358 | 0 | 26.2358 | 0 | 25 | 0 | 25 |  | 2026-03-03 09:40 | 156.697 | 160.867 | 182.5 | 26.8112 | 0 | 26.8112 | 0 | 25.2 | 0 | 25.2 |  | 2026-03-03 09:40 | 148.543 | 150.5 | 173.4 | 25.0833 | 0 | 25.0833 | 0 | 23.9 | 0 | 23.9 |  | 2026-03-03 09:40 | 271.2752 | 0 | 271.2752 | 0 | 259.3 | 0 | 259.3
|  |  | 194.384 | 197.368 | 208.4 | 32.8947 | 0 | 32.8947 | 0 | 31.4 | 0 | 31.4 |  | 2026-03-03 09:30 | 196.8 | 199.513 | 209.8 | 33.2522 | 0 | 33.2522 | 0 | 31.7 | 0 | 31.7 |  | 2026-03-03 09:30 | 192.926 | 196.925 | 206 | 32.8208 | 0 | 32.8208 | 0 | 30.6 | 0 | 30.6 |  | 2026-03-03 09:30 | 196.708 | 199.42 | 210 | 33.2367 | 0 | 33.2367 | 0 | 31.2 | 0 | 31.2 |  | 2026-03-03 09:30 | 145.135 | 147.032 | 154.4 | 24.5053 | 0 | 24.5053 | 0 | 23.1 | 0 | 23.1 |  | 2026-03-03 09:30 | 146.578 | 148.494 | 156.4 | 24.749 | 0 | 24.749 | 0 | 23.6 | 0 | 23.6 |  | 2026-03-03 09:30 | 145.806 | 147.517 | 156.5 | 24.5862 | 0 | 24.5862 | 0 | 23.5 | 0 | 23.5 |  | 2026-03-03 09:30 | 146.59 | 150.619 | 157.3 | 25.1032 | 0 | 25.1032 | 0 | 23.7 | 0 | 23.7 |  | 2026-03-03 09:30 | 139.635 | 141.446 | 149.5 | 23.5743 | 0 | 23.5743 | 0 | 22.6 | 0 | 22.6 |  | 2026-03-03 09:30 | 254.7223 | 0 | 254.7223 | 0 | 241.4 | 0 | 241.4
|  |  | 180.538 | 182.897 | 177 | 30.4828 | 0 | 30.4828 | 0 | 29.4 | 0 | 29.4 |  | 2026-03-03 09:20 | 0 | 184.724 | 178.1 | 30.7873 | 0 | 30.7873 | 0 | 29.5 | 0 | 29.5 |  | 2026-03-03 09:20 | 179.388 | 182.67 | 175.4 | 30.445 | 0 | 30.445 | 0 | 29 | 0 | 29 |  | 2026-03-03 09:20 | 182.964 | 185.417 | 178.8 | 30.9028 | 0 | 30.9028 | 0 | 29.6 | 0 | 29.6 |  | 2026-03-03 09:20 | 134.791 | 136.761 | 131.3 | 22.7935 | 0 | 22.7935 | 0 | 21.8 | 0 | 21.8 |  | 2026-03-03 09:20 | 136.253 | 137.978 | 132.8 | 22.9963 | 0 | 22.9963 | 0 | 21.7 | 0 | 21.7 |  | 2026-03-03 09:20 | 135.834 | 137.553 | 133 | 22.9255 | 0 | 22.9255 | 0 | 21.6 | 0 | 21.6 |  | 2026-03-03 09:20 | 136.546 | 140.069 | 133.6 | 23.3448 | 0 | 23.3448 | 0 | 21.7 | 0 | 21.7 |  | 2026-03-03 09:20 | 130.015 | 131.661 | 126.9 | 21.9435 | 0 | 21.9435 | 0 | 20.7 | 0 | 20.7 |  | 2026-03-03 09:20 | 236.6217 | 0 | 236.6217 | 0 | 225 | 0 | 225
|  |  | 165.349 | 167.425 | 147.6 | 27.9042 | 0 | 27.9042 | 0 | 26 | 0 | 26 |  | 2026-03-03 09:10 | 166.686 | 168.83 | 148.6 | 28.1383 | 0 | 28.1383 | 0 | 26.9 | 0 | 26.9 |  | 2026-03-03 09:10 | 165.051 | 168.07 | 146.4 | 28.0117 | 0 | 28.0117 | 0 | 26.1 | 0 | 26.1 |  | 2026-03-03 09:10 | 168.616 | 170.759 | 149.2 | 28.4598 | 0 | 28.4598 | 0 | 26.6 | 0 | 26.6 |  | 2026-03-03 09:10 | 124.354 | 125.903 | 109.5 | 20.9838 | 0 | 20.9838 | 0 | 19.6 | 0 | 19.6 |  | 2026-03-03 09:10 | 125.813 | 127.354 | 111.1 | 21.2257 | 0 | 21.2257 | 0 | 19.9 | 0 | 19.9 |  | 2026-03-03 09:10 | 125.361 | 126.909 | 111.4 | 21.1515 | 0 | 21.1515 | 0 | 19.8 | 0 | 19.8 |  | 2026-03-03 09:10 | 125.458 | 128.775 | 111.9 | 21.4625 | 0 | 21.4625 | 0 | 20 | 0 | 20 |  | 2026-03-03 09:10 | 119.795 | 121.287 | 106.2 | 20.2145 | 0 | 20.2145 | 0 | 19.2 | 0 | 19.2 |  | 2026-03-03 09:10 | 217.552 | 0 | 217.552 | 0 | 204.1 | 0 | 204.1
|  |  | 151.248 | 153.07 | 121.6 | 25.5117 | 0 | 25.5117 | 0 | 24.1 | 0 | 24.1 |  | 2026-03-03 09:00 | 151.921 | 154.545 | 121.7 | 25.7575 | 0 | 25.7575 | 0 | 23.7 | 0 | 23.7 |  | 2026-03-03 09:00 | 150.408 | 152.67 | 120.3 | 25.445 | 0 | 25.445 | 0 | 23.6 | 0 | 23.6 |  | 2026-03-03 09:00 | 153.304 | 155.213 | 122.6 | 25.8688 | 0 | 25.8688 | 0 | 24.1 | 0 | 24.1 |  | 2026-03-03 09:00 | 112.926 | 114.274 | 89.9 | 19.0457 | 0 | 19.0457 | 0 | 17.7 | 0 | 17.7 |  | 2026-03-03 09:00 | 114.575 | 115.943 | 91.2 | 19.3238 | 0 | 19.3238 | 0 | 18.3 | 0 | 18.3 |  | 2026-03-03 09:00 | 113.874 | 115.234 | 91.6 | 19.2057 | 0 | 19.2057 | 0 | 18.2 | 0 | 18.2 |  | 2026-03-03 09:00 | 114.053 | 117.231 | 91.9 | 19.5385 | 0 | 19.5385 | 0 | 18 | 0 | 18 |  | 2026-03-03 09:00 | 108.984 | 110.206 | 87 | 18.3677 | 0 | 18.3677 | 0 | 17.2 | 0 | 17.2 |  | 2026-03-03 09:00 | 198.0643 | 0 | 198.0643 | 0 | 184.9 | 0 | 184.9
|  |  | 135.037 | 136.541 | 97.5 | 22.7568 | 0 | 22.7568 | 0 | 21 | 0 | 21 |  | 2026-03-03 08:50 | 134.693 | 137.753 | 98 | 22.9588 | 0 | 22.9588 | 0 | 21.5 | 0 | 21.5 |  | 2026-03-03 08:50 | 134.349 | 136.271 | 96.7 | 22.7118 | 0 | 22.7118 | 0 | 21.1 | 0 | 21.1 |  | 2026-03-03 08:50 | 136.941 | 138.576 | 98.5 | 23.096 | 0 | 23.096 | 0 | 21.6 | 0 | 21.6 |  | 2026-03-03 08:50 | 100.807 | 101.99 | 72.2 | 16.9983 | 0 | 16.9983 | 0 | 15.9 | 0 | 15.9 |  | 2026-03-03 08:50 | 102.285 | 103.464 | 72.9 | 17.244 | 0 | 17.244 | 0 | 15.8 | 0 | 15.8 |  | 2026-03-03 08:50 | 101.805 | 102.996 | 73.4 | 17.166 | 0 | 17.166 | 0 | 15.8 | 0 | 15.8 |  | 2026-03-03 08:50 | 102.373 | 105.069 | 73.9 | 17.5115 | 0 | 17.5115 | 0 | 15.9 | 0 | 15.9 |  | 2026-03-03 08:50 | 97.154 | 98.284 | 69.8 | 16.3807 | 0 | 16.3807 | 0 | 15.1 | 0 | 15.1 |  | 2026-03-03 08:50 | 176.824 | 0 | 176.824 | 0 | 163.7 | 0 | 163.7
|  |  | 118.562 | 119.917 | 76.5 | 19.9862 | 0 | 19.9862 | 0 | 18.2 | 0 | 18.2 |  | 2026-03-03 08:40 | 119.775 | 121.181 | 76.5 | 20.1968 | 0 | 20.1968 | 0 | 18.9 | 0 | 18.9 |  | 2026-03-03 08:40 | 117.791 | 119.488 | 75.6 | 19.9147 | 0 | 19.9147 | 0 | 18.1 | 0 | 18.1 |  | 2026-03-03 08:40 | 120.178 | 121.564 | 76.9 | 20.2607 | 0 | 20.2607 | 0 | 18.5 | 0 | 18.5 |  | 2026-03-03 08:40 | 88.376 | 89.404 | 56.3 | 14.9007 | 0 | 14.9007 | 0 | 13.5 | 0 | 13.5 |  | 2026-03-03 08:40 | 90.001 | 90.923 | 57.1 | 15.1538 | 0 | 15.1538 | 0 | 14.1 | 0 | 14.1 |  | 2026-03-03 08:40 | 89.704 | 90.702 | 57.6 | 15.117 | 0 | 15.117 | 0 | 14 | 0 | 14 |  | 2026-03-03 08:40 | 90.003 | 92.349 | 58 | 15.3915 | 0 | 15.3915 | 0 | 14 | 0 | 14 |  | 2026-03-03 08:40 | 85.288 | 86.408 | 54.7 | 14.4013 | 0 | 14.4013 | 0 | 13.3 | 0 | 13.3 |  | 2026-03-03 08:40 | 155.3227 | 0 | 155.3227 | 0 | 142.6 | 0 | 142.6
|  |  | 101.393 | 102.51 | 58.3 | 17.085 | 0 | 17.085 | 0 | 15.5 | 0 | 15.5 |  | 2026-03-03 08:30 | 101.896 | 103.05 | 57.6 | 17.175 | 0 | 17.175 | 0 | 15.7 | 0 | 15.7 |  | 2026-03-03 08:30 | 100.511 | 101.951 | 57.5 | 16.9918 | 0 | 16.9918 | 0 | 15.4 | 0 | 15.4 |  | 2026-03-03 08:30 | 102.769 | 103.912 | 58.4 | 17.3187 | 0 | 17.3187 | 0 | 15.8 | 0 | 15.8 |  | 2026-03-03 08:30 | 75.401 | 76.317 | 42.8 | 12.7195 | 0 | 12.7195 | 0 | 11.7 | 0 | 11.7 |  | 2026-03-03 08:30 | 76.779 | 77.672 | 43 | 12.9453 | 0 | 12.9453 | 0 | 11.7 | 0 | 11.7 |  | 2026-03-03 08:30 | 76.447 | 77.352 | 43.6 | 12.892 | 0 | 12.892 | 0 | 11.6 | 0 | 11.6 |  | 2026-03-03 08:30 | 76.63 | 78.765 | 44 | 13.1275 | 0 | 13.1275 | 0 | 11.7 | 0 | 11.7 |  | 2026-03-03 08:30 | 73.052 | 73.939 | 41.4 | 12.3232 | 0 | 12.3232 | 0 | 11.1 | 0 | 11.1 |  | 2026-03-03 08:30 | 132.578 | 0 | 132.578 | 0 | 120.2 | 0 | 120.2
|  |  | 85.129 | 86.067 | 42.8 | 14.3445 | 0 | 14.3445 | 0 | 12.8 | 0 | 12.8 |  | 2026-03-03 08:20 | 84.71 | 85.678 | 41.9 | 14.2797 | 0 | 14.2797 | 0 | 13 | 0 | 13 |  | 2026-03-03 08:20 | 84.442 | 85.39 | 42.1 | 14.2317 | 0 | 14.2317 | 0 | 12.7 | 0 | 12.7 |  | 2026-03-03 08:20 | 86.025 | 86.882 | 42.6 | 14.4803 | 0 | 14.4803 | 0 | 12.9 | 0 | 12.9 |  | 2026-03-03 08:20 | 63.124 | 63.829 | 31.1 | 10.6382 | 0 | 10.6382 | 0 | 9.5 | 0 | 9.5 |  | 2026-03-03 08:20 | 64.546 | 65.317 | 31.3 | 10.8862 | 0 | 10.8862 | 0 | 9.7 | 0 | 9.7 |  | 2026-03-03 08:20 | 64.281 | 65.105 | 32 | 10.8508 | 0 | 10.8508 | 0 | 9.8 | 0 | 9.8 |  | 2026-03-03 08:20 | 64.519 | 66.426 | 32.3 | 11.071 | 0 | 11.071 | 0 | 9.8 | 0 | 9.8 |  | 2026-03-03 08:20 | 61.383 | 62.141 | 30.3 | 10.3568 | 0 | 10.3568 | 0 | 9.3 | 0 | 9.3 |  | 2026-03-03 08:20 | 111.1392 | 0 | 111.1392 | 0 | 99.5 | 0 | 99.5
|  |  | 68.773 | 69.559 | 30 | 11.5932 | 0 | 11.5932 | 0 | 10.4 | 0 | 10.4 |  | 2026-03-03 08:10 | 68.32 | 69.143 | 28.9 | 11.5238 | 0 | 11.5238 | 0 | 9.8 | 0 | 9.8 |  | 2026-03-03 08:10 | 67.957 | 68.755 | 29.4 | 11.4592 | 0 | 11.4592 | 0 | 10.1 | 0 | 10.1 |  | 2026-03-03 08:10 | 69.472 | 70.294 | 29.7 | 11.7157 | 0 | 11.7157 | 0 | 10.2 | 0 | 10.2 |  | 2026-03-03 08:10 | 50.603 | 51.29 | 21.6 | 8.5483 | 0 | 8.5483 | 0 | 7.5 | 0 | 7.5 |  | 2026-03-03 08:10 | 51.915 | 52.588 | 21.6 | 8.7647 | 0 | 8.7647 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 08:10 | 51.879 | 52.578 | 22.2 | 8.763 | 0 | 8.763 | 0 | 7.6 | 0 | 7.6 |  | 2026-03-03 08:10 | 52.01 | 53.416 | 22.5 | 8.9027 | 0 | 8.9027 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 08:10 | 49.421 | 50.107 | 21 | 8.3512 | 0 | 8.3512 | 0 | 7.3 | 0 | 7.3 |  | 2026-03-03 08:10 | 89.6217 | 0 | 89.6217 | 0 | 78.3 | 0 | 78.3
|  |  | 52.328 | 53.001 | 19.6 | 8.8335 | 0 | 8.8335 | 0 | 7.5 | 0 | 7.5 |  | 2026-03-03 08:00 | 52.748 | 53.41 | 19.1 | 8.9017 | 0 | 8.9017 | 0 | 7.7 | 0 | 7.7 |  | 2026-03-03 08:00 | 52.796 | 53.486 | 19.3 | 8.9143 | 0 | 8.9143 | 0 | 7.6 | 0 | 7.6 |  | 2026-03-03 08:00 | 53.885 | 54.589 | 19.5 | 9.0982 | 0 | 9.0982 | 0 | 7.8 | 0 | 7.8 |  | 2026-03-03 08:00 | 39.206 | 39.791 | 14.1 | 6.6318 | 0 | 6.6318 | 0 | 5.6 | 0 | 5.6 |  | 2026-03-03 08:00 | 40.31 | 40.899 | 13.9 | 6.8165 | 0 | 6.8165 | 0 | 5.7 | 0 | 5.7 |  | 2026-03-03 08:00 | 40.266 | 40.871 | 14.6 | 6.8118 | 0 | 6.8118 | 0 | 5.9 | 0 | 5.9 |  | 2026-03-03 08:00 | 40.45 | 41.492 | 14.8 | 6.9153 | 0 | 6.9153 | 0 | 5.8 | 0 | 5.8 |  | 2026-03-03 08:00 | 38.354 | 38.938 | 13.7 | 6.4897 | 0 | 6.4897 | 0 | 5.5 | 0 | 5.5 |  | 2026-03-03 08:00 | 69.4128 | 0 | 69.4128 | 0 | 59.1 | 0 | 59.1
|  |  | 39.297 | 39.871 | 12.1 | 6.6452 | 0 | 6.6452 | 0 | 5.4 | 0 | 5.4 |  | 2026-03-03 07:50 | 38.172 | 38.749 | 11.4 | 6.4582 | 0 | 6.4582 | 0 | 5.1 | 0 | 5.1 |  | 2026-03-03 07:50 | 38.677 | 39.258 | 11.7 | 6.543 | 0 | 6.543 | 0 | 5.4 | 0 | 5.4 |  | 2026-03-03 07:50 | 39.489 | 40.086 | 11.7 | 6.681 | 0 | 6.681 | 0 | 5.5 | 0 | 5.5 |  | 2026-03-03 07:50 | 28.721 | 29.086 | 8.5 | 4.8477 | 0 | 4.8477 | 0 | 4 | 0 | 4 |  | 2026-03-03 07:50 | 28.043 | 28.528 | 8.2 | 4.7547 | 0 | 4.7547 | 0 | 3.8 | 0 | 3.8 |  | 2026-03-03 07:50 | 29.48 | 29.961 | 8.7 | 4.9935 | 0 | 4.9935 | 0 | 4 | 0 | 4 |  | 2026-03-03 07:50 | 29.731 | 30.742 | 9 | 5.1237 | 0 | 5.1237 | 0 | 4.1 | 0 | 4.1 |  | 2026-03-03 07:50 | 27.982 | 28.466 | 8.2 | 4.7443 | 0 | 4.7443 | 0 | 3.9 | 0 | 3.9 |  | 2026-03-03 07:50 | 50.7912 | 0 | 50.7912 | 0 | 41.2 | 0 | 41.2
|  |  | 25.975 | 26.484 | 6.7 | 4.414 | 0 | 4.414 | 0 | 3.6 | 0 | 3.6 |  | 2026-03-03 07:40 | 25.933 | 26.759 | 6.3 | 4.4598 | 0 | 4.4598 | 0 | 3.5 | 0 | 3.5 |  | 2026-03-03 07:40 | 26.27 | 26.757 | 6.3 | 4.4595 | 0 | 4.4595 | 0 | 3.5 | 0 | 3.5 |  | 2026-03-03 07:40 | 25.942 | 26.431 | 6.2 | 4.4052 | 0 | 4.4052 | 0 | 3.4 | 0 | 3.4 |  | 2026-03-03 07:40 | 19.166 | 19.849 | 4.5 | 3.3082 | 0 | 3.3082 | 0 | 2.5 | 0 | 2.5 |  | 2026-03-03 07:40 | 18.806 | 19.213 | 4.4 | 3.2022 | 0 | 3.2022 | 0 | 2.5 | 0 | 2.5 |  | 2026-03-03 07:40 | 19.817 | 20.25 | 4.7 | 3.375 | 0 | 3.375 | 0 | 2.7 | 0 | 2.7 |  | 2026-03-03 07:40 | 20.029 | 20.914 | 4.9 | 3.4857 | 0 | 3.4857 | 0 | 2.6 | 0 | 2.6 |  | 2026-03-03 07:40 | 18.588 | 18.989 | 4.3 | 3.1648 | 0 | 3.1648 | 0 | 2.4 | 0 | 2.4 |  | 2026-03-03 07:40 | 34.2743 | 0 | 34.2743 | 0 | 26.7 | 0 | 26.7
|  |  | 16.105 | 16.488 | 3.1 | 2.748 | 0 | 2.748 | 0 | 2 | 0 | 2 |  | 2026-03-03 07:30 | 15.268 | 15.794 | 2.8 | 2.6323 | 0 | 2.6323 | 0 | 1.9 | 0 | 1.9 |  | 2026-03-03 07:30 | 15.934 | 16.317 | 2.8 | 2.7195 | 0 | 2.7195 | 0 | 1.9 | 0 | 1.9 |  | 2026-03-03 07:30 | 15.63 | 16.492 | 2.8 | 2.7487 | 0 | 2.7487 | 0 | 1.9 | 0 | 1.9 |  | 2026-03-03 07:30 | 11.609 | 12.415 | 2 | 2.0692 | 0 | 2.0692 | 0 | 1.4 | 0 | 1.4 |  | 2026-03-03 07:30 | 11.262 | 11.62 | 1.9 | 1.9367 | 0 | 1.9367 | 0 | 1.4 | 0 | 1.4 |  | 2026-03-03 07:30 | 11.898 | 12.266 | 2 | 2.0443 | 0 | 2.0443 | 0 | 1.4 | 0 | 1.4 |  | 2026-03-03 07:30 | 11.949 | 12.66 | 2.3 | 2.11 | 0 | 2.11 | 0 | 1.5 | 0 | 1.5 |  | 2026-03-03 07:30 | 11.106 | 11.464 | 1.9 | 1.9107 | 0 | 1.9107 | 0 | 1.4 | 0 | 1.4 |  | 2026-03-03 07:30 | 20.9193 | 0 | 20.9193 | 0 | 14.8 | 0 | 14.8
|  |  | 8.239 | 8.551 | 1.1 | 1.4252 | 0 | 1.4252 | 0 | 0.9 | 0 | 0.9 |  | 2026-03-03 07:20 | 8.042 | 8.739 | 0.9 | 1.4565 | 0 | 1.4565 | 0 | 0.9 | 0 | 0.9 |  | 2026-03-03 07:20 | 8.158 | 8.472 | 0.9 | 1.412 | 0 | 1.412 | 0 | 0.9 | 0 | 0.9 |  | 2026-03-03 07:20 | 8.098 | 8.821 | 0.9 | 1.4702 | 0 | 1.4702 | 0 | 0.9 | 0 | 0.9 |  | 2026-03-03 07:20 | 5.956 | 6.647 | 0.6 | 1.1078 | 0 | 1.1078 | 0 | 0.6 | 0 | 0.6 |  | 2026-03-03 07:20 | 5.583 | 5.822 | 0.5 | 0.97033 | 0 | 0.97033 | 0 | 0.5 | 0 | 0.5 |  | 2026-03-03 07:20 | 6.018 | 6.277 | 0.6 | 1.0462 | 0 | 1.0462 | 0 | 0.6 | 0 | 0.6 |  | 2026-03-03 07:20 | 6.065 | 6.504 | 0.8 | 1.084 | 0 | 1.084 | 0 | 0.7 | 0 | 0.7 |  | 2026-03-03 07:20 | 5.539 | 5.781 | 0.5 | 0.9635 | 0 | 0.9635 | 0 | 0.5 | 0 | 0.5 |  | 2026-03-03 07:20 | 10.9357 | 0 | 10.9357 | 0 | 6.5 | 0 | 6.5
|  |  | 3.105 | 3.258 | 0.2 | 0.543 | 0 | 0.543 | 0 | 0.2 | 0 | 0.2 |  | 2026-03-03 07:10 | 0.958 | 2.265 | 0 | 0.3775 | 0 | 0.3775 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 2.936 | 3.083 | 0 | 0.51383 | 0 | 0.51383 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 2.925 | 4.016 | 0 | 0.66933 | 0 | 0.66933 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 2.237 | 2.744 | 0.1 | 0.45733 | 0 | 0.45733 | 0 | 0.1 | 0 | 0.1 |  | 2026-03-03 07:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:10 | 2.561 | 0 | 2.561 | 0 | 0.3 | 0 | 0.3
|  |  | 0.391 | 0.448 | 0 | 0.074667 | 0 | 0.074667 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-03-03 07:00 | 0.074667 | 0 | 0.074667 | 0 | 0 | 0 | 0
[110 empty] | Total: - | 17502.3047 | #VALUE! | #VALUE! |  | 17226.4 | #VALUE! | #VALUE!
Sum:- | 0 |  | 13129.05 |  | 83763.8 |  |  |  |  | 2227.8 | #VALUE! | #VALUE! | 0.9836 |  | 13377.03 |  | 86903.9 |  |  |  |  | 2261.4 | #VALUE! | #VALUE! | 0.98342 |  | 13300.458 |  | 85224.6 |  |  |  |  | 2216.9 | #VALUE! | #VALUE! | 0.97331 |  | 13489.286 |  | 86508.8 |  |  |  |  | 2248.2 | #VALUE! | #VALUE! | 0.98325 |  | 10057.133 |  | 64411 |  |  |  |  | 1676.7 | #VALUE! | #VALUE! | 0.98462 |  | 9997.319 |  | 64190.8 |  |  |  |  | 1666.5 | #VALUE! | #VALUE! | 0.98229 |  | 9999.239 |  | 64203.5 |  |  |  |  | 1667 | #VALUE! | #VALUE! | 0.98193 |  | 10056.632 |  | 64590.2 |  |  |  |  | 1676.2 | #VALUE! | #VALUE! | 0.97165 |  | 9511.748 |  | 61128.4 |  |  |  |  | 1585.7 | #VALUE! | #VALUE! | 0.98492
Formulas:
Time = [Inverter 09]

## 4 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-04-03 19:00 | 0 | 37.02 | 0.055 | 0.101 | 2332.3 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.055 | 0.101 | 2332.3 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.079 | 0.083 | 2325.1 | 0.013833 | 0 | 0.013833 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.086 | 0.09 | 2355.2 | 0.015 | 0 | 0.015 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.099 | 0.104 | 1759.1 | 0.017333 | 0 | 0.017333 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.071 | 0.098 | 1742.4 | 0.016333 | 0 | 0.016333 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.098 | 0.103 | 1746.3 | 0.017167 | 0 | 0.017167 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.067 | 0.086 | 1765.1 | 0.014333 | 0 | 0.014333 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.089 | 0.094 | 1669 | 0.015667 | 0 | 0.015667 | 0 | 0 | 0 | 0 |  | 2026-04-03 19:00 | 0.14333 | 0 | 0.14333 | 0 | 0 | 0 | 0 | 1 | 98.34%
2026-04-03 18:50 | 0 | 37.88 | 0.092 | 0.097 | 2332.3 | 0.016167 | 0 | 0.016167 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.092 | 0.097 | 2332.3 | 0.016167 | 0 | 0.016167 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.105 | 0.11 | 2325.1 | 0.018333 | 0 | 0.018333 | 0 | 0.2 | 0 | 0.2 |  | 2026-04-03 18:50 | 0.083 | 0.497 | 2355.2 | 0.082833 | 0 | 0.082833 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.083 | 0.087 | 1759.1 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 2026-04-03 18:50 | 0.081 | 0.085 | 1742.4 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 2026-04-03 18:50 | 0.099 | 0.104 | 1746.3 | 0.017333 | 0 | 0.017333 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.017 | 0.25 | 1765.1 | 0.041667 | 0 | 0.041667 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.102 | 0.107 | 1669 | 0.017833 | 0 | 0.017833 | 0 | 0.1 | 0 | 0.1 |  | 2026-04-03 18:50 | 0.239 | 0 | 0.239 | 0 | 0.8 | 0 | 0.8 | 2 | 98.34%
2026-04-03 18:40 | 0 | 39.89 | 1.763 | 1.854 | 2332.2 | 0.309 | 0 | 0.309 | 0 | 0.5 | 0 | 0.5 |  | 2026-04-03 18:40 | 1.763 | 1.854 | 2332.2 | 0.309 | 0 | 0.309 | 0 | 0.5 | 0 | 0.5 |  | 2026-04-03 18:40 | 1.64 | 1.724 | 2324.9 | 0.28733 | 0 | 0.28733 | 0 | 0.5 | 0 | 0.5 |  | 2026-04-03 18:40 | 1.657 | 2.045 | 2355.1 | 0.34083 | 0 | 0.34083 | 0 | 0.6 | 0 | 0.6 |  | 2026-04-03 18:40 | 1.043 | 1.183 | 1759.1 | 0.19717 | 0 | 0.19717 | 0 | 0.4 | 0 | 0.4 |  | 2026-04-03 18:40 | 0.968 | 1.018 | 1742.4 | 0.16967 | 0 | 0.16967 | 0 | 0.4 | 0 | 0.4 |  | 2026-04-03 18:40 | 0.995 | 1.043 | 1746.2 | 0.17383 | 0 | 0.17383 | 0 | 0.3 | 0 | 0.3 |  | 2026-04-03 18:40 | 1.108 | 1.548 | 1765 | 0.258 | 0 | 0.258 | 0 | 0.4 | 0 | 0.4 |  | 2026-04-03 18:40 | 0.951 | 1 | 1668.9 | 0.16667 | 0 | 0.16667 | 0 | 0.3 | 0 | 0.3 |  | 2026-04-03 18:40 | 2.2115 | 0 | 2.2115 | 0 | 3.9 | 0 | 3.9 | 3 | 97.22%
2026-04-03 18:30 | 9 | 42.19 | 5.204 | 5.454 | 2331.7 | 0.909 | 0.54942 | 0.35958 | 3.2965 | 1.3 | 0.54157 | 0.75843 |  | 2026-04-03 18:30 | 5.204 | 5.454 | 2331.7 | 0.909 | 0.54942 | 0.35958 | 3.2965 | 1.3 | 0.54157 | 0.75843 |  | 2026-04-03 18:30 | 5.304 | 5.559 | 2324.4 | 0.9265 | 0.54942 | 0.37708 | 3.2965 | 1.3 | 0.54157 | 0.75843 |  | 2026-04-03 18:30 | 5.344 | 5.649 | 2354.5 | 0.9415 | 0.54942 | 0.39208 | 3.2965 | 1.3 | 0.54157 | 0.75843 |  | 2026-04-03 18:30 | 3.794 | 3.987 | 1758.7 | 0.6645 | 0.40698 | 0.25752 | 2.4419 | 1 | 0.40116 | 0.59884 |  | 2026-04-03 18:30 | 3.458 | 3.636 | 1742 | 0.606 | 0.40698 | 0.19902 | 2.4419 | 0.9 | 0.40116 | 0.49884 |  | 2026-04-03 18:30 | 3.721 | 3.91 | 1745.9 | 0.65167 | 0.40698 | 0.24469 | 2.4419 | 1 | 0.40116 | 0.59884 |  | 2026-04-03 18:30 | 3.792 | 4.135 | 1764.6 | 0.68917 | 0.40698 | 0.28219 | 2.4419 | 0.9 | 0.40116 | 0.49884 |  | 2026-04-03 18:30 | 3.485 | 3.664 | 1668.6 | 0.61067 | 0.38719 | 0.22348 | 2.3231 | 0.9 | 0.38165 | 0.51835 |  | 2026-04-03 18:30 | 6.908 | 4.2128 | 2.6952 | 25.2768 | 9.9 | 4.1526 | 5.7474 | 4 | 98.31%
2026-04-03 18:20 | 23 | 44.2 | 10.837 | 11.115 | 2330.4 | 1.8525 | 1.3936 | 0.45893 | 8.3614 | 2.4 | 1.3736 | 1.0264 |  | 2026-04-03 18:20 | 10.837 | 11.115 | 2330.4 | 1.8525 | 1.3936 | 0.45893 | 8.3614 | 2.4 | 1.3736 | 1.0264 |  | 2026-04-03 18:20 | 10.967 | 11.369 | 2323.1 | 1.8948 | 1.3936 | 0.50126 | 8.3614 | 2.5 | 1.3736 | 1.1264 |  | 2026-04-03 18:20 | 11.216 | 11.623 | 2353.2 | 1.9372 | 1.3936 | 0.5436 | 8.3614 | 2.6 | 1.3736 | 1.2264 |  | 2026-04-03 18:20 | 8.118 | 8.454 | 1757.7 | 1.409 | 1.0323 | 0.37673 | 6.1936 | 1.9 | 1.0175 | 0.88249 |  | 2026-04-03 18:20 | 7.89 | 8.216 | 1741.1 | 1.3693 | 1.0323 | 0.33706 | 6.1936 | 1.8 | 1.0175 | 0.78249 |  | 2026-04-03 18:20 | 7.97 | 8.299 | 1744.9 | 1.3832 | 1.0323 | 0.35089 | 6.1936 | 1.8 | 1.0175 | 0.78249 |  | 2026-04-03 18:20 | 7.245 | 7.82 | 1763.7 | 1.3033 | 1.0323 | 0.27106 | 6.1936 | 1.5 | 1.0175 | 0.48249 |  | 2026-04-03 18:20 | 7.196 | 7.505 | 1667.7 | 1.2508 | 0.98208 | 0.26875 | 5.8925 | 1.7 | 0.96804 | 0.73196 |  | 2026-04-03 18:20 | 14.2527 | 10.6855 | 3.5672 | 64.1127 | 18.6 | 10.5327 | 8.0673 | 5 | 98.45%
2026-04-03 18:10 | 38 | 46.49 | 18.539 | 19.007 | 2328 | 3.1678 | 2.2826 | 0.8852 | 13.6958 | 3.8 | 2.25 | 1.55 |  | 2026-04-03 18:10 | 18.539 | 19.007 | 2328 | 3.1678 | 2.2826 | 0.8852 | 13.6958 | 3.8 | 2.25 | 1.55 |  | 2026-04-03 18:10 | 19.427 | 19.919 | 2320.6 | 3.3198 | 2.2826 | 1.0372 | 13.6958 | 4.3 | 2.25 | 2.05 |  | 2026-04-03 18:10 | 19.506 | 19.998 | 2350.6 | 3.333 | 2.2826 | 1.0504 | 13.6958 | 4.1 | 2.25 | 1.85 |  | 2026-04-03 18:10 | 14.419 | 14.851 | 1755.8 | 2.4752 | 1.6908 | 0.78433 | 10.145 | 3 | 1.6667 | 1.3333 |  | 2026-04-03 18:10 | 13.85 | 14.295 | 1739.3 | 2.3825 | 1.6908 | 0.69166 | 10.145 | 2.9 | 1.6667 | 1.2333 |  | 2026-04-03 18:10 | 14.012 | 14.432 | 1743.1 | 2.4053 | 1.6908 | 0.71449 | 10.145 | 3 | 1.6667 | 1.3333 |  | 2026-04-03 18:10 | 12.047 | 12.715 | 1762.2 | 2.1192 | 1.6908 | 0.42833 | 10.145 | 2.8 | 1.6667 | 1.1333 |  | 2026-04-03 18:10 | 13.074 | 13.494 | 1666 | 2.249 | 1.6086 | 0.64037 | 9.6518 | 2.7 | 1.5856 | 1.1144 |  | 2026-04-03 18:10 | 24.6197 | 17.5025 | 7.1171 | 105.0152 | 30.4 | 17.2522 | 13.1478 | 6 | 98.15%
2026-04-03 18:00 | 54 | 47.64 | 28.927 | 29.502 | 2324.2 | 4.917 | 3.2296 | 1.6874 | 19.3778 | 5.9 | 3.1834 | 2.7166 |  | 2026-04-03 18:00 | 28.927 | 29.502 | 2324.2 | 4.917 | 3.2296 | 1.6874 | 19.3778 | 5.9 | 3.1834 | 2.7166 |  | 2026-04-03 18:00 | 30.678 | 31.256 | 2316.3 | 5.2093 | 3.2296 | 1.9797 | 19.3778 | 5.9 | 3.1834 | 2.7166 |  | 2026-04-03 18:00 | 30.365 | 30.94 | 2346.5 | 5.1567 | 3.2296 | 1.927 | 19.3778 | 6.2 | 3.1834 | 3.0166 |  | 2026-04-03 18:00 | 22.723 | 23.251 | 1752.8 | 3.8752 | 2.3923 | 1.4828 | 14.3539 | 4.7 | 2.3581 | 2.3419 |  | 2026-04-03 18:00 | 21.748 | 22.262 | 1736.4 | 3.7103 | 2.3923 | 1.318 | 14.3539 | 4.5 | 2.3581 | 2.1419 |  | 2026-04-03 18:00 | 22.031 | 22.552 | 1740.1 | 3.7587 | 2.3923 | 1.3663 | 14.3539 | 4.4 | 2.3581 | 2.0419 |  | 2026-04-03 18:00 | 20.995 | 21.625 | 1759.4 | 3.6042 | 2.3923 | 1.2118 | 14.3539 | 4.3 | 2.3581 | 1.9419 |  | 2026-04-03 18:00 | 20.533 | 21.029 | 1663.3 | 3.5048 | 2.276 | 1.2288 | 13.656 | 4.2 | 2.2434 | 1.9566 |  | 2026-04-03 18:00 | 38.6532 | 24.7638 | 13.8894 | 148.5826 | 46 | 24.4097 | 21.5903 | 7 | 98.1%
2026-04-03 17:50 | 130 | 47.93 | 42.191 | 42.912 | 2318.3 | 7.152 | 7.7665 | -0.61446 | 46.5988 | 8.2 | 7.6554 | 0.5446 |  | 2026-04-03 17:50 | 42.191 | 42.912 | 2318.3 | 7.152 | 7.7665 | -0.61446 | 46.5988 | 8.2 | 7.6554 | 0.5446 |  | 2026-04-03 17:50 | 43.13 | 43.867 | 2310.4 | 7.3112 | 7.7665 | -0.45529 | 46.5988 | 8.4 | 7.6554 | 0.7446 |  | 2026-04-03 17:50 | 43.531 | 44.27 | 2340.3 | 7.3783 | 7.7665 | -0.38813 | 46.5988 | 8.3 | 7.6554 | 0.6446 |  | 2026-04-03 17:50 | 32.65 | 33.255 | 1748.1 | 5.5425 | 5.7529 | -0.21043 | 34.5176 | 6.2 | 5.6707 | 0.52933 |  | 2026-04-03 17:50 | 31.313 | 31.9 | 1731.9 | 5.3167 | 5.7529 | -0.43627 | 34.5176 | 6 | 5.6707 | 0.32933 |  | 2026-04-03 17:50 | 31.569 | 32.151 | 1735.7 | 5.3585 | 5.7529 | -0.39443 | 34.5176 | 6.1 | 5.6707 | 0.42933 |  | 2026-04-03 17:50 | 31.484 | 32.555 | 1755.1 | 5.4258 | 5.7529 | -0.3271 | 34.5176 | 6.1 | 5.6707 | 0.42933 |  | 2026-04-03 17:50 | 29.635 | 30.212 | 1659.1 | 5.0353 | 5.4732 | -0.43787 | 32.8392 | 5.8 | 5.3949 | 0.40506 |  | 2026-04-03 17:50 | 55.6723 | 59.5508 | -3.8784 | 357.3046 | 63.3 | 58.6992 | 4.6008 | 8 | 97.14%
2026-04-03 17:40 | 180 | 48.22 | 56.591 | 57.004 | 2310.1 | 9.5007 | 10.7417 | -1.241 | 64.4501 | 11 | 10.5881 | 0.41191 |  | 2026-04-03 17:40 | 56.591 | 57.004 | 2310.1 | 9.5007 | 10.7417 | -1.241 | 64.4501 | 11 | 10.5881 | 0.41191 |  | 2026-04-03 17:40 | 57.16 | 58.019 | 2302 | 9.6698 | 10.7417 | -1.0719 | 64.4501 | 10.8 | 10.5881 | 0.21191 |  | 2026-04-03 17:40 | 57.897 | 58.761 | 2332 | 9.7935 | 10.7417 | -0.94819 | 64.4501 | 10.9 | 10.5881 | 0.31191 |  | 2026-04-03 17:40 | 43.379 | 44.107 | 1741.9 | 7.3512 | 7.9568 | -0.60564 | 47.7409 | 8.2 | 7.843 | 0.35697 |  | 2026-04-03 17:40 | 41.851 | 42.557 | 1725.9 | 7.0928 | 7.9568 | -0.86398 | 47.7409 | 7.9 | 7.843 | 0.056974 |  | 2026-04-03 17:40 | 42.118 | 42.829 | 1729.6 | 7.1382 | 7.9568 | -0.81864 | 47.7409 | 8 | 7.843 | 0.15697 |  | 2026-04-03 17:40 | 42.115 | 43.385 | 1749 | 7.2308 | 7.9568 | -0.72598 | 47.7409 | 8 | 7.843 | 0.15697 |  | 2026-04-03 17:40 | 39.794 | 40.492 | 1653.3 | 6.7487 | 7.5699 | -0.82125 | 45.4195 | 7.6 | 7.4617 | 0.13833 |  | 2026-04-03 17:40 | 74.0263 | 82.3639 | -8.3376 | 494.1835 | 83.4 | 81.1861 | 2.2139 | 9 | 98.47%
2026-04-03 17:30 | 226 | 48.22 | 72.247 | 73.206 | 2299.1 | 12.201 | 13.4868 | -1.2858 | 80.9207 | 13.8 | 13.2939 | 0.50607 |  | 2026-04-03 17:30 | 72.247 | 73.206 | 2299.1 | 12.201 | 13.4868 | -1.2858 | 80.9207 | 13.8 | 13.2939 | 0.50607 |  | 2026-04-03 17:30 | 72.973 | 74.139 | 2291.2 | 12.3565 | 13.4868 | -1.1303 | 80.9207 | 13.4 | 13.2939 | 0.10607 |  | 2026-04-03 17:30 | 73.35 | 74.346 | 2321.1 | 12.391 | 13.4868 | -1.0958 | 80.9207 | 13.5 | 13.2939 | 0.20607 |  | 2026-04-03 17:30 | 55.225 | 56.066 | 1733.7 | 9.3443 | 9.9902 | -0.64588 | 59.9413 | 10.2 | 9.8474 | 0.35264 |  | 2026-04-03 17:30 | 53.401 | 54.214 | 1718 | 9.0357 | 9.9902 | -0.95455 | 59.9413 | 9.8 | 9.8474 | -0.047355 |  | 2026-04-03 17:30 | 53.718 | 54.542 | 1721.6 | 9.0903 | 9.9902 | -0.89988 | 59.9413 | 10 | 9.8474 | 0.15264 |  | 2026-04-03 17:30 | 53.889 | 55.523 | 1741 | 9.2538 | 9.9902 | -0.73638 | 59.9413 | 10.1 | 9.8474 | 0.25264 |  | 2026-04-03 17:30 | 50.906 | 51.713 | 1645.7 | 8.6188 | 9.5045 | -0.88562 | 57.0267 | 9.3 | 9.3685 | -0.068539 |  | 2026-04-03 17:30 | 94.4925 | 103.4125 | -8.92 | 620.4748 | 103.9 | 101.9337 | 1.9663
2026-04-03 17:20 | 270 | 48.22 | 89.552 | 89.105 | 2285.3 | 14.8508 | 16.1125 | -1.2617 | 96.6752 | 14.8 | 15.8821 | -1.0821 |  | 2026-04-03 17:20 | 89.552 | 89.105 | 2285.3 | 14.8508 | 16.1125 | -1.2617 | 96.6752 | 14.8 | 15.8821 | -1.0821 |  | 2026-04-03 17:20 | 88.348 | 90.085 | 2277.8 | 15.0142 | 16.1125 | -1.0984 | 96.6752 | 16 | 15.8821 | 0.11787 |  | 2026-04-03 17:20 | 88.775 | 89.935 | 2307.6 | 14.9892 | 16.1125 | -1.1234 | 96.6752 | 16.1 | 15.8821 | 0.21787 |  | 2026-04-03 17:20 | 66.818 | 67.753 | 1723.5 | 11.2922 | 11.9352 | -0.64305 | 71.6113 | 12.1 | 11.7645 | 0.33546 |  | 2026-04-03 17:20 | 64.874 | 65.78 | 1708.2 | 10.9633 | 11.9352 | -0.97188 | 71.6113 | 12 | 11.7645 | 0.23546 |  | 2026-04-03 17:20 | 65.455 | 66.364 | 1711.6 | 11.0607 | 11.9352 | -0.87455 | 71.6113 | 11.9 | 11.7645 | 0.13546 |  | 2026-04-03 17:20 | 65.83 | 67.631 | 1730.9 | 11.2718 | 11.9352 | -0.66338 | 71.6113 | 11.9 | 11.7645 | 0.13546 |  | 2026-04-03 17:20 | 61.929 | 62.796 | 1636.4 | 10.466 | 11.3549 | -0.88888 | 68.1293 | 11.3 | 11.1925 | 0.1075 |  | 2026-04-03 17:20 | 114.759 | 123.5459 | -8.7869 | 741.2753 | 120.9 | 121.7792 | -0.87917
2026-04-03 17:10 | 317 | 48.5 | 103.076 | 104.381 | 2270.5 | 17.3968 | 18.8971 | -1.5003 | 113.3828 | 18.9 | 18.6269 | 0.2731 |  | 2026-04-03 17:10 | 103.076 | 104.381 | 2270.5 | 17.3968 | 18.8971 | -1.5003 | 113.3828 | 18.9 | 18.6269 | 0.2731 |  | 2026-04-03 17:10 | 104.407 | 106.435 | 2261.8 | 17.7392 | 18.8971 | -1.158 | 113.3828 | 18.8 | 18.6269 | 0.1731 |  | 2026-04-03 17:10 | 104.972 | 106.333 | 2291.5 | 17.7222 | 18.8971 | -1.175 | 113.3828 | 18.9 | 18.6269 | 0.2731 |  | 2026-04-03 17:10 | 78.988 | 80.061 | 1711.4 | 13.3435 | 13.9979 | -0.65438 | 83.9873 | 14.2 | 13.7977 | 0.40229 |  | 2026-04-03 17:10 | 76.946 | 77.975 | 1696.2 | 12.9958 | 13.9979 | -1.002 | 83.9873 | 13.7 | 13.7977 | -0.097707 |  | 2026-04-03 17:10 | 77.33 | 78.372 | 1699.7 | 13.062 | 13.9979 | -0.93588 | 83.9873 | 13.7 | 13.7977 | -0.097707 |  | 2026-04-03 17:10 | 77.777 | 79.796 | 1719 | 13.2993 | 13.9979 | -0.69854 | 83.9873 | 14.1 | 13.7977 | 0.30229 |  | 2026-04-03 17:10 | 73.175 | 74.184 | 1625.1 | 12.364 | 13.3172 | -0.95325 | 79.9035 | 13.2 | 13.1268 | 0.073191 |  | 2026-04-03 17:10 | 135.3197 | 144.8973 | -9.5776 | 869.3837 | 144.4 | 142.8253 | 1.5747
2026-04-03 17:00 | 361 | 48.5 | 120.123 | 121.644 | 2251.6 | 20.274 | 21.5201 | -1.2461 | 129.1205 | 20.7 | 21.2123 | -0.51234 |  | 2026-04-03 17:00 | 120.123 | 121.644 | 2251.6 | 20.274 | 21.5201 | -1.2461 | 129.1205 | 20.7 | 21.2123 | -0.51234 |  | 2026-04-03 17:00 | 120.137 | 122.503 | 2243 | 20.4172 | 21.5201 | -1.1029 | 129.1205 | 21.2 | 21.2123 | -0.012342 |  | 2026-04-03 17:00 | 121.321 | 122.894 | 2272.6 | 20.4823 | 21.5201 | -1.0377 | 129.1205 | 21.6 | 21.2123 | 0.38766 |  | 2026-04-03 17:00 | 90.37 | 91.551 | 1697.2 | 15.2585 | 15.9408 | -0.6823 | 95.6448 | 16.2 | 15.7128 | 0.48715 |  | 2026-04-03 17:00 | 88.81 | 89.971 | 1682.5 | 14.9952 | 15.9408 | -0.94563 | 95.6448 | 15.8 | 15.7128 | 0.087154 |  | 2026-04-03 17:00 | 89.311 | 90.469 | 1686 | 15.0782 | 15.9408 | -0.86263 | 95.6448 | 15.9 | 15.7128 | 0.18715 |  | 2026-04-03 17:00 | 90.113 | 92.63 | 1704.9 | 15.4383 | 15.9408 | -0.50247 | 95.6448 | 15.8 | 15.7128 | 0.087154 |  | 2026-04-03 17:00 | 84.822 | 85.948 | 1611.9 | 14.3247 | 15.1657 | -0.84103 | 90.9942 | 14.9 | 14.9488 | -0.048827 |  | 2026-04-03 17:00 | 156.5423 | 165.0092 | -8.4669 | 990.0553 | 162.8 | 162.6496 | 0.15042
2026-04-03 16:50 | 403 | 48.5 | 134.481 | 135.778 | 2230.9 | 22.6297 | 24.0238 | -1.3941 | 144.1428 | 51.5 | 23.6803 | 27.8197 |  | 2026-04-03 16:50 | 134.481 | 135.778 | 2230.9 | 22.6297 | 24.0238 | -1.3941 | 144.1428 | 24.3 | 23.6803 | 0.61974 |  | 2026-04-03 16:50 | 135.152 | 137.981 | 2221.8 | 22.9968 | 24.0238 | -1.027 | 144.1428 | 23.8 | 23.6803 | 0.11974 |  | 2026-04-03 16:50 | 136.026 | 137.832 | 2251 | 22.972 | 24.0238 | -1.0518 | 144.1428 | 24 | 23.6803 | 0.31974 |  | 2026-04-03 16:50 | 101.826 | 103.167 | 1681 | 17.1945 | 17.7954 | -0.60091 | 106.7724 | 18 | 17.5409 | 0.45907 |  | 2026-04-03 16:50 | 99.867 | 101.162 | 1666.7 | 16.8603 | 17.7954 | -0.93507 | 106.7724 | 17.7 | 17.5409 | 0.15907 |  | 2026-04-03 16:50 | 100.145 | 101.443 | 1670.1 | 16.9072 | 17.7954 | -0.88824 | 106.7724 | 17.7 | 17.5409 | 0.15907 |  | 2026-04-03 16:50 | 100.884 | 103.659 | 1689.1 | 17.2765 | 17.7954 | -0.51891 | 106.7724 | 17.8 | 17.5409 | 0.25907 |  | 2026-04-03 16:50 | 95.144 | 96.387 | 1597 | 16.0645 | 16.9301 | -0.86563 | 101.5808 | 16.8 | 16.688 | 0.11197 |  | 2026-04-03 16:50 | 175.5312 | 184.207 | -8.6758 | 1105.2418 | 211.6 | 181.5728 | 30.0272
2026-04-03 16:40 | 446 | 49.08 | 150.233 | 152.212 | 2206.6 | 25.3687 | 26.5283 | -1.1597 | 159.17 | 0 | 26.149 | -26.149 |  | 2026-04-03 16:40 | 150.233 | 152.212 | 2206.6 | 25.3687 | 26.5283 | -1.1597 | 159.17 | 27.2 | 26.149 | 1.051 |  | 2026-04-03 16:40 | 150.76 | 153.936 | 2198 | 25.656 | 26.5283 | -0.87233 | 159.17 | 26.5 | 26.149 | 0.35103 |  | 2026-04-03 16:40 | 151.814 | 153.892 | 2227 | 25.6487 | 26.5283 | -0.87966 | 159.17 | 26.3 | 26.149 | 0.15103 |  | 2026-04-03 16:40 | 113.96 | 115.461 | 1663 | 19.2435 | 19.6506 | -0.40711 | 117.9037 | 20 | 19.3696 | 0.63039 |  | 2026-04-03 16:40 | 111.644 | 113.131 | 1649 | 18.8552 | 19.6506 | -0.79544 | 117.9037 | 19.6 | 19.3696 | 0.23039 |  | 2026-04-03 16:40 | 111.94 | 113.414 | 1652.4 | 18.9023 | 19.6506 | -0.74828 | 117.9037 | 19.7 | 19.3696 | 0.33039 |  | 2026-04-03 16:40 | 112.838 | 115.966 | 1671.3 | 19.3277 | 19.6506 | -0.32294 | 117.9037 | 19.8 | 19.3696 | 0.43039 |  | 2026-04-03 16:40 | 106.271 | 107.682 | 1580.2 | 17.947 | 18.6951 | -0.74812 | 112.1707 | 18.6 | 18.4278 | 0.17222 |  | 2026-04-03 16:40 | 196.3177 | 203.4109 | -7.0932 | 1220.4652 | 177.7 | 200.5021 | -22.8021
2026-04-03 16:30 | 492 | 49.08 | 167.202 | 169.49 | 2179.4 | 28.2483 | 29.2644 | -1.0161 | 175.5866 | 27.6 | 28.8459 | -1.2459 |  | 2026-04-03 16:30 | 167.202 | 169.49 | 2179.4 | 28.2483 | 29.2644 | -1.0161 | 175.5866 | 27.6 | 28.8459 | -1.2459 |  | 2026-04-03 16:30 | 167.617 | 171.602 | 2171.5 | 28.6003 | 29.2644 | -0.6641 | 175.5866 | 29.2 | 28.8459 | 0.35405 |  | 2026-04-03 16:30 | 169.244 | 171.577 | 2200.7 | 28.5962 | 29.2644 | -0.66826 | 175.5866 | 29.5 | 28.8459 | 0.65405 |  | 2026-04-03 16:30 | 126.971 | 128.682 | 1643 | 21.447 | 21.6774 | -0.23036 | 130.0641 | 21.8 | 21.3674 | 0.43263 |  | 2026-04-03 16:30 | 124.514 | 126.213 | 1629.4 | 21.0355 | 21.6774 | -0.64186 | 130.0641 | 21.4 | 21.3674 | 0.03263 |  | 2026-04-03 16:30 | 124.625 | 126.292 | 1632.7 | 21.0487 | 21.6774 | -0.62869 | 130.0641 | 21.4 | 21.3674 | 0.03263 |  | 2026-04-03 16:30 | 125.325 | 128.921 | 1651.5 | 21.4868 | 21.6774 | -0.19052 | 130.0641 | 21.9 | 21.3674 | 0.53263 |  | 2026-04-03 16:30 | 118.354 | 119.949 | 1561.6 | 19.9915 | 20.6233 | -0.63182 | 123.7399 | 20.8 | 20.3284 | 0.47159 |  | 2026-04-03 16:30 | 218.7027 | 224.3905 | -5.6878 | 1346.3428 | 221.2 | 221.1817 | 0.018319
2026-04-03 16:20 | 533 | 48.79 | 179.712 | 182.208 | 2151.8 | 30.368 | 31.7383 | -1.3703 | 190.4296 | 30.7 | 31.2844 | -0.58442 |  | 2026-04-03 16:20 | 179.712 | 182.208 | 2151.8 | 30.368 | 31.7383 | -1.3703 | 190.4296 | 30.7 | 31.2844 | -0.58442 |  | 2026-04-03 16:20 | 180.892 | 185.049 | 2142.3 | 30.8415 | 31.7383 | -0.89677 | 190.4296 | 31.5 | 31.2844 | 0.21558 |  | 2026-04-03 16:20 | 182.41 | 184.981 | 2171.2 | 30.8302 | 31.7383 | -0.90811 | 190.4296 | 31.7 | 31.2844 | 0.41558 |  | 2026-04-03 16:20 | 136.745 | 138.588 | 1621.2 | 23.098 | 23.5098 | -0.41183 | 141.059 | 23.7 | 23.1736 | 0.52636 |  | 2026-04-03 16:20 | 134.295 | 136.33 | 1608 | 22.7217 | 23.5098 | -0.78817 | 141.059 | 23.4 | 23.1736 | 0.22636 |  | 2026-04-03 16:20 | 134.459 | 136.289 | 1611.3 | 22.7148 | 23.5098 | -0.795 | 141.059 | 23.4 | 23.1736 | 0.22636 |  | 2026-04-03 16:20 | 135.461 | 139.502 | 1629.6 | 23.2503 | 23.5098 | -0.2595 | 141.059 | 23.2 | 23.1736 | 0.026359 |  | 2026-04-03 16:20 | 127.909 | 129.646 | 1540.8 | 21.6077 | 22.3667 | -0.75903 | 134.2002 | 21.8 | 22.0468 | -0.24685 |  | 2026-04-03 16:20 | 235.8002 | 243.3591 | -7.5589 | 1460.1547 | 240.1 | 239.8791 | 0.22092
2026-04-03 16:10 | 579 | 49.08 | 193.656 | 196.426 | 2121.1 | 32.7377 | 34.4392 | -1.7016 | 206.6354 | 33.8 | 33.9468 | -0.14676 |  | 2026-04-03 16:10 | 193.656 | 196.426 | 2121.1 | 32.7377 | 34.4392 | -1.7016 | 206.6354 | 33.8 | 33.9468 | -0.14676 |  | 2026-04-03 16:10 | 194.991 | 199.859 | 2110.8 | 33.3098 | 34.4392 | -1.1294 | 206.6354 | 33.5 | 33.9468 | -0.44676 |  | 2026-04-03 16:10 | 196.968 | 199.88 | 2139.5 | 33.3133 | 34.4392 | -1.1259 | 206.6354 | 33.8 | 33.9468 | -0.14676 |  | 2026-04-03 16:10 | 147.511 | 149.56 | 1597.5 | 24.9267 | 25.5105 | -0.58388 | 153.0633 | 25.4 | 25.1457 | 0.25425 |  | 2026-04-03 16:10 | 145.125 | 147.312 | 1584.6 | 24.552 | 25.5105 | -0.95855 | 153.0633 | 24.9 | 25.1457 | -0.24575 |  | 2026-04-03 16:10 | 145.12 | 147.136 | 1587.9 | 24.5227 | 25.5105 | -0.98788 | 153.0633 | 24.9 | 25.1457 | -0.24575 |  | 2026-04-03 16:10 | 146.252 | 150.113 | 1606.4 | 25.0188 | 25.5105 | -0.49171 | 153.0633 | 25.1 | 25.1457 | -0.045746 |  | 2026-04-03 16:10 | 138.18 | 140.071 | 1519 | 23.3452 | 24.2701 | -0.92496 | 145.6208 | 24.1 | 23.9231 | 0.17694 |  | 2026-04-03 16:10 | 254.4638 | 264.0693 | -9.6054 | 1584.4156 | 259.3 | 260.2931 | -0.99308
2026-04-03 16:00 | 620 | 49.08 | 207.547 | 210.558 | 2087.3 | 35.093 | 36.8779 | -1.7849 | 221.2676 | 35.5 | 36.3506 | -0.85059 |  | 2026-04-03 16:00 | 207.547 | 210.558 | 2087.3 | 35.093 | 36.8779 | -1.7849 | 221.2676 | 35.5 | 36.3506 | -0.85059 |  | 2026-04-03 16:00 | 208.646 | 213.899 | 2077.3 | 35.6498 | 36.8779 | -1.2281 | 221.2676 | 35.7 | 36.3506 | -0.65059 |  | 2026-04-03 16:00 | 210.643 | 213.742 | 2105.7 | 35.6237 | 36.8779 | -1.2543 | 221.2676 | 36 | 36.3506 | -0.35059 |  | 2026-04-03 16:00 | 158.013 | 160.224 | 1572.1 | 26.704 | 27.317 | -0.61299 | 163.902 | 27 | 26.9264 | 0.07364 |  | 2026-04-03 16:00 | 155.327 | 157.72 | 1559.7 | 26.2867 | 27.317 | -1.0303 | 163.902 | 26.5 | 26.9264 | -0.42636 |  | 2026-04-03 16:00 | 155.48 | 158.117 | 1563 | 26.3528 | 27.317 | -0.96416 | 163.902 | 26.7 | 26.9264 | -0.22636 |  | 2026-04-03 16:00 | 156.469 | 161.097 | 1581.3 | 26.8495 | 27.317 | -0.46749 | 163.902 | 26.8 | 26.9264 | -0.12636 |  | 2026-04-03 16:00 | 147.697 | 149.749 | 1494.9 | 24.9582 | 25.9887 | -1.0306 | 155.9324 | 24.9 | 25.6171 | -0.7171 |  | 2026-04-03 16:00 | 272.6107 | 282.7685 | -10.1578 | 1696.6108 | 274.6 | 278.7249 | -4.1249
2026-04-03 15:50 | 657 | 49.36 | 220.151 | 223.413 | 2051.8 | 37.2355 | 39.0369 | -1.8014 | 234.2214 | 38 | 38.4787 | -0.47867 |  | 2026-04-03 15:50 | 220.151 | 223.413 | 2051.8 | 37.2355 | 39.0369 | -1.8014 | 234.2214 | 38 | 38.4787 | -0.47867 |  | 2026-04-03 15:50 | 220.62 | 226.544 | 2041.6 | 37.7573 | 39.0369 | -1.2796 | 234.2214 | 37.5 | 38.4787 | -0.97867 |  | 2026-04-03 15:50 | 222.327 | 225.713 | 2069.7 | 37.6188 | 39.0369 | -1.4181 | 234.2214 | 37.8 | 38.4787 | -0.67867 |  | 2026-04-03 15:50 | 166.927 | 169.332 | 1545.1 | 28.222 | 28.9162 | -0.69422 | 173.4973 | 28.8 | 28.5027 | 0.29728 |  | 2026-04-03 15:50 | 164 | 166.941 | 1533.2 | 27.8235 | 28.9162 | -1.0927 | 173.4973 | 28.3 | 28.5027 | -0.20272 |  | 2026-04-03 15:50 | 164.276 | 167.009 | 1536.3 | 27.8348 | 28.9162 | -1.0814 | 173.4973 | 28.3 | 28.5027 | -0.20272 |  | 2026-04-03 15:50 | 165.456 | 170.346 | 1554.5 | 28.391 | 28.9162 | -0.52522 | 173.4973 | 28.5 | 28.5027 | -0.0027196 |  | 2026-04-03 15:50 | 156.182 | 158.432 | 1470 | 26.4053 | 27.5102 | -1.1049 | 165.0612 | 26.9 | 27.1168 | -0.21681 |  | 2026-04-03 15:50 | 288.5238 | 299.3227 | -10.7989 | 1795.9361 | 292.1 | 295.0424 | -2.9424
2026-04-03 15:40 | 699 | 49.36 | 233.711 | 236.759 | 2013.8 | 39.4598 | 41.5324 | -2.0726 | 249.1945 | 40 | 40.9385 | -0.9385 |  | 2026-04-03 15:40 | 233.711 | 236.759 | 2013.8 | 39.4598 | 41.5324 | -2.0726 | 249.1945 | 40 | 40.9385 | -0.9385 |  | 2026-04-03 15:40 | 233.105 | 239.033 | 2004.1 | 39.8388 | 41.5324 | -1.6936 | 249.1945 | 39.4 | 40.9385 | -1.5385 |  | 2026-04-03 15:40 | 235.617 | 239.298 | 2031.9 | 39.883 | 41.5324 | -1.6494 | 249.1945 | 40.4 | 40.9385 | -0.5385 |  | 2026-04-03 15:40 | 176.499 | 179.068 | 1516.3 | 29.8447 | 30.7647 | -0.92008 | 184.5885 | 29.9 | 30.3248 | -0.42481 |  | 2026-04-03 15:40 | 173.782 | 176.696 | 1504.9 | 29.4493 | 30.7647 | -1.3154 | 184.5885 | 29.4 | 30.3248 | -0.92481 |  | 2026-04-03 15:40 | 173.752 | 176.473 | 1508 | 29.4122 | 30.7647 | -1.3526 | 184.5885 | 29.4 | 30.3248 | -0.92481 |  | 2026-04-03 15:40 | 175.165 | 180.289 | 1526 | 30.0482 | 30.7647 | -0.71658 | 184.5885 | 29.7 | 30.3248 | -0.62481 |  | 2026-04-03 15:40 | 165.56 | 167.945 | 1443.1 | 27.9908 | 29.2688 | -1.278 | 175.6131 | 28.1 | 28.8503 | -0.7503 |  | 2026-04-03 15:40 | 305.3867 | 318.4575 | -13.0708 | 1910.7448 | 306.3 | 313.9035 | -7.6035
2026-04-03 15:30 | 725 | 49.94 | 241.136 | 244.932 | 1973.8 | 40.822 | 42.9817 | -2.1597 | 257.8899 | 41.9 | 42.367 | -0.46701 |  | 2026-04-03 15:30 | 241.136 | 244.932 | 1973.8 | 40.822 | 42.9817 | -2.1597 | 257.8899 | 41.9 | 42.367 | -0.46701 |  | 2026-04-03 15:30 | 240.779 | 247.084 | 1964.7 | 41.1807 | 42.9817 | -1.801 | 257.8899 | 41.1 | 42.367 | -1.267 |  | 2026-04-03 15:30 | 243.435 | 247.318 | 1991.5 | 41.2197 | 42.9817 | -1.762 | 257.8899 | 40.9 | 42.367 | -1.467 |  | 2026-04-03 15:30 | 182.442 | 185.183 | 1486.4 | 30.8638 | 31.8383 | -0.97443 | 191.0296 | 30.6 | 31.383 | -0.78297 |  | 2026-04-03 15:30 | 179.688 | 182.961 | 1475.5 | 30.4935 | 31.8383 | -1.3448 | 191.0296 | 30.6 | 31.383 | -0.78297 |  | 2026-04-03 15:30 | 179.923 | 183.395 | 1478.6 | 30.5658 | 31.8383 | -1.2724 | 191.0296 | 30.6 | 31.383 | -0.78297 |  | 2026-04-03 15:30 | 181.369 | 186.606 | 1496.3 | 31.101 | 31.8383 | -0.73726 | 191.0296 | 30.9 | 31.383 | -0.48297 |  | 2026-04-03 15:30 | 171.622 | 174.147 | 1415 | 29.0245 | 30.2902 | -1.2657 | 181.741 | 29.2 | 29.857 | -0.65701 |  | 2026-04-03 15:30 | 316.093 | 329.5698 | -13.4768 | 1977.4188 | 317.7 | 324.857 | -7.157
2026-04-03 15:20 | 753 | 49.65 | 250.509 | 254.479 | 1931.9 | 42.4132 | 44.6913 | -2.2781 | 268.1477 | 40.9 | 44.0522 | -3.1522 |  | 2026-04-03 15:20 | 250.509 | 254.479 | 1931.9 | 42.4132 | 44.6913 | -2.2781 | 268.1477 | 40.9 | 44.0522 | -3.1522 |  | 2026-04-03 15:20 | 249.87 | 256.513 | 1923.6 | 42.7522 | 44.6913 | -1.9391 | 268.1477 | 42.6 | 44.0522 | -1.4522 |  | 2026-04-03 15:20 | 253.041 | 257.129 | 1950.6 | 42.8548 | 44.6913 | -1.8364 | 268.1477 | 43 | 44.0522 | -1.0522 |  | 2026-04-03 15:20 | 189.065 | 191.905 | 1455.8 | 31.9842 | 33.1046 | -1.1205 | 198.6279 | 32.3 | 32.6313 | -0.33125 |  | 2026-04-03 15:20 | 187.066 | 190.739 | 1444.9 | 31.7898 | 33.1046 | -1.3148 | 198.6279 | 31.9 | 32.6313 | -0.73125 |  | 2026-04-03 15:20 | 186.822 | 190.336 | 1448 | 31.7227 | 33.1046 | -1.382 | 198.6279 | 31.9 | 32.6313 | -0.73125 |  | 2026-04-03 15:20 | 188.594 | 194.089 | 1465.4 | 32.3482 | 33.1046 | -0.75648 | 198.6279 | 32.2 | 32.6313 | -0.43125 |  | 2026-04-03 15:20 | 178.654 | 181.301 | 1385.8 | 30.2168 | 31.495 | -1.2781 | 188.9698 | 30.4 | 31.0446 | -0.6446 |  | 2026-04-03 15:20 | 328.495 | 342.6787 | -14.1837 | 2056.072 | 326.1 | 337.7784 | -11.6784
2026-04-03 15:10 | 786 | 49.36 | 260.405 | 264.585 | 1891 | 44.0975 | 46.7017 | -2.6042 | 280.2101 | 45 | 46.0338 | -1.0338 |  | 2026-04-03 15:10 | 260.405 | 264.585 | 1891 | 44.0975 | 46.7017 | -2.6042 | 280.2101 | 45 | 46.0338 | -1.0338 |  | 2026-04-03 15:10 | 259.609 | 266.562 | 1881 | 44.427 | 46.7017 | -2.2747 | 280.2101 | 44.7 | 46.0338 | -1.3338 |  | 2026-04-03 15:10 | 262.283 | 266.629 | 1907.6 | 44.4382 | 46.7017 | -2.2635 | 280.2101 | 45.3 | 46.0338 | -0.73384 |  | 2026-04-03 15:10 | 196.565 | 199.538 | 1423.5 | 33.2563 | 34.5938 | -1.3375 | 207.563 | 33.9 | 34.0991 | -0.19914 |  | 2026-04-03 15:10 | 194.015 | 197.513 | 1413 | 32.9188 | 34.5938 | -1.675 | 207.563 | 33 | 34.0991 | -1.0991 |  | 2026-04-03 15:10 | 194.109 | 197.822 | 1416.1 | 32.9703 | 34.5938 | -1.6235 | 207.563 | 33.1 | 34.0991 | -0.99914 |  | 2026-04-03 15:10 | 196.025 | 201.799 | 1433.2 | 33.6332 | 34.5938 | -0.96067 | 207.563 | 33.4 | 34.0991 | -0.69914 |  | 2026-04-03 15:10 | 185.176 | 187.939 | 1355.4 | 31.3232 | 32.9118 | -1.5886 | 197.4705 | 32.1 | 32.4411 | -0.34111 |  | 2026-04-03 15:10 | 341.162 | 358.0938 | -16.9318 | 2148.5628 | 345.5 | 352.9731 | -7.4731
2026-04-03 15:00 | 832 | 49.08 | 274.734 | 279.238 | 1846 | 46.5397 | 49.4878 | -2.9482 | 296.9269 | 45.9 | 48.7801 | -2.8801 | 0.98387 | 2026-04-03 15:00 | 274.734 | 279.238 | 1846 | 46.5397 | 49.4878 | -2.9482 | 296.9269 | 45.9 | 48.7801 | -2.8801 | 0.98387 | 2026-04-03 15:00 | 273.352 | 281.284 | 1836.3 | 46.8807 | 49.4878 | -2.6072 | 296.9269 | 45.8 | 48.7801 | -2.9801 | 0.9718 | 2026-04-03 15:00 | 277.667 | 282.297 | 1862.3 | 47.0495 | 49.4878 | -2.4383 | 296.9269 | 46.4 | 48.7801 | -2.3801 | 0.9836 | 2026-04-03 15:00 | 206.986 | 210.138 | 1389.6 | 35.023 | 36.6576 | -1.6346 | 219.9459 | 35.1 | 36.1334 | -1.0334 | 0.985 | 2026-04-03 15:00 | 205.027 | 208.946 | 1380 | 34.8243 | 36.6576 | -1.8333 | 219.9459 | 34.7 | 36.1334 | -1.4334 | 0.98124 | 2026-04-03 15:00 | 204.407 | 208.072 | 1383 | 34.6787 | 36.6576 | -1.979 | 219.9459 | 34.7 | 36.1334 | -1.4334 | 0.98239 | 2026-04-03 15:00 | 206.897 | 212.815 | 1399.8 | 35.4692 | 36.6576 | -1.1885 | 219.9459 | 35.1 | 36.1334 | -1.0334 | 0.97219 | 2026-04-03 15:00 | 196.244 | 199.172 | 1323.3 | 33.1953 | 34.8752 | -1.6799 | 209.2512 | 32.7 | 34.3765 | -1.6765 | 0.9853 | 2026-04-03 15:00 | 360.2 | 379.457 | -19.257 | 2276.7423 | 356.3 | 374.0308 | -17.7308
2026-04-03 14:50 | 857 | 49.36 | 283.129 | 287.761 | 1800.1 | 47.9602 | 50.9203 | -2.9601 | 305.5217 | 97.2 | 50.1921 | 47.0079 | 0.9839 | 2026-04-03 14:50 | 283.129 | 287.761 | 1800.1 | 47.9602 | 50.9203 | -2.9601 | 305.5217 | 97.2 | 50.1921 | 47.0079 | 0.9839 | 2026-04-03 14:50 | 281.517 | 289.404 | 1790.5 | 48.234 | 50.9203 | -2.6863 | 305.5217 | 47.4 | 50.1921 | -2.7921 | 0.97275 | 2026-04-03 14:50 | 284.133 | 288.959 | 1815.9 | 48.1598 | 50.9203 | -2.7604 | 305.5217 | 48.4 | 50.1921 | -1.7921 | 0.9833 | 2026-04-03 14:50 | 213.104 | 216.393 | 1354.5 | 36.0655 | 37.7187 | -1.6532 | 226.3123 | 35.8 | 37.1793 | -1.3793 | 0.9848 | 2026-04-03 14:50 | 209.859 | 213.761 | 1345.3 | 35.6268 | 37.7187 | -2.0919 | 226.3123 | 35.3 | 37.1793 | -1.8793 | 0.98175 | 2026-04-03 14:50 | 210.595 | 214.418 | 1348.3 | 35.7363 | 37.7187 | -1.9824 | 226.3123 | 35.4 | 37.1793 | -1.7793 | 0.98217 | 2026-04-03 14:50 | 212.218 | 218.466 | 1364.7 | 36.411 | 37.7187 | -1.3077 | 226.3123 | 35.7 | 37.1793 | -1.4793 | 0.9714 | 2026-04-03 14:50 | 200.099 | 203.167 | 1290.6 | 33.8612 | 35.8847 | -2.0235 | 215.3082 | 33.7 | 35.3715 | -1.6715 | 0.9849 | 2026-04-03 14:50 | 370.015 | 390.4407 | -20.4257 | 2342.6442 | 466.1 | 384.8574 | 81.2426
2026-04-03 14:40 | 880 | 49.08 |  |  |  | 0 | 52.3429 | -52.3429 | 314.0573 | 0 | 51.5944 | -51.5944 | [5 empty] | 0 | 52.3429 | -52.3429 | 314.0573 | 0 | 51.5944 | -51.5944 |  | 2026-04-03 14:40 | 289.138 | 297.529 | 1743.1 | 49.5882 | 52.3429 | -2.7547 | 314.0573 | 48.9 | 51.5944 | -2.6944 | 0.9718 | 2026-04-03 14:40 | 292.126 | 297.087 | 1767.5 | 49.5145 | 52.3429 | -2.8284 | 314.0573 | 48.7 | 51.5944 | -2.8944 | 0.9833 | 2026-04-03 14:40 | 218.934 | 222.336 | 1318.7 | 37.056 | 38.7725 | -1.7165 | 232.635 | 37.1 | 38.2181 | -1.1181 | 0.9847 | 2026-04-03 14:40 | 215.551 | 219.483 | 1310 | 36.5805 | 38.7725 | -2.192 | 232.635 | 36.5 | 38.2181 | -1.7181 | 0.98209 | 2026-04-03 14:40 | 216.015 | 220.456 | 1312.9 | 36.7427 | 38.7725 | -2.0298 | 232.635 | 36.5 | 38.2181 | -1.7181 | 0.97986 | 2026-04-03 14:40 | 218.095 | 224.291 | 1329 | 37.3818 | 38.7725 | -1.3907 | 232.635 | 36.8 | 38.2181 | -1.4181 | 0.97238 | 2026-04-03 14:40 | 205.924 | 209.102 | 1256.9 | 34.8503 | 36.8872 | -2.0369 | 221.3234 | 34.8 | 36.3598 | -1.5598 | 0.9848 | 2026-04-03 14:40 | 281.714 | 401.3488 | -119.6348 | 2408.0928 | 279.3 | 395.6095 | -116.3095
2026-04-03 14:30 | 899 | 49.08 | 295.287 | 300.302 | 1702.9 | 50.0503 | 53.473 | -3.4227 | 320.8381 | 50.4 | 52.7083 | -2.3083 | 0.9833 | 2026-04-03 14:30 | 295.287 | 300.302 | 1702.9 | 50.0503 | 53.473 | -3.4227 | 320.8381 | 50.4 | 52.7083 | -2.3083 | 0.9833 | 2026-04-03 14:30 | 295.358 | 303.774 | 1694.2 | 50.629 | 53.473 | -2.844 | 320.8381 | 50.3 | 52.7083 | -2.4083 | 0.9723 | 2026-04-03 14:30 | 297.984 | 303.137 | 1718.8 | 50.5228 | 53.473 | -2.9502 | 320.8381 | 50.9 | 52.7083 | -1.8083 | 0.983 | 2026-04-03 14:30 | 223.632 | 227.176 | 1281.6 | 37.8627 | 39.6096 | -1.747 | 237.6578 | 37.6 | 39.0432 | -1.4432 | 0.9844 | 2026-04-03 14:30 | 220.371 | 224.387 | 1273.5 | 37.3978 | 39.6096 | -2.2118 | 237.6578 | 37.1 | 39.0432 | -1.9432 | 0.9821 | 2026-04-03 14:30 | 220.594 | 224.864 | 1276.4 | 37.4773 | 39.6096 | -2.1323 | 237.6578 | 37.2 | 39.0432 | -1.8432 | 0.98101 | 2026-04-03 14:30 | 222.395 | 228.901 | 1292.2 | 38.1502 | 39.6096 | -1.4595 | 237.6578 | 37.5 | 39.0432 | -1.5432 | 0.97158 | 2026-04-03 14:30 | 210.885 | 214.14 | 1222.1 | 35.69 | 37.6837 | -1.9937 | 226.102 | 35.4 | 37.1448 | -1.7448 | 0.9848 | 2026-04-03 14:30 | 387.8305 | 410.0143 | -22.1838 | 2460.0857 | 386.8 | 404.1511 | -17.3511
2026-04-03 14:20 | 922 | 49.36 | 302.915 | 308.192 | 1652.5 | 51.3653 | 54.7824 | -3.417 | 328.6943 | 50.1 | 53.999 | -3.899 | 0.98288 | 2026-04-03 14:20 | 302.915 | 308.192 | 1652.5 | 51.3653 | 54.7824 | -3.417 | 328.6943 | 50.1 | 53.999 | -3.899 | 0.98288 | 2026-04-03 14:20 | 303.089 | 311.971 | 1643.9 | 51.9952 | 54.7824 | -2.7872 | 328.6943 | 50.7 | 53.999 | -3.299 | 0.97153 | 2026-04-03 14:20 | 307.675 | 312.964 | 1667.9 | 52.1607 | 54.7824 | -2.6217 | 328.6943 | 51.6 | 53.999 | -2.399 | 0.9831 | 2026-04-03 14:20 | 230.184 | 233.784 | 1244 | 38.964 | 40.5795 | -1.6155 | 243.4772 | 38.5 | 39.9993 | -1.4993 | 0.9846 | 2026-04-03 14:20 | 227.764 | 232.067 | 1236.4 | 38.6778 | 40.5795 | -1.9017 | 243.4772 | 38.1 | 39.9993 | -1.8993 | 0.98146 | 2026-04-03 14:20 | 227.859 | 231.91 | 1239.2 | 38.6517 | 40.5795 | -1.9279 | 243.4772 | 38.1 | 39.9993 | -1.8993 | 0.98253 | 2026-04-03 14:20 | 230.189 | 237.09 | 1254.7 | 39.515 | 40.5795 | -1.0645 | 243.4772 | 38.5 | 39.9993 | -1.4993 | 0.97089 | 2026-04-03 14:20 | 217.594 | 220.908 | 1186.7 | 36.818 | 38.6064 | -1.7884 | 231.6384 | 36.5 | 38.0543 | -1.5543 | 0.985 | 2026-04-03 14:20 | 399.513 | 420.0541 | -20.5411 | 2520.3244 | 392.2 | 414.0473 | -21.8473
2026-04-03 14:10 | 938 | 48.5 | 307.464 | 312.749 | 1602.4 | 52.1248 | 55.9164 | -3.7916 | 335.4986 | 51 | 55.1168 | -4.1168 | 0.9831 | 2026-04-03 14:10 | 307.464 | 312.749 | 1602.4 | 52.1248 | 55.9164 | -3.7916 | 335.4986 | 51 | 55.1168 | -4.1168 | 0.9831 | 2026-04-03 14:10 | 306.151 | 314.773 | 1593.2 | 52.4622 | 55.9164 | -3.4543 | 335.4986 | 50.9 | 55.1168 | -4.2168 | 0.97261 | 2026-04-03 14:10 | 310.645 | 316.049 | 1616.3 | 52.6748 | 55.9164 | -3.2416 | 335.4986 | 51.5 | 55.1168 | -3.6168 | 0.9829 | 2026-04-03 14:10 | 232.156 | 235.859 | 1205.5 | 39.3098 | 41.4196 | -2.1098 | 248.5175 | 38.6 | 40.8273 | -2.2273 | 0.9843 | 2026-04-03 14:10 | 229.43 | 233.791 | 1198.3 | 38.9652 | 41.4196 | -2.4544 | 248.5175 | 38 | 40.8273 | -2.8273 | 0.98135 | 2026-04-03 14:10 | 229.436 | 234.035 | 1201.1 | 39.0058 | 41.4196 | -2.4138 | 248.5175 | 38.7 | 40.8273 | -2.1273 | 0.98035 | 2026-04-03 14:10 | 231.499 | 238.355 | 1216.2 | 39.7258 | 41.4196 | -1.6938 | 248.5175 | 39.1 | 40.8273 | -1.7273 | 0.97124 | 2026-04-03 14:10 | 219.282 | 222.689 | 1150.2 | 37.1148 | 39.4056 | -2.2908 | 236.4336 | 36.9 | 38.8421 | -1.9421 | 0.9847 | 2026-04-03 14:10 | 403.5082 | 428.7497 | -25.2415 | 2572.4982 | 395.7 | 422.6186 | -26.9186
2026-04-03 14:00 | 956 | 48.5 | 309.129 | 314.547 | 1551.4 | 52.4245 | 56.9895 | -4.565 | 341.9368 | 53.4 | 56.1745 | -2.7745 | 0.98278 | 2026-04-03 14:00 | 309.129 | 314.547 | 1551.4 | 52.4245 | 56.9895 | -4.565 | 341.9368 | 53.4 | 56.1745 | -2.7745 | 0.98278 | 2026-04-03 14:00 | 308.106 | 317.346 | 1542.3 | 52.891 | 56.9895 | -4.0985 | 341.9368 | 52.4 | 56.1745 | -3.7745 | 0.97088 | 2026-04-03 14:00 | 313.106 | 318.683 | 1564.8 | 53.1138 | 56.9895 | -3.8756 | 341.9368 | 53.1 | 56.1745 | -3.0745 | 0.9825 | 2026-04-03 14:00 | 233.811 | 237.613 | 1166.9 | 39.6022 | 42.2144 | -2.6122 | 253.2865 | 39.8 | 41.6108 | -1.8108 | 0.984 | 2026-04-03 14:00 | 230.932 | 235.482 | 1160.3 | 39.247 | 42.2144 | -2.9674 | 253.2865 | 39.3 | 41.6108 | -2.3108 | 0.98068 | 2026-04-03 14:00 | 231.039 | 235.842 | 1162.4 | 39.307 | 42.2144 | -2.9074 | 253.2865 | 38.8 | 41.6108 | -2.8108 | 0.97963 | 2026-04-03 14:00 | 233.407 | 240.418 | 1177.1 | 40.0697 | 42.2144 | -2.1447 | 253.2865 | 39.2 | 41.6108 | -2.4108 | 0.97084 | 2026-04-03 14:00 | 221.008 | 224.488 | 1113.3 | 37.4147 | 40.1618 | -2.7471 | 240.9707 | 37 | 39.5875 | -2.5875 | 0.9845 | 2026-04-03 14:00 | 406.4943 | 436.9773 | -30.483 | 2621.8638 | 406.4 | 430.7285 | -24.3285
2026-04-03 13:50 | 975 | 48.79 | 317.956 | 323.488 | 1498 | 53.9147 | 58.0578 | -4.1432 | 348.3469 | 52.9 | 57.2276 | -4.3276 | 0.9829 | 2026-04-03 13:50 | 317.956 | 323.488 | 1498 | 53.9147 | 58.0578 | -4.1432 | 348.3469 | 52.9 | 57.2276 | -4.3276 | 0.9829 | 2026-04-03 13:50 | 317.537 | 327.31 | 1489.9 | 54.5517 | 58.0578 | -3.5062 | 348.3469 | 53 | 57.2276 | -4.2276 | 0.97014 | 2026-04-03 13:50 | 321.335 | 327.025 | 1511.7 | 54.5042 | 58.0578 | -3.5537 | 348.3469 | 53.7 | 57.2276 | -3.5276 | 0.9826 | 2026-04-03 13:50 | 240.996 | 244.915 | 1127.1 | 40.8192 | 43.0058 | -2.1866 | 258.0347 | 40.3 | 42.3908 | -2.0908 | 0.984 | 2026-04-03 13:50 | 238.124 | 242.839 | 1121 | 40.4732 | 43.0058 | -2.5326 | 258.0347 | 39.8 | 42.3908 | -2.5908 | 0.98058 | 2026-04-03 13:50 | 238.106 | 243.159 | 1123.6 | 40.5265 | 43.0058 | -2.4793 | 258.0347 | 39.8 | 42.3908 | -2.5908 | 0.97922 | 2026-04-03 13:50 | 240.348 | 247.538 | 1137.9 | 41.2563 | 43.0058 | -1.7495 | 258.0347 | 40.1 | 42.3908 | -2.2908 | 0.97095 | 2026-04-03 13:50 | 227.236 | 230.861 | 1076.3 | 38.4768 | 40.9147 | -2.4378 | 245.4881 | 37.9 | 40.3296 | -2.4296 | 0.9843 | 2026-04-03 13:50 | 418.4372 | 445.1691 | -26.7319 | 2671.0147 | 410.4 | 438.8032 | -28.4032
2026-04-03 13:40 | 978 | 48.5 | 320.015 | 324.476 | 1445.1 | 54.0793 | 58.3009 | -4.2216 | 349.8056 | 52.9 | 57.4672 | -4.5672 | 0.98625 | 2026-04-03 13:40 | 320.015 | 324.476 | 1445.1 | 54.0793 | 58.3009 | -4.2216 | 349.8056 | 52.9 | 57.4672 | -4.5672 | 0.98625 | 2026-04-03 13:40 | 319.862 | 329.671 | 1436.9 | 54.9452 | 58.3009 | -3.3558 | 349.8056 | 52.8 | 57.4672 | -4.6672 | 0.97025 | 2026-04-03 13:40 | 322.723 | 328.438 | 1458 | 54.7397 | 58.3009 | -3.5613 | 349.8056 | 53.4 | 57.4672 | -4.0672 | 0.9826 | 2026-04-03 13:40 | 243.754 | 247.667 | 1086.8 | 41.2778 | 43.1859 | -1.908 | 259.1153 | 40.7 | 42.5683 | -1.8683 | 0.9842 | 2026-04-03 13:40 | 239.302 | 244.02 | 1081.2 | 40.67 | 43.1859 | -2.5159 | 259.1153 | 40.1 | 42.5683 | -2.4683 | 0.98067 | 2026-04-03 13:40 | 241.156 | 246.349 | 1083.8 | 41.0582 | 43.1859 | -2.1277 | 259.1153 | 40.2 | 42.5683 | -2.3683 | 0.97892 | 2026-04-03 13:40 | 243.115 | 250.144 | 1097.8 | 41.6907 | 43.1859 | -1.4952 | 259.1153 | 40.7 | 42.5683 | -1.8683 | 0.9719 | 2026-04-03 13:40 | 228.953 | 232.605 | 1038.4 | 38.7675 | 41.086 | -2.3185 | 246.5161 | 38.4 | 40.4985 | -2.0985 | 0.9843 | 2026-04-03 13:40 | 421.3077 | 447.0333 | -25.7256 | 2682.1996 | 412.1 | 440.6407 | -28.5407
2026-04-03 13:30 | 999 | 48.5 | 323.136 | 328.825 | 1392.2 | 54.8042 | 59.5528 | -4.7486 | 357.3168 | 53.9 | 58.7012 | -4.8012 | 0.9827 | 2026-04-03 13:30 | 323.136 | 328.825 | 1392.2 | 54.8042 | 59.5528 | -4.7486 | 357.3168 | 53.9 | 58.7012 | -4.8012 | 0.9827 | 2026-04-03 13:30 | 322.336 | 332.23 | 1384.1 | 55.3717 | 59.5528 | -4.1811 | 357.3168 | 53.8 | 58.7012 | -4.9012 | 0.97022 | 2026-04-03 13:30 | 327.383 | 333.214 | 1404.6 | 55.5357 | 59.5528 | -4.0171 | 357.3168 | 54.3 | 58.7012 | -4.4012 | 0.9825 | 2026-04-03 13:30 | 245.461 | 249.452 | 1046.1 | 41.5753 | 44.1132 | -2.5378 | 264.6791 | 40.9 | 43.4824 | -2.5824 | 0.984 | 2026-04-03 13:30 | 242.213 | 247.018 | 1041.1 | 41.1697 | 44.1132 | -2.9435 | 264.6791 | 40.4 | 43.4824 | -3.0824 | 0.98055 | 2026-04-03 13:30 | 242.731 | 248.028 | 1043.6 | 41.338 | 44.1132 | -2.7752 | 264.6791 | 40.5 | 43.4824 | -2.9824 | 0.97864 | 2026-04-03 13:30 | 245.816 | 253.409 | 1057.1 | 42.2348 | 44.1132 | -1.8783 | 264.6791 | 41 | 43.4824 | -2.4824 | 0.97004 | 2026-04-03 13:30 | 232.207 | 235.953 | 1000 | 39.3255 | 41.9682 | -2.6427 | 251.8094 | 38.7 | 41.3681 | -2.6681 | 0.98412 | 2026-04-03 13:30 | 426.159 | 456.6321 | -30.4731 | 2739.7928 | 417.4 | 450.1023 | -32.7023
2026-04-03 13:20 | 1000 | 49.08 | 322.547 | 328.201 | 1338.3 | 54.7002 | 59.4805 | -4.7804 | 356.8833 | 52.9 | 58.63 | -5.73 | 0.98277 | 2026-04-03 13:20 | 322.547 | 328.201 | 1338.3 | 54.7002 | 59.4805 | -4.7804 | 356.8833 | 52.9 | 58.63 | -5.73 | 0.98277 | 2026-04-03 13:20 | 320.897 | 331.136 | 1330.3 | 55.1893 | 59.4805 | -4.2912 | 356.8833 | 54.1 | 58.63 | -4.53 | 0.96908 | 2026-04-03 13:20 | 317.763 | 322.996 | 1350.3 | 53.8327 | 59.4805 | -5.6479 | 356.8833 | 55 | 58.63 | -3.63 | 0.9838 | 2026-04-03 13:20 | 243.306 | 247.275 | 1005.2 | 41.2125 | 44.0597 | -2.8472 | 264.358 | 40.5 | 43.4296 | -2.9296 | 0.98395 | 2026-04-03 13:20 | 241.419 | 246.46 | 1000.7 | 41.0767 | 44.0597 | -2.983 | 264.358 | 40.2 | 43.4296 | -3.2296 | 0.97955 | 2026-04-03 13:20 | 241.186 | 246.341 | 1003.1 | 41.0568 | 44.0597 | -3.0028 | 264.358 | 40.2 | 43.4296 | -3.2296 | 0.97907 | 2026-04-03 13:20 | 244.121 | 251.553 | 1016.1 | 41.9255 | 44.0597 | -2.1342 | 264.358 | 40.6 | 43.4296 | -2.8296 | 0.97046 | 2026-04-03 13:20 | 230.666 | 234.45 | 961.3 | 39.075 | 41.9173 | -2.8423 | 251.5039 | 38.4 | 41.3179 | -2.9179 | 0.98386 | 2026-04-03 13:20 | 422.7688 | 456.0782 | -33.3093 | 2736.4691 | 414.8 | 449.5563 | -34.7563
2026-04-03 13:10 | 1007 | 49.36 | 325.56 | 331.359 | 1285.4 | 55.2265 | 59.8328 | -4.6063 | 358.9969 | 55.1 | 58.9772 | -3.8772 | 0.9825 | 2026-04-03 13:10 | 325.56 | 331.359 | 1285.4 | 55.2265 | 59.8328 | -4.6063 | 358.9969 | 55.1 | 58.9772 | -3.8772 | 0.9825 | 2026-04-03 13:10 | 324.299 | 333.807 | 1276.2 | 55.6345 | 59.8328 | -4.1983 | 358.9969 | 53.2 | 58.9772 | -5.7772 | 0.97152 | 2026-04-03 13:10 | 329.313 | 335.272 | 1295.3 | 55.8787 | 59.8328 | -3.9541 | 358.9969 | 54.7 | 58.9772 | -4.2772 | 0.98223 | 2026-04-03 13:10 | 246.427 | 250.536 | 964.7 | 41.756 | 44.3206 | -2.5646 | 265.9236 | 41 | 43.6868 | -2.6868 | 0.9836 | 2026-04-03 13:10 | 243.452 | 248.653 | 960.5 | 41.4422 | 44.3206 | -2.8784 | 265.9236 | 40.4 | 43.6868 | -3.2868 | 0.97908 | 2026-04-03 13:10 | 243.927 | 249.058 | 962.9 | 41.5097 | 44.3206 | -2.8109 | 265.9236 | 40.5 | 43.6868 | -3.1868 | 0.9794 | 2026-04-03 13:10 | 246.333 | 253.595 | 975.5 | 42.2658 | 44.3206 | -2.0548 | 265.9236 | 41 | 43.6868 | -2.6868 | 0.97136 | 2026-04-03 13:10 | 232.676 | 236.507 | 922.9 | 39.4178 | 42.1656 | -2.7477 | 252.9934 | 38.7 | 41.5626 | -2.8626 | 0.9838 | 2026-04-03 13:10 | 428.3577 | 458.7792 | -30.4216 | 2752.6753 | 419.7 | 452.2187 | -32.5187
2026-04-03 13:00 | 994 | 49.65 | 323.754 | 329.487 | 1230.3 | 54.9145 | 58.9949 | -4.0804 | 353.9692 | 53.4 | 58.1512 | -4.7512 | 0.9826 | 2026-04-03 13:00 | 323.754 | 329.487 | 1230.3 | 54.9145 | 58.9949 | -4.0804 | 353.9692 | 53.4 | 58.1512 | -4.7512 | 0.9826 | 2026-04-03 13:00 | 321.763 | 331.746 | 1223 | 55.291 | 58.9949 | -3.7039 | 353.9692 | 54 | 58.1512 | -4.1512 | 0.96991 | 2026-04-03 13:00 | 326.511 | 332.428 | 1240.6 | 55.4047 | 58.9949 | -3.5902 | 353.9692 | 53.9 | 58.1512 | -4.2512 | 0.9822 | 2026-04-03 13:00 | 244.862 | 248.869 | 923.7 | 41.4782 | 43.6999 | -2.2217 | 262.1994 | 41.2 | 43.075 | -1.875 | 0.9839 | 2026-04-03 13:00 | 242.191 | 247.094 | 920.1 | 41.1823 | 43.6999 | -2.5176 | 262.1994 | 40.7 | 43.075 | -2.375 | 0.98016 | 2026-04-03 13:00 | 242.732 | 247.854 | 922.4 | 41.309 | 43.6999 | -2.3909 | 262.1994 | 40.9 | 43.075 | -2.175 | 0.97933 | 2026-04-03 13:00 | 245.648 | 252.722 | 934.5 | 42.1203 | 43.6999 | -1.5796 | 262.1994 | 41.3 | 43.075 | -1.775 | 0.97201 | 2026-04-03 13:00 | 231.735 | 235.527 | 884.2 | 39.2545 | 41.575 | -2.3205 | 249.4502 | 38.9 | 40.9805 | -2.0805 | 0.9839 | 2026-04-03 13:00 | 425.869 | 452.3541 | -26.4851 | 2714.1243 | 417.7 | 445.8854 | -28.1854
2026-04-03 12:50 | 1001 | 49.36 | 324.902 | 330.326 | 1176.9 | 55.0543 | 59.4763 | -4.422 | 356.8579 | 56.2 | 58.6258 | -2.4258 | 0.98358 | 2026-04-03 12:50 | 324.902 | 330.326 | 1176.9 | 55.0543 | 59.4763 | -4.422 | 356.8579 | 56.2 | 58.6258 | -2.4258 | 0.98358 | 2026-04-03 12:50 | 324.307 | 333.866 | 1169 | 55.6443 | 59.4763 | -3.832 | 356.8579 | 54.5 | 58.6258 | -4.1258 | 0.97137 | 2026-04-03 12:50 | 328.859 | 334.785 | 1186.7 | 55.7975 | 59.4763 | -3.6788 | 356.8579 | 54.8 | 58.6258 | -3.8258 | 0.9823 | 2026-04-03 12:50 | 246.852 | 250.866 | 882.5 | 41.811 | 44.0565 | -2.2455 | 264.3392 | 41.4 | 43.4265 | -2.0265 | 0.984 | 2026-04-03 12:50 | 244.091 | 249.083 | 879.4 | 41.5138 | 44.0565 | -2.5427 | 264.3392 | 40.9 | 43.4265 | -2.5265 | 0.97996 | 2026-04-03 12:50 | 244.686 | 249.703 | 881.5 | 41.6172 | 44.0565 | -2.4394 | 264.3392 | 41 | 43.4265 | -2.4265 | 0.97991 | 2026-04-03 12:50 | 247.194 | 254.386 | 893.2 | 42.3977 | 44.0565 | -1.6589 | 264.3392 | 41.4 | 43.4265 | -2.0265 | 0.97173 | 2026-04-03 12:50 | 233.435 | 237.182 | 845.3 | 39.5303 | 41.9143 | -2.384 | 251.486 | 39.1 | 41.315 | -2.215 | 0.9842 | 2026-04-03 12:50 | 428.4205 | 456.0457 | -27.6252 | 2736.2741 | 425.5 | 449.5242 | -24.0242
2026-04-03 12:40 | 1014 | 49.08 | 330.641 | 336.428 | 1120.7 | 56.0713 | 60.3133 | -4.2419 | 361.8797 | 54.6 | 59.4508 | -4.8508 | 0.9828 | 2026-04-03 12:40 | 330.641 | 336.428 | 1120.7 | 56.0713 | 60.3133 | -4.2419 | 361.8797 | 54.6 | 59.4508 | -4.8508 | 0.9828 | 2026-04-03 12:40 | 329.642 | 339.418 | 1114.5 | 56.5697 | 60.3133 | -3.7436 | 361.8797 | 55.3 | 59.4508 | -4.1508 | 0.9712 | 2026-04-03 12:40 | 333.428 | 339.436 | 1131.9 | 56.5727 | 60.3133 | -3.7406 | 361.8797 | 55.8 | 59.4508 | -3.6508 | 0.9823 | 2026-04-03 12:40 | 249.623 | 253.699 | 841.1 | 42.2832 | 44.6765 | -2.3933 | 268.059 | 41.2 | 44.0376 | -2.8376 | 0.98393 | 2026-04-03 12:40 | 246.497 | 251.774 | 838.5 | 41.9623 | 44.6765 | -2.7142 | 268.059 | 40.7 | 44.0376 | -3.3376 | 0.97904 | 2026-04-03 12:40 | 247.068 | 252.427 | 840.5 | 42.0712 | 44.6765 | -2.6053 | 268.059 | 40.9 | 44.0376 | -3.1376 | 0.97877 | 2026-04-03 12:40 | 249.498 | 256.866 | 851.8 | 42.811 | 44.6765 | -1.8655 | 268.059 | 41.2 | 44.0376 | -2.8376 | 0.97132 | 2026-04-03 12:40 | 235.785 | 239.57 | 806.2 | 39.9283 | 42.5042 | -2.5758 | 255.0249 | 38.9 | 41.8963 | -2.9963 | 0.9842 | 2026-04-03 12:40 | 434.341 | 462.4633 | -28.1223 | 2774.7796 | 423.2 | 455.85 | -32.65
2026-04-03 12:30 | 1010 | 48.5 | 328.137 | 333.948 | 1066.1 | 55.658 | 60.2085 | -4.5505 | 361.2512 | 53 | 59.3476 | -6.3476 | 0.9826 | 2026-04-03 12:30 | 328.137 | 333.948 | 1066.1 | 55.658 | 60.2085 | -4.5505 | 361.2512 | 53 | 59.3476 | -6.3476 | 0.9826 | 2026-04-03 12:30 | 327.166 | 336.532 | 1059.2 | 56.0887 | 60.2085 | -4.1199 | 361.2512 | 54.8 | 59.3476 | -4.5476 | 0.97217 | 2026-04-03 12:30 | 330.71 | 336.669 | 1076.1 | 56.1115 | 60.2085 | -4.097 | 361.2512 | 54.9 | 59.3476 | -4.4476 | 0.9823 | 2026-04-03 12:30 | 247.548 | 251.624 | 799.9 | 41.9373 | 44.5989 | -2.6616 | 267.5935 | 41 | 43.9611 | -2.9611 | 0.9838 | 2026-04-03 12:30 | 244.794 | 249.857 | 797.8 | 41.6428 | 44.5989 | -2.9561 | 267.5935 | 40.6 | 43.9611 | -3.3611 | 0.97974 | 2026-04-03 12:30 | 245.574 | 250.577 | 799.6 | 41.7628 | 44.5989 | -2.8361 | 267.5935 | 40.6 | 43.9611 | -3.3611 | 0.98003 | 2026-04-03 12:30 | 248.09 | 255.655 | 810.6 | 42.6092 | 44.5989 | -1.9897 | 267.5935 | 41 | 43.9611 | -2.9611 | 0.97041 | 2026-04-03 12:30 | 234.489 | 238.232 | 767.3 | 39.7053 | 42.4303 | -2.725 | 254.5821 | 38.9 | 41.8236 | -2.9236 | 0.98429 | 2026-04-03 12:30 | 431.1737 | 461.6601 | -30.4865 | 2769.9607 | 417.8 | 455.0584 | -37.2584
2026-04-03 12:20 | 1005 | 48.79 | 326.64 | 332.603 | 1013.1 | 55.4338 | 59.8442 | -4.4104 | 359.0653 | 54.8 | 58.9884 | -4.1884 | 0.98207 | 2026-04-03 12:20 | 326.64 | 332.603 | 1013.1 | 55.4338 | 59.8442 | -4.4104 | 359.0653 | 54.8 | 58.9884 | -4.1884 | 0.98207 | 2026-04-03 12:20 | 325.308 | 335.386 | 1004.4 | 55.8977 | 59.8442 | -3.9465 | 359.0653 | 53.1 | 58.9884 | -5.8884 | 0.96995 | 2026-04-03 12:20 | 329.605 | 335.51 | 1021.2 | 55.9183 | 59.8442 | -3.9259 | 359.0653 | 54.6 | 58.9884 | -4.3884 | 0.9824 | 2026-04-03 12:20 | 246.724 | 250.787 | 758.9 | 41.7978 | 44.329 | -2.5312 | 265.9743 | 40.8 | 43.6951 | -2.8951 | 0.9838 | 2026-04-03 12:20 | 244.649 | 249.465 | 757.2 | 41.5775 | 44.329 | -2.7515 | 265.9743 | 40.5 | 43.6951 | -3.1951 | 0.98069 | 2026-04-03 12:20 | 244.595 | 249.488 | 759 | 41.5813 | 44.329 | -2.7477 | 265.9743 | 40.4 | 43.6951 | -3.2951 | 0.98039 | 2026-04-03 12:20 | 247.189 | 254.504 | 769.6 | 42.4173 | 44.329 | -1.9117 | 265.9743 | 40.9 | 43.6951 | -2.7951 | 0.97126 | 2026-04-03 12:20 | 233.944 | 237.7 | 728.4 | 39.6167 | 42.1736 | -2.5569 | 253.0416 | 38.8 | 41.5705 | -2.7705 | 0.9842 | 2026-04-03 12:20 | 429.6743 | 458.8666 | -29.1923 | 2753.1997 | 418.7 | 452.3048 | -33.6048
2026-04-03 12:10 | 993 | 48.79 | 323.761 | 329.427 | 958.3 | 54.9045 | 59.1297 | -4.2252 | 354.7779 | 54.8 | 58.2841 | -3.4841 | 0.9828 | 2026-04-03 12:10 | 323.761 | 329.427 | 958.3 | 54.9045 | 59.1297 | -4.2252 | 354.7779 | 54.8 | 58.2841 | -3.4841 | 0.9828 | 2026-04-03 12:10 | 320.969 | 330.48 | 951.3 | 55.08 | 59.1297 | -4.0497 | 354.7779 | 53.5 | 58.2841 | -4.7841 | 0.97122 | 2026-04-03 12:10 | 327.37 | 333.235 | 966.6 | 55.5392 | 59.1297 | -3.5905 | 354.7779 | 54.5 | 58.2841 | -3.7841 | 0.9824 | 2026-04-03 12:10 | 243.664 | 247.651 | 718.1 | 41.2752 | 43.7997 | -2.5246 | 262.7985 | 40.6 | 43.1734 | -2.5734 | 0.9839 | 2026-04-03 12:10 | 242.818 | 247.657 | 716.7 | 41.2762 | 43.7997 | -2.5236 | 262.7985 | 40.4 | 43.1734 | -2.7734 | 0.98046 | 2026-04-03 12:10 | 242.276 | 247.682 | 718.6 | 41.2803 | 43.7997 | -2.5194 | 262.7985 | 40.4 | 43.1734 | -2.7734 | 0.97817 | 2026-04-03 12:10 | 245.287 | 252.669 | 728.7 | 42.1115 | 43.7997 | -1.6882 | 262.7985 | 40.8 | 43.1734 | -2.3734 | 0.97078 | 2026-04-03 12:10 | 232.98 | 236.744 | 689.6 | 39.4573 | 41.67 | -2.2127 | 250.0202 | 39.1 | 41.0741 | -1.9741 | 0.9841 | 2026-04-03 12:10 | 425.8287 | 453.3876 | -27.559 | 2720.3257 | 418.9 | 446.9042 | -28.0042
2026-04-03 12:00 | 990 | 48.5 | 323.507 | 329.135 | 903.5 | 54.8558 | 59.0163 | -4.1605 | 354.0977 | 52.7 | 58.1724 | -5.4724 | 0.9829 | 2026-04-03 12:00 | 323.507 | 329.135 | 903.5 | 54.8558 | 59.0163 | -4.1605 | 354.0977 | 52.7 | 58.1724 | -5.4724 | 0.9829 | 2026-04-03 12:00 | 319.963 | 329.354 | 897.8 | 54.8923 | 59.0163 | -4.124 | 354.0977 | 53 | 58.1724 | -5.1724 | 0.97149 | 2026-04-03 12:00 | 326.509 | 332.325 | 912.1 | 55.3875 | 59.0163 | -3.6288 | 354.0977 | 53.6 | 58.1724 | -4.5724 | 0.9825 | 2026-04-03 12:00 | 242.246 | 246.185 | 677.5 | 41.0308 | 43.7158 | -2.6849 | 262.2946 | 40.2 | 43.0906 | -2.8906 | 0.984 | 2026-04-03 12:00 | 241.586 | 246.457 | 676.3 | 41.0762 | 43.7158 | -2.6396 | 262.2946 | 39.8 | 43.0906 | -3.2906 | 0.98024 | 2026-04-03 12:00 | 240.795 | 245.687 | 678.2 | 40.9478 | 43.7158 | -2.7679 | 262.2946 | 40.5 | 43.0906 | -2.5906 | 0.98009 | 2026-04-03 12:00 | 243.803 | 251.107 | 687.9 | 41.8512 | 43.7158 | -1.8646 | 262.2946 | 40.8 | 43.0906 | -2.2906 | 0.97091 | 2026-04-03 12:00 | 230.712 | 234.392 | 650.5 | 39.0653 | 41.5901 | -2.5248 | 249.5408 | 38 | 40.9954 | -2.9954 | 0.9843 | 2026-04-03 12:00 | 423.9628 | 452.5183 | -28.5555 | 2715.11 | 411.3 | 446.0473 | -34.7473
2026-04-03 11:50 | 967 | 48.79 | 317.249 | 322.755 | 850.8 | 53.7925 | 57.5814 | -3.7889 | 345.4887 | 53.6 | 56.758 | -3.158 | 0.98294 | 2026-04-03 11:50 | 317.249 | 322.755 | 850.8 | 53.7925 | 57.5814 | -3.7889 | 345.4887 | 53.6 | 56.758 | -3.158 | 0.98294 | 2026-04-03 11:50 | 315.707 | 324.839 | 844.8 | 54.1398 | 57.5814 | -3.4416 | 345.4887 | 51.9 | 56.758 | -4.858 | 0.97189 | 2026-04-03 11:50 | 319.563 | 325.255 | 858.5 | 54.2092 | 57.5814 | -3.3723 | 345.4887 | 53.5 | 56.758 | -3.258 | 0.9825 | 2026-04-03 11:50 | 239.445 | 243.314 | 637.3 | 40.5523 | 42.6529 | -2.1006 | 255.9175 | 40.4 | 42.043 | -1.643 | 0.9841 | 2026-04-03 11:50 | 237.27 | 242.068 | 636.5 | 40.3447 | 42.6529 | -2.3083 | 255.9175 | 39.7 | 42.043 | -2.343 | 0.98018 | 2026-04-03 11:50 | 236.94 | 241.787 | 637.7 | 40.2978 | 42.6529 | -2.3551 | 255.9175 | 39 | 42.043 | -3.043 | 0.97995 | 2026-04-03 11:50 | 239.776 | 247.129 | 647.1 | 41.1882 | 42.6529 | -1.4648 | 255.9175 | 39.7 | 42.043 | -2.343 | 0.97025 | 2026-04-03 11:50 | 226.757 | 230.364 | 612.5 | 38.394 | 40.579 | -2.185 | 243.4738 | 37.5 | 39.9987 | -2.4987 | 0.98434 | 2026-04-03 11:50 | 416.711 | 441.5164 | -24.8054 | 2649.0987 | 408.9 | 435.2028 | -26.3028
2026-04-03 11:40 | 958 | 49.08 | 313.726 | 319.184 | 797.2 | 53.1973 | 56.9824 | -3.785 | 341.8942 | 51 | 56.1675 | -5.1675 | 0.9829 | 2026-04-03 11:40 | 313.726 | 319.184 | 797.2 | 53.1973 | 56.9824 | -3.785 | 341.8942 | 51 | 56.1675 | -5.1675 | 0.9829 | 2026-04-03 11:40 | 312.053 | 321.045 | 792.9 | 53.5075 | 56.9824 | -3.4749 | 341.8942 | 52.1 | 56.1675 | -4.0675 | 0.97199 | 2026-04-03 11:40 | 316.938 | 322.485 | 805 | 53.7475 | 56.9824 | -3.2349 | 341.8942 | 53.5 | 56.1675 | -2.6675 | 0.9828 | 2026-04-03 11:40 | 236.901 | 240.683 | 596.9 | 40.1138 | 42.2092 | -2.0953 | 253.255 | 38.5 | 41.6056 | -3.1056 | 0.98429 | 2026-04-03 11:40 | 235.454 | 240.069 | 596.8 | 40.0115 | 42.2092 | -2.1977 | 253.255 | 38.7 | 41.6056 | -2.9056 | 0.98078 | 2026-04-03 11:40 | 235.616 | 240.218 | 598.7 | 40.0363 | 42.2092 | -2.1728 | 253.255 | 38.8 | 41.6056 | -2.8056 | 0.98084 | 2026-04-03 11:40 | 239.028 | 246.24 | 607.4 | 41.04 | 42.2092 | -1.1692 | 253.255 | 39.2 | 41.6056 | -2.4056 | 0.97071 | 2026-04-03 11:40 | 225.915 | 229.495 | 575 | 38.2492 | 40.1568 | -1.9076 | 240.9407 | 37.1 | 39.5825 | -2.4825 | 0.9844 | 2026-04-03 11:40 | 413.1005 | 436.9229 | -23.8224 | 2621.5374 | 399.9 | 430.6749 | -30.7749
2026-04-03 11:30 | 937 | 48.79 | 308.114 | 313.411 | 746.2 | 52.2352 | 55.7951 | -3.5599 | 334.7703 | 52.8 | 54.9972 | -2.1972 | 0.9831 | 2026-04-03 11:30 | 308.114 | 313.411 | 746.2 | 52.2352 | 55.7951 | -3.5599 | 334.7703 | 52.8 | 54.9972 | -2.1972 | 0.9831 | 2026-04-03 11:30 | 305.532 | 314.011 | 740.8 | 52.3352 | 55.7951 | -3.4599 | 334.7703 | 50.4 | 54.9972 | -4.5972 | 0.973 | 2026-04-03 11:30 | 310.687 | 316.124 | 751.5 | 52.6873 | 55.7951 | -3.1077 | 334.7703 | 50.3 | 54.9972 | -4.6972 | 0.9828 | 2026-04-03 11:30 | 231.445 | 235.124 | 558.4 | 39.1873 | 41.3297 | -2.1423 | 247.978 | 38.5 | 40.7387 | -2.2387 | 0.98435 | 2026-04-03 11:30 | 230.467 | 234.96 | 558.1 | 39.16 | 41.3297 | -2.1697 | 247.978 | 38.3 | 40.7387 | -2.4387 | 0.98088 | 2026-04-03 11:30 | 230.553 | 234.924 | 559.9 | 39.154 | 41.3297 | -2.1757 | 247.978 | 38.4 | 40.7387 | -2.3387 | 0.98139 | 2026-04-03 11:30 | 233.842 | 240.728 | 568.2 | 40.1213 | 41.3297 | -1.2083 | 247.978 | 38.9 | 40.7387 | -1.8387 | 0.9714 | 2026-04-03 11:30 | 221.253 | 224.668 | 537.9 | 37.4447 | 39.3201 | -1.8754 | 235.9204 | 36.8 | 38.7578 | -1.9578 | 0.9848 | 2026-04-03 11:30 | 404.5602 | 427.8189 | -23.2588 | 2566.9136 | 397.2 | 421.7011 | -24.5011
2026-04-03 11:20 | 921 | 49.36 | 304.224 | 309.359 | 693.4 | 51.5598 | 54.723 | -3.1631 | 328.3378 | 47.8 | 53.9404 | -6.1404 | 0.9834 | 2026-04-03 11:20 | 304.224 | 309.359 | 693.4 | 51.5598 | 54.723 | -3.1631 | 328.3378 | 47.8 | 53.9404 | -6.1404 | 0.9834 | 2026-04-03 11:20 | 301.93 | 310.486 | 690.4 | 51.7477 | 54.723 | -2.9753 | 328.3378 | 50.2 | 53.9404 | -3.7404 | 0.97244 | 2026-04-03 11:20 | 306.55 | 311.851 | 701.2 | 51.9752 | 54.723 | -2.7478 | 328.3378 | 50.4 | 53.9404 | -3.5404 | 0.983 | 2026-04-03 11:20 | 228.606 | 232.229 | 519.9 | 38.7048 | 40.5355 | -1.8307 | 243.2132 | 37.7 | 39.9559 | -2.2559 | 0.9844 | 2026-04-03 11:20 | 227.556 | 231.577 | 519.8 | 38.5962 | 40.5355 | -1.9394 | 243.2132 | 37.5 | 39.9559 | -2.4559 | 0.98264 | 2026-04-03 11:20 | 227.805 | 232.233 | 521.5 | 38.7055 | 40.5355 | -1.83 | 243.2132 | 37.6 | 39.9559 | -2.3559 | 0.98093 | 2026-04-03 11:20 | 231.077 | 237.602 | 529.3 | 39.6003 | 40.5355 | -0.93519 | 243.2132 | 38.1 | 39.9559 | -1.8559 | 0.97254 | 2026-04-03 11:20 | 218.407 | 221.778 | 501.1 | 36.963 | 38.5645 | -1.6015 | 231.3872 | 36 | 38.0131 | -2.0131 | 0.9848 | 2026-04-03 11:20 | 399.4123 | 419.5985 | -20.1861 | 2517.5908 | 383.1 | 413.5982 | -30.4982
2026-04-03 11:10 | 899 | 49.08 | 297.909 | 302.502 | 645.6 | 50.417 | 53.473 | -3.056 | 320.8381 | 49.8 | 52.7083 | -2.9083 | 0.98482 | 2026-04-03 11:10 | 297.909 | 302.502 | 645.6 | 50.417 | 53.473 | -3.056 | 320.8381 | 49.8 | 52.7083 | -2.9083 | 0.98482 | 2026-04-03 11:10 | 295.36 | 303.453 | 640.2 | 50.5755 | 53.473 | -2.8975 | 320.8381 | 48.8 | 52.7083 | -3.9083 | 0.97333 | 2026-04-03 11:10 | 301.332 | 306.461 | 650.8 | 51.0768 | 53.473 | -2.3962 | 320.8381 | 49.6 | 52.7083 | -3.1083 | 0.98326 | 2026-04-03 11:10 | 223.965 | 227.399 | 482.2 | 37.8998 | 39.6096 | -1.7098 | 237.6578 | 37 | 39.0432 | -2.0432 | 0.9849 | 2026-04-03 11:10 | 223.534 | 227.698 | 482.3 | 37.9497 | 39.6096 | -1.66 | 237.6578 | 36.8 | 39.0432 | -2.2432 | 0.98171 | 2026-04-03 11:10 | 223.293 | 227.543 | 483.9 | 37.9238 | 39.6096 | -1.6858 | 237.6578 | 36.8 | 39.0432 | -2.2432 | 0.98132 | 2026-04-03 11:10 | 226.649 | 233.431 | 491.2 | 38.9052 | 39.6096 | -0.70447 | 237.6578 | 37.4 | 39.0432 | -1.6432 | 0.97095 | 2026-04-03 11:10 | 214.949 | 218.222 | 465.1 | 36.3703 | 37.6837 | -1.3133 | 226.102 | 35.4 | 37.1448 | -1.7448 | 0.985 | 2026-04-03 11:10 | 391.5352 | 410.0143 | -18.4791 | 2460.0857 | 381.4 | 404.1511 | -22.7511
2026-04-03 11:00 | 878 | 48.79 | 292.565 | 297.413 | 595.8 | 49.5688 | 52.2818 | -2.713 | 313.6909 | 48 | 51.5342 | -3.5342 | 0.9837 | 2026-04-03 11:00 | 292.565 | 297.413 | 595.8 | 49.5688 | 52.2818 | -2.713 | 313.6909 | 48 | 51.5342 | -3.5342 | 0.9837 | 2026-04-03 11:00 | 290.91 | 298.982 | 591.4 | 49.8303 | 52.2818 | -2.4515 | 313.6909 | 47.6 | 51.5342 | -3.9342 | 0.973 | 2026-04-03 11:00 | 295.303 | 300.257 | 601.2 | 50.0428 | 52.2818 | -2.239 | 313.6909 | 48.3 | 51.5342 | -3.2342 | 0.9835 | 2026-04-03 11:00 | 220.397 | 223.753 | 445.2 | 37.2922 | 38.7273 | -1.4351 | 232.3636 | 36 | 38.1735 | -2.1735 | 0.985 | 2026-04-03 11:00 | 219.28 | 222.974 | 445.5 | 37.1623 | 38.7273 | -1.5649 | 232.3636 | 35.8 | 38.1735 | -2.3735 | 0.98343 | 2026-04-03 11:00 | 219.484 | 223.604 | 447.1 | 37.2673 | 38.7273 | -1.4599 | 232.3636 | 35.9 | 38.1735 | -2.2735 | 0.98157 | 2026-04-03 11:00 | 221.81 | 228.579 | 453.8 | 38.0965 | 38.7273 | -0.63077 | 232.3636 | 36.3 | 38.1735 | -1.8735 | 0.97039 | 2026-04-03 11:00 | 209.964 | 213.161 | 429.7 | 35.5268 | 36.8442 | -1.3174 | 221.0652 | 34.4 | 36.3173 | -1.9173 | 0.985 | 2026-04-03 11:00 | 384.356 | 400.8805 | -16.5245 | 2405.283 | 370.3 | 395.1479 | -24.8479
2026-04-03 10:50 | 851 | 49.08 | 285.005 | 289.639 | 547.8 | 48.2732 | 50.6179 | -2.3448 | 303.7077 | 47.2 | 49.8941 | -2.6941 | 0.984 | 2026-04-03 10:50 | 285.005 | 289.639 | 547.8 | 48.2732 | 50.6179 | -2.3448 | 303.7077 | 47.2 | 49.8941 | -2.6941 | 0.984 | 2026-04-03 10:50 | 283.605 | 291.107 | 543.8 | 48.5178 | 50.6179 | -2.1001 | 303.7077 | 46.5 | 49.8941 | -3.3941 | 0.97423 | 2026-04-03 10:50 | 287.66 | 292.397 | 552.9 | 48.7328 | 50.6179 | -1.8851 | 303.7077 | 47.2 | 49.8941 | -2.6941 | 0.9838 | 2026-04-03 10:50 | 214.539 | 217.762 | 409.2 | 36.2937 | 37.4948 | -1.2011 | 224.9687 | 35.2 | 36.9586 | -1.7586 | 0.9852 | 2026-04-03 10:50 | 213.518 | 217.101 | 409.7 | 36.1835 | 37.4948 | -1.3113 | 224.9687 | 35.1 | 36.9586 | -1.8586 | 0.9835 | 2026-04-03 10:50 | 213.713 | 217.74 | 411.2 | 36.29 | 37.4948 | -1.2048 | 224.9687 | 35.4 | 36.9586 | -1.5586 | 0.98151 | 2026-04-03 10:50 | 216.359 | 222.685 | 417.5 | 37.1142 | 37.4948 | -0.38061 | 224.9687 | 36.4 | 36.9586 | -0.5586 | 0.97159 | 2026-04-03 10:50 | 204.689 | 207.764 | 395.3 | 34.6273 | 35.6716 | -1.0443 | 214.0298 | 34 | 35.1615 | -1.1615 | 0.9852 | 2026-04-03 10:50 | 374.3057 | 388.1225 | -13.8169 | 2328.7352 | 364.2 | 382.5724 | -18.3724
2026-04-03 10:40 | 822 | 49.08 | 277.232 | 281.839 | 500.6 | 46.9732 | 48.893 | -1.9198 | 293.3581 | 44.9 | 48.1938 | -3.2938 | 0.98365 | 2026-04-03 10:40 | 277.232 | 281.839 | 500.6 | 46.9732 | 48.893 | -1.9198 | 293.3581 | 44.9 | 48.1938 | -3.2938 | 0.98365 | 2026-04-03 10:40 | 275.758 | 283.103 | 497.3 | 47.1838 | 48.893 | -1.7092 | 293.3581 | 45.1 | 48.1938 | -3.0938 | 0.97406 | 2026-04-03 10:40 | 280.143 | 284.727 | 505.7 | 47.4545 | 48.893 | -1.4385 | 293.3581 | 45.8 | 48.1938 | -2.3938 | 0.9839 | 2026-04-03 10:40 | 208.334 | 211.421 | 374 | 35.2368 | 36.217 | -0.98021 | 217.3023 | 34.1 | 35.6991 | -1.5991 | 0.9854 | 2026-04-03 10:40 | 208.046 | 211.506 | 374.6 | 35.251 | 36.217 | -0.96605 | 217.3023 | 34.4 | 35.6991 | -1.2991 | 0.98364 | 2026-04-03 10:40 | 207.686 | 211.366 | 375.8 | 35.2277 | 36.217 | -0.98938 | 217.3023 | 34.1 | 35.6991 | -1.5991 | 0.98259 | 2026-04-03 10:40 | 210.41 | 216.554 | 381.1 | 36.0923 | 36.217 | -0.12471 | 217.3023 | 34 | 35.6991 | -1.6991 | 0.97163 | 2026-04-03 10:40 | 199.308 | 202.261 | 361.3 | 33.7102 | 34.456 | -0.74587 | 206.7362 | 32.6 | 33.9633 | -1.3633 | 0.9854 | 2026-04-03 10:40 | 364.1027 | 374.8963 | -10.7936 | 2249.3776 | 349.9 | 369.5352 | -19.6352
2026-04-03 10:30 | 792 | 49.08 | 269.095 | 273.248 | 455.7 | 45.5413 | 47.1086 | -1.5673 | 282.6516 | 44 | 46.4349 | -2.4349 | 0.9848 | 2026-04-03 10:30 | 269.095 | 273.248 | 455.7 | 45.5413 | 47.1086 | -1.5673 | 282.6516 | 44 | 46.4349 | -2.4349 | 0.9848 | 2026-04-03 10:30 | 267.308 | 274.156 | 452.2 | 45.6927 | 47.1086 | -1.4159 | 282.6516 | 44.3 | 46.4349 | -2.1349 | 0.97502 | 2026-04-03 10:30 | 271.154 | 275.479 | 459.9 | 45.9132 | 47.1086 | -1.1954 | 282.6516 | 44.9 | 46.4349 | -1.5349 | 0.9843 | 2026-04-03 10:30 | 201.705 | 204.748 | 339.9 | 34.1247 | 34.8953 | -0.77059 | 209.3715 | 33.4 | 34.3963 | -0.99625 | 0.98514 | 2026-04-03 10:30 | 201.376 | 204.565 | 340.2 | 34.0942 | 34.8953 | -0.80109 | 209.3715 | 33 | 34.3963 | -1.3963 | 0.98441 | 2026-04-03 10:30 | 201.375 | 204.65 | 341.7 | 34.1083 | 34.8953 | -0.78692 | 209.3715 | 32.9 | 34.3963 | -1.4963 | 0.984 | 2026-04-03 10:30 | 203.908 | 209.953 | 347.1 | 34.9922 | 34.8953 | 0.096911 | 209.3715 | 33.3 | 34.3963 | -1.0963 | 0.97121 | 2026-04-03 10:30 | 193.231 | 196.054 | 328.7 | 32.6757 | 33.1985 | -0.52285 | 199.1911 | 31.6 | 32.7238 | -1.1238 | 0.9856 | 2026-04-03 10:30 | 352.6835 | 361.2139 | -8.5304 | 2167.2835 | 341.4 | 356.0486 | -14.6486
2026-04-03 10:20 | 763 | 49.08 | 259.22 | 263.194 | 411.7 | 43.8657 | 45.3837 | -1.518 | 272.302 | 43.2 | 44.7347 | -1.5347 | 0.9849 | 2026-04-03 10:20 | 259.22 | 263.194 | 411.7 | 43.8657 | 45.3837 | -1.518 | 272.302 | 43.2 | 44.7347 | -1.5347 | 0.9849 | 2026-04-03 10:20 | 256.951 | 263.35 | 407.9 | 43.8917 | 45.3837 | -1.492 | 272.302 | 41.8 | 44.7347 | -2.9347 | 0.9757 | 2026-04-03 10:20 | 260.978 | 265.06 | 415 | 44.1767 | 45.3837 | -1.207 | 272.302 | 42.4 | 44.7347 | -2.3347 | 0.9846 | 2026-04-03 10:20 | 194.109 | 196.885 | 306.5 | 32.8142 | 33.6175 | -0.80336 | 201.7052 | 31.5 | 33.1368 | -1.6368 | 0.9859 | 2026-04-03 10:20 | 193.612 | 196.476 | 307.2 | 32.746 | 33.6175 | -0.87153 | 201.7052 | 31.5 | 33.1368 | -1.6368 | 0.98542 | 2026-04-03 10:20 | 193.79 | 196.741 | 308.8 | 32.7902 | 33.6175 | -0.82736 | 201.7052 | 31.5 | 33.1368 | -1.6368 | 0.985 | 2026-04-03 10:20 | 196.198 | 201.707 | 313.8 | 33.6178 | 33.6175 | 0.00030791 | 201.7052 | 31.9 | 33.1368 | -1.2368 | 0.97269 | 2026-04-03 10:20 | 185.954 | 188.613 | 297.1 | 31.4355 | 31.9829 | -0.54741 | 191.8975 | 30.6 | 31.5256 | -0.92556 | 0.9859 | 2026-04-03 10:20 | 339.2033 | 347.9877 | -8.7843 | 2087.9259 | 327.6 | 343.0114 | -15.4114
2026-04-03 10:10 | 726 | 48.22 | 247.691 | 251.83 | 368.5 | 41.9717 | 43.3248 | -1.3532 | 259.9489 | 40.6 | 42.7053 | -2.1053 | 0.98356 | 2026-04-03 10:10 | 247.691 | 251.83 | 368.5 | 41.9717 | 43.3248 | -1.3532 | 259.9489 | 40.6 | 42.7053 | -2.1053 | 0.98356 | 2026-04-03 10:10 | 246.688 | 252.833 | 366.1 | 42.1388 | 43.3248 | -1.186 | 259.9489 | 40.3 | 42.7053 | -2.4053 | 0.9757 | 2026-04-03 10:10 | 250.472 | 254.312 | 372.6 | 42.3853 | 43.3248 | -0.93949 | 259.9489 | 40.9 | 42.7053 | -1.8053 | 0.9849 | 2026-04-03 10:10 | 186.201 | 188.864 | 275 | 31.4773 | 32.0925 | -0.61513 | 192.5548 | 30.5 | 31.6335 | -1.1335 | 0.9859 | 2026-04-03 10:10 | 186.301 | 189.017 | 275.7 | 31.5028 | 32.0925 | -0.58963 | 192.5548 | 30.4 | 31.6335 | -1.2335 | 0.98563 | 2026-04-03 10:10 | 186.07 | 188.942 | 277.3 | 31.4903 | 32.0925 | -0.60213 | 192.5548 | 30.4 | 31.6335 | -1.2335 | 0.9848 | 2026-04-03 10:10 | 188.645 | 194.074 | 281.9 | 32.3457 | 32.0925 | 0.25321 | 192.5548 | 30.8 | 31.6335 | -0.83354 | 0.97203 | 2026-04-03 10:10 | 178.316 | 180.848 | 266.5 | 30.1413 | 30.532 | -0.39067 | 183.192 | 28.8 | 30.0954 | -1.2954 | 0.986 | 2026-04-03 10:10 | 325.425 | 332.2011 | -6.7761 | 1993.2068 | 313.3 | 327.4507 | -14.1507
2026-04-03 10:00 | 693 | 47.93 | 236.697 | 240.204 | 327.9 | 40.034 | 41.4012 | -1.3672 | 248.4072 | 37.5 | 40.8092 | -3.3092 | 0.9854 | 2026-04-03 10:00 | 236.697 | 240.204 | 327.9 | 40.034 | 41.4012 | -1.3672 | 248.4072 | 37.5 | 40.8092 | -3.3092 | 0.9854 | 2026-04-03 10:00 | 235.785 | 241.615 | 325.8 | 40.2692 | 41.4012 | -1.132 | 248.4072 | 38.4 | 40.8092 | -2.4092 | 0.97587 | 2026-04-03 10:00 | 239.507 | 243.105 | 331.7 | 40.5175 | 41.4012 | -0.8837 | 248.4072 | 39.1 | 40.8092 | -1.7092 | 0.9852 | 2026-04-03 10:00 | 177.781 | 180.269 | 244.5 | 30.0448 | 30.6676 | -0.62272 | 184.0053 | 28.9 | 30.229 | -1.329 | 0.9862 | 2026-04-03 10:00 | 178.105 | 181.003 | 245.3 | 30.1672 | 30.6676 | -0.50039 | 184.0053 | 29.1 | 30.229 | -1.129 | 0.98399 | 2026-04-03 10:00 | 177.649 | 180.133 | 246.9 | 30.0222 | 30.6676 | -0.64539 | 184.0053 | 29 | 30.229 | -1.229 | 0.98621 | 2026-04-03 10:00 | 180.242 | 185.209 | 251.1 | 30.8682 | 30.6676 | 0.20061 | 184.0053 | 29.4 | 30.229 | -0.82901 | 0.97318 | 2026-04-03 10:00 | 170.729 | 173.108 | 237.7 | 28.8513 | 29.1764 | -0.32505 | 175.0583 | 27.8 | 28.7592 | -0.95916 | 0.98626 | 2026-04-03 10:00 | 310.8083 | 317.4514 | -6.6431 | 1904.7085 | 296.7 | 312.9119 | -16.2119
2026-04-03 09:50 | 655 | 47.93 | 225.524 | 228.796 | 290.4 | 38.1327 | 39.131 | -0.99834 | 234.786 | 36.6 | 38.5714 | -1.9714 |  | 2026-04-03 09:50 | 225.524 | 228.796 | 290.4 | 38.1327 | 39.131 | -0.99834 | 234.786 | 36.6 | 38.5714 | -1.9714 |  | 2026-04-03 09:50 | 223.919 | 228.892 | 287.4 | 38.1487 | 39.131 | -0.98234 | 234.786 | 36.4 | 38.5714 | -2.1714 |  | 2026-04-03 09:50 | 227.553 | 230.925 | 292.6 | 38.4875 | 39.131 | -0.64351 | 234.786 | 37 | 38.5714 | -1.5714 |  | 2026-04-03 09:50 | 168.736 | 171.045 | 215.6 | 28.5075 | 28.9859 | -0.47843 | 173.9156 | 27.5 | 28.5714 | -1.0714 |  | 2026-04-03 09:50 | 169.488 | 171.825 | 216.2 | 28.6375 | 28.9859 | -0.34843 | 173.9156 | 27.5 | 28.5714 | -1.0714 |  | 2026-04-03 09:50 | 169.059 | 171.373 | 217.9 | 28.5622 | 28.9859 | -0.42376 | 173.9156 | 27.5 | 28.5714 | -1.0714 |  | 2026-04-03 09:50 | 171.741 | 176.389 | 221.7 | 29.3982 | 28.9859 | 0.41224 | 173.9156 | 28 | 28.5714 | -0.57143 |  | 2026-04-03 09:50 | 162.767 | 164.961 | 209.9 | 27.4935 | 27.5765 | -0.083022 | 165.4591 | 26.5 | 27.1822 | -0.68218 |  | 2026-04-03 09:50 | 295.5003 | 300.0443 | -4.5439 | 1800.2656 | 283.6 | 295.7536 | -12.1536
2026-04-03 09:40 | 619 | 47.64 | 213.773 | 216.782 | 253.8 | 36.1303 | 37.0211 | -0.89077 | 222.1266 | 34.5 | 36.4917 | -1.9917 |  | 2026-04-03 09:40 | 213.773 | 216.782 | 253.8 | 36.1303 | 37.0211 | -0.89077 | 222.1266 | 34.5 | 36.4917 | -1.9917 |  | 2026-04-03 09:40 | 212.351 | 216.759 | 251 | 36.1265 | 37.0211 | -0.8946 | 222.1266 | 33.7 | 36.4917 | -2.7917 |  | 2026-04-03 09:40 | 216.012 | 219.079 | 255.6 | 36.5132 | 37.0211 | -0.50794 | 222.1266 | 34.8 | 36.4917 | -1.6917 |  | 2026-04-03 09:40 | 159.915 | 162.054 | 188.1 | 27.009 | 27.423 | -0.41404 | 164.5382 | 25.7 | 27.0309 | -1.3309 |  | 2026-04-03 09:40 | 160.994 | 163.291 | 188.7 | 27.2152 | 27.423 | -0.20787 | 164.5382 | 26 | 27.0309 | -1.0309 |  | 2026-04-03 09:40 | 160.256 | 162.42 | 190.4 | 27.07 | 27.423 | -0.35304 | 164.5382 | 25.8 | 27.0309 | -1.2309 |  | 2026-04-03 09:40 | 162.937 | 167.676 | 193.7 | 27.946 | 27.423 | 0.52296 | 164.5382 | 26.3 | 27.0309 | -0.73089 |  | 2026-04-03 09:40 | 154.626 | 156.694 | 183.4 | 26.1157 | 26.0896 | 0.026041 | 156.5378 | 25 | 25.7165 | -0.71654 |  | 2026-04-03 09:40 | 280.2562 | 283.8662 | -3.61 | 1703.1972 | 266.3 | 279.8069 | -13.5069
2026-04-03 09:30 | 580 | 47.64 | 200.253 | 202.973 | 219.3 | 33.8288 | 34.6886 | -0.85976 | 208.1316 | 32.6 | 34.1925 | -1.5925 |  | 2026-04-03 09:30 | 200.253 | 202.973 | 219.3 | 33.8288 | 34.6886 | -0.85976 | 208.1316 | 32.6 | 34.1925 | -1.5925 |  | 2026-04-03 09:30 | 198.901 | 203.23 | 217.3 | 33.8717 | 34.6886 | -0.81693 | 208.1316 | 32.4 | 34.1925 | -1.7925 |  | 2026-04-03 09:30 | 202.408 | 205.22 | 220.8 | 34.2033 | 34.6886 | -0.48526 | 208.1316 | 33 | 34.1925 | -1.1925 |  | 2026-04-03 09:30 | 149.736 | 151.708 | 162.4 | 25.2847 | 25.6953 | -0.41059 | 154.1715 | 24 | 25.3278 | -1.3278 |  | 2026-04-03 09:30 | 150.952 | 152.925 | 162.7 | 25.4875 | 25.6953 | -0.20776 | 154.1715 | 24.2 | 25.3278 | -1.1278 |  | 2026-04-03 09:30 | 150.463 | 152.445 | 164.6 | 25.4075 | 25.6953 | -0.28776 | 154.1715 | 24.1 | 25.3278 | -1.2278 |  | 2026-04-03 09:30 | 153.287 | 157.545 | 167.4 | 26.2575 | 25.6953 | 0.56224 | 154.1715 | 24.5 | 25.3278 | -0.82781 |  | 2026-04-03 09:30 | 144.918 | 146.827 | 158.4 | 24.4712 | 24.4459 | 0.025313 | 146.6751 | 23.5 | 24.0963 | -0.59628 |  | 2026-04-03 09:30 | 262.641 | 265.9813 | -3.3403 | 1595.8875 | 250.9 | 262.1777 | -11.2777
2026-04-03 09:20 | 539 | 47.35 | 186.496 | 188.972 | 186.7 | 31.4953 | 32.272 | -0.77667 | 193.632 | 29.6 | 31.8105 | -2.2105 |  | 2026-04-03 09:20 | 186.496 | 188.972 | 186.7 | 31.4953 | 32.272 | -0.77667 | 193.632 | 29.6 | 31.8105 | -2.2105 |  | 2026-04-03 09:20 | 185.474 | 189.053 | 184.9 | 31.5088 | 32.272 | -0.76317 | 193.632 | 29.8 | 31.8105 | -2.0105 |  | 2026-04-03 09:20 | 188.515 | 191.056 | 187.8 | 31.8427 | 32.272 | -0.42934 | 193.632 | 29.8 | 31.8105 | -2.0105 |  | 2026-04-03 09:20 | 139.669 | 141.466 | 138.4 | 23.5777 | 23.9052 | -0.32752 | 143.4311 | 22.4 | 23.5633 | -1.1633 |  | 2026-04-03 09:20 | 140.766 | 142.562 | 138.5 | 23.7603 | 23.9052 | -0.14486 | 143.4311 | 22.6 | 23.5633 | -0.96335 |  | 2026-04-03 09:20 | 140.507 | 142.3 | 140.5 | 23.7167 | 23.9052 | -0.18852 | 143.4311 | 22.6 | 23.5633 | -0.96335 |  | 2026-04-03 09:20 | 142.952 | 146.726 | 142.9 | 24.4543 | 23.9052 | 0.54914 | 143.4311 | 22.9 | 23.5633 | -0.66335 |  | 2026-04-03 09:20 | 135.139 | 136.891 | 134.9 | 22.8152 | 22.7428 | 0.072339 | 136.457 | 21.4 | 22.4176 | -1.0176 |  | 2026-04-03 09:20 | 244.6663 | 247.4516 | -2.7853 | 1484.7097 | 230.7 | 243.9131 | -13.2131
2026-04-03 09:10 | 497 | 47.07 | 172.013 | 174.562 | 157.1 | 29.0937 | 29.7889 | -0.69527 | 178.7336 | 27.5 | 29.363 | -1.863 |  | 2026-04-03 09:10 | 172.013 | 174.562 | 157.1 | 29.0937 | 29.7889 | -0.69527 | 178.7336 | 27.5 | 29.363 | -1.863 |  | 2026-04-03 09:10 | 170.914 | 173.838 | 155.1 | 28.973 | 29.7889 | -0.81594 | 178.7336 | 26.9 | 29.363 | -2.463 |  | 2026-04-03 09:10 | 174.086 | 176.343 | 158 | 29.3905 | 29.7889 | -0.39844 | 178.7336 | 27.8 | 29.363 | -1.563 |  | 2026-04-03 09:10 | 128.648 | 130.263 | 116 | 21.7105 | 22.0659 | -0.35538 | 132.3953 | 20.5 | 21.7503 | -1.2503 |  | 2026-04-03 09:10 | 129.887 | 131.518 | 115.9 | 21.9197 | 22.0659 | -0.14622 | 132.3953 | 20.8 | 21.7503 | -0.95034 |  | 2026-04-03 09:10 | 129.344 | 130.955 | 117.9 | 21.8258 | 22.0659 | -0.24005 | 132.3953 | 20.6 | 21.7503 | -1.1503 |  | 2026-04-03 09:10 | 131.016 | 134.408 | 120 | 22.4013 | 22.0659 | 0.33545 | 132.3953 | 20.9 | 21.7503 | -0.85034 |  | 2026-04-03 09:10 | 124.802 | 126.369 | 113.5 | 21.0615 | 20.993 | 0.068546 | 125.9577 | 19.9 | 20.6928 | -0.79275 |  | 2026-04-03 09:10 | 225.4697 | 228.4122 | -2.9426 | 1370.4735 | 212.4 | 225.146 | -12.746
2026-04-03 09:00 | 455 | 46.49 | 156.872 | 158.8 | 129.6 | 26.4667 | 27.3316 | -0.86489 | 163.9894 | 24.8 | 26.9407 | -2.1407 |  | 2026-04-03 09:00 | 156.872 | 158.8 | 129.6 | 26.4667 | 27.3316 | -0.86489 | 163.9894 | 24.8 | 26.9407 | -2.1407 |  | 2026-04-03 09:00 | 155.267 | 158.05 | 128.2 | 26.3417 | 27.3316 | -0.98989 | 163.9894 | 24.7 | 26.9407 | -2.2407 |  | 2026-04-03 09:00 | 158.486 | 160.492 | 130.2 | 26.7487 | 27.3316 | -0.58289 | 163.9894 | 24.8 | 26.9407 | -2.1407 |  | 2026-04-03 09:00 | 116.751 | 118.168 | 95.5 | 19.6947 | 20.2456 | -0.55093 | 121.4736 | 18.5 | 19.9561 | -1.4561 |  | 2026-04-03 09:00 | 118.291 | 119.701 | 95.1 | 19.9502 | 20.2456 | -0.29543 | 121.4736 | 18.7 | 19.9561 | -1.2561 |  | 2026-04-03 09:00 | 117.617 | 119.046 | 97.3 | 19.841 | 20.2456 | -0.4046 | 121.4736 | 18.7 | 19.9561 | -1.2561 |  | 2026-04-03 09:00 | 119.276 | 122.888 | 99.1 | 20.4813 | 20.2456 | 0.23573 | 121.4736 | 19 | 19.9561 | -0.95609 |  | 2026-04-03 09:00 | 113.773 | 115.155 | 93.6 | 19.1925 | 19.2612 | -0.068682 | 115.5671 | 18 | 18.9857 | -0.98575 |  | 2026-04-03 09:00 | 205.1833 | 209.5698 | -4.3865 | 1257.419 | 192 | 206.573 | -14.573
2026-04-03 08:50 | 408 | 47.07 | 140.457 | 142.149 | 104.8 | 23.6915 | 24.4545 | -0.763 | 146.727 | 22.4 | 24.1048 | -1.7048 |  | 2026-04-03 08:50 | 140.457 | 142.149 | 104.8 | 23.6915 | 24.4545 | -0.763 | 146.727 | 22.4 | 24.1048 | -1.7048 |  | 2026-04-03 08:50 | 139.531 | 141.88 | 103.5 | 23.6467 | 24.4545 | -0.80784 | 146.727 | 21.9 | 24.1048 | -2.2048 |  | 2026-04-03 08:50 | 142.388 | 144.117 | 105.4 | 24.0195 | 24.4545 | -0.435 | 146.727 | 22.4 | 24.1048 | -1.7048 |  | 2026-04-03 08:50 | 104.538 | 105.765 | 77 | 17.6275 | 18.1144 | -0.48695 | 108.6867 | 16.4 | 17.8554 | -1.4554 |  | 2026-04-03 08:50 | 106.201 | 107.458 | 76.4 | 17.9097 | 18.1144 | -0.20478 | 108.6867 | 16.7 | 17.8554 | -1.1554 |  | 2026-04-03 08:50 | 105.782 | 107.023 | 78.6 | 17.8372 | 18.1144 | -0.27728 | 108.6867 | 16.6 | 17.8554 | -1.2554 |  | 2026-04-03 08:50 | 107.501 | 110.588 | 80.1 | 18.4313 | 18.1144 | 0.31689 | 108.6867 | 16.8 | 17.8554 | -1.0554 |  | 2026-04-03 08:50 | 101.902 | 103.108 | 75.6 | 17.1847 | 17.2337 | -0.048986 | 103.4019 | 16.1 | 16.9872 | -0.88721 |  | 2026-04-03 08:50 | 184.0395 | 187.5095 | -3.47 | 1125.0567 | 171.7 | 184.8281 | -13.1281
2026-04-03 08:40 | 363 | 44.48 | 124.05 | 125.48 | 82.4 | 20.9133 | 21.9711 | -1.0577 | 131.8263 | 19.1 | 21.6569 | -2.5569 |  | 2026-04-03 08:40 | 124.05 | 125.48 | 82.4 | 20.9133 | 21.9711 | -1.0577 | 131.8263 | 19.1 | 21.6569 | -2.5569 |  | 2026-04-03 08:40 | 123.218 | 125.269 | 81.6 | 20.8782 | 21.9711 | -1.0929 | 131.8263 | 19.2 | 21.6569 | -2.4569 |  | 2026-04-03 08:40 | 125.865 | 127.368 | 83 | 21.228 | 21.9711 | -0.74306 | 131.8263 | 19.6 | 21.6569 | -2.0569 |  | 2026-04-03 08:40 | 92.336 | 93.401 | 60.6 | 15.5668 | 16.2749 | -0.70802 | 97.6491 | 14.2 | 16.0421 | -1.8421 |  | 2026-04-03 08:40 | 93.902 | 94.966 | 59.7 | 15.8277 | 16.2749 | -0.44719 | 97.6491 | 14.4 | 16.0421 | -1.6421 |  | 2026-04-03 08:40 | 93.532 | 94.611 | 62 | 15.7685 | 16.2749 | -0.50636 | 97.6491 | 14.6 | 16.0421 | -1.4421 |  | 2026-04-03 08:40 | 95.128 | 97.627 | 63.3 | 16.2712 | 16.2749 | -0.0036894 | 97.6491 | 14.9 | 16.0421 | -1.1421 |  | 2026-04-03 08:40 | 90.334 | 91.346 | 59.5 | 15.2243 | 15.4835 | -0.25918 | 92.9011 | 14.1 | 15.2621 | -1.1621 |  | 2026-04-03 08:40 | 162.5913 | 168.4672 | -5.8758 | 1010.8029 | 149.2 | 166.0581 | -16.8581
2026-04-03 08:30 | 317 | 39.61 | 107.732 | 108.93 | 63.3 | 18.155 | 19.5378 | -1.3828 | 117.2269 | 16.6 | 19.2584 | -2.6584 |  | 2026-04-03 08:30 | 107.732 | 108.93 | 63.3 | 18.155 | 19.5378 | -1.3828 | 117.2269 | 16.6 | 19.2584 | -2.6584 |  | 2026-04-03 08:30 | 106.75 | 108.322 | 62.4 | 18.0537 | 19.5378 | -1.4841 | 117.2269 | 16.5 | 19.2584 | -2.7584 |  | 2026-04-03 08:30 | 109.18 | 110.428 | 63.4 | 18.4047 | 19.5378 | -1.1331 | 117.2269 | 16.8 | 19.2584 | -2.4584 |  | 2026-04-03 08:30 | 79.95 | 80.896 | 46.4 | 13.4827 | 14.4725 | -0.98979 | 86.8347 | 12.3 | 14.2655 | -1.9655 |  | 2026-04-03 08:30 | 77.309 | 78.216 | 45.3 | 13.036 | 14.4725 | -1.4365 | 86.8347 | 11.8 | 14.2655 | -2.4655 |  | 2026-04-03 08:30 | 81.171 | 82.132 | 47.4 | 13.6887 | 14.4725 | -0.78379 | 86.8347 | 12.4 | 14.2655 | -1.8655 |  | 2026-04-03 08:30 | 82.679 | 84.872 | 48.4 | 14.1453 | 14.4725 | -0.32712 | 86.8347 | 12.6 | 14.2655 | -1.6655 |  | 2026-04-03 08:30 | 78.28 | 79.199 | 45.4 | 13.1998 | 13.7687 | -0.56891 | 82.6125 | 12 | 13.5719 | -1.5719 |  | 2026-04-03 08:30 | 140.3208 | 149.8098 | -9.489 | 898.8589 | 127.6 | 147.6675 | -20.0675
2026-04-03 08:20 | 272 | 32.14 | 90.49 | 91.45 | 46.7 | 15.2417 | 17.2262 | -1.9846 | 103.3574 | 13.9 | 16.9799 | -3.0799 |  | 2026-04-03 08:20 | 90.49 | 91.45 | 46.7 | 15.2417 | 17.2262 | -1.9846 | 103.3574 | 13.9 | 16.9799 | -3.0799 |  | 2026-04-03 08:20 | 90.189 | 91.346 | 45.9 | 15.2243 | 17.2262 | -2.0019 | 103.3574 | 13.6 | 16.9799 | -3.3799 |  | 2026-04-03 08:20 | 91.973 | 92.987 | 46.6 | 15.4978 | 17.2262 | -1.7284 | 103.3574 | 14 | 16.9799 | -2.9799 |  | 2026-04-03 08:20 | 67.393 | 68.212 | 34.1 | 11.3687 | 12.7602 | -1.3915 | 76.561 | 10.2 | 12.5777 | -2.3777 |  | 2026-04-03 08:20 | 65.615 | 66.392 | 33.5 | 11.0653 | 12.7602 | -1.6948 | 76.561 | 9.9 | 12.5777 | -2.6777 |  | 2026-04-03 08:20 | 68.781 | 69.616 | 35 | 11.6027 | 12.7602 | -1.1575 | 76.561 | 10.4 | 12.5777 | -2.1777 |  | 2026-04-03 08:20 | 70.048 | 71.837 | 35.8 | 11.9728 | 12.7602 | -0.78734 | 76.561 | 10.6 | 12.5777 | -1.9777 |  | 2026-04-03 08:20 | 65.575 | 66.358 | 33.4 | 11.0597 | 12.1397 | -1.0801 | 72.8383 | 10 | 11.9661 | -1.9661 |  | 2026-04-03 08:20 | 118.2747 | 132.0853 | -13.8107 | 792.5119 | 106.5 | 130.1965 | -23.6965
2026-04-03 08:10 | 226 | 27.84 | 73.799 | 74.635 | 32.8 | 12.4392 | 14.5339 | -2.0947 | 87.2034 | 10.9 | 14.3261 | -3.4261 |  | 2026-04-03 08:10 | 73.799 | 74.635 | 32.8 | 12.4392 | 14.5339 | -2.0947 | 87.2034 | 10.9 | 14.3261 | -3.4261 |  | 2026-04-03 08:10 | 73.509 | 74.357 | 32.3 | 12.3928 | 14.5339 | -2.1411 | 87.2034 | 10.9 | 14.3261 | -3.4261 |  | 2026-04-03 08:10 | 75.222 | 76.097 | 32.6 | 12.6828 | 14.5339 | -1.8511 | 87.2034 | 11.1 | 14.3261 | -3.2261 |  | 2026-04-03 08:10 | 54.83 | 55.558 | 23.9 | 9.2597 | 10.7659 | -1.5062 | 64.5951 | 8.1 | 10.6119 | -2.5119 |  | 2026-04-03 08:10 | 53.591 | 54.28 | 23.6 | 9.0467 | 10.7659 | -1.7192 | 64.5951 | 8 | 10.6119 | -2.6119 |  | 2026-04-03 08:10 | 56.176 | 56.874 | 24.6 | 9.479 | 10.7659 | -1.2869 | 64.5951 | 8.4 | 10.6119 | -2.2119 |  | 2026-04-03 08:10 | 57.289 | 58.914 | 25.2 | 9.819 | 10.7659 | -0.94685 | 64.5951 | 8.6 | 10.6119 | -2.0119 |  | 2026-04-03 08:10 | 53.717 | 54.43 | 23.4 | 9.0717 | 10.2424 | -1.1707 | 61.4543 | 7.9 | 10.0959 | -2.1959 |  | 2026-04-03 08:10 | 96.63 | 111.4414 | -14.8114 | 668.6484 | 84.8 | 109.8478 | -25.0478
2026-04-03 08:00 | 181 | 24.68 | 57.771 | 58.485 | 21.9 | 9.7475 | 11.77 | -2.0225 | 70.6201 | 8.4 | 11.6017 | -3.2017 |  | 2026-04-03 08:00 | 57.771 | 58.485 | 21.9 | 9.7475 | 11.77 | -2.0225 | 70.6201 | 8.4 | 11.6017 | -3.2017 |  | 2026-04-03 08:00 | 57.496 | 58.206 | 21.4 | 9.701 | 11.77 | -2.069 | 70.6201 | 8.3 | 11.6017 | -3.3017 |  | 2026-04-03 08:00 | 58.839 | 59.572 | 21.5 | 9.9287 | 11.77 | -1.8413 | 70.6201 | 8.5 | 11.6017 | -3.1017 |  | 2026-04-03 08:00 | 42.668 | 43.452 | 15.8 | 7.242 | 8.7185 | -1.4765 | 52.3112 | 6.2 | 8.5939 | -2.3939 |  | 2026-04-03 08:00 | 41.857 | 42.447 | 15.6 | 7.0745 | 8.7185 | -1.644 | 52.3112 | 6.1 | 8.5939 | -2.4939 |  | 2026-04-03 08:00 | 43.893 | 44.534 | 16.2 | 7.4223 | 8.7185 | -1.2962 | 52.3112 | 6.4 | 8.5939 | -2.1939 |  | 2026-04-03 08:00 | 44.836 | 45.99 | 16.6 | 7.665 | 8.7185 | -1.0535 | 52.3112 | 6.5 | 8.5939 | -2.0939 |  | 2026-04-03 08:00 | 41.992 | 42.61 | 15.5 | 7.1017 | 8.2946 | -1.1929 | 49.7676 | 6.2 | 8.176 | -1.976 |  | 2026-04-03 08:00 | 75.6302 | 90.2488 | -14.6186 | 541.4926 | 65 | 88.9582 | -23.9582
2026-04-03 07:50 | 138 | 20.38 | 42.858 | 43.426 | 13.5 | 7.2377 | 9.1087 | -1.8711 | 54.6524 | 5.9 | 8.9785 | -3.0785 |  | 2026-04-03 07:50 | 42.858 | 43.426 | 13.5 | 7.2377 | 9.1087 | -1.8711 | 54.6524 | 5.9 | 8.9785 | -3.0785 |  | 2026-04-03 07:50 | 42.439 | 43.05 | 13.1 | 7.175 | 9.1087 | -1.9337 | 54.6524 | 5.9 | 8.9785 | -3.0785 |  | 2026-04-03 07:50 | 43.37 | 44.004 | 13 | 7.334 | 9.1087 | -1.7747 | 54.6524 | 6 | 8.9785 | -2.9785 |  | 2026-04-03 07:50 | 31.493 | 32.002 | 9.6 | 5.3337 | 6.7472 | -1.4135 | 40.4832 | 4.5 | 6.6507 | -2.1507 |  | 2026-04-03 07:50 | 30.822 | 31.429 | 9.5 | 5.2382 | 6.7472 | -1.509 | 40.4832 | 4.3 | 6.6507 | -2.3507 |  | 2026-04-03 07:50 | 32.343 | 32.866 | 9.8 | 5.4777 | 6.7472 | -1.2695 | 40.4832 | 4.5 | 6.6507 | -2.1507 |  | 2026-04-03 07:50 | 33.16 | 34.184 | 10.1 | 5.6973 | 6.7472 | -1.0499 | 40.4832 | 4.6 | 6.6507 | -2.0507 |  | 2026-04-03 07:50 | 31.278 | 31.78 | 9.3 | 5.2967 | 6.4191 | -1.1225 | 38.5148 | 4.3 | 6.3273 | -2.0273 |  | 2026-04-03 07:50 | 56.0278 | 69.8429 | -13.815 | 419.0572 | 45.9 | 68.8441 | -22.9441
2026-04-03 07:40 | 98 | 17.79 | 29.634 | 30.119 | 7.6 | 5.0198 | 6.5262 | -1.5064 | 39.1573 | 4 | 6.4329 | -2.4329 |  | 2026-04-03 07:40 | 29.634 | 30.119 | 7.6 | 5.0198 | 6.5262 | -1.5064 | 39.1573 | 4 | 6.4329 | -2.4329 |  | 2026-04-03 07:40 | 29.185 | 29.681 | 7.2 | 4.9468 | 6.5262 | -1.5794 | 39.1573 | 3.9 | 6.4329 | -2.5329 |  | 2026-04-03 07:40 | 28.708 | 29.375 | 7 | 4.8958 | 6.5262 | -1.6304 | 39.1573 | 3.8 | 6.4329 | -2.6329 |  | 2026-04-03 07:40 | 21.391 | 21.904 | 5.1 | 3.6507 | 4.8342 | -1.1836 | 29.0054 | 2.8 | 4.7651 | -1.9651 |  | 2026-04-03 07:40 | 21.04 | 21.474 | 5.2 | 3.579 | 4.8342 | -1.2552 | 29.0054 | 2.8 | 4.7651 | -1.9651 |  | 2026-04-03 07:40 | 22.104 | 22.562 | 5.3 | 3.7603 | 4.8342 | -1.0739 | 29.0054 | 2.9 | 4.7651 | -1.8651 |  | 2026-04-03 07:40 | 22.706 | 23.356 | 5.5 | 3.8927 | 4.8342 | -0.94157 | 29.0054 | 3 | 4.7651 | -1.7651 |  | 2026-04-03 07:40 | 21.099 | 21.543 | 5 | 3.5905 | 4.5992 | -1.0087 | 27.5951 | 2.8 | 4.5334 | -1.7334 |  | 2026-04-03 07:40 | 38.3555 | 50.041 | -11.6855 | 300.2461 | 30 | 49.3254 | -19.3254
2026-04-03 07:30 | 59 | 16.07 | 18.24 | 18.648 | 3.6 | 3.108 | 3.9521 | -0.84412 | 23.7127 | 3.3 | 3.8956 | -0.59561 |  | 2026-04-03 07:30 | 18.24 | 18.648 | 3.6 | 3.108 | 3.9521 | -0.84412 | 23.7127 | 3.3 | 3.8956 | -0.59561 |  | 2026-04-03 07:30 | 17.929 | 18.345 | 3.3 | 3.0575 | 3.9521 | -0.89462 | 23.7127 | 2.2 | 3.8956 | -1.6956 |  | 2026-04-03 07:30 | 17.323 | 18.068 | 3.2 | 3.0113 | 3.9521 | -0.94079 | 23.7127 | 2.1 | 3.8956 | -1.7956 |  | 2026-04-03 07:30 | 12.878 | 13.566 | 2.3 | 2.261 | 2.9275 | -0.6665 | 17.565 | 1.6 | 2.8856 | -1.2856 |  | 2026-04-03 07:30 | 12.7 | 13.06 | 2.4 | 2.1767 | 2.9275 | -0.75083 | 17.565 | 1.5 | 2.8856 | -1.3856 |  | 2026-04-03 07:30 | 13.468 | 13.828 | 2.4 | 2.3047 | 2.9275 | -0.62283 | 17.565 | 1.7 | 2.8856 | -1.1856 |  | 2026-04-03 07:30 | 13.758 | 14.637 | 2.5 | 2.4395 | 2.9275 | -0.488 | 17.565 | 1.7 | 2.8856 | -1.1856 |  | 2026-04-03 07:30 | 12.562 | 12.932 | 2.2 | 2.1553 | 2.7852 | -0.62982 | 16.7109 | 1.5 | 2.7453 | -1.2453 |  | 2026-04-03 07:30 | 23.622 | 30.3036 | -6.6816 | 181.8218 | 18.9 | 29.8703 | -10.9703
2026-04-03 07:20 | 24 | 15.21 |  |  |  | 0 | 1.6123 | -1.6123 | 9.674 | 0 | 1.5893 | -1.5893 | [5 empty] | 0 | 1.6123 | -1.6123 | 9.674 | 0 | 1.5893 | -1.5893 |  | 2026-04-03 07:20 | 9.209 | 9.541 | 1.1 | 1.5902 | 1.6123 | -0.022169 | 9.674 | 1.1 | 1.5893 | -0.48928 |  | 2026-04-03 07:20 | 9.01 | 9.859 | 1.1 | 1.6432 | 1.6123 | 0.030831 | 9.674 | 1.1 | 1.5893 | -0.48928 |  | 2026-04-03 07:20 | 6.712 | 7.349 | 0.7 | 1.2248 | 1.1943 | 0.030511 | 7.1659 | 0.7 | 1.1772 | -0.47724 |  | 2026-04-03 07:20 | 6.365 | 6.625 | 0.9 | 1.1042 | 1.1943 | -0.090156 | 7.1659 | 0.7 | 1.1772 | -0.47724 |  | 2026-04-03 07:20 | 6.928 | 7.211 | 0.7 | 1.2018 | 1.1943 | 0.0075109 | 7.1659 | 0.7 | 1.1772 | -0.47724 |  | 2026-04-03 07:20 | 7 | 7.634 | 0.8 | 1.2723 | 1.1943 | 0.078011 | 7.1659 | 0.8 | 1.1772 | -0.37724 |  | 2026-04-03 07:20 | 6.263 | 6.52 | 0.7 | 1.0867 | 1.1362 | -0.049583 | 6.8175 | 0.7 | 1.12 | -0.42 |  | 2026-04-03 07:20 | 9.1232 | 12.3629 | -3.2397 | 74.1773 | 5.8 | 12.1861 | -6.3861
2026-04-03 07:10 | 10 | 14.64 | 3.588 | 3.761 | 0.3 | 0.62683 | 0.6731 | -0.046269 | 4.0386 | 0.3 | 0.66348 | -0.36348 |  | 2026-04-03 07:10 | 3.588 | 3.761 | 0.3 | 0.62683 | 0.6731 | -0.046269 | 4.0386 | 0.3 | 0.66348 | -0.36348 |  | 2026-04-03 07:10 | 3.586 | 3.756 | 0 | 0.626 | 0.6731 | -0.047102 | 4.0386 | 0 | 0.66348 | -0.66348 |  | 2026-04-03 07:10 | 3.646 | 4.4 | 0 | 0.73333 | 0.6731 | 0.060231 | 4.0386 | 0 | 0.66348 | -0.66348 |  | 2026-04-03 07:10 | 2.377 | 3.176 | 0 | 0.52933 | 0.49859 | 0.030739 | 2.9916 | 0 | 0.49146 | -0.49146 |  | 2026-04-03 07:10 | 2.401 | 2.522 | 0.2 | 0.42033 | 0.49859 | -0.078261 | 2.9916 | 0.2 | 0.49146 | -0.29146 |  | 2026-04-03 07:10 | 2.435 | 2.534 | 0 | 0.42233 | 0.49859 | -0.076261 | 2.9916 | 0 | 0.49146 | -0.49146 |  | 2026-04-03 07:10 | 2.682 | 2.982 | 0 | 0.497 | 0.49859 | -0.0015942 | 2.9916 | 0 | 0.49146 | -0.49146 |  | 2026-04-03 07:10 | 2.212 | 2.326 | 0 | 0.38767 | 0.47435 | -0.086684 | 2.8461 | 0 | 0.46757 | -0.46757 |  | 2026-04-03 07:10 | 4.8697 | 5.1611 | -0.29147 | 30.9668 | 0.8 | 5.0873 | -4.2873
2026-04-03 07:00 | 2 | 14.92 | 0.685 | 0.726 | 0 | 0.121 | 0.13449 | -0.013493 | 0.80696 | 0 | 0.13257 | -0.13257 |  | 2026-04-03 07:00 | 0.685 | 0.726 | 0 | 0.121 | 0.13449 | -0.013493 | 0.80696 | 0 | 0.13257 | -0.13257 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.13449 | -0.13449 | 0.80696 | 0 | 0.13257 | -0.13257 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.13449 | -0.13449 | 0.80696 | 0 | 0.13257 | -0.13257 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.099625 | -0.099625 | 0.59775 | 0 | 0.0982 | -0.0982 |  | 2026-04-03 07:00 | 0.409 | 0.43 | 0 | 0.071667 | 0.099625 | -0.027958 | 0.59775 | 0 | 0.0982 | -0.0982 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.099625 | -0.099625 | 0.59775 | 0 | 0.0982 | -0.0982 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.099625 | -0.099625 | 0.59775 | 0 | 0.0982 | -0.0982 |  | 2026-04-03 07:00 | 0 | 0 | 0 | 0 | 0.09478 | -0.09478 | 0.56868 | 0 | 0.093425 | -0.093425 |  | 2026-04-03 07:00 | 0.31367 | 1.0313 | -0.71758 | 6.1875 | 0 | 1.0165 | -1.0165
[110 empty] | Total: - | 18276.2203 | 19316.5557 | -1040.3354 |  | 18026.8 | 19040.329 | -1013.529
Sum:- | 42201 |  | 13704.116 |  | 86023.6 |  |  |  |  | 2332.3 | 2483.191 | -150.891 | 0.98345 |  | 13704.116 |  | 86023.6 |  |  |  |  | 2332.3 | 2483.191 | -150.891 | 0.98345 |  | 13954.61 |  | 87351.8 |  |  |  |  | 2325.1 | 2483.191 | -158.091 | 0.97221 |  | 14139.627 |  | 88578.2 |  |  |  |  | 2355.2 | 2483.191 | -127.991 | 0.98311 |  | 10557.952 |  | 66035.9 |  |  |  |  | 1759.1 | 1839.4007 | -80.3007 | 0.9845 |  | 10461.763 |  | 65593 |  |  |  |  | 1742.4 | 1839.4007 | -97.0007 | 0.98153 |  | 10481.688 |  | 65762.6 |  |  |  |  | 1746.3 | 1839.4007 | -93.1007 | 0.98097 |  | 10597.399 |  | 66566.6 |  |  |  |  | 1765.1 | 1839.4007 | -74.3007 | 0.97136 |  | 10023.005 |  | 62951.9 |  |  |  |  | 1669 | 1749.962 | -80.962 | 0.98472
Formulas:
Time = [Time]

## 5 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-05-03 19:00 | 0 | 35.01 | 0.059 | 0.078 | 2485.2 | 0.013 | 0 | 0.013 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.098 | 0.169 | 2530.6 | 0.028167 | 0 | 0.028167 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.07 | 0.08 | 2501.7 | 0.013333 | 0 | 0.013333 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.057 | 0.067 | 2507.9 | 0.011167 | 0 | 0.011167 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.055 | 0.071 | 1882.1 | 0.011833 | 0 | 0.011833 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.083 | 0.085 | 1864.3 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.072 | 0.101 | 1872.3 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.065 | 0.084 | 1884.9 | 0.014 | 0 | 0.014 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.06 | 0.079 | 1781.6 | 0.013167 | 0 | 0.013167 | 0 | 0 | 0 | 0 |  | 2026-05-03 19:00 | 0.13567 | 0 | 0.13567 | 0 | 0 | 0 | 0 | 1 | 98.33%
2026-05-03 18:50 | 0 | 36.16 | 0.29 | 0.245 | 2485.2 | 0.040833 | 0 | 0.040833 | 0 | 0.2 | 0 | 0.2 |  | 2026-05-03 18:50 | 0.398 | 0.718 | 2530.6 | 0.11967 | 0 | 0.11967 | 0 | 0.2 | 0 | 0.2 |  | 2026-05-03 18:50 | 0.261 | 0.283 | 2501.7 | 0.047167 | 0 | 0.047167 | 0 | 0.2 | 0 | 0.2 |  | 2026-05-03 18:50 | 0.267 | 0.69 | 2507.9 | 0.115 | 0 | 0.115 | 0 | 0.2 | 0 | 0.2 |  | 2026-05-03 18:50 | 0.09 | 0.177 | 1882.1 | 0.0295 | 0 | 0.0295 | 0 | 0.1 | 0 | 0.1 |  | 2026-05-03 18:50 | 0.028 | 0.096 | 1864.3 | 0.016 | 0 | 0.016 | 0 | 0.1 | 0 | 0.1 |  | 2026-05-03 18:50 | 0.004 | 0.062 | 1872.3 | 0.010333 | 0 | 0.010333 | 0 | 0.1 | 0 | 0.1 |  | 2026-05-03 18:50 | 0.147 | 0.446 | 1884.9 | 0.074333 | 0 | 0.074333 | 0 | 0.1 | 0 | 0.1 |  | 2026-05-03 18:50 | 0.018 | 0.082 | 1781.6 | 0.013667 | 0 | 0.013667 | 0 | 0.1 | 0 | 0.1 |  | 2026-05-03 18:50 | 0.4665 | 0 | 0.4665 | 0 | 1.3 | 0 | 1.3 | 2 | 98.61%
2026-05-03 18:40 | 0 | 37.6 | 2.239 | 2.354 | 2485 | 0.39233 | 0 | 0.39233 | 0 | 0.6 | 0 | 0.6 |  | 2026-05-03 18:40 | 2.351 | 2.938 | 2530.4 | 0.48967 | 0 | 0.48967 | 0 | 0.7 | 0 | 0.7 |  | 2026-05-03 18:40 | 2.235 | 2.35 | 2501.5 | 0.39167 | 0 | 0.39167 | 0 | 0.6 | 0 | 0.6 |  | 2026-05-03 18:40 | 2.157 | 2.73 | 2507.7 | 0.455 | 0 | 0.455 | 0 | 0.7 | 0 | 0.7 |  | 2026-05-03 18:40 | 1.581 | 1.711 | 1882 | 0.28517 | 0 | 0.28517 | 0 | 0.5 | 0 | 0.5 |  | 2026-05-03 18:40 | 1.533 | 1.603 | 1864.2 | 0.26717 | 0 | 0.26717 | 0 | 0.5 | 0 | 0.5 |  | 2026-05-03 18:40 | 1.501 | 1.578 | 1872.2 | 0.263 | 0 | 0.263 | 0 | 0.5 | 0 | 0.5 |  | 2026-05-03 18:40 | 1.574 | 1.899 | 1884.8 | 0.3165 | 0 | 0.3165 | 0 | 0.5 | 0 | 0.5 |  | 2026-05-03 18:40 | 1.426 | 1.499 | 1781.5 | 0.24983 | 0 | 0.24983 | 0 | 0.4 | 0 | 0.4 |  | 2026-05-03 18:40 | 3.1103 | 0 | 3.1103 | 0 | 5 | 0 | 5 | 3 | 97.21%
2026-05-03 18:30 | 11 | 39.61 | 5.847 | 6.113 | 2484.4 | 1.0188 | 0.67797 | 0.34087 | 4.0678 | 1.4 | 0.66827 | 0.73173 |  | 2026-05-03 18:30 | 7.43 | 6.967 | 2529.7 | 1.1612 | 0.67797 | 0.4832 | 4.0678 | 1.7 | 0.66827 | 1.0317 |  | 2026-05-03 18:30 | 6.169 | 6.402 | 2500.9 | 1.067 | 0.67797 | 0.38903 | 4.0678 | 1.6 | 0.66827 | 0.93173 |  | 2026-05-03 18:30 | 6.418 | 6.721 | 2507 | 1.1202 | 0.67797 | 0.4422 | 4.0678 | 1.6 | 0.66827 | 0.93173 |  | 2026-05-03 18:30 | 4.681 | 4.898 | 1881.5 | 0.81633 | 0.5022 | 0.31413 | 3.0132 | 1.1 | 0.49502 | 0.60498 |  | 2026-05-03 18:30 | 4.462 | 4.671 | 1863.7 | 0.7785 | 0.5022 | 0.2763 | 3.0132 | 1.1 | 0.49502 | 0.60498 |  | 2026-05-03 18:30 | 4.363 | 4.57 | 1871.7 | 0.76167 | 0.5022 | 0.25947 | 3.0132 | 1.1 | 0.49502 | 0.60498 |  | 2026-05-03 18:30 | 3.952 | 4.236 | 1884.3 | 0.706 | 0.5022 | 0.2038 | 3.0132 | 0.9 | 0.49502 | 0.40498 |  | 2026-05-03 18:30 | 3.836 | 4.02 | 1781.1 | 0.67 | 0.47778 | 0.19222 | 2.8667 | 1 | 0.47095 | 0.52905 |  | 2026-05-03 18:30 | 8.0997 | 5.1984 | 2.9012 | 31.1907 | 11.5 | 5.1241 | 6.3759 | 4 | 98.34%
2026-05-03 18:20 | 23 | 41.9 | 11.601 | 12.005 | 2483 | 2.0008 | 1.4056 | 0.59524 | 8.4336 | 2.7 | 1.3855 | 1.3145 |  | 2026-05-03 18:20 | 14.098 | 14.716 | 2528 | 2.4527 | 1.4056 | 1.0471 | 8.4336 | 3.2 | 1.3855 | 1.8145 |  | 2026-05-03 18:20 | 13.097 | 13.501 | 2499.3 | 2.2502 | 1.4056 | 0.84457 | 8.4336 | 3 | 1.3855 | 1.6145 |  | 2026-05-03 18:20 | 13.641 | 14.062 | 2505.4 | 2.3437 | 1.4056 | 0.93807 | 8.4336 | 3.1 | 1.3855 | 1.7145 |  | 2026-05-03 18:20 | 9.841 | 10.201 | 1880.4 | 1.7002 | 1.0412 | 0.65898 | 6.2471 | 2.3 | 1.0263 | 1.2737 |  | 2026-05-03 18:20 | 9.582 | 9.934 | 1862.6 | 1.6557 | 1.0412 | 0.61448 | 6.2471 | 2.2 | 1.0263 | 1.1737 |  | 2026-05-03 18:20 | 9.606 | 9.962 | 1870.6 | 1.6603 | 1.0412 | 0.61915 | 6.2471 | 2.2 | 1.0263 | 1.1737 |  | 2026-05-03 18:20 | 6.826 | 7.327 | 1883.4 | 1.2212 | 1.0412 | 0.17998 | 6.2471 | 1.5 | 1.0263 | 0.47371 |  | 2026-05-03 18:20 | 7.878 | 8.198 | 1780.1 | 1.3663 | 0.99056 | 0.37578 | 5.9433 | 1.8 | 0.97639 | 0.82361 |  | 2026-05-03 18:20 | 16.651 | 10.7777 | 5.8733 | 64.666 | 22 | 10.6235 | 11.3765 | 5 | 98.45%
2026-05-03 18:10 | 34 | 43.91 | 21.347 | 21.836 | 2480.3 | 3.6393 | 2.0623 | 1.577 | 12.3738 | 4.6 | 2.0328 | 2.5672 |  | 2026-05-03 18:10 | 25.469 | 25.247 | 2524.8 | 4.2078 | 2.0623 | 2.1455 | 12.3738 | 4.9 | 2.0328 | 2.8672 |  | 2026-05-03 18:10 | 23.586 | 24.104 | 2496.3 | 4.0173 | 2.0623 | 1.955 | 12.3738 | 5 | 2.0328 | 2.9672 |  | 2026-05-03 18:10 | 23.766 | 24.305 | 2502.3 | 4.0508 | 2.0623 | 1.9885 | 12.3738 | 4.8 | 2.0328 | 2.7672 |  | 2026-05-03 18:10 | 17.365 | 17.808 | 1878.1 | 2.968 | 1.5276 | 1.4404 | 9.1658 | 3.7 | 1.5058 | 2.1942 |  | 2026-05-03 18:10 | 16.944 | 17.373 | 1860.4 | 2.8955 | 1.5276 | 1.3679 | 9.1658 | 3.6 | 1.5058 | 2.0942 |  | 2026-05-03 18:10 | 17.097 | 17.528 | 1868.4 | 2.9213 | 1.5276 | 1.3937 | 9.1658 | 3.6 | 1.5058 | 2.0942 |  | 2026-05-03 18:10 | 12.121 | 12.639 | 1881.9 | 2.1065 | 1.5276 | 0.57887 | 9.1658 | 2.9 | 1.5058 | 1.3942 |  | 2026-05-03 18:10 | 15.424 | 15.824 | 1778.3 | 2.6373 | 1.4534 | 1.184 | 8.7201 | 3.4 | 1.4326 | 1.9674 |  | 2026-05-03 18:10 | 29.444 | 15.8131 | 13.6309 | 94.8785 | 36.5 | 15.5869 | 20.9131 | 6 | 98.16%
2026-05-03 18:00 | 46 | 46.21 | 34.113 | 34.529 | 2475.7 | 5.7548 | 2.7661 | 2.9887 | 16.5967 | 6.8 | 2.7266 | 4.0734 |  | 2026-05-03 18:00 | 37.131 | 37.777 | 2519.9 | 6.2962 | 2.7661 | 3.53 | 16.5967 | 7.5 | 2.7266 | 4.7734 |  | 2026-05-03 18:00 | 36.462 | 37.085 | 2491.3 | 6.1808 | 2.7661 | 3.4147 | 16.5967 | 7.3 | 2.7266 | 4.5734 |  | 2026-05-03 18:00 | 35.56 | 36.179 | 2497.5 | 6.0298 | 2.7661 | 3.2637 | 16.5967 | 7.3 | 2.7266 | 4.5734 |  | 2026-05-03 18:00 | 27.364 | 27.9 | 1874.4 | 4.65 | 2.049 | 2.601 | 12.2939 | 5.4 | 2.0197 | 3.3803 |  | 2026-05-03 18:00 | 26.317 | 26.86 | 1856.8 | 4.4767 | 2.049 | 2.4277 | 12.2939 | 5.2 | 2.0197 | 3.1803 |  | 2026-05-03 18:00 | 26.457 | 26.991 | 1864.8 | 4.4985 | 2.049 | 2.4495 | 12.2939 | 5.3 | 2.0197 | 3.2803 |  | 2026-05-03 18:00 | 24.132 | 25.018 | 1879 | 4.1697 | 2.049 | 2.1207 | 12.2939 | 5.1 | 2.0197 | 3.0803 |  | 2026-05-03 18:00 | 24.329 | 24.846 | 1774.9 | 4.141 | 1.9493 | 2.1917 | 11.6961 | 4.9 | 1.9215 | 2.9785 |  | 2026-05-03 18:00 | 46.1975 | 21.2097 | 24.9878 | 127.2584 | 54.8 | 20.9064 | 33.8936 | 7 | 98.09%
2026-05-03 17:50 | 162 | 47.64 | 48.398 | 49.17 | 2468.9 | 8.195 | 9.6889 | -1.4939 | 58.1333 | 9.5 | 9.5503 | -0.050332 |  | 2026-05-03 17:50 | 52.361 | 52.359 | 2512.4 | 8.7265 | 9.6889 | -0.96238 | 58.1333 | 10.1 | 9.5503 | 0.54967 |  | 2026-05-03 17:50 | 51.466 | 52.239 | 2484 | 8.7065 | 9.6889 | -0.98238 | 58.1333 | 10 | 9.5503 | 0.44967 |  | 2026-05-03 17:50 | 49.997 | 50.758 | 2490.2 | 8.4597 | 9.6889 | -1.2292 | 58.1333 | 9.7 | 9.5503 | 0.14967 |  | 2026-05-03 17:50 | 38.341 | 38.992 | 1869 | 6.4987 | 7.177 | -0.67828 | 43.0617 | 7.4 | 7.0743 | 0.32568 |  | 2026-05-03 17:50 | 37.166 | 37.805 | 1851.6 | 6.3008 | 7.177 | -0.87612 | 43.0617 | 7.2 | 7.0743 | 0.12568 |  | 2026-05-03 17:50 | 37.469 | 38.109 | 1859.5 | 6.3515 | 7.177 | -0.82545 | 43.0617 | 7.2 | 7.0743 | 0.12568 |  | 2026-05-03 17:50 | 36.931 | 37.958 | 1873.9 | 6.3263 | 7.177 | -0.85062 | 43.0617 | 7.2 | 7.0743 | 0.12568 |  | 2026-05-03 17:50 | 34.745 | 35.339 | 1770 | 5.8898 | 6.828 | -0.93815 | 40.9679 | 6.8 | 6.7303 | 0.06966 |  | 2026-05-03 17:50 | 65.4548 | 74.2913 | -8.8365 | 445.7479 | 75.1 | 73.229 | 1.871 | 8 | 97.1%
2026-05-03 17:40 | 216 | 48.22 | 64.998 | 65.834 | 2459.4 | 10.9723 | 12.89 | -1.9177 | 77.3402 | 12.1 | 12.7057 | -0.6057 |  | 2026-05-03 17:40 | 68.739 | 69.651 | 2502.3 | 11.6085 | 12.89 | -1.2815 | 77.3402 | 12.4 | 12.7057 | -0.3057 |  | 2026-05-03 17:40 | 68.165 | 69.145 | 2474 | 11.5242 | 12.89 | -1.3659 | 77.3402 | 12.6 | 12.7057 | -0.1057 |  | 2026-05-03 17:40 | 67.226 | 68.118 | 2480.5 | 11.353 | 12.89 | -1.537 | 77.3402 | 12.5 | 12.7057 | -0.2057 |  | 2026-05-03 17:40 | 50.339 | 51.106 | 1861.6 | 8.5177 | 9.5482 | -1.0305 | 57.289 | 9.5 | 9.4116 | 0.088369 |  | 2026-05-03 17:40 | 48.965 | 49.711 | 1844.4 | 8.2852 | 9.5482 | -1.263 | 57.289 | 9.3 | 9.4116 | -0.11163 |  | 2026-05-03 17:40 | 49.696 | 50.463 | 1852.3 | 8.4105 | 9.5482 | -1.1377 | 57.289 | 9.4 | 9.4116 | -0.011631 |  | 2026-05-03 17:40 | 49.144 | 50.506 | 1866.7 | 8.4177 | 9.5482 | -1.1305 | 57.289 | 9.3 | 9.4116 | -0.11163 |  | 2026-05-03 17:40 | 46.34 | 47.06 | 1763.2 | 7.8433 | 9.0839 | -1.2406 | 54.5034 | 8.6 | 8.954 | -0.354 |  | 2026-05-03 17:40 | 86.9323 | 98.8367 | -11.9044 | 593.0202 | 95.7 | 97.4233 | -1.7233 | 9 | 98.46%
2026-05-03 17:30 | 263 | 48.5 | 82.385 | 82.967 | 2447.3 | 13.8278 | 15.6781 | -1.8502 | 94.0684 | 15 | 15.4539 | -0.45387 |  | 2026-05-03 17:30 | 86.079 | 86.872 | 2489.9 | 14.4787 | 15.6781 | -1.1994 | 94.0684 | 16 | 15.4539 | 0.54613 |  | 2026-05-03 17:30 | 85.582 | 87.001 | 2461.4 | 14.5002 | 15.6781 | -1.1779 | 94.0684 | 15.7 | 15.4539 | 0.24613 |  | 2026-05-03 17:30 | 84.218 | 85.294 | 2468 | 14.2157 | 15.6781 | -1.4624 | 94.0684 | 15.5 | 15.4539 | 0.046133 |  | 2026-05-03 17:30 | 63.505 | 64.354 | 1852.1 | 10.7257 | 11.6134 | -0.88771 | 69.6803 | 11.5 | 11.4473 | 0.052691 |  | 2026-05-03 17:30 | 62.099 | 62.93 | 1835.1 | 10.4883 | 11.6134 | -1.125 | 69.6803 | 11.2 | 11.4473 | -0.24731 |  | 2026-05-03 17:30 | 61.982 | 62.816 | 1842.9 | 10.4693 | 11.6134 | -1.144 | 69.6803 | 11.5 | 11.4473 | 0.052691 |  | 2026-05-03 17:30 | 62.302 | 64.002 | 1857.4 | 10.667 | 11.6134 | -0.94638 | 69.6803 | 11.5 | 11.4473 | 0.052691 |  | 2026-05-03 17:30 | 58.596 | 59.422 | 1754.6 | 9.9037 | 11.0487 | -1.145 | 66.2922 | 10.8 | 10.8907 | -0.090697 |  | 2026-05-03 17:30 | 109.2763 | 120.2145 | -10.9381 | 721.2868 | 118.7 | 118.4954 | 0.2046
2026-05-03 17:20 | 311 | 48.5 | 99.274 | 100.459 | 2432.3 | 16.7432 | 18.5395 | -1.7963 | 111.2368 | 18.2 | 18.2743 | -0.074345 |  | 2026-05-03 17:20 | 0 | 0 | 2473.9 | 0 | 18.5395 | -18.5395 | 111.2368 | 18.6 | 18.2743 | 0.32566 |  | 2026-05-03 17:20 | 103.096 | 104.83 | 2445.7 | 17.4717 | 18.5395 | -1.0678 | 111.2368 | 18.5 | 18.2743 | 0.22566 |  | 2026-05-03 17:20 | 101.872 | 103.13 | 2452.5 | 17.1883 | 18.5395 | -1.3511 | 111.2368 | 18.6 | 18.2743 | 0.32566 |  | 2026-05-03 17:20 | 76.487 | 77.487 | 1840.6 | 12.9145 | 13.7329 | -0.81843 | 82.3976 | 13.8 | 13.5366 | 0.26345 |  | 2026-05-03 17:20 | 74.833 | 75.796 | 1823.9 | 12.6327 | 13.7329 | -1.1003 | 82.3976 | 13.6 | 13.5366 | 0.063448 |  | 2026-05-03 17:20 | 75.756 | 76.738 | 1831.4 | 12.7897 | 13.7329 | -0.94327 | 82.3976 | 13.5 | 13.5366 | -0.036552 |  | 2026-05-03 17:20 | 75.733 | 77.737 | 1845.9 | 12.9562 | 13.7329 | -0.77677 | 82.3976 | 13.6 | 13.5366 | 0.063448 |  | 2026-05-03 17:20 | 71.124 | 72.068 | 1743.8 | 12.0113 | 13.0652 | -1.0539 | 78.3911 | 12.8 | 12.8784 | -0.078352 |  | 2026-05-03 17:20 | 114.7075 | 142.1548 | -27.4473 | 852.9285 | 141.2 | 140.1219 | 1.0781
2026-05-03 17:10 | 357 | 48.5 | 116.452 | 117.878 | 2414.1 | 19.6463 | 21.2816 | -1.6353 | 127.6898 | 20.7 | 20.9773 | -0.2773 |  | 2026-05-03 17:10 | 121.265 | 122.8 | 2455.3 | 20.4667 | 21.2816 | -0.81496 | 127.6898 | 21.9 | 20.9773 | 0.9227 |  | 2026-05-03 17:10 | 120.231 | 122.304 | 2427.2 | 20.384 | 21.2816 | -0.89763 | 127.6898 | 22 | 20.9773 | 1.0227 |  | 2026-05-03 17:10 | 119.204 | 120.701 | 2433.9 | 20.1168 | 21.2816 | -1.1648 | 127.6898 | 21.3 | 20.9773 | 0.3227 |  | 2026-05-03 17:10 | 89.257 | 90.387 | 1826.8 | 15.0645 | 15.7642 | -0.69967 | 94.585 | 16 | 15.5387 | 0.46126 |  | 2026-05-03 17:10 | 87.347 | 88.464 | 1810.3 | 14.744 | 15.7642 | -1.0202 | 94.585 | 15.6 | 15.5387 | 0.061257 |  | 2026-05-03 17:10 | 88.037 | 89.142 | 1817.9 | 14.857 | 15.7642 | -0.90717 | 94.585 | 15.8 | 15.5387 | 0.26126 |  | 2026-05-03 17:10 | 87.956 | 90.396 | 1832.3 | 15.066 | 15.7642 | -0.69817 | 94.585 | 15.7 | 15.5387 | 0.16126 |  | 2026-05-03 17:10 | 82.912 | 83.97 | 1731 | 13.995 | 14.9977 | -1.0027 | 89.9859 | 14.8 | 14.7832 | 0.016811 |  | 2026-05-03 17:10 | 154.3403 | 163.1809 | -8.8405 | 979.0851 | 163.8 | 160.8474 | 2.9526
2026-05-03 17:00 | 402 | 48.5 | 133.866 | 135.519 | 2393.4 | 22.5865 | 23.9642 | -1.3777 | 143.7851 | 23.4 | 23.6215 | -0.2215 |  | 2026-05-03 17:00 | 138.255 | 140.048 | 2433.4 | 23.3413 | 23.9642 | -0.62285 | 143.7851 | 23.8 | 23.6215 | 0.1785 |  | 2026-05-03 17:00 | 137.214 | 139.732 | 2405.2 | 23.2887 | 23.9642 | -0.67552 | 143.7851 | 24 | 23.6215 | 0.3785 |  | 2026-05-03 17:00 | 136.129 | 137.88 | 2412.6 | 22.98 | 23.9642 | -0.98419 | 143.7851 | 24.1 | 23.6215 | 0.4785 |  | 2026-05-03 17:00 | 102.135 | 103.417 | 1810.8 | 17.2362 | 17.7513 | -0.51508 | 106.5075 | 18.1 | 17.4974 | 0.60259 |  | 2026-05-03 17:00 | 99.908 | 101.195 | 1794.7 | 16.8658 | 17.7513 | -0.88542 | 106.5075 | 17.7 | 17.4974 | 0.20259 |  | 2026-05-03 17:00 | 100.678 | 101.932 | 1802.1 | 16.9887 | 17.7513 | -0.76258 | 106.5075 | 17.8 | 17.4974 | 0.30259 |  | 2026-05-03 17:00 | 100.786 | 103.72 | 1816.6 | 17.2867 | 17.7513 | -0.46458 | 106.5075 | 17.9 | 17.4974 | 0.40259 |  | 2026-05-03 17:00 | 94.994 | 96.156 | 1716.2 | 16.026 | 16.8881 | -0.86212 | 101.3287 | 16.8 | 16.6466 | 0.15338 |  | 2026-05-03 17:00 | 176.5998 | 183.7499 | -7.15 | 1102.4992 | 183.6 | 181.1222 | 2.4778
2026-05-03 16:50 | 446 | 48.5 | 149.814 | 151.71 | 2370 | 25.285 | 26.5871 | -1.3021 | 159.5228 | 56.1 | 26.2069 | 29.8931 |  | 2026-05-03 16:50 | 156.725 | 157.723 | 2409.6 | 26.2872 | 26.5871 | -0.29997 | 159.5228 | 27.7 | 26.2069 | 1.4931 |  | 2026-05-03 16:50 | 153.498 | 156.754 | 2381.2 | 26.1257 | 26.5871 | -0.46147 | 159.5228 | 26.6 | 26.2069 | 0.39306 |  | 2026-05-03 16:50 | 152.684 | 154.664 | 2388.5 | 25.7773 | 26.5871 | -0.8098 | 159.5228 | 26.6 | 26.2069 | 0.39306 |  | 2026-05-03 16:50 | 114.411 | 115.871 | 1792.7 | 19.3118 | 19.6942 | -0.38234 | 118.165 | 19.9 | 19.4125 | 0.48745 |  | 2026-05-03 16:50 | 112.243 | 113.664 | 1777 | 18.944 | 19.6942 | -0.75017 | 118.165 | 19.5 | 19.4125 | 0.087453 |  | 2026-05-03 16:50 | 112.917 | 114.323 | 1784.3 | 19.0538 | 19.6942 | -0.64034 | 118.165 | 19.6 | 19.4125 | 0.18745 |  | 2026-05-03 16:50 | 113.186 | 116.355 | 1798.7 | 19.3925 | 19.6942 | -0.30167 | 118.165 | 19.9 | 19.4125 | 0.48745 |  | 2026-05-03 16:50 | 106.648 | 108.009 | 1699.4 | 18.0015 | 18.7366 | -0.73507 | 112.4194 | 18.9 | 18.4686 | 0.43137 |  | 2026-05-03 16:50 | 198.1788 | 203.8618 | -5.683 | 1223.1708 | 234.8 | 200.9466 | 33.8534
2026-05-03 16:40 | 492 | 48.79 | 167.269 | 169.196 | 2343.2 | 28.1993 | 29.2969 | -1.0975 | 175.7812 | 0 | 28.8779 | -28.8779 |  | 2026-05-03 16:40 | 171.895 | 174.23 | 2381.9 | 29.0383 | 29.2969 | -0.25853 | 175.7812 | 30.1 | 28.8779 | 1.2221 |  | 2026-05-03 16:40 | 169.937 | 173.605 | 2354.6 | 28.9342 | 29.2969 | -0.3627 | 175.7812 | 29.7 | 28.8779 | 0.82208 |  | 2026-05-03 16:40 | 169.572 | 171.84 | 2361.9 | 28.64 | 29.2969 | -0.65687 | 175.7812 | 29.6 | 28.8779 | 0.72208 |  | 2026-05-03 16:40 | 127.063 | 128.71 | 1772.8 | 21.4517 | 21.7014 | -0.24972 | 130.2083 | 22.2 | 21.3911 | 0.80895 |  | 2026-05-03 16:40 | 124.728 | 126.32 | 1757.5 | 21.0533 | 21.7014 | -0.64805 | 130.2083 | 21.8 | 21.3911 | 0.40895 |  | 2026-05-03 16:40 | 125.473 | 127.043 | 1764.7 | 21.1738 | 21.7014 | -0.52755 | 130.2083 | 22 | 21.3911 | 0.60895 |  | 2026-05-03 16:40 | 125.631 | 129.096 | 1778.8 | 21.516 | 21.7014 | -0.18538 | 130.2083 | 21.8 | 21.3911 | 0.40895 |  | 2026-05-03 16:40 | 118.592 | 120.13 | 1680.5 | 20.0217 | 20.6462 | -0.62451 | 123.8771 | 20.8 | 20.3509 | 0.44906 |  | 2026-05-03 16:40 | 220.0283 | 224.6392 | -4.6108 | 1347.8351 | 198 | 221.4268 | -23.4268
2026-05-03 16:30 | 537 | 49.08 | 182.071 | 184.506 | 2313.9 | 30.751 | 31.9411 | -1.1901 | 191.6463 | 30.8 | 31.4843 | -0.6843 |  | 2026-05-03 16:30 | 187.621 | 190.246 | 2351.8 | 31.7077 | 31.9411 | -0.23339 | 191.6463 | 32.6 | 31.4843 | 1.1157 |  | 2026-05-03 16:30 | 185.009 | 188.914 | 2324.9 | 31.4857 | 31.9411 | -0.45539 | 191.6463 | 32.3 | 31.4843 | 0.8157 |  | 2026-05-03 16:30 | 184.787 | 187.335 | 2332.3 | 31.2225 | 31.9411 | -0.71856 | 191.6463 | 32.2 | 31.4843 | 0.7157 |  | 2026-05-03 16:30 | 138.308 | 140.115 | 1750.6 | 23.3525 | 23.66 | -0.30754 | 141.9602 | 24.2 | 23.3217 | 0.8783 |  | 2026-05-03 16:30 | 136.107 | 137.891 | 1735.7 | 22.9818 | 23.66 | -0.67821 | 141.9602 | 23.8 | 23.3217 | 0.4783 |  | 2026-05-03 16:30 | 136.721 | 138.494 | 1742.7 | 23.0823 | 23.66 | -0.57771 | 141.9602 | 23.9 | 23.3217 | 0.5783 |  | 2026-05-03 16:30 | 137.427 | 140.928 | 1757 | 23.488 | 23.66 | -0.17204 | 141.9602 | 24 | 23.3217 | 0.6783 |  | 2026-05-03 16:30 | 129.703 | 131.425 | 1659.7 | 21.9042 | 22.5096 | -0.60543 | 135.0576 | 23 | 22.1877 | 0.81229 |  | 2026-05-03 16:30 | 239.9757 | 244.914 | -4.9383 | 1469.4839 | 246.8 | 241.4117 | 5.3883
2026-05-03 16:20 | 581 | 49.08 | 197.019 | 199.735 | 2283.1 | 33.2892 | 34.5582 | -1.269 | 207.3492 | 35.5 | 34.064 | 1.436 |  | 2026-05-03 16:20 | 202.866 | 205.746 | 2319.2 | 34.291 | 34.5582 | -0.2672 | 207.3492 | 34.6 | 34.064 | 0.53598 |  | 2026-05-03 16:20 | 200.815 | 205.587 | 2292.6 | 34.2645 | 34.5582 | -0.2937 | 207.3492 | 34.7 | 34.064 | 0.63598 |  | 2026-05-03 16:20 | 200.124 | 202.945 | 2300.1 | 33.8242 | 34.5582 | -0.73403 | 207.3492 | 34.6 | 34.064 | 0.53598 |  | 2026-05-03 16:20 | 150.517 | 152.546 | 1726.4 | 25.4243 | 25.5987 | -0.17433 | 153.592 | 26 | 25.2326 | 0.76739 |  | 2026-05-03 16:20 | 147.686 | 149.805 | 1711.9 | 24.9675 | 25.5987 | -0.63117 | 153.592 | 25.6 | 25.2326 | 0.36739 |  | 2026-05-03 16:20 | 148.663 | 150.728 | 1718.8 | 25.1213 | 25.5987 | -0.47733 | 153.592 | 25.7 | 25.2326 | 0.46739 |  | 2026-05-03 16:20 | 149.174 | 153.584 | 1733 | 25.5973 | 25.5987 | -0.0013328 | 153.592 | 25.7 | 25.2326 | 0.46739 |  | 2026-05-03 16:20 | 140.602 | 142.468 | 1636.7 | 23.7447 | 24.354 | -0.60929 | 146.1238 | 24 | 24.0057 | -0.0056987 |  | 2026-05-03 16:20 | 260.524 | 264.9814 | -4.4574 | 1589.8885 | 266.4 | 261.1922 | 5.2078
2026-05-03 16:10 | 624 | 49.08 | 212.21 | 215.179 | 2247.6 | 35.8632 | 37.1159 | -1.2527 | 222.6952 | 36.1 | 36.5851 | -0.48511 |  | 2026-05-03 16:10 | 217.256 | 220.408 | 2284.6 | 36.7347 | 37.1159 | -0.3812 | 222.6952 | 78.5 | 36.5851 | 41.9149 |  | 2026-05-03 16:10 | 214.71 | 220.017 | 2257.9 | 36.6695 | 37.1159 | -0.44636 | 222.6952 | 36.6 | 36.5851 | 0.014894 |  | 2026-05-03 16:10 | 214.562 | 217.631 | 2265.5 | 36.2718 | 37.1159 | -0.84403 | 222.6952 | 37.1 | 36.5851 | 0.51489 |  | 2026-05-03 16:10 | 161.139 | 163.328 | 1700.4 | 27.2213 | 27.4932 | -0.2719 | 164.9594 | 27.9 | 27.1001 | 0.79992 |  | 2026-05-03 16:10 | 158.295 | 160.573 | 1686.3 | 26.7622 | 27.4932 | -0.73107 | 164.9594 | 27.4 | 27.1001 | 0.29992 |  | 2026-05-03 16:10 | 159.297 | 161.756 | 1693.1 | 26.9593 | 27.4932 | -0.5339 | 164.9594 | 27.6 | 27.1001 | 0.49992 |  | 2026-05-03 16:10 | 159.806 | 164.047 | 1707.3 | 27.3412 | 27.4932 | -0.15207 | 164.9594 | 27.7 | 27.1001 | 0.59992 |  | 2026-05-03 16:10 | 150.777 | 152.778 | 1612.7 | 25.463 | 26.1564 | -0.6934 | 156.9384 | 25.7 | 25.7824 | -0.082368 |  | 2026-05-03 16:10 | 279.2862 | 284.5928 | -5.3066 | 1707.5567 | 324.6 | 280.5231 | 44.0769
2026-05-03 16:00 | 665 | 49.08 | 225.232 | 228.476 | 2211.5 | 38.0793 | 39.5546 | -1.4752 | 237.3274 | 37.6 | 38.9889 | -1.3889 | [5 empty] | 0 | 39.5546 | -39.5546 | 237.3274 | 0 | 38.9889 | -38.9889 |  | 2026-05-03 16:00 | 228.323 | 233.837 | 2221.3 | 38.9728 | 39.5546 | -0.58173 | 237.3274 | 39.3 | 38.9889 | 0.31106 |  | 2026-05-03 16:00 | 228.712 | 232.077 | 2228.4 | 38.6795 | 39.5546 | -0.87507 | 237.3274 | 38.7 | 38.9889 | -0.28894 |  | 2026-05-03 16:00 | 171.586 | 173.934 | 1672.5 | 28.989 | 29.2997 | -0.31068 | 175.7981 | 29 | 28.8807 | 0.11931 |  | 2026-05-03 16:00 | 169.009 | 171.524 | 1658.9 | 28.5873 | 29.2997 | -0.71234 | 175.7981 | 29 | 28.8807 | 0.11931 |  | 2026-05-03 16:00 | 169.729 | 172.249 | 1665.5 | 28.7082 | 29.2997 | -0.59151 | 175.7981 | 29.2 | 28.8807 | 0.31931 |  | 2026-05-03 16:00 | 170.537 | 175.48 | 1679.6 | 29.2467 | 29.2997 | -0.053011 | 175.7981 | 29.3 | 28.8807 | 0.41931 |  | 2026-05-03 16:00 | 160.834 | 163.035 | 1587 | 27.1725 | 27.875 | -0.70251 | 167.2501 | 27.6 | 27.4764 | 0.1236 |  | 2026-05-03 16:00 | 258.4353 | 303.292 | -44.8567 | 1819.7519 | 259.7 | 298.9549 | -39.2549
2026-05-03 15:50 | 707 | 49.36 | 238.24 | 241.745 | 2173.9 | 40.2908 | 42.0077 | -1.7169 | 252.0465 | 40.7 | 41.407 | -0.70703 |  | 2026-05-03 15:50 | 245.939 | 249.659 | 2206.1 | 41.6098 | 42.0077 | -0.39791 | 252.0465 | 40 | 41.407 | -1.407 |  | 2026-05-03 15:50 | 241.308 | 247.362 | 2182 | 41.227 | 42.0077 | -0.78074 | 252.0465 | 41.1 | 41.407 | -0.30703 |  | 2026-05-03 15:50 | 241.62 | 245.275 | 2189.7 | 40.8792 | 42.0077 | -1.1286 | 252.0465 | 41.2 | 41.407 | -0.20703 |  | 2026-05-03 15:50 | 181.404 | 183.733 | 1643.5 | 30.6222 | 31.1168 | -0.49468 | 186.7011 | 30.9 | 30.6719 | 0.22812 |  | 2026-05-03 15:50 | 178.516 | 181.406 | 1629.9 | 30.2343 | 31.1168 | -0.88251 | 186.7011 | 30.4 | 30.6719 | -0.27188 |  | 2026-05-03 15:50 | 179.143 | 181.898 | 1636.3 | 30.3163 | 31.1168 | -0.80051 | 186.7011 | 30.5 | 30.6719 | -0.17188 |  | 2026-05-03 15:50 | 179.754 | 185.028 | 1650.3 | 30.838 | 31.1168 | -0.27885 | 186.7011 | 30.6 | 30.6719 | -0.071876 |  | 2026-05-03 15:50 | 170.124 | 172.487 | 1559.4 | 28.7478 | 29.6038 | -0.85599 | 177.623 | 29 | 29.1805 | -0.18049 |  | 2026-05-03 15:50 | 314.7655 | 322.1022 | -7.3367 | 1932.6131 | 314.4 | 317.4961 | -3.0961
2026-05-03 15:40 | 735 | 49.36 | 248.443 | 252.18 | 2133.2 | 42.03 | 43.6714 | -1.6414 | 262.0285 | 42.4 | 43.0469 | -0.64692 |  | 2026-05-03 15:40 | 254.793 | 258.648 | 2166.1 | 43.108 | 43.6714 | -0.56342 | 262.0285 | 43.7 | 43.0469 | 0.65308 |  | 2026-05-03 15:40 | 251.936 | 258.472 | 2140.9 | 43.0787 | 43.6714 | -0.59275 | 262.0285 | 43 | 43.0469 | -0.046916 |  | 2026-05-03 15:40 | 251.69 | 255.549 | 2148.5 | 42.5915 | 43.6714 | -1.0799 | 262.0285 | 43.1 | 43.0469 | 0.053084 |  | 2026-05-03 15:40 | 189.429 | 192.099 | 1612.6 | 32.0165 | 32.3492 | -0.3327 | 194.0952 | 32.3 | 31.8866 | 0.4134 |  | 2026-05-03 15:40 | 186.02 | 189.321 | 1599.5 | 31.5535 | 32.3492 | -0.7957 | 194.0952 | 31.3 | 31.8866 | -0.5866 |  | 2026-05-03 15:40 | 187.02 | 190.137 | 1605.8 | 31.6895 | 32.3492 | -0.6597 | 194.0952 | 31.5 | 31.8866 | -0.3866 |  | 2026-05-03 15:40 | 187.431 | 192.807 | 1619.7 | 32.1345 | 32.3492 | -0.2147 | 194.0952 | 32.1 | 31.8866 | 0.2134 |  | 2026-05-03 15:40 | 176.798 | 179.29 | 1530.4 | 29.8817 | 30.7763 | -0.89459 | 184.6575 | 30.2 | 30.3362 | -0.13615 |  | 2026-05-03 15:40 | 328.0838 | 334.8587 | -6.7749 | 2009.1523 | 329.6 | 330.0702 | -0.47023
2026-05-03 15:30 | 772 | 49.36 | 258.99 | 262.934 | 2090.8 | 43.8223 | 45.8698 | -2.0475 | 275.2191 | 45.3 | 45.2139 | 0.086097 |  | 2026-05-03 15:30 | 267.574 | 269.988 | 2122.4 | 44.998 | 45.8698 | -0.87184 | 275.2191 | 45.2 | 45.2139 | -0.013903 |  | 2026-05-03 15:30 | 262.221 | 268.975 | 2097.9 | 44.8292 | 45.8698 | -1.0407 | 275.2191 | 44.6 | 45.2139 | -0.6139 |  | 2026-05-03 15:30 | 262.392 | 266.523 | 2105.4 | 44.4205 | 45.8698 | -1.4493 | 275.2191 | 44.6 | 45.2139 | -0.6139 |  | 2026-05-03 15:30 | 197.147 | 199.963 | 1580.3 | 33.3272 | 33.9777 | -0.65049 | 203.866 | 34.1 | 33.4918 | 0.60822 |  | 2026-05-03 15:30 | 194.004 | 197.555 | 1568.2 | 32.9258 | 33.9777 | -1.0518 | 203.866 | 33.6 | 33.4918 | 0.10822 |  | 2026-05-03 15:30 | 195.195 | 198.432 | 1574.3 | 33.072 | 33.9777 | -0.90566 | 203.866 | 33.7 | 33.4918 | 0.20822 |  | 2026-05-03 15:30 | 196.056 | 201.417 | 1587.6 | 33.5695 | 33.9777 | -0.40816 | 203.866 | 33.3 | 33.4918 | -0.19178 |  | 2026-05-03 15:30 | 185.228 | 187.877 | 1500.2 | 31.3128 | 32.3255 | -1.0127 | 193.9532 | 31.5 | 31.8633 | -0.36328 |  | 2026-05-03 15:30 | 342.2773 | 351.7155 | -9.4382 | 2110.2933 | 345.9 | 346.686 | -0.78601
2026-05-03 15:20 | 813 | 49.36 | 272.535 | 276.826 | 2045.5 | 46.1377 | 48.3059 | -2.1683 | 289.8356 | 45.5 | 47.6152 | -2.1152 |  | 2026-05-03 15:20 | 278.856 | 283.361 | 2077.2 | 47.2268 | 48.3059 | -1.0791 | 289.8356 | 49.3 | 47.6152 | 1.6848 |  | 2026-05-03 15:20 | 274.758 | 282.399 | 2053.3 | 47.0665 | 48.3059 | -1.2394 | 289.8356 | 46.6 | 47.6152 | -1.0152 |  | 2026-05-03 15:20 | 275.114 | 279.502 | 2060.8 | 46.5837 | 48.3059 | -1.7223 | 289.8356 | 46.7 | 47.6152 | -0.91516 |  | 2026-05-03 15:20 | 207.016 | 210.019 | 1546.2 | 35.0032 | 35.7822 | -0.77901 | 214.693 | 34.6 | 35.2705 | -0.67049 |  | 2026-05-03 15:20 | 203.556 | 207.415 | 1534.6 | 34.5692 | 35.7822 | -1.213 | 214.693 | 33.9 | 35.2705 | -1.3705 |  | 2026-05-03 15:20 | 204.597 | 208.221 | 1540.6 | 34.7035 | 35.7822 | -1.0787 | 214.693 | 34.2 | 35.2705 | -1.0705 |  | 2026-05-03 15:20 | 205.386 | 211.413 | 1554.3 | 35.2355 | 35.7822 | -0.54667 | 214.693 | 34.7 | 35.2705 | -0.57049 |  | 2026-05-03 15:20 | 193.686 | 196.516 | 1468.7 | 32.7527 | 34.0423 | -1.2896 | 204.2538 | 32.7 | 33.5555 | -0.8555 |  | 2026-05-03 15:20 | 359.2787 | 370.3947 | -11.1161 | 2222.3684 | 358.2 | 365.0981 | -6.8981
2026-05-03 15:10 | 837 | 49.08 | 279.131 | 283.554 | 2000 | 47.259 | 49.7852 | -2.5262 | 298.7113 | 47.9 | 49.0733 | -1.1733 |  | 2026-05-03 15:10 | 286.589 | 291.249 | 2027.9 | 48.5415 | 49.7852 | -1.2437 | 298.7113 | 47.8 | 49.0733 | -1.2733 |  | 2026-05-03 15:10 | 282.2 | 289.713 | 2006.7 | 48.2855 | 49.7852 | -1.4997 | 298.7113 | 47.6 | 49.0733 | -1.4733 |  | 2026-05-03 15:10 | 283.086 | 287.689 | 2014.1 | 47.9482 | 49.7852 | -1.8371 | 298.7113 | 47.8 | 49.0733 | -1.2733 |  | 2026-05-03 15:10 | 212.338 | 215.44 | 1511.6 | 35.9067 | 36.8779 | -0.97127 | 221.2676 | 36.4 | 36.3506 | 0.049414 |  | 2026-05-03 15:10 | 208.894 | 212.466 | 1500.7 | 35.411 | 36.8779 | -1.4669 | 221.2676 | 35.9 | 36.3506 | -0.45059 |  | 2026-05-03 15:10 | 209.658 | 213.331 | 1506.4 | 35.5552 | 36.8779 | -1.3228 | 221.2676 | 36 | 36.3506 | -0.35059 |  | 2026-05-03 15:10 | 210.147 | 216.192 | 1519.6 | 36.032 | 36.8779 | -0.84594 | 221.2676 | 35.8 | 36.3506 | -0.55059 |  | 2026-05-03 15:10 | 198.654 | 201.556 | 1436 | 33.5927 | 35.0848 | -1.4921 | 210.5088 | 33.7 | 34.5831 | -0.88308 |  | 2026-05-03 15:10 | 368.5317 | 381.7374 | -13.2058 | 2290.4246 | 368.9 | 376.2786 | -7.3786
2026-05-03 15:00 | 869 | 48.79 | 290.181 | 294.899 | 1952.1 | 49.1498 | 51.7459 | -2.5961 | 310.4753 | 48.3 | 51.0059 | -2.7059 | 0.984 | 2026-05-03 15:00 | 297.083 | 302.006 | 1980.1 | 50.3343 | 51.7459 | -1.4116 | 310.4753 | 49.5 | 51.0059 | -1.5059 | 0.9837 | 2026-05-03 15:00 | 292.872 | 300.778 | 1959.1 | 50.1297 | 51.7459 | -1.6162 | 310.4753 | 49.5 | 51.0059 | -1.5059 | 0.97371 | 2026-05-03 15:00 | 293.512 | 298.357 | 1966.3 | 49.7262 | 51.7459 | -2.0197 | 310.4753 | 49.6 | 51.0059 | -1.4059 | 0.98376 | 2026-05-03 15:00 | 221.141 | 224.395 | 1475.2 | 37.3992 | 38.3303 | -0.93112 | 229.9817 | 36.8 | 37.7822 | -0.98217 | 0.9855 | 2026-05-03 15:00 | 217.4 | 221.04 | 1464.8 | 36.84 | 38.3303 | -1.4903 | 229.9817 | 36.5 | 37.7822 | -1.2822 | 0.98353 | 2026-05-03 15:00 | 218.761 | 222.782 | 1470.4 | 37.1303 | 38.3303 | -1.2 | 229.9817 | 36.8 | 37.7822 | -0.98217 | 0.98195 | 2026-05-03 15:00 | 219.51 | 225.846 | 1483.8 | 37.641 | 38.3303 | -0.68929 | 229.9817 | 36.9 | 37.7822 | -0.88217 | 0.97195 | 2026-05-03 15:00 | 206.894 | 209.959 | 1402.3 | 34.9932 | 36.4665 | -1.4734 | 218.7991 | 34.9 | 35.9451 | -1.0451 | 0.9854 | 2026-05-03 15:00 | 383.3437 | 396.7712 | -13.4276 | 2380.6274 | 378.8 | 391.0974 | -12.2974
2026-05-03 14:50 | 898 | 49.08 | 297.09 | 301.982 | 1903.8 | 50.3303 | 53.4135 | -3.0832 | 320.4812 | 50.1 | 52.6497 | -2.5497 | 0.9838 | 2026-05-03 14:50 | 304.043 | 309.144 | 1930.6 | 51.524 | 53.4135 | -1.8895 | 320.4812 | 51.3 | 52.6497 | -1.3497 | 0.9835 | 2026-05-03 14:50 | 299.13 | 307.454 | 1909.6 | 51.2423 | 53.4135 | -2.1712 | 320.4812 | 51 | 52.6497 | -1.6497 | 0.97293 | 2026-05-03 14:50 | 300.284 | 305.322 | 1916.7 | 50.887 | 53.4135 | -2.5265 | 320.4812 | 51.2 | 52.6497 | -1.4497 | 0.9835 | 2026-05-03 14:50 | 225.786 | 229.224 | 1438.4 | 38.204 | 39.5656 | -1.3616 | 237.3935 | 38.4 | 38.9998 | -0.59979 | 0.985 | 2026-05-03 14:50 | 221.972 | 225.991 | 1428.3 | 37.6652 | 39.5656 | -1.9004 | 237.3935 | 37.4 | 38.9998 | -1.5998 | 0.98222 | 2026-05-03 14:50 | 223.309 | 227.284 | 1433.6 | 37.8807 | 39.5656 | -1.6849 | 237.3935 | 37.6 | 38.9998 | -1.3998 | 0.98251 | 2026-05-03 14:50 | 224.021 | 230.374 | 1446.9 | 38.3957 | 39.5656 | -1.1699 | 237.3935 | 37.8 | 38.9998 | -1.1998 | 0.97242 | 2026-05-03 14:50 | 211.249 | 214.444 | 1367.4 | 35.7407 | 37.6417 | -1.9011 | 225.8505 | 35.6 | 37.1035 | -1.5035 | 0.9851 | 2026-05-03 14:50 | 391.8698 | 409.5582 | -17.6884 | 2457.3492 | 390.4 | 403.7015 | -13.3015
2026-05-03 14:40 | 927 | 49.08 | 306.365 | 311.41 | 1853.7 | 51.9017 | 55.1385 | -3.2368 | 330.8308 | 51.4 | 54.35 | -2.95 | 0.9838 | 2026-05-03 14:40 | 314.029 | 319.33 | 1879.3 | 53.2217 | 55.1385 | -1.9168 | 330.8308 | 52.7 | 54.35 | -1.65 | 0.9834 | 2026-05-03 14:40 | 308.024 | 316.515 | 1858.6 | 52.7525 | 55.1385 | -2.386 | 330.8308 | 51.7 | 54.35 | -2.65 | 0.97317 | 2026-05-03 14:40 | 309.569 | 314.795 | 1865.5 | 52.4658 | 55.1385 | -2.6726 | 330.8308 | 52.1 | 54.35 | -2.25 | 0.9834 | 2026-05-03 14:40 | 232.074 | 235.68 | 1400 | 39.28 | 40.8433 | -1.5633 | 245.0599 | 39.1 | 40.2593 | -1.1593 | 0.9847 | 2026-05-03 14:40 | 228.545 | 232.681 | 1390.9 | 38.7802 | 40.8433 | -2.0631 | 245.0599 | 39.2 | 40.2593 | -1.0593 | 0.98222 | 2026-05-03 14:40 | 229.469 | 233.777 | 1396 | 38.9628 | 40.8433 | -1.8805 | 245.0599 | 38.8 | 40.2593 | -1.4593 | 0.98157 | 2026-05-03 14:40 | 230.531 | 237.225 | 1409.1 | 39.5375 | 40.8433 | -1.3058 | 245.0599 | 39 | 40.2593 | -1.2593 | 0.97178 | 2026-05-03 14:40 | 217.582 | 220.873 | 1331.8 | 36.8122 | 38.8574 | -2.0452 | 233.1441 | 36.7 | 38.3017 | -1.6017 | 0.9851 | 2026-05-03 14:40 | 403.7143 | 422.7845 | -19.0701 | 2536.7068 | 400.7 | 416.7387 | -16.0387
2026-05-03 14:30 | 951 | 48.79 | 313.377 | 318.634 | 1802.3 | 53.1057 | 56.6287 | -3.523 | 339.7722 | 52.7 | 55.8189 | -3.1189 | 0.9835 | 2026-05-03 14:30 | 322.393 | 326.296 | 1826.6 | 54.3827 | 56.6287 | -2.246 | 339.7722 | 54.8 | 55.8189 | -1.0189 | 0.98804 | 2026-05-03 14:30 | 315.291 | 324.131 | 1806.9 | 54.0218 | 56.6287 | -2.6069 | 339.7722 | 53.2 | 55.8189 | -2.6189 | 0.97273 | 2026-05-03 14:30 | 316.968 | 322.384 | 1813.4 | 53.7307 | 56.6287 | -2.898 | 339.7722 | 53.4 | 55.8189 | -2.4189 | 0.9832 | 2026-05-03 14:30 | 238.161 | 241.837 | 1360.9 | 40.3062 | 41.9472 | -1.641 | 251.6831 | 40.1 | 41.3473 | -1.2473 | 0.9848 | 2026-05-03 14:30 | 234.445 | 238.739 | 1351.7 | 39.7898 | 41.9472 | -2.1574 | 251.6831 | 38.9 | 41.3473 | -2.4473 | 0.98201 | 2026-05-03 14:30 | 235.825 | 240.363 | 1357.2 | 40.0605 | 41.9472 | -1.8867 | 251.6831 | 39.7 | 41.3473 | -1.6473 | 0.98112 | 2026-05-03 14:30 | 236.746 | 243.959 | 1370.1 | 40.6598 | 41.9472 | -1.2874 | 251.6831 | 39.9 | 41.3473 | -1.4473 | 0.97043 | 2026-05-03 14:30 | 223.036 | 226.443 | 1295.1 | 37.7405 | 39.9076 | -2.1671 | 239.4453 | 37.6 | 39.3369 | -1.7369 | 0.98495 | 2026-05-03 14:30 | 413.7977 | 434.2111 | -20.4134 | 2605.2666 | 410.3 | 428.0019 | -17.7019
2026-05-03 14:20 | 974 | 49.08 | 320.631 | 326.11 | 1749.6 | 54.3517 | 57.9341 | -3.5824 | 347.6043 | 53.1 | 57.1056 | -4.0056 | 0.9832 | 2026-05-03 14:20 | 328.292 | 333.969 | 1771.8 | 55.6615 | 57.9341 | -2.2726 | 347.6043 | 55.2 | 57.1056 | -1.9056 | 0.983 | 2026-05-03 14:20 | 322.986 | 332.385 | 1753.7 | 55.3975 | 57.9341 | -2.5366 | 347.6043 | 54.3 | 57.1056 | -2.8056 | 0.97172 | 2026-05-03 14:20 | 323.746 | 329.378 | 1760 | 54.8963 | 57.9341 | -3.0377 | 347.6043 | 54.5 | 57.1056 | -2.6056 | 0.9829 | 2026-05-03 14:20 | 243.998 | 247.814 | 1320.8 | 41.3023 | 42.9141 | -1.6118 | 257.4847 | 41.1 | 42.3004 | -1.2004 | 0.9846 | 2026-05-03 14:20 | 240.214 | 244.863 | 1312.8 | 40.8105 | 42.9141 | -2.1036 | 257.4847 | 40.4 | 42.3004 | -1.9004 | 0.98101 | 2026-05-03 14:20 | 241.622 | 246.639 | 1317.5 | 41.1065 | 42.9141 | -1.8076 | 257.4847 | 40.7 | 42.3004 | -1.6004 | 0.97966 | 2026-05-03 14:20 | 242.944 | 250.21 | 1330.2 | 41.7017 | 42.9141 | -1.2124 | 257.4847 | 40.9 | 42.3004 | -1.4004 | 0.97096 | 2026-05-03 14:20 | 228.833 | 232.412 | 1257.5 | 38.7353 | 40.8275 | -2.0921 | 244.9648 | 38.5 | 40.2436 | -1.7436 | 0.9846 | 2026-05-03 14:20 | 423.9633 | 444.2201 | -20.2568 | 2665.3209 | 418.7 | 437.8678 | -19.1678
2026-05-03 14:10 | 997 | 48.79 | 326.61 | 331.638 | 1696.5 | 55.273 | 59.3678 | -4.0948 | 356.207 | 57.7 | 58.5189 | -0.81888 | 0.98484 | 2026-05-03 14:10 | 334.846 | 340.741 | 1716.6 | 56.7902 | 59.3678 | -2.5777 | 356.207 | 54.8 | 58.5189 | -3.7189 | 0.9827 | 2026-05-03 14:10 | 328.738 | 338.243 | 1699.4 | 56.3738 | 59.3678 | -2.994 | 356.207 | 54.5 | 58.5189 | -4.0189 | 0.9719 | 2026-05-03 14:10 | 330.7 | 336.569 | 1705.5 | 56.0948 | 59.3678 | -3.273 | 356.207 | 54.8 | 58.5189 | -3.7189 | 0.98256 | 2026-05-03 14:10 | 248.134 | 252.066 | 1279.7 | 42.011 | 43.9762 | -1.9652 | 263.8571 | 41.8 | 43.3473 | -1.5473 | 0.9844 | 2026-05-03 14:10 | 244.919 | 249.426 | 1272.4 | 41.571 | 43.9762 | -2.4052 | 263.8571 | 41.2 | 43.3473 | -2.1473 | 0.98193 | 2026-05-03 14:10 | 245.452 | 250.43 | 1276.8 | 41.7383 | 43.9762 | -2.2378 | 263.8571 | 41.3 | 43.3473 | -2.0473 | 0.98012 | 2026-05-03 14:10 | 246.764 | 253.98 | 1289.3 | 42.33 | 43.9762 | -1.6462 | 263.8571 | 41.6 | 43.3473 | -1.7473 | 0.97159 | 2026-05-03 14:10 | 232.996 | 236.64 | 1219 | 39.44 | 41.8379 | -2.3979 | 251.0273 | 39.3 | 41.2396 | -1.9396 | 0.9846 | 2026-05-03 14:10 | 431.6222 | 455.214 | -23.5918 | 2731.2837 | 427 | 448.7044 | -21.7044
2026-05-03 14:00 | 1007 | 48.79 | 328.611 | 333.8 | 1638.8 | 55.6333 | 59.9633 | -4.33 | 359.7798 | 54 | 59.1058 | -5.1058 | 0.98445 | 2026-05-03 14:00 | 336.601 | 342.475 | 1661.8 | 57.0792 | 59.9633 | -2.8841 | 359.7798 | 59.7 | 59.1058 | 0.59417 | 0.98285 | 2026-05-03 14:00 | 330.717 | 340.39 | 1644.9 | 56.7317 | 59.9633 | -3.2316 | 359.7798 | 55.8 | 59.1058 | -3.3058 | 0.97158 | 2026-05-03 14:00 | 333.083 | 338.912 | 1650.7 | 56.4853 | 59.9633 | -3.478 | 359.7798 | 56 | 59.1058 | -3.1058 | 0.9828 | 2026-05-03 14:00 | 249.926 | 253.861 | 1237.9 | 42.3102 | 44.4173 | -2.1071 | 266.5036 | 41.7 | 43.7821 | -2.0821 | 0.9845 | 2026-05-03 14:00 | 246.289 | 251.178 | 1231.2 | 41.863 | 44.4173 | -2.5543 | 266.5036 | 41 | 43.7821 | -2.7821 | 0.98054 | 2026-05-03 14:00 | 247.807 | 252.951 | 1235.5 | 42.1585 | 44.4173 | -2.2588 | 266.5036 | 41.8 | 43.7821 | -1.9821 | 0.97966 | 2026-05-03 14:00 | 249.149 | 256.349 | 1247.7 | 42.7248 | 44.4173 | -1.6924 | 266.5036 | 41.9 | 43.7821 | -1.8821 | 0.97191 | 2026-05-03 14:00 | 235.193 | 238.872 | 1179.7 | 39.812 | 42.2575 | -2.4455 | 253.5451 | 39.6 | 41.6532 | -2.0532 | 0.9846 | 2026-05-03 14:00 | 434.798 | 459.7798 | -24.9818 | 2758.6787 | 431.5 | 453.2049 | -21.7049
2026-05-03 13:50 | 1030 | 48.5 | 334.811 | 340.636 | 1584.8 | 56.7727 | 61.4008 | -4.6281 | 368.4047 | 55.1 | 60.5227 | -5.4227 | 0.9829 | 2026-05-03 13:50 | 338.148 | 339.932 | 1602.1 | 56.6553 | 61.4008 | -4.7454 | 368.4047 | 52.8 | 60.5227 | -7.7227 | 0.99475 | 2026-05-03 13:50 | 324.413 | 334.366 | 1589.1 | 55.7277 | 61.4008 | -5.6731 | 368.4047 | 56.1 | 60.5227 | -4.4227 | 0.97023 | 2026-05-03 13:50 | 332.398 | 337.872 | 1594.7 | 56.312 | 61.4008 | -5.0888 | 368.4047 | 55.6 | 60.5227 | -4.9227 | 0.9838 | 2026-05-03 13:50 | 255.061 | 259.156 | 1196.2 | 43.1927 | 45.4821 | -2.2894 | 272.8924 | 42.5 | 44.8317 | -2.3317 | 0.9842 | 2026-05-03 13:50 | 251.489 | 256.651 | 1190.2 | 42.7752 | 45.4821 | -2.7069 | 272.8924 | 42 | 44.8317 | -2.8317 | 0.97989 | 2026-05-03 13:50 | 252.635 | 257.731 | 1193.7 | 42.9552 | 45.4821 | -2.5269 | 272.8924 | 42.2 | 44.8317 | -2.6317 | 0.98023 | 2026-05-03 13:50 | 253.377 | 260.905 | 1205.8 | 43.4842 | 45.4821 | -1.9979 | 272.8924 | 42.4 | 44.8317 | -2.4317 | 0.97115 | 2026-05-03 13:50 | 239.307 | 243.149 | 1140.1 | 40.5248 | 43.2705 | -2.7457 | 259.6233 | 40 | 42.6518 | -2.6518 | 0.9842 | 2026-05-03 13:50 | 438.3997 | 470.8019 | -32.4022 | 2824.8114 | 428.7 | 464.0694 | -35.3694
2026-05-03 13:40 | 1034 | 48.5 | 337.017 | 343.151 | 1529.7 | 57.1918 | 61.6392 | -4.4474 | 369.8354 | 56.3 | 60.7578 | -4.4578 | 0.98212 | 2026-05-03 13:40 | 330.586 | 335.859 | 1549.3 | 55.9765 | 61.6392 | -5.6627 | 369.8354 | 55.3 | 60.7578 | -5.4578 | 0.9843 | 2026-05-03 13:40 | 329.355 | 339.281 | 1533 | 56.5468 | 61.6392 | -5.0924 | 369.8354 | 55.8 | 60.7578 | -4.9578 | 0.97074 | 2026-05-03 13:40 | 335.617 | 341.178 | 1539.1 | 56.863 | 61.6392 | -4.7762 | 369.8354 | 55.6 | 60.7578 | -5.1578 | 0.9837 | 2026-05-03 13:40 | 255.976 | 260.039 | 1153.7 | 43.3398 | 45.6587 | -2.3189 | 273.9521 | 42.7 | 45.0058 | -2.3058 | 0.98438 | 2026-05-03 13:40 | 252.201 | 257.144 | 1148.2 | 42.8573 | 45.6587 | -2.8014 | 273.9521 | 42.1 | 45.0058 | -2.9058 | 0.98078 | 2026-05-03 13:40 | 253.999 | 258.955 | 1151.5 | 43.1592 | 45.6587 | -2.4995 | 273.9521 | 41.9 | 45.0058 | -3.1058 | 0.98086 | 2026-05-03 13:40 | 255.002 | 262.445 | 1163.4 | 43.7408 | 45.6587 | -1.9179 | 273.9521 | 42.5 | 45.0058 | -2.5058 | 0.97164 | 2026-05-03 13:40 | 240.71 | 244.525 | 1100.1 | 40.7542 | 43.4386 | -2.6844 | 260.6315 | 40.2 | 42.8174 | -2.6174 | 0.9844 | 2026-05-03 13:40 | 440.4295 | 472.6303 | -32.2008 | 2835.7816 | 432.4 | 465.8717 | -33.4717
2026-05-03 13:30 | 1038 | 48.79 | 337.246 | 343.133 | 1473.4 | 57.1888 | 61.8092 | -4.6204 | 370.8555 | 56.6 | 60.9254 | -4.3254 | 0.98284 | 2026-05-03 13:30 | 332.156 | 337.557 | 1494 | 56.2595 | 61.8092 | -5.5497 | 370.8555 | 56.6 | 60.9254 | -4.3254 | 0.984 | 2026-05-03 13:30 | 338.722 | 348.518 | 1477.2 | 58.0863 | 61.8092 | -3.7229 | 370.8555 | 56 | 60.9254 | -4.9254 | 0.97189 | 2026-05-03 13:30 | 335.12 | 340.777 | 1483.5 | 56.7962 | 61.8092 | -5.0131 | 370.8555 | 55.6 | 60.9254 | -5.3254 | 0.9834 | 2026-05-03 13:30 | 256.415 | 260.584 | 1111 | 43.4307 | 45.7846 | -2.354 | 274.7078 | 42.9 | 45.1299 | -2.2299 | 0.984 | 2026-05-03 13:30 | 252.04 | 257.015 | 1106.1 | 42.8358 | 45.7846 | -2.9488 | 274.7078 | 42.2 | 45.1299 | -2.9299 | 0.98064 | 2026-05-03 13:30 | 253.983 | 259.387 | 1109.6 | 43.2312 | 45.7846 | -2.5535 | 274.7078 | 42.5 | 45.1299 | -2.6299 | 0.97917 | 2026-05-03 13:30 | 255.013 | 262.532 | 1120.9 | 43.7553 | 45.7846 | -2.0293 | 274.7078 | 42.2 | 45.1299 | -2.9299 | 0.97136 | 2026-05-03 13:30 | 240.183 | 244.064 | 1059.9 | 40.6773 | 43.5584 | -2.8811 | 261.3504 | 39.6 | 42.9355 | -3.3355 | 0.9841 | 2026-05-03 13:30 | 442.2612 | 473.9339 | -31.6727 | 2843.6033 | 434.2 | 467.1566 | -32.9566
2026-05-03 13:20 | 1048 | 49.36 | 337.786 | 343.803 | 1416.8 | 57.3005 | 62.2689 | -4.9684 | 373.6134 | 55.8 | 61.3785 | -5.5785 | 0.9825 | 2026-05-03 13:20 | 332.485 | 338.458 | 1437.4 | 56.4097 | 62.2689 | -5.8592 | 373.6134 | 55 | 61.3785 | -6.3785 | 0.98235 | 2026-05-03 13:20 | 330.912 | 341.056 | 1421.2 | 56.8427 | 62.2689 | -5.4262 | 373.6134 | 55.6 | 61.3785 | -5.7785 | 0.97026 | 2026-05-03 13:20 | 334.386 | 340.031 | 1427.9 | 56.6718 | 62.2689 | -5.5971 | 373.6134 | 55.5 | 61.3785 | -5.8785 | 0.9834 | 2026-05-03 13:20 | 254.622 | 258.867 | 1068.1 | 43.1445 | 46.1251 | -2.9806 | 276.7507 | 42.1 | 45.4655 | -3.3655 | 0.9836 | 2026-05-03 13:20 | 251.275 | 256.16 | 1063.9 | 42.6933 | 46.1251 | -3.4318 | 276.7507 | 41.7 | 45.4655 | -3.7655 | 0.98093 | 2026-05-03 13:20 | 252.6 | 258.154 | 1067.1 | 43.0257 | 46.1251 | -3.0994 | 276.7507 | 41.7 | 45.4655 | -3.7655 | 0.97849 | 2026-05-03 13:20 | 254.392 | 262.379 | 1078.7 | 43.7298 | 46.1251 | -2.3953 | 276.7507 | 42.7 | 45.4655 | -2.7655 | 0.96956 | 2026-05-03 13:20 | 239.561 | 243.506 | 1020.3 | 40.5843 | 43.8823 | -3.298 | 263.294 | 40.4 | 43.2548 | -2.8548 | 0.9838 | 2026-05-03 13:20 | 440.4023 | 477.4584 | -37.0561 | 2864.7505 | 430.5 | 470.6308 | -40.1308
2026-05-03 13:10 | 1049 | 49.08 | 336.885 | 342.886 | 1361 | 57.1477 | 62.3951 | -5.2474 | 374.3706 | 55.6 | 61.5028 | -5.9028 | 0.9825 | 2026-05-03 13:10 | 335.867 | 331.653 | 1382.4 | 55.2755 | 62.3951 | -7.1196 | 374.3706 | 56.7 | 61.5028 | -4.8028 | 1.0127 | 2026-05-03 13:10 | 337.823 | 348.741 | 1365.6 | 58.1235 | 62.3951 | -4.2716 | 374.3706 | 56.2 | 61.5028 | -5.3028 | 0.96869 | 2026-05-03 13:10 | 340.977 | 347.156 | 1372.4 | 57.8593 | 62.3951 | -4.5358 | 374.3706 | 56.4 | 61.5028 | -5.1028 | 0.9822 | 2026-05-03 13:10 | 255.541 | 259.775 | 1026 | 43.2958 | 46.2186 | -2.9228 | 277.3115 | 42.6 | 45.5577 | -2.9577 | 0.9837 | 2026-05-03 13:10 | 252.725 | 258.037 | 1022.2 | 43.0062 | 46.2186 | -3.2124 | 277.3115 | 42.7 | 45.5577 | -2.8577 | 0.97941 | 2026-05-03 13:10 | 253.139 | 258.789 | 1025.4 | 43.1315 | 46.2186 | -3.0871 | 277.3115 | 42.9 | 45.5577 | -2.6577 | 0.97817 | 2026-05-03 13:10 | 255.395 | 263.38 | 1036 | 43.8967 | 46.2186 | -2.3219 | 277.3115 | 42.6 | 45.5577 | -2.9577 | 0.96968 | 2026-05-03 13:10 | 241.266 | 245.264 | 979.9 | 40.8773 | 43.9713 | -3.0939 | 263.8276 | 40.2 | 43.3425 | -3.1425 | 0.9837 | 2026-05-03 13:10 | 442.6135 | 478.426 | -35.8125 | 2870.5561 | 435.9 | 471.5845 | -35.6845
2026-05-03 13:00 | 1058 | 48.79 | 340.92 | 346.992 | 1305.4 | 57.832 | 63.0002 | -5.1682 | 378.001 | 55.9 | 62.0993 | -6.1993 | 0.9825 | 2026-05-03 13:00 | 340.997 | 339.942 | 1325.7 | 56.657 | 63.0002 | -6.3432 | 378.001 | 57.7 | 62.0993 | -4.3993 | 1.0031 | 2026-05-03 13:00 | 341.314 | 351.687 | 1309.4 | 58.6145 | 63.0002 | -4.3857 | 378.001 | 56.6 | 62.0993 | -5.4993 | 0.97051 | 2026-05-03 13:00 | 343.519 | 349.78 | 1316 | 58.2967 | 63.0002 | -4.7035 | 378.001 | 57 | 62.0993 | -5.0993 | 0.9821 | 2026-05-03 13:00 | 256.71 | 260.99 | 983.4 | 43.4983 | 46.6668 | -3.1685 | 280.0008 | 43.4 | 45.9995 | -2.5995 | 0.9836 | 2026-05-03 13:00 | 253.726 | 258.863 | 979.5 | 43.1438 | 46.6668 | -3.523 | 280.0008 | 42.3 | 45.9995 | -3.6995 | 0.98016 | 2026-05-03 13:00 | 254.313 | 259.633 | 982.5 | 43.2722 | 46.6668 | -3.3946 | 280.0008 | 42.4 | 45.9995 | -3.5995 | 0.97951 | 2026-05-03 13:00 | 256.07 | 263.999 | 993.4 | 43.9998 | 46.6668 | -2.667 | 280.0008 | 42.8 | 45.9995 | -3.1995 | 0.96997 | 2026-05-03 13:00 | 241.556 | 245.559 | 939.7 | 40.9265 | 44.3977 | -3.4712 | 266.3861 | 40.3 | 43.7628 | -3.4628 | 0.9837 | 2026-05-03 13:00 | 446.2408 | 483.0656 | -36.8247 | 2898.3934 | 438.4 | 476.1577 | -37.7577
2026-05-03 12:50 | 1066 | 48.79 | 342.416 | 348.406 | 1249.5 | 58.0677 | 63.4765 | -5.4089 | 380.8593 | 57.2 | 62.5688 | -5.3688 | 0.98281 | 2026-05-03 12:50 | 338.134 | 343.772 | 1268 | 57.2953 | 63.4765 | -6.1812 | 380.8593 | 55.4 | 62.5688 | -7.1688 | 0.9836 | 2026-05-03 12:50 | 342.326 | 352.903 | 1252.8 | 58.8172 | 63.4765 | -4.6594 | 380.8593 | 56.4 | 62.5688 | -6.1688 | 0.97003 | 2026-05-03 12:50 | 341.863 | 347.669 | 1259 | 57.9448 | 63.4765 | -5.5317 | 380.8593 | 55.8 | 62.5688 | -6.7688 | 0.9833 | 2026-05-03 12:50 | 257.612 | 261.907 | 940 | 43.6512 | 47.0197 | -3.3685 | 282.118 | 43.1 | 46.3473 | -3.2473 | 0.9836 | 2026-05-03 12:50 | 255.888 | 261.216 | 937.2 | 43.536 | 47.0197 | -3.4837 | 282.118 | 42.8 | 46.3473 | -3.5473 | 0.9796 | 2026-05-03 12:50 | 255.772 | 261.124 | 940.1 | 43.5207 | 47.0197 | -3.499 | 282.118 | 42.7 | 46.3473 | -3.6473 | 0.9795 | 2026-05-03 12:50 | 258.42 | 266.329 | 950.6 | 44.3882 | 47.0197 | -2.6315 | 282.118 | 43.5 | 46.3473 | -2.8473 | 0.9703 | 2026-05-03 12:50 | 244.252 | 248.299 | 899.4 | 41.3832 | 44.7334 | -3.3502 | 268.4003 | 41.8 | 44.0937 | -2.2937 | 0.9837 | 2026-05-03 12:50 | 448.6042 | 486.7182 | -38.1141 | 2920.3094 | 438.7 | 479.7582 | -41.0582
2026-05-03 12:40 | 1068 | 49.08 | 336.031 | 341.495 | 1192.3 | 56.9158 | 63.5252 | -6.6094 | 381.1514 | 56.8 | 62.6168 | -5.8168 | 0.984 | 2026-05-03 12:40 | 336.561 | 345.616 | 1212.6 | 57.6027 | 63.5252 | -5.9226 | 381.1514 | 55.1 | 62.6168 | -7.5168 | 0.9738 | 2026-05-03 12:40 | 337.442 | 347.919 | 1196.4 | 57.9865 | 63.5252 | -5.5387 | 381.1514 | 55.7 | 62.6168 | -6.9168 | 0.96989 | 2026-05-03 12:40 | 335.346 | 340.66 | 1203.2 | 56.7767 | 63.5252 | -6.7486 | 381.1514 | 56 | 62.6168 | -6.6168 | 0.9844 | 2026-05-03 12:40 | 259.438 | 263.737 | 896.9 | 43.9562 | 47.0557 | -3.0996 | 282.3343 | 43.7 | 46.3828 | -2.6828 | 0.9837 | 2026-05-03 12:40 | 257.34 | 262.582 | 894.4 | 43.7637 | 47.0557 | -3.2921 | 282.3343 | 42.8 | 46.3828 | -3.5828 | 0.98004 | 2026-05-03 12:40 | 257.286 | 262.661 | 897.4 | 43.7768 | 47.0557 | -3.2789 | 282.3343 | 42.9 | 46.3828 | -3.4828 | 0.97954 | 2026-05-03 12:40 | 259.065 | 266.864 | 907.1 | 44.4773 | 47.0557 | -2.5784 | 282.3343 | 42.8 | 46.3828 | -3.5828 | 0.97078 | 2026-05-03 12:40 | 245.387 | 249.428 | 857.6 | 41.5713 | 44.7677 | -3.1964 | 268.6062 | 39.9 | 44.1275 | -4.2275 | 0.9838 | 2026-05-03 12:40 | 446.827 | 487.0915 | -40.2645 | 2922.549 | 435.7 | 480.1261 | -44.4261
2026-05-03 12:30 | 1064 | 49.08 | 342.629 | 348.803 | 1135.5 | 58.1338 | 63.2873 | -5.1535 | 379.7238 | 56 | 62.3823 | -6.3823 | 0.9823 | 2026-05-03 12:30 | 342.379 | 348.123 | 1157.5 | 58.0205 | 63.2873 | -5.2668 | 379.7238 | 59 | 62.3823 | -3.3823 | 0.9835 | 2026-05-03 12:30 | 333.881 | 344.152 | 1140.7 | 57.3587 | 63.2873 | -5.9286 | 379.7238 | 57.1 | 62.3823 | -5.2823 | 0.97016 | 2026-05-03 12:30 | 337.46 | 342.982 | 1147.2 | 57.1637 | 63.2873 | -6.1236 | 379.7238 | 56.1 | 62.3823 | -6.2823 | 0.9839 | 2026-05-03 12:30 | 258.555 | 262.873 | 853.2 | 43.8122 | 46.8795 | -3.0673 | 281.2769 | 42.3 | 46.2091 | -3.9091 | 0.98357 | 2026-05-03 12:30 | 256.708 | 261.863 | 851.6 | 43.6438 | 46.8795 | -3.2357 | 281.2769 | 42.6 | 46.2091 | -3.6091 | 0.98031 | 2026-05-03 12:30 | 257.556 | 263.042 | 854.5 | 43.8403 | 46.8795 | -3.0392 | 281.2769 | 42.6 | 46.2091 | -3.6091 | 0.97914 | 2026-05-03 12:30 | 259.885 | 267.837 | 864.3 | 44.6395 | 46.8795 | -2.24 | 281.2769 | 43 | 46.2091 | -3.2091 | 0.97031 | 2026-05-03 12:30 | 245.568 | 249.637 | 817.7 | 41.6062 | 44.6 | -2.9939 | 267.6001 | 40.7 | 43.9622 | -3.2622 | 0.9837 | 2026-05-03 12:30 | 448.2187 | 485.2672 | -37.0485 | 2911.6031 | 439.4 | 478.3279 | -38.9279
2026-05-03 12:20 | 1060 | 49.08 | 341.223 | 347.336 | 1079.5 | 57.8893 | 63.0494 | -5.16 | 378.2963 | 58.6 | 62.1478 | -3.5478 | 0.9824 | 2026-05-03 12:20 | 342.12 | 347.895 | 1098.5 | 57.9825 | 63.0494 | -5.0669 | 378.2963 | 56.1 | 62.1478 | -6.0478 | 0.9834 | 2026-05-03 12:20 | 340.806 | 351.169 | 1083.6 | 58.5282 | 63.0494 | -4.5212 | 378.2963 | 56 | 62.1478 | -6.1478 | 0.97049 | 2026-05-03 12:20 | 336.824 | 342.37 | 1091.1 | 57.0617 | 63.0494 | -5.9877 | 378.2963 | 55.7 | 62.1478 | -6.4478 | 0.9838 | 2026-05-03 12:20 | 257.389 | 261.681 | 810.9 | 43.6135 | 46.7032 | -3.0897 | 280.2195 | 42.4 | 46.0354 | -3.6354 | 0.9836 | 2026-05-03 12:20 | 256.307 | 261.528 | 809 | 43.588 | 46.7032 | -3.1152 | 280.2195 | 42.2 | 46.0354 | -3.8354 | 0.98004 | 2026-05-03 12:20 | 255.96 | 261.227 | 811.9 | 43.5378 | 46.7032 | -3.1654 | 280.2195 | 42.8 | 46.0354 | -3.2354 | 0.97984 | 2026-05-03 12:20 | 258.105 | 265.823 | 821.3 | 44.3038 | 46.7032 | -2.3994 | 280.2195 | 43.1 | 46.0354 | -2.9354 | 0.97097 | 2026-05-03 12:20 | 244.469 | 248.469 | 777 | 41.4115 | 44.4324 | -3.0209 | 266.5941 | 40.7 | 43.797 | -3.097 | 0.9839 | 2026-05-03 12:20 | 447.9163 | 483.4429 | -35.5265 | 2900.6572 | 437.6 | 476.5296 | -38.9296
2026-05-03 12:10 | 1052 | 49.65 | 339.335 | 345.494 | 1020.9 | 57.5823 | 62.4372 | -4.8549 | 374.6233 | 54.7 | 61.5444 | -6.8444 | 0.98217 | 2026-05-03 12:10 | 339.531 | 348.828 | 1042.4 | 58.138 | 62.4372 | -4.2992 | 374.6233 | 55.8 | 61.5444 | -5.7444 | 0.97335 | 2026-05-03 12:10 | 340.038 | 349.972 | 1027.6 | 58.3287 | 62.4372 | -4.1085 | 374.6233 | 56.4 | 61.5444 | -5.1444 | 0.97161 | 2026-05-03 12:10 | 334.321 | 339.792 | 1035.4 | 56.632 | 62.4372 | -5.8052 | 374.6233 | 56.7 | 61.5444 | -4.8444 | 0.9839 | 2026-05-03 12:10 | 256.148 | 260.366 | 768.5 | 43.3943 | 46.2498 | -2.8555 | 277.4987 | 42.5 | 45.5884 | -3.0884 | 0.9838 | 2026-05-03 12:10 | 254.406 | 259.458 | 766.8 | 43.243 | 46.2498 | -3.0068 | 277.4987 | 42.1 | 45.5884 | -3.4884 | 0.98053 | 2026-05-03 12:10 | 254.82 | 259.649 | 769.1 | 43.2748 | 46.2498 | -2.975 | 277.4987 | 41.6 | 45.5884 | -3.9884 | 0.9814 | 2026-05-03 12:10 | 256.301 | 263.934 | 778.2 | 43.989 | 46.2498 | -2.2608 | 277.4987 | 42.6 | 45.5884 | -2.9884 | 0.97108 | 2026-05-03 12:10 | 241.945 | 245.879 | 736.3 | 40.9798 | 44.0009 | -3.0211 | 264.0057 | 40.2 | 43.3717 | -3.1717 | 0.984 | 2026-05-03 12:10 | 445.562 | 478.749 | -33.187 | 2872.4937 | 432.6 | 471.9028 | -39.3028
2026-05-03 12:00 | 1042 | 49.36 | 336.012 | 342.101 | 966.2 | 57.0168 | 61.9124 | -4.8956 | 371.4744 | 56.2 | 61.0271 | -4.8271 | 0.9822 | 2026-05-03 12:00 | 344.4 | 350.677 | 986.6 | 58.4462 | 61.9124 | -3.4662 | 371.4744 | 56.1 | 61.0271 | -4.9271 | 0.9821 | 2026-05-03 12:00 | 336.799 | 346.976 | 971.2 | 57.8293 | 61.9124 | -4.0831 | 371.4744 | 55.6 | 61.0271 | -5.4271 | 0.97067 | 2026-05-03 12:00 | 340.496 | 346.667 | 978.7 | 57.7778 | 61.9124 | -4.1346 | 371.4744 | 56.5 | 61.0271 | -4.5271 | 0.9822 | 2026-05-03 12:00 | 253.786 | 257.999 | 726 | 42.9998 | 45.861 | -2.8612 | 275.1662 | 42.3 | 45.2052 | -2.9052 | 0.98367 | 2026-05-03 12:00 | 252.102 | 256.978 | 724.7 | 42.8297 | 45.861 | -3.0314 | 275.1662 | 42.1 | 45.2052 | -3.1052 | 0.98103 | 2026-05-03 12:00 | 252.8 | 258.301 | 727.5 | 43.0502 | 45.861 | -2.8109 | 275.1662 | 42.2 | 45.2052 | -3.0052 | 0.9787 | 2026-05-03 12:00 | 255.237 | 262.959 | 735.6 | 43.8265 | 45.861 | -2.0345 | 275.1662 | 42 | 45.2052 | -3.2052 | 0.97063 | 2026-05-03 12:00 | 240.883 | 244.8 | 696.1 | 40.8 | 43.6311 | -2.8311 | 261.7866 | 39.6 | 43.0072 | -3.4072 | 0.984 | 2026-05-03 12:00 | 444.5763 | 474.7249 | -30.1485 | 2848.3492 | 432.6 | 467.9363 | -35.3363
2026-05-03 11:50 | 1023 | 49.65 | 332.423 | 338.275 | 910 | 56.3792 | 60.716 | -4.3369 | 364.2962 | 56.1 | 59.8478 | -3.7478 | 0.9827 | 2026-05-03 11:50 | 341.048 | 335.38 | 930.5 | 55.8967 | 60.716 | -4.8194 | 364.2962 | 56.8 | 59.8478 | -3.0478 | 1.0169 | 2026-05-03 11:50 | 333.026 | 342.838 | 915.6 | 57.1397 | 60.716 | -3.5764 | 364.2962 | 55.4 | 59.8478 | -4.4478 | 0.97138 | 2026-05-03 11:50 | 337.284 | 343.314 | 922.2 | 57.219 | 60.716 | -3.497 | 364.2962 | 56.2 | 59.8478 | -3.6478 | 0.98244 | 2026-05-03 11:50 | 251.252 | 255.312 | 683.7 | 42.552 | 44.9748 | -2.4228 | 269.8491 | 41.9 | 44.3317 | -2.4317 | 0.9841 | 2026-05-03 11:50 | 249.678 | 254.39 | 682.6 | 42.3983 | 44.9748 | -2.5765 | 269.8491 | 41.7 | 44.3317 | -2.6317 | 0.98148 | 2026-05-03 11:50 | 250.391 | 255.687 | 685.3 | 42.6145 | 44.9748 | -2.3603 | 269.8491 | 41.8 | 44.3317 | -2.5317 | 0.97929 | 2026-05-03 11:50 | 252.495 | 260.059 | 693.6 | 43.3432 | 44.9748 | -1.6317 | 269.8491 | 42.1 | 44.3317 | -2.2317 | 0.97091 | 2026-05-03 11:50 | 238.657 | 242.467 | 656.5 | 40.4112 | 42.788 | -2.3768 | 256.728 | 39.9 | 42.1761 | -2.2761 | 0.98429 | 2026-05-03 11:50 | 437.9537 | 465.5515 | -27.5978 | 2793.309 | 431.9 | 458.8941 | -26.9941
2026-05-03 11:40 | 1010 | 49.65 | 331.01 | 336.734 | 853.9 | 56.1223 | 59.9445 | -3.8221 | 359.6668 | 54.5 | 59.0873 | -4.5873 | 0.983 | 2026-05-03 11:40 | 338.144 | 344.202 | 873.7 | 57.367 | 59.9445 | -2.5775 | 359.6668 | 55.7 | 59.0873 | -3.3873 | 0.9824 | 2026-05-03 11:40 | 331.82 | 341.639 | 860.2 | 56.9398 | 59.9445 | -3.0046 | 359.6668 | 55.3 | 59.0873 | -3.7873 | 0.97126 | 2026-05-03 11:40 | 334.762 | 340.725 | 866 | 56.7875 | 59.9445 | -3.157 | 359.6668 | 55 | 59.0873 | -4.0873 | 0.9825 | 2026-05-03 11:40 | 249.38 | 253.409 | 641.8 | 42.2348 | 44.4033 | -2.1685 | 266.4199 | 40.9 | 43.7683 | -2.8683 | 0.9841 | 2026-05-03 11:40 | 248.273 | 252.965 | 640.9 | 42.1608 | 44.4033 | -2.2425 | 266.4199 | 40.7 | 43.7683 | -3.0683 | 0.98145 | 2026-05-03 11:40 | 248.233 | 253.062 | 643.5 | 42.177 | 44.4033 | -2.2263 | 266.4199 | 41.3 | 43.7683 | -2.4683 | 0.98092 | 2026-05-03 11:40 | 251.188 | 258.749 | 651.5 | 43.1248 | 44.4033 | -1.2785 | 266.4199 | 41.7 | 43.7683 | -2.0683 | 0.97078 | 2026-05-03 11:40 | 237.503 | 241.316 | 616.6 | 40.2193 | 42.2443 | -2.0249 | 253.4655 | 39.4 | 41.6402 | -2.2402 | 0.9842 | 2026-05-03 11:40 | 437.1335 | 459.6354 | -22.5019 | 2757.8124 | 424.5 | 453.0626 | -28.5626
2026-05-03 11:30 | 997 | 49.36 | 326.439 | 332.308 | 799.4 | 55.3847 | 59.2386 | -3.854 | 355.4319 | 53.7 | 58.3915 | -4.6915 | 0.98234 | 2026-05-03 11:30 | 334.389 | 340.31 | 818 | 56.7183 | 59.2386 | -2.5203 | 355.4319 | 110.6 | 58.3915 | 52.2085 | 0.9826 | 2026-05-03 11:30 | 327.573 | 337.157 | 804.9 | 56.1928 | 59.2386 | -3.0458 | 355.4319 | 54.6 | 58.3915 | -3.7915 | 0.97157 | 2026-05-03 11:30 | 330.236 | 336.05 | 811 | 56.0083 | 59.2386 | -3.2303 | 355.4319 | 55 | 58.3915 | -3.3915 | 0.9827 | 2026-05-03 11:30 | 245.372 | 249.311 | 600.9 | 41.5518 | 43.8805 | -2.3286 | 263.2829 | 41 | 43.253 | -2.253 | 0.9842 | 2026-05-03 11:30 | 243.951 | 248.913 | 600.2 | 41.4855 | 43.8805 | -2.395 | 263.2829 | 40.7 | 43.253 | -2.553 | 0.98007 | 2026-05-03 11:30 | 243.853 | 248.835 | 602.2 | 41.4725 | 43.8805 | -2.408 | 263.2829 | 40.2 | 43.253 | -3.053 | 0.97998 | 2026-05-03 11:30 | 246.399 | 253.899 | 609.8 | 42.3165 | 43.8805 | -1.564 | 263.2829 | 41.2 | 43.253 | -2.053 | 0.97046 | 2026-05-03 11:30 | 233.209 | 236.881 | 577.2 | 39.4802 | 41.7468 | -2.2667 | 250.481 | 39 | 41.1499 | -2.1499 | 0.9845 | 2026-05-03 11:30 | 430.6107 | 454.2233 | -23.6126 | 2725.3399 | 476 | 447.7279 | 28.2721
2026-05-03 11:20 | 981 | 49.36 | 324.007 | 329.51 | 745.7 | 54.9183 | 58.288 | -3.3696 | 349.7278 | 53 | 57.4545 | -4.4545 | 0.9833 |  |  |  |  | 0 | 58.288 | -58.288 | 349.7278 | 0 | 57.4545 | -57.4545 |  | 2026-05-03 11:20 | 325.137 | 334.302 | 750.3 | 55.717 | 58.288 | -2.571 | 349.7278 | 54 | 57.4545 | -3.4545 | 0.97258 | 2026-05-03 11:20 | 327.214 | 332.907 | 756 | 55.4845 | 58.288 | -2.8035 | 349.7278 | 54.4 | 57.4545 | -3.0545 | 0.9829 | 2026-05-03 11:20 | 244.362 | 248.209 | 559.9 | 41.3682 | 43.1763 | -1.8081 | 259.0577 | 40.6 | 42.5589 | -1.9589 | 0.9845 | 2026-05-03 11:20 | 242.561 | 247.147 | 559.5 | 41.1912 | 43.1763 | -1.9851 | 259.0577 | 40.4 | 42.5589 | -2.1589 | 0.98144 | 2026-05-03 11:20 | 242.872 | 247.641 | 562 | 41.2735 | 43.1763 | -1.9028 | 259.0577 | 40.4 | 42.5589 | -2.1589 | 0.98074 | 2026-05-03 11:20 | 244.744 | 252.169 | 568.6 | 42.0282 | 43.1763 | -1.1481 | 259.0577 | 40 | 42.5589 | -2.5589 | 0.97056 | 2026-05-03 11:20 | 231.325 | 234.919 | 538.2 | 39.1532 | 41.0769 | -1.9237 | 246.4613 | 37.8 | 40.4895 | -2.6895 | 0.9847 | 2026-05-03 11:20 | 371.134 | 446.9339 | -75.7999 | 2681.6032 | 360.6 | 440.5427 | -79.9427
2026-05-03 11:10 | 960 | 49.36 | 318.289 | 323.629 | 692.7 | 53.9382 | 57.0402 | -3.1021 | 342.2413 | 53.2 | 56.2245 | -3.0245 | 0.9835 | 2026-05-03 11:10 | 326.32 | 331.93 | 707.4 | 55.3217 | 57.0402 | -1.7186 | 342.2413 | 53.6 | 56.2245 | -2.6245 | 0.9831 | 2026-05-03 11:10 | 320.763 | 329.649 | 696.3 | 54.9415 | 57.0402 | -2.0987 | 342.2413 | 52.7 | 56.2245 | -3.5245 | 0.97304 | 2026-05-03 11:10 | 323.555 | 329.05 | 701.6 | 54.8417 | 57.0402 | -2.1986 | 342.2413 | 53.1 | 56.2245 | -3.1245 | 0.9833 | 2026-05-03 11:10 | 241.38 | 245.13 | 519.3 | 40.855 | 42.252 | -1.397 | 253.5121 | 39.6 | 41.6478 | -2.0478 | 0.9847 | 2026-05-03 11:10 | 240.165 | 244.639 | 519.1 | 40.7732 | 42.252 | -1.4788 | 253.5121 | 39.9 | 41.6478 | -1.7478 | 0.98171 | 2026-05-03 11:10 | 240.074 | 244.633 | 521.6 | 40.7722 | 42.252 | -1.4798 | 253.5121 | 40 | 41.6478 | -1.6478 | 0.98136 | 2026-05-03 11:10 | 241.923 | 249.481 | 528.6 | 41.5802 | 42.252 | -0.67185 | 253.5121 | 40.3 | 41.6478 | -1.3478 | 0.96971 | 2026-05-03 11:10 | 228.889 | 232.445 | 500.4 | 38.7408 | 40.1976 | -1.4567 | 241.1853 | 38.1 | 39.6227 | -1.5227 | 0.9847 | 2026-05-03 11:10 | 421.7643 | 437.3665 | -15.6021 | 2624.1989 | 410.5 | 431.1121 | -20.6121
2026-05-03 11:00 | 936 | 49.36 | 313.004 | 318.191 | 639.5 | 53.0318 | 55.6142 | -2.5824 | 333.6853 | 51.9 | 54.8189 | -2.9189 | 0.9837 | 2026-05-03 11:00 | 319.489 | 324.882 | 653.8 | 54.147 | 55.6142 | -1.4672 | 333.6853 | 53 | 54.8189 | -1.8189 | 0.9834 | 2026-05-03 11:00 | 314.304 | 322.828 | 643.6 | 53.8047 | 55.6142 | -1.8095 | 333.6853 | 51.4 | 54.8189 | -3.4189 | 0.9736 | 2026-05-03 11:00 | 316.005 | 321.307 | 648.5 | 53.5512 | 55.6142 | -2.063 | 333.6853 | 51.8 | 54.8189 | -3.0189 | 0.9835 | 2026-05-03 11:00 | 236.13 | 239.726 | 479.7 | 39.9543 | 41.1957 | -1.2414 | 247.1743 | 39.2 | 40.6066 | -1.4066 | 0.985 | 2026-05-03 11:00 | 234.737 | 238.8 | 479.2 | 39.8 | 41.1957 | -1.3957 | 247.1743 | 38.3 | 40.6066 | -2.3066 | 0.98299 | 2026-05-03 11:00 | 235.078 | 239.477 | 481.6 | 39.9128 | 41.1957 | -1.2829 | 247.1743 | 38.4 | 40.6066 | -2.2066 | 0.98163 | 2026-05-03 11:00 | 236.433 | 243.622 | 488.3 | 40.6037 | 41.1957 | -0.59205 | 247.1743 | 38.7 | 40.6066 | -1.9066 | 0.97049 | 2026-05-03 11:00 | 223.728 | 227.089 | 462.3 | 37.8482 | 39.1926 | -1.3445 | 235.1557 | 36.6 | 38.6322 | -2.0322 | 0.9852 | 2026-05-03 11:00 | 412.6537 | 426.4323 | -13.7787 | 2558.5939 | 399.3 | 420.3343 | -21.0343
2026-05-03 10:50 | 905 | 49.36 | 302.784 | 308.314 | 587.6 | 51.3857 | 53.7723 | -2.3866 | 322.6337 | 49.7 | 53.0033 | -3.3033 | 0.98206 | 2026-05-03 10:50 | 309.646 | 314.873 | 600.8 | 52.4788 | 53.7723 | -1.2935 | 322.6337 | 53.6 | 53.0033 | 0.59665 | 0.9834 | 2026-05-03 10:50 | 304.541 | 312.564 | 592.2 | 52.094 | 53.7723 | -1.6783 | 322.6337 | 49.9 | 53.0033 | -3.1033 | 0.97433 | 2026-05-03 10:50 | 306.719 | 311.86 | 596.7 | 51.9767 | 53.7723 | -1.7956 | 322.6337 | 50.9 | 53.0033 | -2.1033 | 0.98352 | 2026-05-03 10:50 | 228.756 | 232.192 | 440.5 | 38.6987 | 39.8313 | -1.1327 | 238.988 | 37.4 | 39.2617 | -1.8617 | 0.9852 | 2026-05-03 10:50 | 227.861 | 231.836 | 440.9 | 38.6393 | 39.8313 | -1.192 | 238.988 | 37.4 | 39.2617 | -1.8617 | 0.98285 | 2026-05-03 10:50 | 228.475 | 232.642 | 443.2 | 38.7737 | 39.8313 | -1.0577 | 238.988 | 37.4 | 39.2617 | -1.8617 | 0.98209 | 2026-05-03 10:50 | 230.598 | 237.274 | 449.6 | 39.5457 | 39.8313 | -0.28566 | 238.988 | 37.8 | 39.2617 | -1.4617 | 0.97186 | 2026-05-03 10:50 | 217.76 | 220.986 | 425.7 | 36.831 | 37.8946 | -1.0636 | 227.3674 | 35.8 | 37.3527 | -1.5527 | 0.9854 | 2026-05-03 10:50 | 400.4235 | 412.309 | -11.8855 | 2473.8542 | 389.9 | 406.413 | -16.513
2026-05-03 10:40 | 873 | 49.36 | 294.131 | 298.823 | 537.9 | 49.8038 | 51.8709 | -2.0671 | 311.2257 | 47.4 | 51.1292 | -3.7292 | 0.9843 | 2026-05-03 10:40 | 299.814 | 304.751 | 547.2 | 50.7918 | 51.8709 | -1.0791 | 311.2257 | 46.5 | 51.1292 | -4.6292 | 0.9838 | 2026-05-03 10:40 | 295.114 | 303.439 | 542.3 | 50.5732 | 51.8709 | -1.2978 | 311.2257 | 48.9 | 51.1292 | -2.2292 | 0.97256 | 2026-05-03 10:40 | 297.704 | 302.66 | 545.8 | 50.4433 | 51.8709 | -1.4276 | 311.2257 | 48.7 | 51.1292 | -2.4292 | 0.98363 | 2026-05-03 10:40 | 221.324 | 224.558 | 403.1 | 37.4263 | 38.4229 | -0.99659 | 230.5375 | 36.2 | 37.8735 | -1.6735 | 0.9856 | 2026-05-03 10:40 | 220.952 | 224.874 | 403.5 | 37.479 | 38.4229 | -0.94392 | 230.5375 | 36.2 | 37.8735 | -1.6735 | 0.98256 | 2026-05-03 10:40 | 221.104 | 224.791 | 405.8 | 37.4652 | 38.4229 | -0.95776 | 230.5375 | 36.3 | 37.8735 | -1.5735 | 0.9836 | 2026-05-03 10:40 | 223.186 | 229.895 | 411.8 | 38.3158 | 38.4229 | -0.10709 | 230.5375 | 36.5 | 37.8735 | -1.3735 | 0.97082 | 2026-05-03 10:40 | 211.398 | 214.53 | 389.9 | 35.755 | 36.5547 | -0.79965 | 219.3279 | 34.6 | 36.0319 | -1.4319 | 0.9854 | 2026-05-03 10:40 | 388.0535 | 397.7301 | -9.6766 | 2386.3809 | 371.3 | 392.0426 | -20.7426
2026-05-03 10:30 | 839 | 49.36 | 284.22 | 289.088 | 490.5 | 48.1813 | 49.8508 | -1.6694 | 299.1046 | 47.9 | 49.1379 | -1.2379 | 0.98316 | 2026-05-03 10:30 | 290.344 | 295.035 | 500.7 | 49.1725 | 49.8508 | -0.67827 | 299.1046 | 50.1 | 49.1379 | 0.96209 | 0.9841 | 2026-05-03 10:30 | 285.365 | 292.755 | 493.4 | 48.7925 | 49.8508 | -1.0583 | 299.1046 | 46.8 | 49.1379 | -2.3379 | 0.97476 | 2026-05-03 10:30 | 287.267 | 291.908 | 497.1 | 48.6513 | 49.8508 | -1.1994 | 299.1046 | 47.1 | 49.1379 | -2.0379 | 0.9841 | 2026-05-03 10:30 | 213.962 | 217.044 | 366.9 | 36.174 | 36.9265 | -0.7525 | 221.559 | 35.1 | 36.3985 | -1.2985 | 0.9858 | 2026-05-03 10:30 | 213.455 | 217.135 | 367.3 | 36.1892 | 36.9265 | -0.73733 | 221.559 | 35 | 36.3985 | -1.3985 | 0.98305 | 2026-05-03 10:30 | 214.176 | 217.734 | 369.5 | 36.289 | 36.9265 | -0.6375 | 221.559 | 35 | 36.3985 | -1.3985 | 0.98366 | 2026-05-03 10:30 | 216.004 | 222.206 | 375.3 | 37.0343 | 36.9265 | 0.10783 | 221.559 | 35.4 | 36.3985 | -0.99845 | 0.97209 | 2026-05-03 10:30 | 204.536 | 207.503 | 355.3 | 34.5838 | 35.131 | -0.54716 | 210.7859 | 33.9 | 34.6286 | -0.72862 | 0.9857 | 2026-05-03 10:30 | 375.068 | 382.2401 | -7.1721 | 2293.4405 | 366.3 | 376.774 | -10.474
2026-05-03 10:20 | 810 | 49.36 | 275.207 | 279.383 | 442.6 | 46.5638 | 48.1277 | -1.5639 | 288.7661 | 44 | 47.4395 | -3.4395 | 0.98505 | 2026-05-03 10:20 | 279.767 | 284.201 | 450.6 | 47.3668 | 48.1277 | -0.76085 | 288.7661 | 44.3 | 47.4395 | -3.1395 | 0.9844 | 2026-05-03 10:20 | 276.166 | 283.172 | 446.6 | 47.1953 | 48.1277 | -0.93235 | 288.7661 | 44.8 | 47.4395 | -2.6395 | 0.97526 | 2026-05-03 10:20 | 278.664 | 283.051 | 450 | 47.1752 | 48.1277 | -0.95252 | 288.7661 | 45.9 | 47.4395 | -1.5395 | 0.9845 | 2026-05-03 10:20 | 206.774 | 209.71 | 331.8 | 34.9517 | 35.6501 | -0.69847 | 213.9008 | 34 | 35.1403 | -1.1403 | 0.986 | 2026-05-03 10:20 | 207.233 | 210.296 | 332.3 | 35.0493 | 35.6501 | -0.6008 | 213.9008 | 34 | 35.1403 | -1.1403 | 0.98543 | 2026-05-03 10:20 | 207.226 | 210.526 | 334.5 | 35.0877 | 35.6501 | -0.56247 | 213.9008 | 34.2 | 35.1403 | -0.94034 | 0.98432 | 2026-05-03 10:20 | 208.992 | 215.107 | 339.9 | 35.8512 | 35.6501 | 0.20103 | 213.9008 | 34.4 | 35.1403 | -0.74034 | 0.97157 | 2026-05-03 10:20 | 198.208 | 201.022 | 321.4 | 33.5037 | 33.9167 | -0.41302 | 203.5001 | 32.2 | 33.4317 | -1.2317 | 0.986 | 2026-05-03 10:20 | 362.7447 | 369.028 | -6.2833 | 2214.1678 | 347.8 | 363.7509 | -15.9509
2026-05-03 10:10 | 774 | 49.36 | 263.734 | 267.573 | 398.6 | 44.5955 | 45.9887 | -1.3932 | 275.9321 | 44.8 | 45.331 | -0.53104 | 0.98565 | 2026-05-03 10:10 | 269.518 | 273.706 | 406.3 | 45.6177 | 45.9887 | -0.37101 | 275.9321 | 43.3 | 45.331 | -2.031 | 0.9847 | 2026-05-03 10:10 | 265.5 | 271.946 | 401.8 | 45.3243 | 45.9887 | -0.66434 | 275.9321 | 43.4 | 45.331 | -1.931 | 0.9763 | 2026-05-03 10:10 | 266.706 | 270.795 | 404.1 | 45.1325 | 45.9887 | -0.85618 | 275.9321 | 42.9 | 45.331 | -2.431 | 0.9849 | 2026-05-03 10:10 | 197.837 | 200.646 | 297.8 | 33.441 | 34.0657 | -0.62469 | 204.3941 | 31.9 | 33.5785 | -1.6785 | 0.986 | 2026-05-03 10:10 | 198.012 | 201.088 | 298.3 | 33.5147 | 34.0657 | -0.55102 | 204.3941 | 32 | 33.5785 | -1.5785 | 0.9847 | 2026-05-03 10:10 | 198.364 | 201.485 | 300.3 | 33.5808 | 34.0657 | -0.48485 | 204.3941 | 32 | 33.5785 | -1.5785 | 0.98451 | 2026-05-03 10:10 | 199.931 | 206.008 | 305.5 | 34.3347 | 34.0657 | 0.26898 | 204.3941 | 32.4 | 33.5785 | -1.1785 | 0.9705 | 2026-05-03 10:10 | 189.443 | 192.152 | 289.2 | 32.0253 | 32.4093 | -0.38395 | 194.4557 | 30.6 | 31.9458 | -1.3458 | 0.9859 | 2026-05-03 10:10 | 347.5665 | 352.6267 | -5.0602 | 2115.7604 | 333.3 | 347.5842 | -14.2842
2026-05-03 10:00 | 733 | 49.36 | 250.988 | 254.844 | 353.8 | 42.474 | 43.5526 | -1.0786 | 261.3155 | 39.1 | 42.9298 | -3.8298 | 0.98487 | 2026-05-03 10:00 | 257.067 | 260.982 | 363 | 43.497 | 43.5526 | -0.055583 | 261.3155 | 43.5 | 42.9298 | 0.57022 | 0.985 | 2026-05-03 10:00 | 253.061 | 259.233 | 358.4 | 43.2055 | 43.5526 | -0.34708 | 261.3155 | 40.9 | 42.9298 | -2.0298 | 0.97619 | 2026-05-03 10:00 | 254.631 | 258.482 | 361.2 | 43.0803 | 43.5526 | -0.47225 | 261.3155 | 41.8 | 42.9298 | -1.1298 | 0.9851 | 2026-05-03 10:00 | 188.676 | 191.297 | 265.9 | 31.8828 | 32.2612 | -0.37834 | 193.567 | 31 | 31.7998 | -0.79984 | 0.9863 | 2026-05-03 10:00 | 189.485 | 192.308 | 266.3 | 32.0513 | 32.2612 | -0.20984 | 193.567 | 31.1 | 31.7998 | -0.69984 | 0.98532 | 2026-05-03 10:00 | 189.45 | 192.458 | 268.3 | 32.0763 | 32.2612 | -0.18484 | 193.567 | 31.1 | 31.7998 | -0.69984 | 0.98437 | 2026-05-03 10:00 | 191.567 | 197.111 | 273.1 | 32.8518 | 32.2612 | 0.59066 | 193.567 | 31.4 | 31.7998 | -0.39984 | 0.97187 | 2026-05-03 10:00 | 181.469 | 184.008 | 258.6 | 30.668 | 30.6925 | -0.02451 | 184.1551 | 29.8 | 30.2536 | -0.45361 | 0.9862 | 2026-05-03 10:00 | 331.7872 | 333.9475 | -2.1604 | 2003.6852 | 319.7 | 329.1721 | -9.4721
2026-05-03 09:50 | 697 | 49.65 | 240.326 | 244.099 | 314.7 | 40.6832 | 41.3676 | -0.68446 | 248.2057 | 38.9 | 40.7761 | -1.8761 |  | 2026-05-03 09:50 | 243.231 | 246.835 | 319.5 | 41.1392 | 41.3676 | -0.22846 | 248.2057 | 38.6 | 40.7761 | -2.1761 |  | 2026-05-03 09:50 | 241.799 | 247.546 | 317.5 | 41.2577 | 41.3676 | -0.10996 | 248.2057 | 39.8 | 40.7761 | -0.97607 |  | 2026-05-03 09:50 | 243.421 | 247.028 | 319.4 | 41.1713 | 41.3676 | -0.19629 | 248.2057 | 39.6 | 40.7761 | -1.1761 |  | 2026-05-03 09:50 | 180.174 | 182.64 | 234.9 | 30.44 | 30.6427 | -0.20268 | 183.8561 | 29.3 | 30.2045 | -0.90449 |  | 2026-05-03 09:50 | 180.862 | 183.377 | 235.2 | 30.5628 | 30.6427 | -0.07985 | 183.8561 | 29.5 | 30.2045 | -0.70449 |  | 2026-05-03 09:50 | 181.142 | 183.863 | 237.2 | 30.6438 | 30.6427 | 0.0011502 | 183.8561 | 29.4 | 30.2045 | -0.80449 |  | 2026-05-03 09:50 | 182.999 | 188.335 | 241.7 | 31.3892 | 30.6427 | 0.74648 | 183.8561 | 29.7 | 30.2045 | -0.50449 |  | 2026-05-03 09:50 | 173.33 | 175.72 | 228.8 | 29.2867 | 29.1527 | 0.13395 | 174.9163 | 28.2 | 28.7358 | -0.53583 |  | 2026-05-03 09:50 | 316.5738 | 317.1939 | -0.62011 | 1903.1636 | 303 | 312.6581 | -9.6581
2026-05-03 09:40 | 659 | 49.36 | 227.686 | 230.895 | 275.8 | 38.4825 | 39.1557 | -0.67323 | 234.9344 | 37.5 | 38.5958 | -1.0958 |  | 2026-05-03 09:40 | 232.884 | 236.263 | 280.9 | 39.3772 | 39.1557 | 0.22143 | 234.9344 | 37.9 | 38.5958 | -0.69581 |  | 2026-05-03 09:40 | 229.011 | 234.149 | 277.7 | 39.0248 | 39.1557 | -0.1309 | 234.9344 | 36.7 | 38.5958 | -1.8958 |  | 2026-05-03 09:40 | 230.854 | 234.179 | 279.8 | 39.0298 | 39.1557 | -0.1259 | 234.9344 | 37 | 38.5958 | -1.5958 |  | 2026-05-03 09:40 | 171.187 | 173.477 | 205.6 | 28.9128 | 29.0042 | -0.091413 | 174.0255 | 27.3 | 28.5895 | -1.2895 |  | 2026-05-03 09:40 | 172.183 | 174.504 | 205.7 | 29.084 | 29.0042 | 0.079753 | 174.0255 | 27.9 | 28.5895 | -0.68949 |  | 2026-05-03 09:40 | 172.42 | 174.709 | 207.8 | 29.1182 | 29.0042 | 0.11392 | 174.0255 | 27.9 | 28.5895 | -0.68949 |  | 2026-05-03 09:40 | 174.157 | 178.945 | 212 | 29.8242 | 29.0042 | 0.81992 | 174.0255 | 28.3 | 28.5895 | -0.28949 |  | 2026-05-03 09:40 | 164.972 | 167.125 | 200.6 | 27.8542 | 27.5939 | 0.26022 | 165.5637 | 26.8 | 27.1994 | -0.39935 |  | 2026-05-03 09:40 | 300.7077 | 300.2339 | 0.4738 | 1801.4032 | 287.3 | 295.9405 | -8.6405
2026-05-03 09:30 | 617 | 49.08 | 213.982 | 216.91 | 238.3 | 36.1517 | 36.6995 | -0.54783 | 220.197 | 34.3 | 36.1747 | -1.8747 |  | 2026-05-03 09:30 | 218.952 | 221.978 | 243 | 36.9963 | 36.6995 | 0.29683 | 220.197 | 34.2 | 36.1747 | -1.9747 |  | 2026-05-03 09:30 | 216.059 | 220.595 | 241 | 36.7658 | 36.6995 | 0.066334 | 220.197 | 34.6 | 36.1747 | -1.5747 |  | 2026-05-03 09:30 | 217.892 | 220.941 | 242.8 | 36.8235 | 36.6995 | 0.124 | 220.197 | 34.8 | 36.1747 | -1.3747 |  | 2026-05-03 09:30 | 160.827 | 162.929 | 178.3 | 27.1548 | 27.1848 | -0.029981 | 163.1089 | 26.1 | 26.7961 | -0.69607 |  | 2026-05-03 09:30 | 161.797 | 163.945 | 177.8 | 27.3242 | 27.1848 | 0.13935 | 163.1089 | 25.9 | 26.7961 | -0.89607 |  | 2026-05-03 09:30 | 161.991 | 164.108 | 179.9 | 27.3513 | 27.1848 | 0.16652 | 163.1089 | 26 | 26.7961 | -0.79607 |  | 2026-05-03 09:30 | 163.464 | 167.896 | 183.7 | 27.9827 | 27.1848 | 0.79785 | 163.1089 | 26.3 | 26.7961 | -0.49607 |  | 2026-05-03 09:30 | 154.869 | 156.893 | 173.8 | 26.1488 | 25.863 | 0.28585 | 155.1779 | 24.9 | 25.4931 | -0.59314 |  | 2026-05-03 09:30 | 282.6992 | 281.4002 | 1.2989 | 1688.4014 | 267.1 | 277.3762 | -10.2762
2026-05-03 09:20 | 570 | 48.5 | 199.214 | 201.858 | 204 | 33.643 | 33.9791 | -0.33607 | 203.8744 | 33 | 33.4932 | -0.49317 |  | 2026-05-03 09:20 | 204.146 | 206.94 | 208.8 | 34.49 | 33.9791 | 0.51093 | 203.8744 | 33 | 33.4932 | -0.49317 |  | 2026-05-03 09:20 | 200.945 | 205.034 | 206.4 | 34.1723 | 33.9791 | 0.19326 | 203.8744 | 32.5 | 33.4932 | -0.99317 |  | 2026-05-03 09:20 | 202.733 | 205.487 | 208 | 34.2478 | 33.9791 | 0.26876 | 203.8744 | 32.9 | 33.4932 | -0.59317 |  | 2026-05-03 09:20 | 149.36 | 151.266 | 152.2 | 25.211 | 25.1697 | 0.041317 | 151.0181 | 23.8 | 24.8098 | -1.0098 |  | 2026-05-03 09:20 | 149.649 | 151.574 | 151.9 | 25.2623 | 25.1697 | 0.09265 | 151.0181 | 23.9 | 24.8098 | -0.90976 |  | 2026-05-03 09:20 | 150.795 | 152.735 | 153.9 | 25.4558 | 25.1697 | 0.28615 | 151.0181 | 24.1 | 24.8098 | -0.70976 |  | 2026-05-03 09:20 | 152.593 | 156.869 | 157.4 | 26.1448 | 25.1697 | 0.97515 | 151.0181 | 24.4 | 24.8098 | -0.40976 |  | 2026-05-03 09:20 | 144.598 | 146.463 | 148.9 | 24.4105 | 23.9458 | 0.46466 | 143.675 | 23.1 | 23.6034 | -0.50341 |  | 2026-05-03 09:20 | 263.0377 | 260.5409 | 2.4968 | 1563.2452 | 250.7 | 256.8151 | -6.1151
2026-05-03 09:10 | 528 | 48.22 | 183.769 | 186.133 | 171 | 31.0222 | 31.509 | -0.4868 | 189.0538 | 28.3 | 31.0584 | -2.7584 |  | 2026-05-03 09:10 | 188.607 | 191.091 | 175.8 | 31.8485 | 31.509 | 0.33954 | 189.0538 | 30.8 | 31.0584 | -0.25838 |  | 2026-05-03 09:10 | 185.878 | 189.421 | 173.9 | 31.5702 | 31.509 | 0.061205 | 189.0538 | 29.9 | 31.0584 | -1.1584 |  | 2026-05-03 09:10 | 187.818 | 190.292 | 175.1 | 31.7153 | 31.509 | 0.20637 | 189.0538 | 30.1 | 31.0584 | -0.95838 |  | 2026-05-03 09:10 | 138.066 | 139.8 | 128.4 | 23.3 | 23.34 | -0.039972 | 140.0398 | 22.2 | 23.0062 | -0.80621 |  | 2026-05-03 09:10 | 137.803 | 139.378 | 128 | 23.2297 | 23.34 | -0.11031 | 140.0398 | 22.4 | 23.0062 | -0.60621 |  | 2026-05-03 09:10 | 139.755 | 141.562 | 129.8 | 23.5937 | 23.34 | 0.25369 | 140.0398 | 22.3 | 23.0062 | -0.70621 |  | 2026-05-03 09:10 | 141.579 | 145.245 | 133 | 24.2075 | 23.34 | 0.86753 | 140.0398 | 22.7 | 23.0062 | -0.30621 |  | 2026-05-03 09:10 | 134.33 | 136.017 | 125.8 | 22.6695 | 22.2051 | 0.46441 | 133.2306 | 21.6 | 21.8876 | -0.28756 |  | 2026-05-03 09:10 | 243.1565 | 241.6008 | 1.5557 | 1449.605 | 230.3 | 238.1459 | -7.8459
2026-05-03 09:00 | 484 | 47.35 | 168.633 | 170.75 | 142.7 | 28.4583 | 28.9789 | -0.52061 | 173.8737 | 26.4 | 28.5645 | -2.1645 |  | 2026-05-03 09:00 | 172.985 | 175.192 | 145 | 29.1987 | 28.9789 | 0.21972 | 173.8737 | 28 | 28.5645 | -0.56455 |  | 2026-05-03 09:00 | 170.445 | 173.677 | 144 | 28.9462 | 28.9789 | -0.032778 | 173.8737 | 27 | 28.5645 | -1.5645 |  | 2026-05-03 09:00 | 172.002 | 174.179 | 145 | 29.0298 | 28.9789 | 0.050889 | 173.8737 | 27.3 | 28.5645 | -1.2645 |  | 2026-05-03 09:00 | 126.249 | 127.795 | 106.2 | 21.2992 | 21.4659 | -0.16672 | 128.7953 | 20 | 21.1589 | -1.1589 |  | 2026-05-03 09:00 | 126.301 | 127.835 | 105.6 | 21.3058 | 21.4659 | -0.16005 | 128.7953 | 20.2 | 21.1589 | -0.95892 |  | 2026-05-03 09:00 | 127.544 | 129.087 | 107.5 | 21.5145 | 21.4659 | 0.048615 | 128.7953 | 20.1 | 21.1589 | -1.0589 |  | 2026-05-03 09:00 | 129.851 | 133.201 | 110.3 | 22.2002 | 21.4659 | 0.73428 | 128.7953 | 20.7 | 21.1589 | -0.45892 |  | 2026-05-03 09:00 | 123.411 | 124.91 | 104.2 | 20.8183 | 20.4221 | 0.3962 | 122.5328 | 19.6 | 20.1301 | -0.53009 |  | 2026-05-03 09:00 | 222.771 | 222.2014 | 0.56955 | 1333.2087 | 209.3 | 219.024 | -9.724
2026-05-03 08:50 | 438 | 47.64 | 152.676 | 154.53 | 116.3 | 25.755 | 26.1959 | -0.44087 | 157.1752 | 24.7 | 25.8213 | -1.1213 |  | 2026-05-03 08:50 | 154.157 | 156.061 | 117 | 26.0102 | 26.1959 | -0.1857 | 157.1752 | 23.8 | 25.8213 | -2.0213 |  | 2026-05-03 08:50 | 153.615 | 156.083 | 117 | 26.0138 | 26.1959 | -0.18204 | 157.1752 | 24.2 | 25.8213 | -1.6213 |  | 2026-05-03 08:50 | 155.539 | 157.444 | 117.7 | 26.2407 | 26.1959 | 0.044797 | 157.1752 | 24.4 | 25.8213 | -1.4213 |  | 2026-05-03 08:50 | 113.827 | 115.18 | 86.2 | 19.1967 | 19.4043 | -0.20768 | 116.4261 | 17.9 | 19.1269 | -1.2269 |  | 2026-05-03 08:50 | 114.559 | 115.892 | 85.4 | 19.3153 | 19.4043 | -0.089015 | 116.4261 | 18.1 | 19.1269 | -1.0269 |  | 2026-05-03 08:50 | 115.051 | 116.401 | 87.4 | 19.4002 | 19.4043 | -0.0041815 | 116.4261 | 17.9 | 19.1269 | -1.2269 |  | 2026-05-03 08:50 | 117.969 | 121.124 | 89.6 | 20.1873 | 19.4043 | 0.78299 | 116.4261 | 18.7 | 19.1269 | -0.42687 |  | 2026-05-03 08:50 | 111.936 | 113.276 | 84.6 | 18.8793 | 18.4608 | 0.4185 | 110.765 | 17.6 | 18.1968 | -0.59684 |  | 2026-05-03 08:50 | 200.9985 | 200.8617 | 0.13679 | 1205.1702 | 187.3 | 197.9894 | -10.6894
2026-05-03 08:40 | 393 | 44.48 | 136.006 | 137.583 | 91.6 | 22.9305 | 23.7868 | -0.85635 | 142.7211 | 21 | 23.4467 | -2.4467 |  | 2026-05-03 08:40 | 139.588 | 141.255 | 93.2 | 23.5425 | 23.7868 | -0.24435 | 142.7211 | 22.4 | 23.4467 | -1.0467 |  | 2026-05-03 08:40 | 137.747 | 139.867 | 92.8 | 23.3112 | 23.7868 | -0.47568 | 142.7211 | 21.5 | 23.4467 | -1.9467 |  | 2026-05-03 08:40 | 139.119 | 140.752 | 93.3 | 23.4587 | 23.7868 | -0.32818 | 142.7211 | 21.7 | 23.4467 | -1.7467 |  | 2026-05-03 08:40 | 101.782 | 102.956 | 68.3 | 17.1593 | 17.6199 | -0.46055 | 105.7193 | 15.9 | 17.3679 | -1.4679 |  | 2026-05-03 08:40 | 103.242 | 104.411 | 67.3 | 17.4018 | 17.6199 | -0.21805 | 105.7193 | 16.1 | 17.3679 | -1.2679 |  | 2026-05-03 08:40 | 102.594 | 103.767 | 69.5 | 17.2945 | 17.6199 | -0.32539 | 105.7193 | 16.1 | 17.3679 | -1.2679 |  | 2026-05-03 08:40 | 105.507 | 108.479 | 70.9 | 18.0798 | 17.6199 | 0.45995 | 105.7193 | 16.2 | 17.3679 | -1.1679 |  | 2026-05-03 08:40 | 98.469 | 99.615 | 67 | 16.6025 | 16.7631 | -0.16064 | 100.5788 | 15.6 | 16.5234 | -0.92343 |  | 2026-05-03 08:40 | 179.7808 | 182.3901 | -2.6092 | 1094.3404 | 166.5 | 179.7819 | -13.2819
2026-05-03 08:30 | 344 | 40.47 | 117.42 | 118.726 | 70.6 | 19.7877 | 21.1347 | -1.347 | 126.808 | 17.9 | 20.8324 | -2.9324 |  | 2026-05-03 08:30 | 119.339 | 120.909 | 70.8 | 20.1515 | 21.1347 | -0.98316 | 126.808 | 17.9 | 20.8324 | -2.9324 |  | 2026-05-03 08:30 | 118.896 | 120.553 | 71.3 | 20.0922 | 21.1347 | -1.0425 | 126.808 | 18.4 | 20.8324 | -2.4324 |  | 2026-05-03 08:30 | 119.893 | 121.212 | 71.6 | 20.202 | 21.1347 | -0.93266 | 126.808 | 18.6 | 20.8324 | -2.2324 |  | 2026-05-03 08:30 | 87.722 | 88.725 | 52.4 | 14.7875 | 15.6553 | -0.8678 | 93.9318 | 13.6 | 15.4314 | -1.8314 |  | 2026-05-03 08:30 | 88.953 | 89.942 | 51.2 | 14.9903 | 15.6553 | -0.66497 | 93.9318 | 13.4 | 15.4314 | -2.0314 |  | 2026-05-03 08:30 | 88.76 | 89.774 | 53.4 | 14.9623 | 15.6553 | -0.69297 | 93.9318 | 13.8 | 15.4314 | -1.6314 |  | 2026-05-03 08:30 | 91.117 | 93.566 | 54.7 | 15.5943 | 15.6553 | -0.060971 | 93.9318 | 14 | 15.4314 | -1.4314 |  | 2026-05-03 08:30 | 85.199 | 86.154 | 51.4 | 14.359 | 14.8941 | -0.53508 | 89.3645 | 13.1 | 14.6811 | -1.5811 |  | 2026-05-03 08:30 | 154.9268 | 162.0539 | -7.1271 | 972.3237 | 140.7 | 159.7366 | -19.0366
2026-05-03 08:20 | 301 | 36.16 | 100.908 | 102.233 | 52.7 | 17.0388 | 18.7878 | -1.7489 | 112.7266 | 15.3 | 18.5191 | -3.2191 |  | 2026-05-03 08:20 | 102.351 | 104.702 | 52.9 | 17.4503 | 18.7878 | -1.3374 | 112.7266 | 15.7 | 18.5191 | -2.8191 |  | 2026-05-03 08:20 | 102.042 | 103.274 | 52.9 | 17.2123 | 18.7878 | -1.5754 | 112.7266 | 15.3 | 18.5191 | -3.2191 |  | 2026-05-03 08:20 | 102.986 | 104.131 | 53 | 17.3552 | 18.7878 | -1.4326 | 112.7266 | 15.6 | 18.5191 | -2.9191 |  | 2026-05-03 08:20 | 75.152 | 76.034 | 38.8 | 12.6723 | 13.9169 | -1.2445 | 83.5012 | 11.3 | 13.7178 | -2.4178 |  | 2026-05-03 08:20 | 72.675 | 73.506 | 37.8 | 12.251 | 13.9169 | -1.6659 | 83.5012 | 11.1 | 13.7178 | -2.6178 |  | 2026-05-03 08:20 | 76.363 | 77.251 | 39.6 | 12.8752 | 13.9169 | -1.0417 | 83.5012 | 11.6 | 13.7178 | -2.1178 |  | 2026-05-03 08:20 | 78.326 | 80.404 | 40.7 | 13.4007 | 13.9169 | -0.51619 | 83.5012 | 11.9 | 13.7178 | -1.8178 |  | 2026-05-03 08:20 | 73.199 | 74.058 | 38.3 | 12.343 | 13.2402 | -0.89717 | 79.441 | 11.2 | 13.0508 | -1.8508 |  | 2026-05-03 08:20 | 132.5988 | 144.0587 | -11.4598 | 864.3519 | 119 | 141.9986 | -22.9986
2026-05-03 08:10 | 251 | 29.56 | 82.386 | 83.269 | 37.4 | 13.8782 | 16.0435 | -2.1653 | 96.2609 | 12.4 | 15.8141 | -3.4141 |  | 2026-05-03 08:10 | 84.735 | 85.639 | 37.2 | 14.2732 | 16.0435 | -1.7703 | 96.2609 | 12.9 | 15.8141 | -2.9141 |  | 2026-05-03 08:10 | 83.588 | 84.952 | 37.6 | 14.1587 | 16.0435 | -1.8848 | 96.2609 | 12.5 | 15.8141 | -3.3141 |  | 2026-05-03 08:10 | 84.292 | 85.221 | 37.4 | 14.2035 | 16.0435 | -1.84 | 96.2609 | 12.5 | 15.8141 | -3.3141 |  | 2026-05-03 08:10 | 61.449 | 62.18 | 27.5 | 10.3633 | 11.8841 | -1.5207 | 71.3044 | 9.1 | 11.7141 | -2.6141 |  | 2026-05-03 08:10 | 59.486 | 60.196 | 26.7 | 10.0327 | 11.8841 | -1.8514 | 71.3044 | 8.8 | 11.7141 | -2.9141 |  | 2026-05-03 08:10 | 62.609 | 63.363 | 28 | 10.5605 | 11.8841 | -1.3236 | 71.3044 | 9.4 | 11.7141 | -2.3141 |  | 2026-05-03 08:10 | 64.182 | 66.27 | 28.8 | 11.045 | 11.8841 | -0.83906 | 71.3044 | 9.5 | 11.7141 | -2.2141 |  | 2026-05-03 08:10 | 60.651 | 61.327 | 27.1 | 10.2212 | 11.3062 | -1.085 | 67.8373 | 9 | 11.1445 | -2.1445 |  | 2026-05-03 08:10 | 108.7362 | 123.0164 | -14.2802 | 738.0985 | 96.1 | 121.2573 | -25.1573
2026-05-03 08:00 | 205 | 24.97 | 65.741 | 66.486 | 25 | 11.081 | 13.3172 | -2.2362 | 79.903 | 9.7 | 13.1267 | -3.4267 |  | 2026-05-03 08:00 | 66.307 | 67.078 | 24.3 | 11.1797 | 13.3172 | -2.1375 | 79.903 | 9.3 | 13.1267 | -3.8267 |  | 2026-05-03 08:00 | 65.117 | 65.861 | 25.1 | 10.9768 | 13.3172 | -2.3403 | 79.903 | 9.5 | 13.1267 | -3.6267 |  | 2026-05-03 08:00 | 66.863 | 67.647 | 24.9 | 11.2745 | 13.3172 | -2.0427 | 79.903 | 9.8 | 13.1267 | -3.3267 |  | 2026-05-03 08:00 | 48.491 | 49.16 | 18.4 | 8.1933 | 9.8646 | -1.6712 | 59.1874 | 7.1 | 9.7235 | -2.6235 |  | 2026-05-03 08:00 | 47.214 | 47.85 | 17.9 | 7.975 | 9.8646 | -1.8896 | 59.1874 | 6.9 | 9.7235 | -2.8235 |  | 2026-05-03 08:00 | 49.311 | 49.92 | 18.6 | 8.32 | 9.8646 | -1.5446 | 59.1874 | 7.1 | 9.7235 | -2.6235 |  | 2026-05-03 08:00 | 50.893 | 52.479 | 19.3 | 8.7465 | 9.8646 | -1.1181 | 59.1874 | 7.4 | 9.7235 | -2.3235 |  | 2026-05-03 08:00 | 48.294 | 48.955 | 18.1 | 8.1592 | 9.3849 | -1.2257 | 56.3095 | 7.1 | 9.2507 | -2.1507 |  | 2026-05-03 08:00 | 85.906 | 102.1118 | -16.2058 | 612.671 | 73.9 | 100.6516 | -26.7516
2026-05-03 07:50 | 159 | 21.24 | 48.908 | 49.547 | 15.3 | 8.2578 | 10.4638 | -2.2059 | 62.7825 | 6.8 | 10.3141 | -3.5141 |  | 2026-05-03 07:50 | 48.492 | 49.549 | 15 | 8.2582 | 10.4638 | -2.2056 | 62.7825 | 6.7 | 10.3141 | -3.6141 |  | 2026-05-03 07:50 | 49.137 | 49.789 | 15.6 | 8.2982 | 10.4638 | -2.1656 | 62.7825 | 6.9 | 10.3141 | -3.4141 |  | 2026-05-03 07:50 | 49.851 | 50.523 | 15.1 | 8.4205 | 10.4638 | -2.0433 | 62.7825 | 6.8 | 10.3141 | -3.5141 |  | 2026-05-03 07:50 | 35.993 | 36.545 | 11.3 | 6.0908 | 7.7509 | -1.6601 | 46.5056 | 5 | 7.6401 | -2.6401 |  | 2026-05-03 07:50 | 35.223 | 35.741 | 11 | 5.9568 | 7.7509 | -1.7941 | 46.5056 | 4.9 | 7.6401 | -2.7401 |  | 2026-05-03 07:50 | 37.055 | 37.615 | 11.5 | 6.2692 | 7.7509 | -1.4818 | 46.5056 | 5.2 | 7.6401 | -2.4401 |  | 2026-05-03 07:50 | 38.156 | 39.397 | 11.9 | 6.5662 | 7.7509 | -1.1848 | 46.5056 | 5.4 | 7.6401 | -2.2401 |  | 2026-05-03 07:50 | 36.113 | 36.606 | 11 | 6.101 | 7.374 | -1.273 | 44.2443 | 5 | 7.2686 | -2.2686 |  | 2026-05-03 07:50 | 64.2187 | 80.2328 | -16.0141 | 481.3966 | 52.7 | 79.0854 | -26.3854
2026-05-03 07:40 | 114 | 18.37 | 33.575 | 34.086 | 8.5 | 5.681 | 7.5767 | -1.8957 | 45.4602 | 4.6 | 7.4683 | -2.8683 |  | 2026-05-03 07:40 | 32.168 | 33.086 | 8.3 | 5.5143 | 7.5767 | -2.0624 | 45.4602 | 4.4 | 7.4683 | -3.0683 |  | 2026-05-03 07:40 | 33.616 | 34.138 | 8.7 | 5.6897 | 7.5767 | -1.887 | 45.4602 | 4.5 | 7.4683 | -2.9683 |  | 2026-05-03 07:40 | 33.064 | 33.591 | 8.3 | 5.5985 | 7.5767 | -1.9782 | 45.4602 | 4.4 | 7.4683 | -3.0683 |  | 2026-05-03 07:40 | 24.629 | 25.208 | 6.3 | 4.2013 | 5.6124 | -1.411 | 33.6742 | 3.3 | 5.5321 | -2.2321 |  | 2026-05-03 07:40 | 24.25 | 24.707 | 6.1 | 4.1178 | 5.6124 | -1.4945 | 33.6742 | 3.2 | 5.5321 | -2.3321 |  | 2026-05-03 07:40 | 25.472 | 25.939 | 6.3 | 4.3232 | 5.6124 | -1.2892 | 33.6742 | 3.4 | 5.5321 | -2.1321 |  | 2026-05-03 07:40 | 26.311 | 27.18 | 6.5 | 4.53 | 5.6124 | -1.0824 | 33.6742 | 3.5 | 5.5321 | -2.0321 |  | 2026-05-03 07:40 | 24.577 | 25.036 | 6 | 4.1727 | 5.3395 | -1.1668 | 32.0368 | 3.2 | 5.2631 | -2.0631 |  | 2026-05-03 07:40 | 43.8285 | 58.0957 | -14.2672 | 348.5743 | 34.5 | 57.2649 | -22.7649
2026-05-03 07:30 | 74 | 16.65 | 20.752 | 21.18 | 3.9 | 3.53 | 4.9471 | -1.4171 | 29.6828 | 2.5 | 4.8764 | -2.3764 |  | 2026-05-03 07:30 | 18.774 | 19.265 | 3.9 | 3.2108 | 4.9471 | -1.7363 | 29.6828 | 2.3 | 4.8764 | -2.5764 |  | 2026-05-03 07:30 | 21.024 | 21.466 | 4.2 | 3.5777 | 4.9471 | -1.3695 | 29.6828 | 2.6 | 4.8764 | -2.2764 |  | 2026-05-03 07:30 | 19.49 | 20.199 | 3.9 | 3.3665 | 4.9471 | -1.5806 | 29.6828 | 2.4 | 4.8764 | -2.4764 |  | 2026-05-03 07:30 | 15.107 | 15.803 | 3 | 2.6338 | 3.6645 | -1.0307 | 21.9873 | 1.9 | 3.6121 | -1.7121 |  | 2026-05-03 07:30 | 14.872 | 15.238 | 2.9 | 2.5397 | 3.6645 | -1.1249 | 21.9873 | 1.9 | 3.6121 | -1.7121 |  | 2026-05-03 07:30 | 15.798 | 16.17 | 2.9 | 2.695 | 3.6645 | -0.96955 | 21.9873 | 1.9 | 3.6121 | -1.7121 |  | 2026-05-03 07:30 | 16.289 | 17.047 | 3 | 2.8412 | 3.6645 | -0.82338 | 21.9873 | 2 | 3.6121 | -1.6121 |  | 2026-05-03 07:30 | 14.553 | 14.915 | 2.8 | 2.4858 | 3.4864 | -1.0005 | 20.9182 | 1.8 | 3.4365 | -1.6365 |  | 2026-05-03 07:30 | 26.8805 | 37.9331 | -11.0526 | 227.5988 | 19.3 | 37.3907 | -18.0907
2026-05-03 07:20 | 22 | 16.07 | 10.903 | 11.264 | 1.4 | 1.8773 | 1.4737 | 0.40366 | 8.842 | 1.3 | 1.4526 | -0.1526 |  | 2026-05-03 07:20 | 10.047 | 10.902 | 1.6 | 1.817 | 1.4737 | 0.34333 | 8.842 | 1.2 | 1.4526 | -0.2526 |  | 2026-05-03 07:20 | 10.871 | 11.223 | 1.6 | 1.8705 | 1.4737 | 0.39683 | 8.842 | 1.2 | 1.4526 | -0.2526 |  | 2026-05-03 07:20 | 10.079 | 10.9 | 1.5 | 1.8167 | 1.4737 | 0.34299 | 8.842 | 1.1 | 1.4526 | -0.3526 |  | 2026-05-03 07:20 | 7.972 | 8.625 | 1.1 | 1.4375 | 1.0916 | 0.34589 | 6.5497 | 0.9 | 1.076 | -0.176 |  | 2026-05-03 07:20 | 7.437 | 7.713 | 1 | 1.2855 | 1.0916 | 0.19389 | 6.5497 | 0.8 | 1.076 | -0.276 |  | 2026-05-03 07:20 | 8.281 | 8.587 | 1 | 1.4312 | 1.0916 | 0.33956 | 6.5497 | 1 | 1.076 | -0.075999 |  | 2026-05-03 07:20 | 8.392 | 9.018 | 1 | 1.503 | 1.0916 | 0.41139 | 6.5497 | 1 | 1.076 | -0.075999 |  | 2026-05-03 07:20 | 7.182 | 7.463 | 1 | 1.2438 | 1.0385 | 0.2053 | 6.2312 | 0.8 | 1.0237 | -0.22368 |  | 2026-05-03 07:20 | 14.2825 | 11.2997 | 2.9828 | 67.798 | 9.3 | 11.1381 | -1.8381
2026-05-03 07:10 | 10 | 15.5 | 4.183 | 4.389 | 0.1 | 0.7315 | 0.67115 | 0.060353 | 4.0269 | 0.1 | 0.66155 | -0.56155 |  | 2026-05-03 07:10 | 4.318 | 5.094 | 0.4 | 0.849 | 0.67115 | 0.17785 | 4.0269 | 0.4 | 0.66155 | -0.26155 |  | 2026-05-03 07:10 | 4.244 | 4.444 | 0.4 | 0.74067 | 0.67115 | 0.06952 | 4.0269 | 0.4 | 0.66155 | -0.26155 |  | 2026-05-03 07:10 | 4.205 | 4.957 | 0.4 | 0.82617 | 0.67115 | 0.15502 | 4.0269 | 0.4 | 0.66155 | -0.26155 |  | 2026-05-03 07:10 | 2.996 | 3.639 | 0.2 | 0.6065 | 0.49715 | 0.10935 | 2.9829 | 0.2 | 0.49004 | -0.29004 |  | 2026-05-03 07:10 | 2.971 | 3.117 | 0.2 | 0.5195 | 0.49715 | 0.022354 | 2.9829 | 0.2 | 0.49004 | -0.29004 |  | 2026-05-03 07:10 | 3.072 | 3.223 | 0 | 0.53717 | 0.49715 | 0.040021 | 2.9829 | 0 | 0.49004 | -0.49004 |  | 2026-05-03 07:10 | 3.161 | 3.645 | 0 | 0.6075 | 0.49715 | 0.11035 | 2.9829 | 0 | 0.49004 | -0.49004 |  | 2026-05-03 07:10 | 2.833 | 2.974 | 0.2 | 0.49567 | 0.47297 | 0.022694 | 2.8378 | 0.2 | 0.46621 | -0.26621 |  | 2026-05-03 07:10 | 5.9137 | 5.1461 | 0.76752 | 30.8769 | 1.9 | 5.0726 | -3.1726
2026-05-03 07:00 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 1.088 | 1.636 | 0 | 0.27267 | 0 | 0.27267 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 1.072 | 1.127 | 0 | 0.18783 | 0 | 0.18783 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 1.076 | 1.936 | 0 | 0.32267 | 0 | 0.32267 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 0.631 | 1.158 | 0 | 0.193 | 0 | 0.193 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 0.584 | 0.614 | 0 | 0.10233 | 0 | 0.10233 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 0.532 | 0.559 | 0 | 0.093167 | 0 | 0.093167 | 0 | 0 | 0 | 0 |  | 2026-05-03 07:00 | 1.1717 | 0 | 1.1717 | 0 | 0 | 0 | 0
[110 empty] | Total: - | 19561.0233 | 20565.7608 | -1004.7375 |  | 19310.6 | 20271.6704 | -961.0704
Sum:- | 44973 |  | 14920.303 |  | 93340.2 |  |  |  |  | 2485.2 | 2643.7794 | -158.5794 | 0.98331 |  | 14522.154 |  | 91880.9 |  |  |  |  | 2530.6 | 2643.7794 | -113.1794 | 0.98606 |  | 15001.414 |  | 93796.8 |  |  |  |  | 2501.7 | 2643.7794 | -142.0794 | 0.97212 |  | 15062.968 |  | 94152.3 |  |  |  |  | 2507.9 | 2643.7794 | -135.8794 | 0.9834 |  | 11294.691 |  | 70488.3 |  |  |  |  | 1882.1 | 1958.3551 | -76.2551 | 0.98453 |  | 11184.74 |  | 70004.2 |  |  |  |  | 1864.3 | 1958.3551 | -94.0551 | 0.98161 |  | 11235.548 |  | 70300.3 |  |  |  |  | 1872.3 | 1958.3551 | -86.0551 | 0.98089 |  | 11310.537 |  | 70954.4 |  |  |  |  | 1884.9 | 1958.3551 | -73.4551 | 0.97097 |  | 10689.371 |  | 67066.4 |  |  |  |  | 1781.6 | 1863.1323 | -81.5323 | 0.98463
Formulas:
Time = [Time]

## 6 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-06-03 19:00 | 0 | 34.73 | 0.102 | 0.107 | 2484.2 | 0.017833 | 0 | 0.017833 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 19:00 | 0.088 | 0.17 | 2505.2 | 0.028333 | 0 | 0.028333 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 19:00 | 0.068 | 0.071 | 2458.7 | 0.011833 | 0 | 0.011833 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.068 | 0.142 | 2492 | 0.023667 | 0 | 0.023667 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.067 | 0.088 | 1859.3 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.084 | 0.075 | 1839.9 | 0.0125 | 0 | 0.0125 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.051 | 0.081 | 1837.7 | 0.0135 | 0 | 0.0135 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.067 | 0.085 | 1845.7 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.097 | 0.102 | 1746 | 0.017 | 0 | 0.017 | 0 | 0 | 0 | 0 |  | 2026-06-03 19:00 | 0.1535 | 0 | 0.1535 | 0 | 0.2 | 0 | 0.2 | 1 | 0.98301
2026-06-03 18:50 | 0 | 36.16 | 0.301 | 0.265 | 2484.1 | 0.044167 | 0 | 0.044167 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.44 | 0.71 | 2505.1 | 0.11833 | 0 | 0.11833 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.307 | 0.323 | 2458.7 | 0.053833 | 0 | 0.053833 | 0 | 0.2 | 0 | 0.2 |  | 2026-06-03 18:50 | 0.307 | 0.691 | 2492 | 0.11517 | 0 | 0.11517 | 0 | 0.2 | 0 | 0.2 |  | 2026-06-03 18:50 | 0.109 | 0.175 | 1859.3 | 0.029167 | 0 | 0.029167 | 0 | 0.2 | 0 | 0.2 |  | 2026-06-03 18:50 | 0.041 | 0.088 | 1839.9 | 0.014667 | 0 | 0.014667 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.017 | 0.078 | 1837.7 | 0.013 | 0 | 0.013 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.112 | 0.442 | 1845.7 | 0.073667 | 0 | 0.073667 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.014 | 0.069 | 1746 | 0.0115 | 0 | 0.0115 | 0 | 0.1 | 0 | 0.1 |  | 2026-06-03 18:50 | 0.4735 | 0 | 0.4735 | 0 | 1.2 | 0 | 1.2 | 2 | 0.98285
2026-06-03 18:40 | 1 | 37.6 | 2.303 | 2.389 | 2484 | 0.39817 | 0.06209 | 0.33608 | 0.37254 | 0.7 | 0.061203 | 0.6388 |  | 2026-06-03 18:40 | 2.339 | 2.831 | 2505 | 0.47183 | 0.06209 | 0.40974 | 0.37254 | 0.8 | 0.061203 | 0.7388 |  | 2026-06-03 18:40 | 2.325 | 2.445 | 2458.5 | 0.4075 | 0.06209 | 0.34541 | 0.37254 | 0.7 | 0.061203 | 0.6388 |  | 2026-06-03 18:40 | 2.19 | 2.744 | 2491.8 | 0.45733 | 0.06209 | 0.39524 | 0.37254 | 0.7 | 0.061203 | 0.6388 |  | 2026-06-03 18:40 | 1.585 | 1.768 | 1859.1 | 0.29467 | 0.045993 | 0.24867 | 0.27596 | 0.4 | 0.045335 | 0.35466 |  | 2026-06-03 18:40 | 1.532 | 1.611 | 1839.8 | 0.2685 | 0.045993 | 0.22251 | 0.27596 | 0.5 | 0.045335 | 0.45466 |  | 2026-06-03 18:40 | 1.545 | 1.615 | 1837.6 | 0.26917 | 0.045993 | 0.22317 | 0.27596 | 0.5 | 0.045335 | 0.45466 |  | 2026-06-03 18:40 | 1.623 | 1.99 | 1845.6 | 0.33167 | 0.045993 | 0.28567 | 0.27596 | 0.5 | 0.045335 | 0.45466 |  | 2026-06-03 18:40 | 1.422 | 1.495 | 1745.9 | 0.24917 | 0.043757 | 0.20541 | 0.26254 | 0.5 | 0.043131 | 0.45687 |  | 2026-06-03 18:40 | 3.148 | 0.47609 | 2.6719 | 2.8565 | 5.3 | 0.46928 | 4.8307 | 3 | 0.97295
2026-06-03 18:30 | 13 | 39.61 | 6.095 | 6.37 | 2483.3 | 1.0617 | 0.80124 | 0.26043 | 4.8074 | 1.5 | 0.78978 | 0.71022 |  | 2026-06-03 18:30 | 6.801 | 7.144 | 2504.2 | 1.1907 | 0.80124 | 0.38943 | 4.8074 | 1.7 | 0.78978 | 0.91022 |  | 2026-06-03 18:30 | 6.384 | 6.674 | 2457.8 | 1.1123 | 0.80124 | 0.3111 | 4.8074 | 1.6 | 0.78978 | 0.81022 |  | 2026-06-03 18:30 | 6.595 | 7.037 | 2491.1 | 1.1728 | 0.80124 | 0.3716 | 4.8074 | 1.7 | 0.78978 | 0.91022 |  | 2026-06-03 18:30 | 4.729 | 4.952 | 1858.7 | 0.82533 | 0.59351 | 0.23183 | 3.561 | 1.3 | 0.58502 | 0.71498 |  | 2026-06-03 18:30 | 4.62 | 4.839 | 1839.3 | 0.8065 | 0.59351 | 0.21299 | 3.561 | 1.2 | 0.58502 | 0.61498 |  | 2026-06-03 18:30 | 4.559 | 4.722 | 1837.1 | 0.787 | 0.59351 | 0.19349 | 3.561 | 1.1 | 0.58502 | 0.51498 |  | 2026-06-03 18:30 | 4.125 | 4.463 | 1845.1 | 0.74383 | 0.59351 | 0.15033 | 3.561 | 0.9 | 0.58502 | 0.31498 |  | 2026-06-03 18:30 | 3.977 | 4.17 | 1745.4 | 0.695 | 0.56465 | 0.13035 | 3.3879 | 0.9 | 0.55657 | 0.34343 |  | 2026-06-03 18:30 | 8.3952 | 6.1436 | 2.2515 | 36.8617 | 11.9 | 6.0558 | 5.8442 | 4 | 0.983
2026-06-03 18:20 | 24 | 41.61 | 12.128 | 12.522 | 2481.8 | 2.087 | 1.4683 | 0.61871 | 8.8097 | 2.8 | 1.4473 | 1.3527 |  | 2026-06-03 18:20 | 14.566 | 14.282 | 2502.5 | 2.3803 | 1.4683 | 0.91204 | 8.8097 | 3.1 | 1.4473 | 1.6527 |  | 2026-06-03 18:20 | 13.21 | 13.616 | 2456.2 | 2.2693 | 1.4683 | 0.80104 | 8.8097 | 3 | 1.4473 | 1.5527 |  | 2026-06-03 18:20 | 13.625 | 14.125 | 2489.4 | 2.3542 | 1.4683 | 0.88588 | 8.8097 | 3 | 1.4473 | 1.5527 |  | 2026-06-03 18:20 | 9.968 | 10.327 | 1857.4 | 1.7212 | 1.0876 | 0.63354 | 6.5257 | 2.2 | 1.0721 | 1.1279 |  | 2026-06-03 18:20 | 9.648 | 10.003 | 1838.1 | 1.6672 | 1.0876 | 0.57954 | 6.5257 | 2.1 | 1.0721 | 1.0279 |  | 2026-06-03 18:20 | 9.618 | 9.973 | 1836 | 1.6622 | 1.0876 | 0.57454 | 6.5257 | 2.2 | 1.0721 | 1.1279 |  | 2026-06-03 18:20 | 7.034 | 7.563 | 1844.2 | 1.2605 | 1.0876 | 0.17288 | 6.5257 | 1.5 | 1.0721 | 0.42793 |  | 2026-06-03 18:20 | 7.962 | 8.283 | 1744.5 | 1.3805 | 1.0347 | 0.34576 | 6.2084 | 1.9 | 1.0199 | 0.88006 |  | 2026-06-03 18:20 | 16.7823 | 11.2584 | 5.5239 | 67.5504 | 21.8 | 11.0974 | 10.7026 | 5 | 0.98447
2026-06-03 18:10 | 36 | 43.62 | 22.201 | 22.707 | 2479 | 3.7845 | 2.186 | 1.5985 | 13.1159 | 4.7 | 2.1547 | 2.5453 |  | 2026-06-03 18:10 | 24.043 | 24.271 | 2499.4 | 4.0452 | 2.186 | 1.8592 | 13.1159 | 5.1 | 2.1547 | 2.9453 |  | 2026-06-03 18:10 | 23.586 | 24.109 | 2453.2 | 4.0182 | 2.186 | 1.8322 | 13.1159 | 5 | 2.1547 | 2.8453 |  | 2026-06-03 18:10 | 23.457 | 23.977 | 2486.4 | 3.9962 | 2.186 | 1.8102 | 13.1159 | 5 | 2.1547 | 2.8453 |  | 2026-06-03 18:10 | 17.515 | 17.959 | 1855.2 | 2.9932 | 1.6192 | 1.3739 | 9.7155 | 3.7 | 1.5961 | 2.1039 |  | 2026-06-03 18:10 | 16.783 | 17.21 | 1836 | 2.8683 | 1.6192 | 1.2491 | 9.7155 | 3.6 | 1.5961 | 2.0039 |  | 2026-06-03 18:10 | 16.984 | 17.416 | 1833.8 | 2.9027 | 1.6192 | 1.2834 | 9.7155 | 3.6 | 1.5961 | 2.0039 |  | 2026-06-03 18:10 | 12.098 | 12.704 | 1842.7 | 2.1173 | 1.6192 | 0.49808 | 9.7155 | 2.9 | 1.5961 | 1.3039 |  | 2026-06-03 18:10 | 15.21 | 15.61 | 1742.6 | 2.6017 | 1.5405 | 1.0612 | 9.2431 | 3.3 | 1.5185 | 1.7815 |  | 2026-06-03 18:10 | 29.3272 | 16.7615 | 12.5657 | 100.5687 | 36.9 | 16.5218 | 20.3782 | 6 | 0.98196
2026-06-03 18:00 | 48 | 45.92 | 35.141 | 35.745 | 2474.3 | 5.9575 | 2.8895 | 3.068 | 17.3373 | 7 | 2.8482 | 4.1518 |  | 2026-06-03 18:00 | 37.454 | 38.102 | 2494.3 | 6.3503 | 2.8895 | 3.4608 | 17.3373 | 7.3 | 2.8482 | 4.4518 |  | 2026-06-03 18:00 | 36.422 | 37.048 | 2448.2 | 6.1747 | 2.8895 | 3.2851 | 17.3373 | 7.3 | 2.8482 | 4.4518 |  | 2026-06-03 18:00 | 36.42 | 37.067 | 2481.4 | 6.1778 | 2.8895 | 3.2883 | 17.3373 | 7.3 | 2.8482 | 4.4518 |  | 2026-06-03 18:00 | 27.426 | 27.974 | 1851.5 | 4.6623 | 2.1404 | 2.5219 | 12.8424 | 5.5 | 2.1098 | 3.3902 |  | 2026-06-03 18:00 | 26.145 | 26.679 | 1832.4 | 4.4465 | 2.1404 | 2.3061 | 12.8424 | 5.2 | 2.1098 | 3.0902 |  | 2026-06-03 18:00 | 26.38 | 26.918 | 1830.2 | 4.4863 | 2.1404 | 2.3459 | 12.8424 | 5.4 | 2.1098 | 3.2902 |  | 2026-06-03 18:00 | 23.907 | 24.62 | 1839.8 | 4.1033 | 2.1404 | 1.9629 | 12.8424 | 5.2 | 2.1098 | 3.0902 |  | 2026-06-03 18:00 | 24.137 | 24.657 | 1739.3 | 4.1095 | 2.0363 | 2.0732 | 12.218 | 4.9 | 2.0072 | 2.8928 |  | 2026-06-03 18:00 | 46.4683 | 22.1562 | 24.3122 | 132.937 | 55.1 | 21.8393 | 33.2607 | 7 | 0.98121
2026-06-03 17:50 | 162 | 47.64 | 49.908 | 50.683 | 2467.3 | 8.4472 | 9.6889 | -1.2417 | 58.1333 | 9.8 | 9.5503 | 0.24967 |  | 2026-06-03 17:50 | 52.598 | 53.394 | 2487 | 8.899 | 9.6889 | -0.78988 | 58.1333 | 10 | 9.5503 | 0.44967 |  | 2026-06-03 17:50 | 51.102 | 51.88 | 2440.9 | 8.6467 | 9.6889 | -1.0422 | 58.1333 | 9.9 | 9.5503 | 0.34967 |  | 2026-06-03 17:50 | 50.916 | 51.697 | 2474.1 | 8.6162 | 9.6889 | -1.0727 | 58.1333 | 9.8 | 9.5503 | 0.24967 |  | 2026-06-03 17:50 | 38.449 | 39.098 | 1846 | 6.5163 | 7.177 | -0.66062 | 43.0617 | 7.4 | 7.0743 | 0.32568 |  | 2026-06-03 17:50 | 36.771 | 37.407 | 1827.2 | 6.2345 | 7.177 | -0.94245 | 43.0617 | 7.1 | 7.0743 | 0.02568 |  | 2026-06-03 17:50 | 37.219 | 37.851 | 1824.8 | 6.3085 | 7.177 | -0.86845 | 43.0617 | 7 | 7.0743 | -0.07432 |  | 2026-06-03 17:50 | 36.517 | 37.486 | 1834.6 | 6.2477 | 7.177 | -0.92928 | 43.0617 | 6.9 | 7.0743 | -0.17432 |  | 2026-06-03 17:50 | 34.295 | 34.885 | 1734.4 | 5.8142 | 6.828 | -1.0138 | 40.9679 | 6.5 | 6.7303 | -0.23034 |  | 2026-06-03 17:50 | 65.7302 | 74.2913 | -8.5611 | 445.7479 | 74.4 | 73.229 | 1.171 | 8 | 0.9715
2026-06-03 17:40 | 212 | 48.22 | 67.429 | 68.296 | 2457.5 | 11.3827 | 12.6513 | -1.2687 | 75.908 | 12.6 | 12.4704 | 0.12959 |  | 2026-06-03 17:40 | 68.085 | 68.996 | 2477 | 11.4993 | 12.6513 | -1.152 | 75.908 | 12.8 | 12.4704 | 0.32959 |  | 2026-06-03 17:40 | 67.852 | 68.778 | 2431 | 11.463 | 12.6513 | -1.1883 | 75.908 | 12.6 | 12.4704 | 0.12959 |  | 2026-06-03 17:40 | 67.259 | 68.152 | 2464.3 | 11.3587 | 12.6513 | -1.2927 | 75.908 | 12.6 | 12.4704 | 0.12959 |  | 2026-06-03 17:40 | 50.567 | 51.362 | 1838.6 | 8.5603 | 9.3714 | -0.81102 | 56.2281 | 9.5 | 9.2373 | 0.26266 |  | 2026-06-03 17:40 | 48.531 | 49.27 | 1820.1 | 8.2117 | 9.3714 | -1.1597 | 56.2281 | 9.1 | 9.2373 | -0.13734 |  | 2026-06-03 17:40 | 48.859 | 49.608 | 1817.8 | 8.268 | 9.3714 | -1.1034 | 56.2281 | 9.2 | 9.2373 | -0.037342 |  | 2026-06-03 17:40 | 48.009 | 49.436 | 1827.7 | 8.2393 | 9.3714 | -1.132 | 56.2281 | 9.1 | 9.2373 | -0.13734 |  | 2026-06-03 17:40 | 45.257 | 45.965 | 1727.9 | 7.6608 | 8.9157 | -1.2548 | 53.4941 | 8.5 | 8.7882 | -0.28819 |  | 2026-06-03 17:40 | 86.6438 | 97.0064 | -10.3626 | 582.0384 | 96 | 95.6192 | 0.3808 | 9 | 0.9848
2026-06-03 17:30 | 258 | 48.5 | 83.632 | 84.639 | 2444.9 | 14.1065 | 15.38 | -1.2735 | 92.28 | 14.9 | 15.1601 | -0.26007 |  | 2026-06-03 17:30 | 85.197 | 86.275 | 2464.2 | 14.3792 | 15.38 | -1.0008 | 92.28 | 15.4 | 15.1601 | 0.23993 |  | 2026-06-03 17:30 | 83.498 | 84.869 | 2418.4 | 14.1448 | 15.38 | -1.2352 | 92.28 | 15.5 | 15.1601 | 0.33993 |  | 2026-06-03 17:30 | 84.033 | 85.105 | 2451.7 | 14.1842 | 15.38 | -1.1958 | 92.28 | 15.5 | 15.1601 | 0.33993 |  | 2026-06-03 17:30 | 63.099 | 63.956 | 1829.1 | 10.6593 | 11.3926 | -0.73326 | 68.3556 | 11.6 | 11.2297 | 0.37032 |  | 2026-06-03 17:30 | 61.003 | 61.813 | 1811 | 10.3022 | 11.3926 | -1.0904 | 68.3556 | 11.3 | 11.2297 | 0.070321 |  | 2026-06-03 17:30 | 61.219 | 62.044 | 1808.6 | 10.3407 | 11.3926 | -1.0519 | 68.3556 | 11.3 | 11.2297 | 0.070321 |  | 2026-06-03 17:30 | 60.594 | 62.404 | 1818.6 | 10.4007 | 11.3926 | -0.99193 | 68.3556 | 11.2 | 11.2297 | -0.029679 |  | 2026-06-03 17:30 | 56.953 | 57.768 | 1719.4 | 9.628 | 10.8386 | -1.2106 | 65.0319 | 10.6 | 10.6836 | -0.083649 |  | 2026-06-03 17:30 | 108.1455 | 117.929 | -9.7835 | 707.5741 | 117.3 | 116.2426 | 1.0574
2026-06-03 17:20 | 306 | 48.22 | 100.989 | 102.195 | 2430 | 17.0325 | 18.2609 | -1.2284 | 109.5653 | 19.3 | 17.9997 | 1.3003 |  | 2026-06-03 17:20 | 103.207 | 104.482 | 2448.8 | 17.4137 | 18.2609 | -0.84721 | 109.5653 | 18.4 | 17.9997 | 0.40025 |  | 2026-06-03 17:20 | 101.063 | 102.78 | 2402.9 | 17.13 | 18.2609 | -1.1309 | 109.5653 | 18.2 | 17.9997 | 0.20025 |  | 2026-06-03 17:20 | 101.825 | 103.093 | 2436.2 | 17.1822 | 18.2609 | -1.0787 | 109.5653 | 18.3 | 17.9997 | 0.30025 |  | 2026-06-03 17:20 | 76.437 | 77.428 | 1817.5 | 12.9047 | 13.5266 | -0.62191 | 81.1594 | 13.7 | 13.3331 | 0.36686 |  | 2026-06-03 17:20 | 74.135 | 75.096 | 1799.7 | 12.516 | 13.5266 | -1.0106 | 81.1594 | 13.3 | 13.3331 | -0.033144 |  | 2026-06-03 17:20 | 74.395 | 75.367 | 1797.3 | 12.5612 | 13.5266 | -0.96541 | 81.1594 | 13.3 | 13.3331 | -0.033144 |  | 2026-06-03 17:20 | 73.787 | 75.758 | 1807.4 | 12.6263 | 13.5266 | -0.90024 | 81.1594 | 13.4 | 13.3331 | 0.066856 |  | 2026-06-03 17:20 | 69.452 | 70.381 | 1708.8 | 11.7302 | 12.8689 | -1.1387 | 77.2132 | 12.6 | 12.6848 | -0.084836 |  | 2026-06-03 17:20 | 131.0967 | 140.0187 | -8.922 | 840.112 | 140.5 | 138.0164 | 2.4836
2026-06-03 17:10 | 352 | 48.22 | 120.291 | 121.243 | 2410.7 | 20.2072 | 21.006 | -0.79881 | 126.0358 | 16 | 20.7056 | -4.7056 |  | 2026-06-03 17:10 | 119.049 | 120.556 | 2430.4 | 20.0927 | 21.006 | -0.91331 | 126.0358 | 16.9 | 20.7056 | -3.8056 |  | 2026-06-03 17:10 | 118.424 | 120.503 | 2384.7 | 20.0838 | 21.006 | -0.92214 | 126.0358 | 16.9 | 20.7056 | -3.8056 |  | 2026-06-03 17:10 | 118.734 | 120.249 | 2417.9 | 20.0415 | 21.006 | -0.96447 | 126.0358 | 17 | 20.7056 | -3.7056 |  | 2026-06-03 17:10 | 88.899 | 90.065 | 1803.8 | 15.0108 | 15.56 | -0.54915 | 93.3599 | 13 | 15.3375 | -2.3375 |  | 2026-06-03 17:10 | 86.475 | 87.578 | 1786.4 | 14.5963 | 15.56 | -0.96365 | 93.3599 | 12.7 | 15.3375 | -2.6375 |  | 2026-06-03 17:10 | 86.588 | 87.675 | 1784 | 14.6125 | 15.56 | -0.94748 | 93.3599 | 12.7 | 15.3375 | -2.6375 |  | 2026-06-03 17:10 | 86.208 | 88.204 | 1794 | 14.7007 | 15.56 | -0.85931 | 93.3599 | 13 | 15.3375 | -2.3375 |  | 2026-06-03 17:10 | 81.364 | 82.419 | 1696.2 | 13.7365 | 14.8034 | -1.0669 | 88.8204 | 11.9 | 14.5917 | -2.6917 |  | 2026-06-03 17:10 | 153.082 | 161.0672 | -7.9852 | 966.4033 | 130.1 | 158.764 | -28.664
2026-06-03 17:00 | 398 | 48.5 | 0 | 0 | 2394.7 | 0 | 23.7257 | -23.7257 | 142.3544 | 0.4 | 23.3865 | -22.9865 |  | 2026-06-03 17:00 | 0 | 0 | 2413.5 | 0 | 23.7257 | -23.7257 | 142.3544 | 0.1 | 23.3865 | -23.2865 |  | 2026-06-03 17:00 | 0 | 0 | 2367.8 | 0 | 23.7257 | -23.7257 | 142.3544 | 0 | 23.3865 | -23.3865 |  | 2026-06-03 17:00 | 0 | 0 | 2400.9 | 0 | 23.7257 | -23.7257 | 142.3544 | 0 | 23.3865 | -23.3865 |  | 2026-06-03 17:00 | 0 | 0 | 1790.8 | 0 | 17.5746 | -17.5746 | 105.4477 | 0 | 17.3233 | -17.3233 |  | 2026-06-03 17:00 | 0 | 0 | 1773.7 | 0 | 17.5746 | -17.5746 | 105.4477 | 0 | 17.3233 | -17.3233 |  | 2026-06-03 17:00 | 0 | 0 | 1771.3 | 0 | 17.5746 | -17.5746 | 105.4477 | 0 | 17.3233 | -17.3233 |  | 2026-06-03 17:00 | 0 | 0 | 1781 | 0 | 17.5746 | -17.5746 | 105.4477 | 0 | 17.3233 | -17.3233 |  | 2026-06-03 17:00 | 0 | 0 | 1684.3 | 0 | 16.7201 | -16.7201 | 100.3205 | 0 | 16.481 | -16.481 |  | 2026-06-03 17:00 | 0 | 181.9215 | -181.9215 | 1091.5291 | 0.5 | 179.32 | -178.82
2026-06-03 16:50 | 442 | 48.79 | 153.9 | 155.848 | 2394.3 | 25.9747 | 26.3195 | -0.34488 | 157.9173 | 25.7 | 25.9432 | -0.24317 |  | 2026-06-03 16:50 | 154.816 | 156.871 | 2413.4 | 26.1452 | 26.3195 | -0.17438 | 157.9173 | 27.7 | 25.9432 | 1.7568 |  | 2026-06-03 16:50 | 0 | 0 | 2367.8 | 0 | 26.3195 | -26.3195 | 157.9173 | 25.5 | 25.9432 | -0.44317 |  | 2026-06-03 16:50 | 0 | 0 | 2400.9 | 0 | 26.3195 | -26.3195 | 157.9173 | 25.6 | 25.9432 | -0.34317 |  | 2026-06-03 16:50 | 0 | 0 | 1790.8 | 0 | 19.496 | -19.496 | 116.9757 | 19.2 | 19.2172 | -0.017166 |  | 2026-06-03 16:50 | 0 | 0 | 1773.7 | 0 | 19.496 | -19.496 | 116.9757 | 18.9 | 19.2172 | -0.31717 |  | 2026-06-03 16:50 | 0 | 0 | 1771.3 | 0 | 19.496 | -19.496 | 116.9757 | 19 | 19.2172 | -0.21717 |  | 2026-06-03 16:50 | 0 | 0 | 1781 | 0 | 19.496 | -19.496 | 116.9757 | 18.8 | 19.2172 | -0.41717 |  | 2026-06-03 16:50 | 0 | 0 | 1684.3 | 0 | 18.548 | -18.548 | 111.2879 | 17.7 | 18.2828 | -0.58275 |  | 2026-06-03 16:50 | 52.1198 | 201.81 | -149.6902 | 1210.86 | 198.1 | 198.9241 | -0.82411
2026-06-03 16:40 | 488 | 49.08 | 170.277 | 172.502 | 2368.6 | 28.7503 | 29.0265 | -0.27617 | 174.159 | 29.1 | 28.6114 | 0.48857 |  | 2026-06-03 16:40 | 172.684 | 175.012 | 2385.7 | 29.1687 | 29.0265 | 0.14216 | 174.159 | 28.2 | 28.6114 | -0.41143 |  | 2026-06-03 16:40 | 169.318 | 172.892 | 2342.3 | 28.8153 | 29.0265 | -0.21117 | 174.159 | 29.8 | 28.6114 | 1.1886 |  | 2026-06-03 16:40 | 170.034 | 172.308 | 2375.3 | 28.718 | 29.0265 | -0.30851 | 174.159 | 30 | 28.6114 | 1.3886 |  | 2026-06-03 16:40 | 128.04 | 129.692 | 1771.6 | 21.6153 | 21.5011 | 0.11422 | 129.0067 | 22.5 | 21.1937 | 1.3063 |  | 2026-06-03 16:40 | 124.522 | 126.133 | 1754.8 | 21.0222 | 21.5011 | -0.47895 | 129.0067 | 21.7 | 21.1937 | 0.50635 |  | 2026-06-03 16:40 | 124.899 | 126.493 | 1752.3 | 21.0822 | 21.5011 | -0.41895 | 129.0067 | 21.6 | 21.1937 | 0.40635 |  | 2026-06-03 16:40 | 124.361 | 127.669 | 1762.2 | 21.2782 | 21.5011 | -0.22295 | 129.0067 | 21.6 | 21.1937 | 0.40635 |  | 2026-06-03 16:40 | 117.218 | 118.738 | 1666.6 | 19.7897 | 20.4557 | -0.66598 | 122.7339 | 20.4 | 20.1631 | 0.23687 |  | 2026-06-03 16:40 | 220.2398 | 222.5662 | -2.3263 | 1335.3969 | 224.9 | 219.3835 | 5.5165
2026-06-03 16:30 | 528 | 48.79 | 183.854 | 186.313 | 2339.5 | 31.0522 | 31.4405 | -0.38837 | 188.6432 | 32.3 | 30.9909 | 1.3091 |  | 2026-06-03 16:30 | 185.944 | 188.1 | 2357.5 | 31.35 | 31.4405 | -0.090541 | 188.6432 | 67.5 | 30.9909 | 36.5091 |  | 2026-06-03 16:30 | 183.216 | 187.107 | 2312.5 | 31.1845 | 31.4405 | -0.25604 | 188.6432 | 31.6 | 30.9909 | 0.60906 |  | 2026-06-03 16:30 | 184.652 | 187.198 | 2345.3 | 31.1997 | 31.4405 | -0.24087 | 188.6432 | 31.8 | 30.9909 | 0.80906 |  | 2026-06-03 16:30 | 138.379 | 140.173 | 1749.1 | 23.3622 | 23.2893 | 0.072877 | 139.7357 | 23.9 | 22.9563 | 0.94375 |  | 2026-06-03 16:30 | 134.993 | 136.857 | 1733.1 | 22.8095 | 23.2893 | -0.47979 | 139.7357 | 23.3 | 22.9563 | 0.34375 |  | 2026-06-03 16:30 | 134.878 | 136.751 | 1730.7 | 22.7918 | 23.2893 | -0.49746 | 139.7357 | 23.4 | 22.9563 | 0.44375 |  | 2026-06-03 16:30 | 134.604 | 138.241 | 1740.6 | 23.0402 | 23.2893 | -0.24912 | 139.7357 | 23.3 | 22.9563 | 0.34375 |  | 2026-06-03 16:30 | 127.193 | 128.896 | 1646.2 | 21.4827 | 22.1569 | -0.67421 | 132.9412 | 22.3 | 21.84 | 0.45997 |  | 2026-06-03 16:30 | 238.2727 | 241.0762 | -2.8035 | 1446.4572 | 279.4 | 237.6288 | 41.7712
2026-06-03 16:20 | 571 | 49.08 | 199.483 | 202.213 | 2307.2 | 33.7022 | 33.9634 | -0.26123 | 203.7804 | 34.8 | 33.4777 | 1.3223 | [5 empty] | 0 | 33.9634 | -33.9634 | 203.7804 | 0 | 33.4777 | -33.4777 |  | 2026-06-03 16:20 | 197.985 | 202.806 | 2280.9 | 33.801 | 33.9634 | -0.16239 | 203.7804 | 34.1 | 33.4777 | 0.62228 |  | 2026-06-03 16:20 | 199.197 | 202.005 | 2313.5 | 33.6675 | 33.9634 | -0.29589 | 203.7804 | 34.3 | 33.4777 | 0.82228 |  | 2026-06-03 16:20 | 149.669 | 151.656 | 1725.2 | 25.276 | 25.1581 | 0.11793 | 150.9484 | 25.7 | 24.7983 | 0.90169 |  | 2026-06-03 16:20 | 146.107 | 148.119 | 1709.8 | 24.6865 | 25.1581 | -0.47157 | 150.9484 | 25.1 | 24.7983 | 0.30169 |  | 2026-06-03 16:20 | 146.446 | 148.39 | 1707.3 | 24.7317 | 25.1581 | -0.4264 | 150.9484 | 25.5 | 24.7983 | 0.70169 |  | 2026-06-03 16:20 | 145.984 | 149.873 | 1717.3 | 24.9788 | 25.1581 | -0.17924 | 150.9484 | 25.5 | 24.7983 | 0.70169 |  | 2026-06-03 16:20 | 137.815 | 139.659 | 1623.9 | 23.2765 | 23.9348 | -0.65829 | 143.6087 | 23.7 | 23.5925 | 0.10748 |  | 2026-06-03 16:20 | 224.1202 | 260.4206 | -36.3005 | 1562.5238 | 228.7 | 256.6966 | -27.9966
2026-06-03 16:10 | 618 | 48.5 | 215.76 | 218.779 | 2272.4 | 36.4632 | 36.8405 | -0.3773 | 221.0428 | 36.6 | 36.3136 | 0.28635 |  | 2026-06-03 16:10 | 217.898 | 220.985 | 2290 | 36.8308 | 36.8405 | -0.0096349 | 221.0428 | 36.9 | 36.3136 | 0.58635 |  | 2026-06-03 16:10 | 213.986 | 219.008 | 2246.8 | 36.5013 | 36.8405 | -0.33913 | 221.0428 | 36.3 | 36.3136 | -0.01365 |  | 2026-06-03 16:10 | 215.17 | 218.247 | 2279.2 | 36.3745 | 36.8405 | -0.46597 | 221.0428 | 36.5 | 36.3136 | 0.18635 |  | 2026-06-03 16:10 | 161.712 | 163.875 | 1699.5 | 27.3125 | 27.2892 | 0.023264 | 163.7354 | 27.5 | 26.899 | 0.601 |  | 2026-06-03 16:10 | 158.068 | 160.361 | 1684.7 | 26.7268 | 27.2892 | -0.5624 | 163.7354 | 27.3 | 26.899 | 0.401 |  | 2026-06-03 16:10 | 158.269 | 160.72 | 1681.8 | 26.7867 | 27.2892 | -0.50257 | 163.7354 | 26.9 | 26.899 | 0.0010004 |  | 2026-06-03 16:10 | 157.698 | 162.051 | 1691.8 | 27.0085 | 27.2892 | -0.28074 | 163.7354 | 26.8 | 26.899 | -0.099 |  | 2026-06-03 16:10 | 149.082 | 151.092 | 1600.2 | 25.182 | 25.9623 | -0.78033 | 155.774 | 25.3 | 25.5911 | -0.29107 |  | 2026-06-03 16:10 | 279.1863 | 282.4811 | -3.2948 | 1694.8869 | 280.1 | 278.4417 | 1.6583
2026-06-03 16:00 | 651 | 49.36 | 228.471 | 230.791 | 2235.8 | 38.4652 | 38.6804 | -0.21523 | 232.0824 | 40.1 | 38.1273 | 1.9727 |  | 2026-06-03 16:00 | 227.889 | 231.242 | 2253.1 | 38.5403 | 38.6804 | -0.14006 | 232.0824 | 39.2 | 38.1273 | 1.0727 |  | 2026-06-03 16:00 | 223.999 | 229.255 | 2210.5 | 38.2092 | 38.6804 | -0.47123 | 232.0824 | 38.6 | 38.1273 | 0.47273 |  | 2026-06-03 16:00 | 225.984 | 229.332 | 2242.7 | 38.222 | 38.6804 | -0.4584 | 232.0824 | 38.9 | 38.1273 | 0.77273 |  | 2026-06-03 16:00 | 169.952 | 172.295 | 1672 | 28.7158 | 28.6521 | 0.063687 | 171.9129 | 29.2 | 28.2424 | 0.95758 |  | 2026-06-03 16:00 | 166.211 | 168.657 | 1657.4 | 28.1095 | 28.6521 | -0.54265 | 171.9129 | 28.1 | 28.2424 | -0.14242 |  | 2026-06-03 16:00 | 166.529 | 169.218 | 1654.9 | 28.203 | 28.6521 | -0.44915 | 171.9129 | 28.6 | 28.2424 | 0.35758 |  | 2026-06-03 16:00 | 166.16 | 170.827 | 1665 | 28.4712 | 28.6521 | -0.18098 | 171.9129 | 28.2 | 28.2424 | -0.042421 |  | 2026-06-03 16:00 | 157.04 | 159.205 | 1574.9 | 26.5342 | 27.259 | -0.7248 | 163.5538 | 27 | 26.8692 | 0.13083 |  | 2026-06-03 16:00 | 293.4703 | 296.5891 | -3.1188 | 1779.5349 | 297.9 | 292.3479 | 5.5521
2026-06-03 15:50 | 690 | 49.36 | 240.474 | 242.914 | 2195.7 | 40.4857 | 40.9977 | -0.51199 | 245.9859 | 39 | 40.4114 | -1.4114 |  | 2026-06-03 15:50 | 241.917 | 244.337 | 2213.9 | 40.7228 | 40.9977 | -0.27482 | 245.9859 | 40.4 | 40.4114 | -0.01139 |  | 2026-06-03 15:50 | 236.527 | 242.482 | 2171.9 | 40.4137 | 40.9977 | -0.58399 | 245.9859 | 40.9 | 40.4114 | 0.48861 |  | 2026-06-03 15:50 | 238.257 | 241.917 | 2203.8 | 40.3195 | 40.9977 | -0.67816 | 245.9859 | 41.2 | 40.4114 | 0.78861 |  | 2026-06-03 15:50 | 178.725 | 181.251 | 1642.8 | 30.2085 | 30.3686 | -0.16013 | 182.2118 | 30.9 | 29.9344 | 0.96564 |  | 2026-06-03 15:50 | 174.772 | 177.567 | 1629.3 | 29.5945 | 30.3686 | -0.77413 | 182.2118 | 30.3 | 29.9344 | 0.36564 |  | 2026-06-03 15:50 | 175.267 | 178.007 | 1626.3 | 29.6678 | 30.3686 | -0.7008 | 182.2118 | 29.9 | 29.9344 | -0.034363 |  | 2026-06-03 15:50 | 174.796 | 179.79 | 1636.8 | 29.965 | 30.3686 | -0.40363 | 182.2118 | 30.2 | 29.9344 | 0.26564 |  | 2026-06-03 15:50 | 165.315 | 167.668 | 1547.9 | 27.9447 | 28.892 | -0.94733 | 173.352 | 28.2 | 28.4788 | -0.27884 |  | 2026-06-03 15:50 | 309.3222 | 314.3572 | -5.035 | 1886.143 | 311 | 309.8619 | 1.1381
2026-06-03 15:40 | 729 | 49.08 | 251.052 | 254.188 | 2156.7 | 42.3647 | 43.3613 | -0.99665 | 260.1679 | 42.7 | 42.7413 | -0.041254 |  | 2026-06-03 15:40 | 252.559 | 256.483 | 2173.5 | 42.7472 | 43.3613 | -0.61415 | 260.1679 | 43 | 42.7413 | 0.25875 |  | 2026-06-03 15:40 | 249.117 | 255.644 | 2131 | 42.6073 | 43.3613 | -0.75399 | 260.1679 | 42.3 | 42.7413 | -0.44125 |  | 2026-06-03 15:40 | 251.104 | 255.006 | 2162.6 | 42.501 | 43.3613 | -0.86032 | 260.1679 | 42.6 | 42.7413 | -0.14125 |  | 2026-06-03 15:40 | 188.567 | 191.283 | 1611.9 | 31.8805 | 32.1195 | -0.239 | 192.717 | 32.1 | 31.6602 | 0.43981 |  | 2026-06-03 15:40 | 184.43 | 187.683 | 1599 | 31.2805 | 32.1195 | -0.839 | 192.717 | 31.3 | 31.6602 | -0.36019 |  | 2026-06-03 15:40 | 184.624 | 187.837 | 1596.4 | 31.3062 | 32.1195 | -0.81333 | 192.717 | 31.4 | 31.6602 | -0.26019 |  | 2026-06-03 15:40 | 184.655 | 189.722 | 1606.6 | 31.6203 | 32.1195 | -0.49916 | 192.717 | 31.4 | 31.6602 | -0.26019 |  | 2026-06-03 15:40 | 174.278 | 176.753 | 1519.7 | 29.4588 | 30.5577 | -1.0989 | 183.3463 | 29.7 | 30.1207 | -0.42075 |  | 2026-06-03 15:40 | 325.7665 | 332.481 | -6.7145 | 1994.886 | 326.5 | 327.7265 | -1.2265
2026-06-03 15:30 | 765 | 49.65 | 262.017 | 266.088 | 2114 | 44.348 | 45.4035 | -1.0555 | 272.4209 | 44.9 | 44.7542 | 0.14578 |  | 2026-06-03 15:30 | 265.072 | 269.245 | 2130.5 | 44.8742 | 45.4035 | -0.52932 | 272.4209 | 44.5 | 44.7542 | -0.25422 |  | 2026-06-03 15:30 | 260.015 | 266.427 | 2088.7 | 44.4045 | 45.4035 | -0.99899 | 272.4209 | 43.8 | 44.7542 | -0.95422 |  | 2026-06-03 15:30 | 261.647 | 265.793 | 2120 | 44.2988 | 45.4035 | -1.1047 | 272.4209 | 44.2 | 44.7542 | -0.55422 |  | 2026-06-03 15:30 | 196.537 | 199.368 | 1579.8 | 33.228 | 33.6322 | -0.40421 | 201.7933 | 33.6 | 33.1513 | 0.44873 |  | 2026-06-03 15:30 | 191.99 | 195.314 | 1567.7 | 32.5523 | 33.6322 | -1.0799 | 201.7933 | 32.9 | 33.1513 | -0.25127 |  | 2026-06-03 15:30 | 192.082 | 195.186 | 1565 | 32.531 | 33.6322 | -1.1012 | 201.7933 | 33.8 | 33.1513 | 0.64873 |  | 2026-06-03 15:30 | 192.165 | 197.55 | 1575.2 | 32.925 | 33.6322 | -0.70721 | 201.7933 | 33 | 33.1513 | -0.15127 |  | 2026-06-03 15:30 | 181.835 | 184.454 | 1490 | 30.7423 | 31.9969 | -1.2546 | 191.9813 | 31.2 | 31.5393 | -0.33933 |  | 2026-06-03 15:30 | 339.9042 | 348.1397 | -8.2355 | 2088.8381 | 341.9 | 343.1613 | -1.2613
2026-06-03 15:20 | 800 | 49.36 | 273.25 | 277.496 | 2069.1 | 46.2493 | 47.5335 | -1.2842 | 285.2011 | 47.1 | 46.8538 | 0.24621 |  | 2026-06-03 15:20 | 274.494 | 278.911 | 2086 | 46.4852 | 47.5335 | -1.0483 | 285.2011 | 47.4 | 46.8538 | 0.54621 |  | 2026-06-03 15:20 | 269.817 | 277.279 | 2044.9 | 46.2132 | 47.5335 | -1.3203 | 285.2011 | 46.1 | 46.8538 | -0.75379 |  | 2026-06-03 15:20 | 271.94 | 276.306 | 2075.8 | 46.051 | 47.5335 | -1.4825 | 285.2011 | 46.4 | 46.8538 | -0.45379 |  | 2026-06-03 15:20 | 204.341 | 207.327 | 1546.2 | 34.5545 | 35.21 | -0.65551 | 211.2601 | 34.5 | 34.7065 | -0.20651 |  | 2026-06-03 15:20 | 199.893 | 203.331 | 1534.8 | 33.8885 | 35.21 | -1.3215 | 211.2601 | 33.8 | 34.7065 | -0.90651 |  | 2026-06-03 15:20 | 200.25 | 204.074 | 1531.2 | 34.0123 | 35.21 | -1.1977 | 211.2601 | 33 | 34.7065 | -1.7065 |  | 2026-06-03 15:20 | 200.099 | 205.934 | 1542.2 | 34.3223 | 35.21 | -0.88768 | 211.2601 | 33.8 | 34.7065 | -0.90651 |  | 2026-06-03 15:20 | 189.159 | 191.923 | 1458.8 | 31.9872 | 33.498 | -1.5108 | 200.9878 | 32.3 | 33.0189 | -0.71894 |  | 2026-06-03 15:20 | 353.7635 | 364.4721 | -10.7086 | 2186.8324 | 354.4 | 359.2601 | -4.8601
2026-06-03 15:10 | 826 | 49.36 | 281.638 | 286.13 | 2022 | 47.6883 | 49.0784 | -1.39 | 294.4701 | 47.9 | 48.3765 | -0.47653 |  | 2026-06-03 15:10 | 283.292 | 287.898 | 2038.6 | 47.983 | 49.0784 | -1.0954 | 294.4701 | 48.3 | 48.3765 | -0.076534 |  | 2026-06-03 15:10 | 278.739 | 286.224 | 1998.8 | 47.704 | 49.0784 | -1.3744 | 294.4701 | 47.5 | 48.3765 | -0.87653 |  | 2026-06-03 15:10 | 281.022 | 285.621 | 2029.4 | 47.6035 | 49.0784 | -1.4749 | 294.4701 | 48 | 48.3765 | -0.37653 |  | 2026-06-03 15:10 | 211.704 | 214.797 | 1511.7 | 35.7995 | 36.3543 | -0.55484 | 218.126 | 36.1 | 35.8345 | 0.26553 |  | 2026-06-03 15:10 | 207.164 | 210.49 | 1501 | 35.0817 | 36.3543 | -1.2727 | 218.126 | 35.3 | 35.8345 | -0.53447 |  | 2026-06-03 15:10 | 207.783 | 211.592 | 1498.2 | 35.2653 | 36.3543 | -1.089 | 218.126 | 35.4 | 35.8345 | -0.43447 |  | 2026-06-03 15:10 | 207.501 | 213.35 | 1508.4 | 35.5583 | 36.3543 | -0.796 | 218.126 | 35.4 | 35.8345 | -0.43447 |  | 2026-06-03 15:10 | 196.061 | 198.946 | 1426.5 | 33.1577 | 34.5866 | -1.429 | 207.5199 | 33.1 | 34.0921 | -0.99206 |  | 2026-06-03 15:10 | 365.8413 | 376.3174 | -10.4761 | 2257.9045 | 367 | 370.9361 | -3.9361
2026-06-03 15:00 | 861 | 48.79 | 291.777 | 296.551 | 1974.1 | 49.4252 | 51.2695 | -1.8444 | 307.6171 | 49.6 | 50.5364 | -0.93636 | 0.9839 | 2026-06-03 15:00 | 294.34 | 299.217 | 1990.3 | 49.8695 | 51.2695 | -1.4 | 307.6171 | 49.4 | 50.5364 | -1.1364 | 0.9837 | 2026-06-03 15:00 | 288.563 | 296.368 | 1951.3 | 49.3947 | 51.2695 | -1.8749 | 307.6171 | 48.6 | 50.5364 | -1.9364 | 0.97366 | 2026-06-03 15:00 | 291.818 | 296.623 | 1981.4 | 49.4372 | 51.2695 | -1.8324 | 307.6171 | 49.1 | 50.5364 | -1.4364 | 0.9838 | 2026-06-03 15:00 | 218.972 | 222.261 | 1475.6 | 37.0435 | 37.9774 | -0.93392 | 227.8645 | 36.8 | 37.4343 | -0.63434 | 0.9852 | 2026-06-03 15:00 | 214.817 | 218.508 | 1465.7 | 36.418 | 37.9774 | -1.5594 | 227.8645 | 36.1 | 37.4343 | -1.3343 | 0.98311 | 2026-06-03 15:00 | 214.94 | 219.212 | 1462.8 | 36.5353 | 37.9774 | -1.4421 | 227.8645 | 36.2 | 37.4343 | -1.2343 | 0.98051 | 2026-06-03 15:00 | 214.991 | 221.12 | 1473 | 36.8533 | 37.9774 | -1.1241 | 227.8645 | 36.2 | 37.4343 | -1.2343 | 0.97228 | 2026-06-03 15:00 | 203.094 | 206.124 | 1393.4 | 34.354 | 36.1308 | -1.7768 | 216.7849 | 34.5 | 35.6141 | -1.1141 | 0.9853 | 2026-06-03 15:00 | 379.3307 | 393.1186 | -13.7879 | 2358.7114 | 376.5 | 387.497 | -10.997
2026-06-03 14:50 | 887 | 48.79 | 299.95 | 304.858 | 1924.5 | 50.8097 | 52.8177 | -2.0081 | 316.9064 | 49.2 | 52.0624 | -2.8624 | 0.9839 | 2026-06-03 14:50 | 302.579 | 307.655 | 1940.9 | 51.2758 | 52.8177 | -1.5419 | 316.9064 | 51.2 | 52.0624 | -0.86243 | 0.9835 | 2026-06-03 14:50 | 297.52 | 305.646 | 1902.7 | 50.941 | 52.8177 | -1.8767 | 316.9064 | 50.1 | 52.0624 | -1.9624 | 0.97341 | 2026-06-03 14:50 | 300.314 | 305.332 | 1932.3 | 50.8887 | 52.8177 | -1.9291 | 316.9064 | 50.5 | 52.0624 | -1.5624 | 0.98357 | 2026-06-03 14:50 | 225.946 | 229.387 | 1438.8 | 38.2312 | 39.1242 | -0.89308 | 234.7455 | 38 | 38.5648 | -0.56477 | 0.985 | 2026-06-03 14:50 | 221.119 | 225.275 | 1429.6 | 37.5458 | 39.1242 | -1.5784 | 234.7455 | 37.2 | 38.5648 | -1.3648 | 0.98155 | 2026-06-03 14:50 | 221.604 | 225.558 | 1426.6 | 37.593 | 39.1242 | -1.5312 | 234.7455 | 37.2 | 38.5648 | -1.3648 | 0.98247 | 2026-06-03 14:50 | 221.848 | 228.281 | 1436.8 | 38.0468 | 39.1242 | -1.0774 | 234.7455 | 37.3 | 38.5648 | -1.2648 | 0.97182 | 2026-06-03 14:50 | 209.71 | 212.817 | 1358.9 | 35.4695 | 37.2219 | -1.7524 | 223.3312 | 34.9 | 36.6896 | -1.7896 | 0.9854 | 2026-06-03 14:50 | 390.8015 | 404.9897 | -14.1882 | 2429.9385 | 385.6 | 399.1984 | -13.5984
2026-06-03 14:40 | 907 | 49.08 | 305.08 | 310.167 | 1875.3 | 51.6945 | 53.9489 | -2.2544 | 323.6932 | 53.9 | 53.1774 | 0.72261 | 0.9836 | 2026-06-03 14:40 | 307.992 | 313.191 | 1889.7 | 52.1985 | 53.9489 | -1.7504 | 323.6932 | 50.6 | 53.1774 | -2.5774 | 0.9834 | 2026-06-03 14:40 | 302.199 | 310.605 | 1852.6 | 51.7675 | 53.9489 | -2.1814 | 323.6932 | 51.3 | 53.1774 | -1.8774 | 0.97294 | 2026-06-03 14:40 | 305.168 | 310.351 | 1881.8 | 51.7252 | 53.9489 | -2.2237 | 323.6932 | 51.7 | 53.1774 | -1.4774 | 0.9833 | 2026-06-03 14:40 | 229.014 | 232.549 | 1400.8 | 38.7582 | 39.9621 | -1.204 | 239.7727 | 38.8 | 39.3907 | -0.59066 | 0.9848 | 2026-06-03 14:40 | 225.029 | 229.419 | 1392.4 | 38.2365 | 39.9621 | -1.7256 | 239.7727 | 38.1 | 39.3907 | -1.2907 | 0.98086 | 2026-06-03 14:40 | 225.129 | 229.078 | 1389.4 | 38.1797 | 39.9621 | -1.7825 | 239.7727 | 38.1 | 39.3907 | -1.2907 | 0.98276 | 2026-06-03 14:40 | 226.194 | 232.933 | 1399.5 | 38.8222 | 39.9621 | -1.14 | 239.7727 | 38.3 | 39.3907 | -1.0907 | 0.97107 | 2026-06-03 14:40 | 213.835 | 217.047 | 1324 | 36.1745 | 38.019 | -1.8445 | 228.114 | 36.2 | 37.4753 | -1.2753 | 0.9852 | 2026-06-03 14:40 | 397.5567 | 413.6629 | -16.1062 | 2481.9775 | 397 | 407.7475 | -10.7475
2026-06-03 14:30 | 933 | 49.36 | 312.281 | 317.544 | 1821.4 | 52.924 | 55.436 | -2.512 | 332.6158 | 50.5 | 54.6432 | -4.1432 | 0.98343 | 2026-06-03 14:30 | 315.371 | 320.76 | 1839.1 | 53.46 | 55.436 | -1.976 | 332.6158 | 53.9 | 54.6432 | -0.74323 | 0.9832 | 2026-06-03 14:30 | 308.804 | 317.443 | 1801.3 | 52.9072 | 55.436 | -2.5288 | 332.6158 | 51.4 | 54.6432 | -3.2432 | 0.97279 | 2026-06-03 14:30 | 312.389 | 317.791 | 1830.1 | 52.9652 | 55.436 | -2.4708 | 332.6158 | 52 | 54.6432 | -2.6432 | 0.983 | 2026-06-03 14:30 | 234.533 | 238.177 | 1362 | 39.6962 | 41.0637 | -1.3675 | 246.3821 | 39.5 | 40.4765 | -0.97646 | 0.9847 | 2026-06-03 14:30 | 229.961 | 234.427 | 1354.3 | 39.0712 | 41.0637 | -1.9925 | 246.3821 | 38.9 | 40.4765 | -1.5765 | 0.98095 | 2026-06-03 14:30 | 230.564 | 234.932 | 1351.3 | 39.1553 | 41.0637 | -1.9083 | 246.3821 | 38.9 | 40.4765 | -1.5765 | 0.98141 | 2026-06-03 14:30 | 230.577 | 237.469 | 1361.2 | 39.5782 | 41.0637 | -1.4855 | 246.3821 | 39 | 40.4765 | -1.4765 | 0.97098 | 2026-06-03 14:30 | 217.753 | 221.069 | 1287.8 | 36.8448 | 39.067 | -2.2222 | 234.402 | 36.8 | 38.5083 | -1.7083 | 0.985 | 2026-06-03 14:30 | 406.602 | 425.0656 | -18.4636 | 2550.3933 | 400.9 | 418.9871 | -18.0871
2026-06-03 14:20 | 961 | 48.5 | 319.402 | 324.926 | 1770.9 | 54.1543 | 57.2875 | -3.1332 | 343.7251 | 53.2 | 56.4683 | -3.2683 | 0.983 | 2026-06-03 14:20 | 322.196 | 327.835 | 1785.2 | 54.6392 | 57.2875 | -2.6484 | 343.7251 | 56.6 | 56.4683 | 0.13169 | 0.9828 | 2026-06-03 14:20 | 315.772 | 324.882 | 1749.9 | 54.147 | 57.2875 | -3.1405 | 343.7251 | 53.4 | 56.4683 | -3.0683 | 0.97196 | 2026-06-03 14:20 | 319.036 | 324.653 | 1778.1 | 54.1088 | 57.2875 | -3.1787 | 343.7251 | 53.9 | 56.4683 | -2.5683 | 0.9827 | 2026-06-03 14:20 | 240.355 | 244.164 | 1322.5 | 40.694 | 42.4352 | -1.7412 | 254.6112 | 40.1 | 41.8284 | -1.7284 | 0.9844 | 2026-06-03 14:20 | 235.936 | 240.366 | 1315.4 | 40.061 | 42.4352 | -2.3742 | 254.6112 | 39.3 | 41.8284 | -2.5284 | 0.98157 | 2026-06-03 14:20 | 236.32 | 241.369 | 1312.4 | 40.2282 | 42.4352 | -2.207 | 254.6112 | 39.4 | 41.8284 | -2.4284 | 0.97908 | 2026-06-03 14:20 | 236.805 | 243.724 | 1322.2 | 40.6207 | 42.4352 | -1.8145 | 254.6112 | 39.5 | 41.8284 | -2.3284 | 0.97161 | 2026-06-03 14:20 | 223.969 | 227.449 | 1251 | 37.9082 | 40.3718 | -2.4637 | 242.231 | 38 | 39.7945 | -1.7945 | 0.9847 | 2026-06-03 14:20 | 416.5613 | 439.2627 | -22.7014 | 2635.5765 | 413.4 | 432.9813 | -19.5813
2026-06-03 14:10 | 977 | 48.22 | 324.545 | 330.166 | 1717.7 | 55.0277 | 58.3035 | -3.2758 | 349.8211 | 55.8 | 57.4698 | -1.6698 | 0.98298 | 2026-06-03 14:10 | 328.306 | 334.12 | 1728.6 | 55.6867 | 58.3035 | -2.6168 | 349.8211 | 52.7 | 57.4698 | -4.7698 | 0.9826 | 2026-06-03 14:10 | 321.683 | 330.688 | 1696.5 | 55.1147 | 58.3035 | -3.1888 | 349.8211 | 53.9 | 57.4698 | -3.5698 | 0.97277 | 2026-06-03 14:10 | 324.836 | 330.555 | 1724.2 | 55.0925 | 58.3035 | -3.211 | 349.8211 | 54.4 | 57.4698 | -3.0698 | 0.9827 | 2026-06-03 14:10 | 244.718 | 248.683 | 1282.4 | 41.4472 | 43.1878 | -1.7406 | 259.1267 | 40.9 | 42.5702 | -1.6702 | 0.98406 | 2026-06-03 14:10 | 240.311 | 244.823 | 1276.1 | 40.8038 | 43.1878 | -2.384 | 259.1267 | 40.2 | 42.5702 | -2.3702 | 0.98157 | 2026-06-03 14:10 | 241.054 | 245.604 | 1273 | 40.934 | 43.1878 | -2.2538 | 259.1267 | 40.2 | 42.5702 | -2.3702 | 0.98147 | 2026-06-03 14:10 | 242.224 | 249.083 | 1282.7 | 41.5138 | 43.1878 | -1.674 | 259.1267 | 41.1 | 42.5702 | -1.4702 | 0.97246 | 2026-06-03 14:10 | 228.119 | 231.734 | 1213 | 38.6223 | 41.0878 | -2.4655 | 246.527 | 38 | 40.5003 | -2.5003 | 0.9844 | 2026-06-03 14:10 | 424.2427 | 447.053 | -22.8104 | 2682.3183 | 417.2 | 440.6602 | -23.4602
2026-06-03 14:00 | 995 | 48.5 | 330.315 | 336.062 | 1661.9 | 56.0103 | 59.3143 | -3.304 | 355.8861 | 53.7 | 58.4662 | -4.7662 | 0.9829 | 2026-06-03 14:00 | 333.775 | 340.08 | 1675.9 | 56.68 | 59.3143 | -2.6343 | 355.8861 | 55 | 58.4662 | -3.4662 | 0.98146 | 2026-06-03 14:00 | 328.032 | 337.446 | 1642.6 | 56.241 | 59.3143 | -3.0733 | 355.8861 | 54.6 | 58.4662 | -3.8662 | 0.9721 | 2026-06-03 14:00 | 330.942 | 336.768 | 1669.8 | 56.128 | 59.3143 | -3.1863 | 355.8861 | 55.3 | 58.4662 | -3.1662 | 0.9827 | 2026-06-03 14:00 | 248.411 | 252.399 | 1241.5 | 42.0665 | 43.9366 | -1.8701 | 263.6193 | 41.5 | 43.3083 | -1.8083 | 0.9842 | 2026-06-03 14:00 | 244.137 | 248.838 | 1235.9 | 41.473 | 43.9366 | -2.4636 | 263.6193 | 40.8 | 43.3083 | -2.5083 | 0.98111 | 2026-06-03 14:00 | 244.525 | 249.458 | 1232.8 | 41.5763 | 43.9366 | -2.3602 | 263.6193 | 42 | 43.3083 | -1.3083 | 0.98023 | 2026-06-03 14:00 | 246.072 | 253.439 | 1241.6 | 42.2398 | 43.9366 | -1.6967 | 263.6193 | 41.2 | 43.3083 | -2.1083 | 0.97093 | 2026-06-03 14:00 | 231.533 | 235.178 | 1175 | 39.1963 | 41.8002 | -2.6039 | 250.8011 | 38.9 | 41.2024 | -2.3024 | 0.9845 | 2026-06-03 14:00 | 431.6113 | 454.8038 | -23.1924 | 2728.8227 | 423 | 448.3001 | -25.3001
2026-06-03 13:50 | 1008 | 48.5 | 0 | 337.801 | 1608.2 | 56.3002 | 60.0893 | -3.7891 | 360.5358 | 55.7 | 59.23 | -3.53 |  | 2026-06-03 13:50 | 336.138 | 342.288 | 1620.9 | 57.048 | 60.0893 | -3.0413 | 360.5358 | 57.2 | 59.23 | -2.03 | 0.98203 | 2026-06-03 13:50 | 329.279 | 339.159 | 1588 | 56.5265 | 60.0893 | -3.5628 | 360.5358 | 55.2 | 59.23 | -4.03 | 0.97087 | 2026-06-03 13:50 | 333.81 | 339.756 | 1614.5 | 56.626 | 60.0893 | -3.4633 | 360.5358 | 56 | 59.23 | -3.23 | 0.9825 | 2026-06-03 13:50 | 250.401 | 254.473 | 1200 | 42.4122 | 44.5106 | -2.0984 | 267.0636 | 41.9 | 43.8741 | -1.9741 | 0.984 | 2026-06-03 13:50 | 246.741 | 251.632 | 1195.1 | 41.9387 | 44.5106 | -2.5719 | 267.0636 | 41.9 | 43.8741 | -1.9741 | 0.98056 | 2026-06-03 13:50 | 246.273 | 251.41 | 1190.8 | 41.9017 | 44.5106 | -2.6089 | 267.0636 | 40.7 | 43.8741 | -3.1741 | 0.97957 | 2026-06-03 13:50 | 247.514 | 254.8 | 1200.4 | 42.4667 | 44.5106 | -2.0439 | 267.0636 | 41.3 | 43.8741 | -2.5741 | 0.97141 | 2026-06-03 13:50 | 234.288 | 238.001 | 1136.1 | 39.6668 | 42.3463 | -2.6795 | 254.0779 | 39.2 | 41.7408 | -2.5408 | 0.9844 | 2026-06-03 13:50 | 434.8867 | 460.7459 | -25.8593 | 2764.4757 | 429.1 | 454.1573 | -25.0573
2026-06-03 13:40 | 1019 | 48.5 | 338.478 | 344.402 | 1552.5 | 57.4003 | 60.745 | -3.3447 | 364.4703 | 59 | 59.8764 | -0.87639 | 0.9828 | 2026-06-03 13:40 | 342.11 | 348.168 | 1563.7 | 58.028 | 60.745 | -2.717 | 364.4703 | 56.3 | 59.8764 | -3.5764 | 0.9826 | 2026-06-03 13:40 | 335.032 | 344.725 | 1532.8 | 57.4542 | 60.745 | -3.2909 | 364.4703 | 56 | 59.8764 | -3.8764 | 0.97188 | 2026-06-03 13:40 | 339.602 | 345.616 | 1558.5 | 57.6027 | 60.745 | -3.1424 | 364.4703 | 57.4 | 59.8764 | -2.4764 | 0.9826 | 2026-06-03 13:40 | 254.05 | 258.181 | 1158.1 | 43.0302 | 44.9963 | -1.9662 | 269.978 | 43 | 44.3529 | -1.3529 | 0.984 | 2026-06-03 13:40 | 250.647 | 255.475 | 1153.2 | 42.5792 | 44.9963 | -2.4172 | 269.978 | 41.8 | 44.3529 | -2.5529 | 0.9811 | 2026-06-03 13:40 | 249.725 | 255.002 | 1150.1 | 42.5003 | 44.9963 | -2.496 | 269.978 | 41.8 | 44.3529 | -2.5529 | 0.97931 | 2026-06-03 13:40 | 250.984 | 258.218 | 1159.1 | 43.0363 | 44.9963 | -1.96 | 269.978 | 42 | 44.3529 | -2.3529 | 0.97198 | 2026-06-03 13:40 | 237.915 | 241.71 | 1096.9 | 40.285 | 42.8084 | -2.5234 | 256.8506 | 39.6 | 42.1963 | -2.5963 | 0.9843 | 2026-06-03 13:40 | 441.9162 | 465.7739 | -23.8578 | 2794.6435 | 436.9 | 459.1134 | -22.2134
2026-06-03 13:30 | 1031 | 48.5 | 340.609 | 346.57 | 1493.5 | 57.7617 | 61.4604 | -3.6987 | 368.7624 | 55.2 | 60.5815 | -5.3815 | 0.9828 | 2026-06-03 13:30 | 344.778 | 350.955 | 1507.4 | 58.4925 | 61.4604 | -2.9679 | 368.7624 | 59 | 60.5815 | -1.5815 | 0.9824 | 2026-06-03 13:30 | 337.132 | 346.933 | 1476.8 | 57.8222 | 61.4604 | -3.6382 | 368.7624 | 57.8 | 60.5815 | -2.7815 | 0.97175 | 2026-06-03 13:30 | 342.353 | 348.486 | 1501.1 | 58.081 | 61.4604 | -3.3794 | 368.7624 | 57 | 60.5815 | -3.5815 | 0.9824 | 2026-06-03 13:30 | 256.11 | 260.248 | 1115.1 | 43.3747 | 45.5262 | -2.1516 | 273.1573 | 42.7 | 44.8752 | -2.1752 | 0.9841 | 2026-06-03 13:30 | 252.316 | 257.227 | 1111.4 | 42.8712 | 45.5262 | -2.6551 | 273.1573 | 42.1 | 44.8752 | -2.7752 | 0.98091 | 2026-06-03 13:30 | 252.322 | 257.848 | 1108.3 | 42.9747 | 45.5262 | -2.5516 | 273.1573 | 42.1 | 44.8752 | -2.7752 | 0.97857 | 2026-06-03 13:30 | 253.485 | 261.139 | 1117.1 | 43.5232 | 45.5262 | -2.0031 | 273.1573 | 42.3 | 44.8752 | -2.5752 | 0.97069 | 2026-06-03 13:30 | 239.258 | 243.074 | 1057.3 | 40.5123 | 43.3126 | -2.8002 | 259.8753 | 39.9 | 42.6932 | -2.7932 | 0.9843 | 2026-06-03 13:30 | 445.4133 | 471.259 | -25.8457 | 2827.554 | 438.1 | 464.52 | -26.42
2026-06-03 13:20 | 1041 | 48.5 | 343.909 | 349.999 | 1438.3 | 58.3332 | 62.0565 | -3.7234 | 372.3391 | 57.2 | 61.1691 | -3.9691 | 0.9826 | 2026-06-03 13:20 | 347.871 | 354.131 | 1448.4 | 59.0218 | 62.0565 | -3.0347 | 372.3391 | 57.8 | 61.1691 | -3.3691 | 0.98232 | 2026-06-03 13:20 | 341.387 | 351.906 | 1419 | 58.651 | 62.0565 | -3.4055 | 372.3391 | 55.8 | 61.1691 | -5.3691 | 0.97011 | 2026-06-03 13:20 | 344.931 | 351.146 | 1444.1 | 58.5243 | 62.0565 | -3.5322 | 372.3391 | 57.1 | 61.1691 | -4.0691 | 0.9823 | 2026-06-03 13:20 | 258.463 | 262.719 | 1072.4 | 43.7865 | 45.9678 | -2.1813 | 275.8067 | 42.8 | 45.3105 | -2.5105 | 0.9838 | 2026-06-03 13:20 | 254.871 | 259.871 | 1069.3 | 43.3118 | 45.9678 | -2.656 | 275.8067 | 42.7 | 45.3105 | -2.6105 | 0.98076 | 2026-06-03 13:20 | 254.672 | 260.055 | 1066.2 | 43.3425 | 45.9678 | -2.6253 | 275.8067 | 42.8 | 45.3105 | -2.5105 | 0.9793 | 2026-06-03 13:20 | 255.794 | 263.082 | 1074.8 | 43.847 | 45.9678 | -2.1208 | 275.8067 | 43 | 45.3105 | -2.3105 | 0.9723 | 2026-06-03 13:20 | 241.817 | 245.724 | 1017.4 | 40.954 | 43.7327 | -2.7787 | 262.396 | 40.7 | 43.1073 | -2.4073 | 0.9841 | 2026-06-03 13:20 | 449.7722 | 475.8299 | -26.0577 | 2854.9793 | 439.9 | 469.0255 | -29.1255
2026-06-03 13:10 | 1048 | 48.79 | 346.23 | 352.433 | 1381.1 | 58.7388 | 62.4047 | -3.6659 | 374.4283 | 57.9 | 61.5123 | -3.6123 | 0.9824 | 2026-06-03 13:10 | 349.338 | 355.419 | 1390.6 | 59.2365 | 62.4047 | -3.1682 | 374.4283 | 57.5 | 61.5123 | -4.0123 | 0.98289 | 2026-06-03 13:10 | 342.434 | 352.49 | 1363.2 | 58.7483 | 62.4047 | -3.6564 | 374.4283 | 57.1 | 61.5123 | -4.4123 | 0.97147 | 2026-06-03 13:10 | 345.117 | 351.414 | 1387 | 58.569 | 62.4047 | -3.8357 | 374.4283 | 57.9 | 61.5123 | -3.6123 | 0.98208 | 2026-06-03 13:10 | 259.371 | 263.642 | 1029.6 | 43.9403 | 46.2257 | -2.2854 | 277.3543 | 43.4 | 45.5647 | -2.1647 | 0.9838 | 2026-06-03 13:10 | 254.913 | 260.159 | 1026.6 | 43.3598 | 46.2257 | -2.8659 | 277.3543 | 42.1 | 45.5647 | -3.4647 | 0.97984 | 2026-06-03 13:10 | 255.132 | 260.894 | 1023.4 | 43.4823 | 46.2257 | -2.7434 | 277.3543 | 42 | 45.5647 | -3.5647 | 0.97791 | 2026-06-03 13:10 | 256.37 | 264.26 | 1031.8 | 44.0433 | 46.2257 | -2.1824 | 277.3543 | 42.2 | 45.5647 | -3.3647 | 0.97014 | 2026-06-03 13:10 | 242.245 | 246.184 | 976.7 | 41.0307 | 43.978 | -2.9474 | 263.8682 | 39.9 | 43.3492 | -3.4492 | 0.984 | 2026-06-03 13:10 | 451.1492 | 478.4997 | -27.3506 | 2870.9983 | 440 | 471.6572 | -31.6572
2026-06-03 13:00 | 1045 | 48.5 | 344.084 | 349.496 | 1323.2 | 58.2493 | 62.295 | -4.0456 | 373.7698 | 56.5 | 61.4041 | -4.9041 | 0.98451 | 2026-06-03 13:00 | 347.6 | 353.429 | 1333.1 | 58.9048 | 62.295 | -3.3901 | 373.7698 | 58.3 | 61.4041 | -3.1041 | 0.98351 | 2026-06-03 13:00 | 338.694 | 349.053 | 1306.1 | 58.1755 | 62.295 | -4.1195 | 373.7698 | 56 | 61.4041 | -5.4041 | 0.97032 | 2026-06-03 13:00 | 344.845 | 351.095 | 1329.1 | 58.5158 | 62.295 | -3.7791 | 373.7698 | 57.1 | 61.4041 | -4.3041 | 0.9822 | 2026-06-03 13:00 | 256.372 | 260.647 | 986.2 | 43.4412 | 46.1444 | -2.7033 | 276.8665 | 42.4 | 45.4846 | -3.0846 | 0.9836 | 2026-06-03 13:00 | 254.277 | 259.386 | 984.5 | 43.231 | 46.1444 | -2.9134 | 276.8665 | 42.2 | 45.4846 | -3.2846 | 0.9803 | 2026-06-03 13:00 | 253.251 | 258.392 | 981.4 | 43.0653 | 46.1444 | -3.0791 | 276.8665 | 42.7 | 45.4846 | -2.7846 | 0.9801 | 2026-06-03 13:00 | 255.045 | 262.672 | 989.6 | 43.7787 | 46.1444 | -2.3658 | 276.8665 | 43.2 | 45.4846 | -2.2846 | 0.97096 | 2026-06-03 13:00 | 241.281 | 245.189 | 936.8 | 40.8648 | 43.9007 | -3.0359 | 263.4042 | 40.8 | 43.2729 | -2.4729 | 0.98406 | 2026-06-03 13:00 | 448.2265 | 477.6582 | -29.4317 | 2865.9495 | 439.2 | 470.8277 | -31.6277
2026-06-03 12:50 | 1044 | 48.79 | 341.09 | 347.201 | 1266.7 | 57.8668 | 62.1665 | -4.2997 | 372.9991 | 57.5 | 61.2775 | -3.7775 | 0.9824 | 2026-06-03 12:50 | 345.634 | 351.934 | 1274.8 | 58.6557 | 62.1665 | -3.5109 | 372.9991 | 56.4 | 61.2775 | -4.8775 | 0.9821 | 2026-06-03 12:50 | 336.587 | 346.312 | 1250.1 | 57.7187 | 62.1665 | -4.4479 | 372.9991 | 55.9 | 61.2775 | -5.3775 | 0.97192 | 2026-06-03 12:50 | 342.905 | 349.155 | 1272 | 58.1925 | 62.1665 | -3.974 | 372.9991 | 57 | 61.2775 | -4.2775 | 0.9821 | 2026-06-03 12:50 | 254.844 | 259.067 | 943.8 | 43.1778 | 46.0493 | -2.8714 | 276.2957 | 43.1 | 45.3908 | -2.2908 | 0.9837 | 2026-06-03 12:50 | 252.723 | 257.652 | 942.3 | 42.942 | 46.0493 | -3.1073 | 276.2957 | 42.7 | 45.3908 | -2.6908 | 0.98087 | 2026-06-03 12:50 | 252.524 | 257.707 | 938.7 | 42.9512 | 46.0493 | -3.0981 | 276.2957 | 42.1 | 45.3908 | -3.2908 | 0.97989 | 2026-06-03 12:50 | 255.615 | 263.442 | 946.4 | 43.907 | 46.0493 | -2.1423 | 276.2957 | 42.4 | 45.3908 | -2.9908 | 0.97029 | 2026-06-03 12:50 | 240.877 | 244.744 | 896 | 40.7907 | 43.8102 | -3.0195 | 262.8611 | 40 | 43.1837 | -3.1837 | 0.9842 | 2026-06-03 12:50 | 446.2023 | 476.6734 | -30.4711 | 2860.0403 | 437.1 | 469.857 | -32.757
2026-06-03 12:40 | 1045 | 48.79 | 341.51 | 347.699 | 1209.2 | 57.9498 | 62.2261 | -4.2762 | 373.3564 | 58.8 | 61.3362 | -2.5362 | 0.9822 | 2026-06-03 12:40 | 343.472 | 351.663 | 1218.4 | 58.6105 | 62.2261 | -3.6156 | 373.3564 | 59.5 | 61.3362 | -1.8362 | 0.97671 | 2026-06-03 12:40 | 336.102 | 345.72 | 1194.2 | 57.62 | 62.2261 | -4.6061 | 373.3564 | 56.6 | 61.3362 | -4.7362 | 0.97218 | 2026-06-03 12:40 | 341.798 | 348.063 | 1215 | 58.0105 | 62.2261 | -4.2156 | 373.3564 | 57.6 | 61.3362 | -3.7362 | 0.982 | 2026-06-03 12:40 | 255.249 | 259.505 | 900.7 | 43.2508 | 46.0934 | -2.8426 | 276.5603 | 42.3 | 45.4343 | -3.1343 | 0.9836 | 2026-06-03 12:40 | 251.922 | 256.889 | 899.6 | 42.8148 | 46.0934 | -3.2786 | 276.5603 | 41.8 | 45.4343 | -3.6343 | 0.98066 | 2026-06-03 12:40 | 253.292 | 258.397 | 896.6 | 43.0662 | 46.0934 | -3.0272 | 276.5603 | 41.9 | 45.4343 | -3.5343 | 0.98024 | 2026-06-03 12:40 | 255.223 | 262.765 | 904 | 43.7942 | 46.0934 | -2.2992 | 276.5603 | 42.4 | 45.4343 | -3.0343 | 0.9713 | 2026-06-03 12:40 | 239.561 | 243.432 | 856 | 40.572 | 43.8521 | -3.2801 | 263.1129 | 39.9 | 43.2251 | -3.3251 | 0.9841 | 2026-06-03 12:40 | 445.6888 | 477.13 | -31.4411 | 2862.7798 | 440.8 | 470.307 | -29.507
2026-06-03 12:30 | 1043 | 48.79 | 342.179 | 348.127 | 1150.4 | 58.0212 | 62.107 | -4.0858 | 372.6419 | 54.6 | 61.2188 | -6.6188 | 0.98291 | 2026-06-03 12:30 | 346.529 | 352.809 | 1158.9 | 58.8015 | 62.107 | -3.3055 | 372.6419 | 55.4 | 61.2188 | -5.8188 | 0.9822 | 2026-06-03 12:30 | 337.733 | 347.851 | 1137.6 | 57.9752 | 62.107 | -4.1318 | 372.6419 | 56.4 | 61.2188 | -4.8188 | 0.97091 | 2026-06-03 12:30 | 342.93 | 349.216 | 1157.4 | 58.2027 | 62.107 | -3.9043 | 372.6419 | 57.3 | 61.2188 | -3.9188 | 0.982 | 2026-06-03 12:30 | 256.267 | 260.554 | 858.4 | 43.4257 | 46.0052 | -2.5795 | 276.031 | 42.7 | 45.3473 | -2.6473 | 0.98355 | 2026-06-03 12:30 | 253.267 | 258.49 | 857.8 | 43.0817 | 46.0052 | -2.9235 | 276.031 | 42.3 | 45.3473 | -3.0473 | 0.97979 | 2026-06-03 12:30 | 254.153 | 259.385 | 854.7 | 43.2308 | 46.0052 | -2.7743 | 276.031 | 42.3 | 45.3473 | -3.0473 | 0.97983 | 2026-06-03 12:30 | 257.354 | 265.223 | 861.6 | 44.2038 | 46.0052 | -1.8013 | 276.031 | 42.7 | 45.3473 | -2.6473 | 0.97033 | 2026-06-03 12:30 | 241.204 | 245.101 | 816.1 | 40.8502 | 43.7682 | -2.9181 | 262.6093 | 40.2 | 43.1423 | -2.9423 | 0.9841 | 2026-06-03 12:30 | 447.7927 | 476.2168 | -28.4241 | 2857.3008 | 433.9 | 469.4069 | -35.5069
2026-06-03 12:20 | 1041 | 49.65 | 342.115 | 348.188 | 1095.8 | 58.0313 | 61.7844 | -3.753 | 370.7061 | 59 | 60.9008 | -1.9008 | 0.98256 | 2026-06-03 12:20 | 347.186 | 353.29 | 1103.5 | 58.8817 | 61.7844 | -2.9027 | 370.7061 | 58.8 | 60.9008 | -2.1008 | 0.98272 | 2026-06-03 12:20 | 338.759 | 348.558 | 1081.2 | 58.093 | 61.7844 | -3.6914 | 370.7061 | 56 | 60.9008 | -4.9008 | 0.97189 | 2026-06-03 12:20 | 345.581 | 351.844 | 1100.1 | 58.6407 | 61.7844 | -3.1437 | 370.7061 | 57.1 | 60.9008 | -3.8008 | 0.9822 | 2026-06-03 12:20 | 256.534 | 260.727 | 815.7 | 43.4545 | 45.7662 | -2.3117 | 274.5971 | 42.4 | 45.1117 | -2.7117 | 0.98392 | 2026-06-03 12:20 | 254.773 | 259.966 | 815.5 | 43.3277 | 45.7662 | -2.4385 | 274.5971 | 42.2 | 45.1117 | -2.9117 | 0.98002 | 2026-06-03 12:20 | 253.765 | 258.877 | 812.4 | 43.1462 | 45.7662 | -2.62 | 274.5971 | 42 | 45.1117 | -3.1117 | 0.98025 | 2026-06-03 12:20 | 255.345 | 262.777 | 818.9 | 43.7962 | 45.7662 | -1.97 | 274.5971 | 42.3 | 45.1117 | -2.8117 | 0.97172 | 2026-06-03 12:20 | 241.864 | 245.772 | 775.9 | 40.962 | 43.5409 | -2.5789 | 261.2452 | 40.5 | 42.9182 | -2.4182 | 0.9841 | 2026-06-03 12:20 | 448.3332 | 473.743 | -25.4099 | 2842.4582 | 440.3 | 466.9685 | -26.6685
2026-06-03 12:10 | 1031 | 49.65 | 340.239 | 346.286 | 1036.8 | 57.7143 | 61.1908 | -3.4765 | 367.1451 | 54.5 | 60.3158 | -5.8158 | 0.98254 | 2026-06-03 12:10 | 344.138 | 350.31 | 1044.7 | 58.385 | 61.1908 | -2.8058 | 367.1451 | 56.7 | 60.3158 | -3.6158 | 0.98238 | 2026-06-03 12:10 | 336.716 | 346.534 | 1025.2 | 57.7557 | 61.1908 | -3.4352 | 367.1451 | 55.4 | 60.3158 | -4.9158 | 0.97167 | 2026-06-03 12:10 | 343.044 | 349.225 | 1043 | 58.2042 | 61.1908 | -2.9867 | 367.1451 | 56.8 | 60.3158 | -3.5158 | 0.9823 | 2026-06-03 12:10 | 254.908 | 259.079 | 773.3 | 43.1798 | 45.3266 | -2.1467 | 271.9593 | 42.4 | 44.6784 | -2.2784 | 0.9839 | 2026-06-03 12:10 | 253.164 | 258.116 | 773.3 | 43.0193 | 45.3266 | -2.3072 | 271.9593 | 41.9 | 44.6784 | -2.7784 | 0.98081 | 2026-06-03 12:10 | 252.53 | 257.405 | 770.4 | 42.9008 | 45.3266 | -2.4257 | 271.9593 | 41.9 | 44.6784 | -2.7784 | 0.98106 | 2026-06-03 12:10 | 254.821 | 262.17 | 776.6 | 43.695 | 45.3266 | -1.6316 | 271.9593 | 42.2 | 44.6784 | -2.4784 | 0.97197 | 2026-06-03 12:10 | 240.536 | 244.398 | 735.4 | 40.733 | 43.1226 | -2.3896 | 258.7356 | 39.5 | 42.5059 | -3.0059 | 0.9842 | 2026-06-03 12:10 | 445.5872 | 469.1922 | -23.605 | 2815.1531 | 431.3 | 462.4827 | -31.1827
2026-06-03 12:00 | 1016 | 49.94 | 336.975 | 342.907 | 982.3 | 57.1512 | 60.2336 | -3.0824 | 361.4016 | 55.8 | 59.3723 | -3.5723 | 0.9827 | 2026-06-03 12:00 | 340.638 | 346.741 | 988 | 57.7902 | 60.2336 | -2.4434 | 361.4016 | 56.3 | 59.3723 | -3.0723 | 0.9824 | 2026-06-03 12:00 | 332.26 | 341.508 | 969.8 | 56.918 | 60.2336 | -3.3156 | 361.4016 | 55.6 | 59.3723 | -3.7723 | 0.97292 | 2026-06-03 12:00 | 337.947 | 344.001 | 986.2 | 57.3335 | 60.2336 | -2.9001 | 361.4016 | 55.8 | 59.3723 | -3.5723 | 0.9824 | 2026-06-03 12:00 | 252.022 | 256.094 | 730.9 | 42.6823 | 44.6175 | -1.9351 | 267.7049 | 41.6 | 43.9794 | -2.3794 | 0.9841 | 2026-06-03 12:00 | 249.58 | 254.087 | 731.4 | 42.3478 | 44.6175 | -2.2696 | 267.7049 | 41.3 | 43.9794 | -2.6794 | 0.98226 | 2026-06-03 12:00 | 249.189 | 253.992 | 728.5 | 42.332 | 44.6175 | -2.2855 | 267.7049 | 41.9 | 43.9794 | -2.0794 | 0.98109 | 2026-06-03 12:00 | 250.737 | 258.354 | 734.4 | 43.059 | 44.6175 | -1.5585 | 267.7049 | 42.1 | 43.9794 | -1.8794 | 0.97052 | 2026-06-03 12:00 | 237.6 | 241.39 | 695.9 | 40.2317 | 42.448 | -2.2163 | 254.688 | 39.9 | 41.841 | -1.941 | 0.9843 | 2026-06-03 12:00 | 439.8457 | 461.8523 | -22.0066 | 2771.1138 | 430.3 | 455.2478 | -24.9478
2026-06-03 11:50 | 1005 | 49.65 | 334.638 | 340.495 | 926.5 | 56.7492 | 59.6477 | -2.8986 | 357.8863 | 55 | 58.7948 | -3.7948 | 0.9828 | 2026-06-03 11:50 | 338.765 | 344.743 | 931.7 | 57.4572 | 59.6477 | -2.1906 | 357.8863 | 56.6 | 58.7948 | -2.1948 | 0.98266 | 2026-06-03 11:50 | 329.833 | 338.942 | 914.2 | 56.4903 | 59.6477 | -3.1574 | 357.8863 | 54.4 | 58.7948 | -4.3948 | 0.97313 | 2026-06-03 11:50 | 336.151 | 342.094 | 930.4 | 57.0157 | 59.6477 | -2.6321 | 357.8863 | 55.4 | 58.7948 | -3.3948 | 0.98263 | 2026-06-03 11:50 | 249.786 | 253.834 | 689.3 | 42.3057 | 44.1835 | -1.8778 | 265.101 | 41.8 | 43.5517 | -1.7517 | 0.98405 | 2026-06-03 11:50 | 247.947 | 252.377 | 690.1 | 42.0628 | 44.1835 | -2.1207 | 265.101 | 41.5 | 43.5517 | -2.0517 | 0.98245 | 2026-06-03 11:50 | 246.938 | 251.668 | 686.6 | 41.9447 | 44.1835 | -2.2388 | 265.101 | 40.7 | 43.5517 | -2.8517 | 0.98121 | 2026-06-03 11:50 | 248.362 | 255.58 | 692.3 | 42.5967 | 44.1835 | -1.5868 | 265.101 | 41 | 43.5517 | -2.5517 | 0.97176 | 2026-06-03 11:50 | 235.746 | 239.458 | 656 | 39.9097 | 42.0351 | -2.1255 | 252.2107 | 38.8 | 41.434 | -2.634 | 0.9845 | 2026-06-03 11:50 | 436.5318 | 457.36 | -20.8282 | 2744.1599 | 425.2 | 450.8197 | -25.6197
2026-06-03 11:40 | 992 | 49.94 | 332.077 | 337.88 | 871.5 | 56.3133 | 58.8108 | -2.4974 | 352.8645 | 57 | 57.9698 | -0.96976 | 0.98283 | 2026-06-03 11:40 | 335.614 | 341.488 | 875.1 | 56.9147 | 58.8108 | -1.8961 | 352.8645 | 57.4 | 57.9698 | -0.56976 | 0.9828 | 2026-06-03 11:40 | 327.668 | 337.038 | 859.8 | 56.173 | 58.8108 | -2.6378 | 352.8645 | 54.7 | 57.9698 | -3.2698 | 0.9722 | 2026-06-03 11:40 | 332.366 | 338.252 | 875 | 56.3753 | 58.8108 | -2.4354 | 352.8645 | 55.6 | 57.9698 | -2.3698 | 0.9826 | 2026-06-03 11:40 | 247.329 | 251.351 | 647.5 | 41.8918 | 43.5635 | -1.6717 | 261.3811 | 40.7 | 42.9406 | -2.2406 | 0.984 | 2026-06-03 11:40 | 245.734 | 250.056 | 648.6 | 41.676 | 43.5635 | -1.8875 | 261.3811 | 40.4 | 42.9406 | -2.5406 | 0.98272 | 2026-06-03 11:40 | 244.862 | 249.628 | 645.9 | 41.6047 | 43.5635 | -1.9589 | 261.3811 | 40.3 | 42.9406 | -2.6406 | 0.98091 | 2026-06-03 11:40 | 246.807 | 254.304 | 651.3 | 42.384 | 43.5635 | -1.1795 | 261.3811 | 40.7 | 42.9406 | -2.2406 | 0.97052 | 2026-06-03 11:40 | 234.087 | 237.746 | 617.2 | 39.6243 | 41.4453 | -1.821 | 248.6718 | 38.6 | 40.8526 | -2.2526 | 0.98461 | 2026-06-03 11:40 | 432.9572 | 450.9424 | -17.9852 | 2705.6544 | 425.4 | 444.4939 | -19.0939
2026-06-03 11:30 | 976 | 49.65 | 327.033 | 332.655 | 814.5 | 55.4425 | 57.9265 | -2.484 | 347.5592 | 53.1 | 57.0982 | -3.9982 | 0.9831 | 2026-06-03 11:30 | 329.834 | 335.572 | 817.7 | 55.9287 | 57.9265 | -1.9979 | 347.5592 | 52.1 | 57.0982 | -4.9982 | 0.9829 | 2026-06-03 11:30 | 323.199 | 332.01 | 805.1 | 55.335 | 57.9265 | -2.5915 | 347.5592 | 53 | 57.0982 | -4.0982 | 0.97346 | 2026-06-03 11:30 | 327.852 | 333.556 | 819.4 | 55.5927 | 57.9265 | -2.3339 | 347.5592 | 53.7 | 57.0982 | -3.3982 | 0.9829 | 2026-06-03 11:30 | 243.774 | 247.713 | 606.8 | 41.2855 | 42.9085 | -1.623 | 257.4513 | 40.6 | 42.295 | -1.695 | 0.9841 | 2026-06-03 11:30 | 241.704 | 246.394 | 608.2 | 41.0657 | 42.9085 | -1.8429 | 257.4513 | 40.3 | 42.295 | -1.995 | 0.98097 | 2026-06-03 11:30 | 241.391 | 245.906 | 605.6 | 40.9843 | 42.9085 | -1.9242 | 257.4513 | 40.2 | 42.295 | -2.095 | 0.98164 | 2026-06-03 11:30 | 243 | 250.211 | 610.6 | 41.7018 | 42.9085 | -1.2067 | 257.4513 | 40.4 | 42.295 | -1.895 | 0.97118 | 2026-06-03 11:30 | 229.931 | 233.527 | 578.6 | 38.9212 | 40.8222 | -1.901 | 244.933 | 38.3 | 40.2384 | -1.9384 | 0.9846 | 2026-06-03 11:30 | 426.2573 | 444.1625 | -17.9052 | 2664.9752 | 411.7 | 437.811 | -26.111
2026-06-03 11:20 | 954 | 49.65 | 321.311 | 326.801 | 761.4 | 54.4668 | 56.6208 | -2.154 | 339.7249 | 52.2 | 55.8111 | -3.6111 | 0.9832 | 2026-06-03 11:20 | 323.976 | 329.585 | 765.6 | 54.9308 | 56.6208 | -1.69 | 339.7249 | 54.3 | 55.8111 | -1.5111 | 0.98298 | 2026-06-03 11:20 | 317.188 | 326 | 752.1 | 54.3333 | 56.6208 | -2.2875 | 339.7249 | 52.4 | 55.8111 | -3.4111 | 0.97297 | 2026-06-03 11:20 | 321.804 | 327.436 | 765.7 | 54.5727 | 56.6208 | -2.0482 | 339.7249 | 53.2 | 55.8111 | -2.6111 | 0.9828 | 2026-06-03 11:20 | 239.735 | 243.534 | 566.2 | 40.589 | 41.9413 | -1.3523 | 251.6481 | 39.5 | 41.3416 | -1.8416 | 0.9844 | 2026-06-03 11:20 | 238.025 | 242.266 | 567.9 | 40.3777 | 41.9413 | -1.5637 | 251.6481 | 39.3 | 41.3416 | -2.0416 | 0.98249 | 2026-06-03 11:20 | 237.22 | 241.735 | 565.4 | 40.2892 | 41.9413 | -1.6522 | 251.6481 | 39.1 | 41.3416 | -2.2416 | 0.98132 | 2026-06-03 11:20 | 238.442 | 245.464 | 570.2 | 40.9107 | 41.9413 | -1.0307 | 251.6481 | 39.3 | 41.3416 | -2.0416 | 0.97139 | 2026-06-03 11:20 | 226.069 | 229.582 | 540.3 | 38.2637 | 39.902 | -1.6383 | 239.412 | 37.4 | 39.3314 | -1.9314 | 0.9847 | 2026-06-03 11:20 | 418.7338 | 434.1507 | -15.4168 | 2604.904 | 406.7 | 427.9423 | -21.2423
2026-06-03 11:10 | 936 | 49.65 | 316.708 | 322.364 | 709.2 | 53.7273 | 55.5525 | -1.8252 | 333.315 | 52.3 | 54.7581 | -2.4581 | 0.98245 | 2026-06-03 11:10 | 319.83 | 325.262 | 711.3 | 54.2103 | 55.5525 | -1.3422 | 333.315 | 52.7 | 54.7581 | -2.0581 | 0.9833 | 2026-06-03 11:10 | 313.029 | 321.179 | 699.7 | 53.5298 | 55.5525 | -2.0227 | 333.315 | 51.5 | 54.7581 | -3.2581 | 0.97462 | 2026-06-03 11:10 | 317.341 | 322.682 | 712.5 | 53.7803 | 55.5525 | -1.7722 | 333.315 | 52.3 | 54.7581 | -2.4581 | 0.98345 | 2026-06-03 11:10 | 235.937 | 239.627 | 526.7 | 39.9378 | 41.15 | -1.2122 | 246.9 | 39 | 40.5616 | -1.5616 | 0.9846 | 2026-06-03 11:10 | 234.769 | 238.679 | 528.6 | 39.7798 | 41.15 | -1.3702 | 246.9 | 38.7 | 40.5616 | -1.8616 | 0.98362 | 2026-06-03 11:10 | 233.583 | 237.748 | 526.3 | 39.6247 | 41.15 | -1.5253 | 246.9 | 38.6 | 40.5616 | -1.9616 | 0.98248 | 2026-06-03 11:10 | 235.119 | 242.036 | 530.9 | 40.3393 | 41.15 | -0.81067 | 246.9 | 38.9 | 40.5616 | -1.6616 | 0.97142 | 2026-06-03 11:10 | 223.053 | 226.438 | 502.9 | 37.7397 | 39.1491 | -1.4095 | 234.8948 | 36.8 | 38.5893 | -1.7893 | 0.98505 | 2026-06-03 11:10 | 412.6692 | 425.9591 | -13.29 | 2555.7549 | 400.8 | 419.8679 | -19.0679
2026-06-03 11:00 | 908 | 50.23 | 310.728 | 315.909 | 656.9 | 52.6515 | 53.7709 | -1.1194 | 322.6257 | 51.4 | 53.002 | -1.602 | 0.9836 | 2026-06-03 11:00 | 312.394 | 317.635 | 658.6 | 52.9392 | 53.7709 | -0.83178 | 322.6257 | 51.8 | 53.002 | -1.202 | 0.9835 | 2026-06-03 11:00 | 306.54 | 314.715 | 648.2 | 52.4525 | 53.7709 | -1.3184 | 322.6257 | 50.7 | 53.002 | -2.302 | 0.97402 | 2026-06-03 11:00 | 309.873 | 315.035 | 660.2 | 52.5058 | 53.7709 | -1.2651 | 322.6257 | 51.5 | 53.002 | -1.502 | 0.98361 | 2026-06-03 11:00 | 231.89 | 235.493 | 487.7 | 39.2488 | 39.8303 | -0.5815 | 238.982 | 37.7 | 39.2608 | -1.5608 | 0.9847 | 2026-06-03 11:00 | 229.659 | 233.478 | 489.9 | 38.913 | 39.8303 | -0.91733 | 238.982 | 37.6 | 39.2608 | -1.6608 | 0.98364 | 2026-06-03 11:00 | 230.023 | 234.016 | 487.7 | 39.0027 | 39.8303 | -0.82767 | 238.982 | 38.1 | 39.2608 | -1.1608 | 0.98294 | 2026-06-03 11:00 | 231.242 | 237.863 | 492 | 39.6438 | 39.8303 | -0.1865 | 238.982 | 38.4 | 39.2608 | -0.86076 | 0.97216 | 2026-06-03 11:00 | 218.739 | 222.025 | 466.1 | 37.0042 | 37.8936 | -0.88946 | 227.3618 | 36.4 | 37.3517 | -0.95175 | 0.9852 | 2026-06-03 11:00 | 404.3615 | 412.2987 | -7.9372 | 2473.7925 | 393.6 | 406.4029 | -12.8029
2026-06-03 10:50 | 893 | 49.65 | 304.115 | 309.091 | 605.5 | 51.5152 | 53.0004 | -1.4852 | 318.0025 | 49.9 | 52.2425 | -2.3425 | 0.9839 | 2026-06-03 10:50 | 307.176 | 312.298 | 606.8 | 52.0497 | 53.0004 | -0.95074 | 318.0025 | 50.2 | 52.2425 | -2.0425 | 0.9836 | 2026-06-03 10:50 | 299.982 | 308.324 | 597.5 | 51.3873 | 53.0004 | -1.6131 | 318.0025 | 49.2 | 52.2425 | -3.0425 | 0.97294 | 2026-06-03 10:50 | 305.536 | 310.63 | 608.7 | 51.7717 | 53.0004 | -1.2287 | 318.0025 | 50 | 52.2425 | -2.2425 | 0.9836 | 2026-06-03 10:50 | 226.387 | 229.835 | 450 | 38.3058 | 39.2596 | -0.95373 | 235.5574 | 37.7 | 38.6982 | -0.99815 | 0.985 | 2026-06-03 10:50 | 226.312 | 230.183 | 452.3 | 38.3638 | 39.2596 | -0.89573 | 235.5574 | 37.5 | 38.6982 | -1.1982 | 0.98318 | 2026-06-03 10:50 | 224.761 | 229.021 | 449.6 | 38.1702 | 39.2596 | -1.0894 | 235.5574 | 36.7 | 38.6982 | -1.9982 | 0.9814 | 2026-06-03 10:50 | 226.971 | 233.584 | 453.6 | 38.9307 | 39.2596 | -0.3289 | 235.5574 | 37 | 38.6982 | -1.6982 | 0.97169 | 2026-06-03 10:50 | 215.927 | 219.082 | 429.7 | 36.5137 | 37.3506 | -0.83695 | 224.1037 | 35.2 | 36.8165 | -1.6165 | 0.9856 | 2026-06-03 10:50 | 397.008 | 406.3905 | -9.3825 | 2438.3431 | 383.4 | 400.5791 | -17.1791
2026-06-03 10:40 | 863 | 49.65 | 296.932 | 303.384 | 555.6 | 50.564 | 51.2199 | -0.65588 | 307.3193 | 50.5 | 50.4874 | 0.012562 | 0.97873 | 2026-06-03 10:40 | 298.761 | 303.852 | 556.6 | 50.642 | 51.2199 | -0.57788 | 307.3193 | 49.4 | 50.4874 | -1.0874 | 0.98325 | 2026-06-03 10:40 | 293.61 | 301.566 | 548.3 | 50.261 | 51.2199 | -0.95888 | 307.3193 | 48.3 | 50.4874 | -2.1874 | 0.97362 | 2026-06-03 10:40 | 297.844 | 302.721 | 558.7 | 50.4535 | 51.2199 | -0.76638 | 307.3193 | 49.2 | 50.4874 | -1.2874 | 0.98389 | 2026-06-03 10:40 | 221.371 | 224.674 | 412.3 | 37.4457 | 37.9407 | -0.49499 | 227.6439 | 35.9 | 37.3981 | -1.4981 | 0.9853 | 2026-06-03 10:40 | 220.576 | 223.978 | 414.8 | 37.3297 | 37.9407 | -0.61099 | 227.6439 | 35.9 | 37.3981 | -1.4981 | 0.98481 | 2026-06-03 10:40 | 219.648 | 223.344 | 412.9 | 37.224 | 37.9407 | -0.71665 | 227.6439 | 35.7 | 37.3981 | -1.6981 | 0.98345 | 2026-06-03 10:40 | 221.17 | 227.422 | 416.6 | 37.9037 | 37.9407 | -0.036987 | 227.6439 | 36.5 | 37.3981 | -0.8981 | 0.97251 | 2026-06-03 10:40 | 210.291 | 213.363 | 394.5 | 35.5605 | 36.0958 | -0.53533 | 216.575 | 34.7 | 35.5797 | -0.87966 | 0.9856 | 2026-06-03 10:40 | 387.384 | 392.738 | -5.354 | 2356.4279 | 376.1 | 387.1218 | -11.0218
2026-06-03 10:30 | 838 | 49.65 | 289.044 | 293.654 | 505.1 | 48.9423 | 49.7361 | -0.79377 | 298.4166 | 45.7 | 49.0249 | -3.3249 | 0.9843 | 2026-06-03 10:30 | 290.697 | 295.394 | 507.2 | 49.2323 | 49.7361 | -0.50377 | 298.4166 | 47.8 | 49.0249 | -1.2249 | 0.9841 | 2026-06-03 10:30 | 284.241 | 291.415 | 500 | 48.5692 | 49.7361 | -1.1669 | 298.4166 | 47 | 49.0249 | -2.0249 | 0.97538 | 2026-06-03 10:30 | 289.629 | 294.249 | 509.5 | 49.0415 | 49.7361 | -0.69461 | 298.4166 | 47.8 | 49.0249 | -1.2249 | 0.9843 | 2026-06-03 10:30 | 214.186 | 217.258 | 376.4 | 36.2097 | 36.8416 | -0.63189 | 221.0494 | 35.5 | 36.3147 | -0.81473 | 0.98586 | 2026-06-03 10:30 | 214.338 | 217.875 | 378.9 | 36.3125 | 36.8416 | -0.52906 | 221.0494 | 35.5 | 36.3147 | -0.81473 | 0.98377 | 2026-06-03 10:30 | 213.116 | 216.828 | 377.2 | 36.138 | 36.8416 | -0.70356 | 221.0494 | 35.3 | 36.3147 | -1.0147 | 0.98288 | 2026-06-03 10:30 | 214.886 | 221.167 | 380.1 | 36.8612 | 36.8416 | 0.019605 | 221.0494 | 35 | 36.3147 | -1.3147 | 0.9716 | 2026-06-03 10:30 | 204.146 | 207.087 | 359.8 | 34.5145 | 35.0502 | -0.53568 | 210.3011 | 33.3 | 34.549 | -1.249 | 0.9858 | 2026-06-03 10:30 | 375.8212 | 381.3609 | -5.5397 | 2288.1652 | 362.9 | 375.9074 | -13.0074
2026-06-03 10:20 | 803 | 49.65 | 276.529 | 281.985 | 459.4 | 46.9975 | 47.6588 | -0.66132 | 285.9529 | 47.3 | 46.9773 | 0.3227 | 0.98065 | 2026-06-03 10:20 | 279.624 | 284.055 | 459.4 | 47.3425 | 47.6588 | -0.31632 | 285.9529 | 45.7 | 46.9773 | -1.2773 | 0.9844 | 2026-06-03 10:20 | 274.418 | 281.144 | 453 | 46.8573 | 47.6588 | -0.80149 | 285.9529 | 44.2 | 46.9773 | -2.7773 | 0.97608 | 2026-06-03 10:20 | 278.869 | 283.288 | 461.7 | 47.2147 | 47.6588 | -0.44416 | 285.9529 | 45.5 | 46.9773 | -1.4773 | 0.9844 | 2026-06-03 10:20 | 206.517 | 209.492 | 340.9 | 34.9153 | 35.3028 | -0.3875 | 211.817 | 33.7 | 34.798 | -1.098 | 0.9858 | 2026-06-03 10:20 | 206.848 | 210.083 | 343.4 | 35.0138 | 35.3028 | -0.289 | 211.817 | 33.7 | 34.798 | -1.098 | 0.9846 | 2026-06-03 10:20 | 205.63 | 208.922 | 341.9 | 34.8203 | 35.3028 | -0.4825 | 211.817 | 33.6 | 34.798 | -1.198 | 0.98424 | 2026-06-03 10:20 | 206.844 | 212.598 | 345.1 | 35.433 | 35.3028 | 0.13017 | 211.817 | 33.7 | 34.798 | -1.098 | 0.97293 | 2026-06-03 10:20 | 196.625 | 199.417 | 326.5 | 33.2362 | 33.5863 | -0.35011 | 201.5176 | 32 | 33.106 | -1.106 | 0.986 | 2026-06-03 10:20 | 361.8307 | 365.4329 | -3.6022 | 2192.5974 | 349.4 | 360.2072 | -10.8072
2026-06-03 10:10 | 764 | 49.65 | 266.907 | 270.972 | 412.1 | 45.162 | 45.3441 | -0.18214 | 272.0648 | 42 | 44.6957 | -2.6957 | 0.985 | 2026-06-03 10:10 | 268.405 | 272.548 | 413.7 | 45.4247 | 45.3441 | 0.08053 | 272.0648 | 43.4 | 44.6957 | -1.2957 | 0.9848 | 2026-06-03 10:10 | 263.846 | 269.926 | 408.8 | 44.9877 | 45.3441 | -0.35647 | 272.0648 | 43.2 | 44.6957 | -1.4957 | 0.97748 | 2026-06-03 10:10 | 267.063 | 271.157 | 416.2 | 45.1928 | 45.3441 | -0.1513 | 272.0648 | 43.8 | 44.6957 | -0.89572 | 0.9849 | 2026-06-03 10:10 | 198.631 | 201.451 | 307.2 | 33.5752 | 33.5882 | -0.013083 | 201.5295 | 32.5 | 33.1079 | -0.60794 | 0.986 | 2026-06-03 10:10 | 198.056 | 201.143 | 309.7 | 33.5238 | 33.5882 | -0.064416 | 201.5295 | 32.5 | 33.1079 | -0.60794 | 0.98465 | 2026-06-03 10:10 | 197.564 | 200.83 | 308.3 | 33.4717 | 33.5882 | -0.11658 | 201.5295 | 32.3 | 33.1079 | -0.80794 | 0.98374 | 2026-06-03 10:10 | 198.919 | 204.596 | 311.4 | 34.0993 | 33.5882 | 0.51108 | 201.5295 | 32.6 | 33.1079 | -0.50794 | 0.97225 | 2026-06-03 10:10 | 188.211 | 190.845 | 294.5 | 31.8075 | 31.9551 | -0.14756 | 191.7304 | 30.9 | 31.4981 | -0.5981 | 0.9862 | 2026-06-03 10:10 | 347.2447 | 347.6846 | -0.43994 | 2086.1076 | 333.2 | 342.7127 | -9.5127
2026-06-03 10:00 | 734 | 49.08 | 257.616 | 261.399 | 370.1 | 43.5665 | 43.6587 | -0.092223 | 261.9523 | 42 | 43.0344 | -1.0344 | 0.98553 | 2026-06-03 10:00 | 258.991 | 262.882 | 370.3 | 43.8137 | 43.6587 | 0.15494 | 261.9523 | 42.3 | 43.0344 | -0.7344 | 0.9852 | 2026-06-03 10:00 | 253.987 | 259.68 | 365.6 | 43.28 | 43.6587 | -0.37872 | 261.9523 | 41.4 | 43.0344 | -1.6344 | 0.97808 | 2026-06-03 10:00 | 258.834 | 262.749 | 372.4 | 43.7915 | 43.6587 | 0.13278 | 261.9523 | 41.6 | 43.0344 | -1.4344 | 0.9851 | 2026-06-03 10:00 | 191.019 | 193.653 | 274.7 | 32.2755 | 32.3398 | -0.064295 | 194.0388 | 30.8 | 31.8773 | -1.0773 | 0.9864 | 2026-06-03 10:00 | 191.53 | 194.389 | 277.2 | 32.3982 | 32.3398 | 0.058372 | 194.0388 | 30.8 | 31.8773 | -1.0773 | 0.98529 | 2026-06-03 10:00 | 189.948 | 192.616 | 276 | 32.1027 | 32.3398 | -0.23713 | 194.0388 | 30.6 | 31.8773 | -1.2773 | 0.98615 | 2026-06-03 10:00 | 191.134 | 196.597 | 278.8 | 32.7662 | 32.3398 | 0.42637 | 194.0388 | 30.9 | 31.8773 | -0.97734 | 0.97221 | 2026-06-03 10:00 | 181.552 | 184.055 | 263.6 | 30.6758 | 30.7673 | -0.091476 | 184.6039 | 29.7 | 30.3273 | -0.62734 | 0.9864 | 2026-06-03 10:00 | 334.67 | 334.7614 | -0.091384 | 2008.5683 | 320.1 | 329.9743 | -9.8743
2026-06-03 09:50 | 691 | 49.36 | 242.734 | 246.255 | 328.1 | 41.0425 | 41.0571 | -0.014574 | 246.3424 | 40.4 | 40.47 | -0.069957 |  | 2026-06-03 09:50 | 245.393 | 248.997 | 328 | 41.4995 | 41.0571 | 0.44243 | 246.3424 | 39.7 | 40.47 | -0.76996 |  | 2026-06-03 09:50 | 240.066 | 245.421 | 324.2 | 40.9035 | 41.0571 | -0.15357 | 246.3424 | 39.2 | 40.47 | -1.27 |  | 2026-06-03 09:50 | 245.042 | 248.623 | 330.8 | 41.4372 | 41.0571 | 0.38009 | 246.3424 | 39.8 | 40.47 | -0.66996 |  | 2026-06-03 09:50 | 180.75 | 183.092 | 243.9 | 30.5153 | 30.4126 | 0.10269 | 182.4759 | 29.5 | 29.9777 | -0.47775 |  | 2026-06-03 09:50 | 181.686 | 184.135 | 246.4 | 30.6892 | 30.4126 | 0.27652 | 182.4759 | 29.6 | 29.9777 | -0.37775 |  | 2026-06-03 09:50 | 180.668 | 183.102 | 245.4 | 30.517 | 30.4126 | 0.10435 | 182.4759 | 29.5 | 29.9777 | -0.47775 |  | 2026-06-03 09:50 | 182.544 | 187.829 | 247.9 | 31.3048 | 30.4126 | 0.89219 | 182.4759 | 29.7 | 29.9777 | -0.27775 |  | 2026-06-03 09:50 | 172.454 | 174.779 | 233.9 | 29.1298 | 28.9339 | 0.19597 | 173.6032 | 28 | 28.5201 | -0.52011 |  | 2026-06-03 09:50 | 317.0388 | 314.8127 | 2.2261 | 1888.8765 | 305.4 | 310.3109 | -4.9109
2026-06-03 09:40 | 655 | 48.79 | 234.124 | 237.424 | 287.7 | 39.5707 | 39.0029 | 0.56772 | 234.0177 | 37.2 | 38.4452 | -1.2452 |  | 2026-06-03 09:40 | 235.076 | 238.438 | 288.3 | 39.7397 | 39.0029 | 0.73672 | 234.0177 | 37.3 | 38.4452 | -1.1452 |  | 2026-06-03 09:40 | 231.135 | 236.067 | 285 | 39.3445 | 39.0029 | 0.34156 | 234.0177 | 37.1 | 38.4452 | -1.3452 |  | 2026-06-03 09:40 | 234.462 | 237.839 | 291 | 39.6398 | 39.0029 | 0.63689 | 234.0177 | 38.4 | 38.4452 | -0.045202 |  | 2026-06-03 09:40 | 174.004 | 176.332 | 214.4 | 29.3887 | 28.8911 | 0.4976 | 173.3464 | 28.4 | 28.4779 | -0.077927 |  | 2026-06-03 09:40 | 173.896 | 176.204 | 216.8 | 29.3673 | 28.8911 | 0.47626 | 173.3464 | 28.4 | 28.4779 | -0.077927 |  | 2026-06-03 09:40 | 173.538 | 175.842 | 215.9 | 29.307 | 28.8911 | 0.41593 | 173.3464 | 28.3 | 28.4779 | -0.17793 |  | 2026-06-03 09:40 | 174.501 | 179.264 | 218.2 | 29.8773 | 28.8911 | 0.98626 | 173.3464 | 28.5 | 28.4779 | 0.022073 |  | 2026-06-03 09:40 | 165.086 | 167.277 | 205.9 | 27.8795 | 27.4863 | 0.39323 | 164.9176 | 26.7 | 27.0932 | -0.39322 |  | 2026-06-03 09:40 | 304.1145 | 299.0623 | 5.0522 | 1794.374 | 290.3 | 294.7857 | -4.4857
2026-06-03 09:30 | 618 | 48.5 | 221.693 | 224.727 | 250.5 | 37.4545 | 36.8405 | 0.61403 | 221.0428 | 36.9 | 36.3136 | 0.58635 |  | 2026-06-03 09:30 | 219.921 | 222.953 | 251 | 37.1588 | 36.8405 | 0.31837 | 221.0428 | 36.3 | 36.3136 | -0.01365 |  | 2026-06-03 09:30 | 218.329 | 222.941 | 247.9 | 37.1568 | 36.8405 | 0.31637 | 221.0428 | 35.3 | 36.3136 | -1.0136 |  | 2026-06-03 09:30 | 221.857 | 224.911 | 252.6 | 37.4852 | 36.8405 | 0.6447 | 221.0428 | 35.3 | 36.3136 | -1.0136 |  | 2026-06-03 09:30 | 163.921 | 166.046 | 186 | 27.6743 | 27.2892 | 0.3851 | 163.7354 | 26.1 | 26.899 | -0.799 |  | 2026-06-03 09:30 | 164.436 | 166.585 | 188.4 | 27.7642 | 27.2892 | 0.47493 | 163.7354 | 26.6 | 26.899 | -0.299 |  | 2026-06-03 09:30 | 163.616 | 165.737 | 187.6 | 27.6228 | 27.2892 | 0.3336 | 163.7354 | 26.4 | 26.899 | -0.499 |  | 2026-06-03 09:30 | 165.219 | 169.853 | 189.7 | 28.3088 | 27.2892 | 1.0196 | 163.7354 | 26.6 | 26.899 | -0.299 |  | 2026-06-03 09:30 | 156.399 | 158.411 | 179.2 | 26.4018 | 25.9623 | 0.43951 | 155.774 | 25.3 | 25.5911 | -0.29107 |  | 2026-06-03 09:30 | 287.0273 | 282.4811 | 4.5462 | 1694.8869 | 274.8 | 278.4417 | -3.6417
2026-06-03 09:20 | 578 | 48.5 | 207.768 | 210.526 | 213.6 | 35.0877 | 34.456 | 0.63169 | 206.7358 | 32.8 | 33.9633 | -1.1633 |  | 2026-06-03 09:20 | 205.97 | 208.746 | 214.7 | 34.791 | 34.456 | 0.33503 | 206.7358 | 33.5 | 33.9633 | -0.46325 |  | 2026-06-03 09:20 | 204.446 | 208.648 | 212.6 | 34.7747 | 34.456 | 0.31869 | 206.7358 | 32.6 | 33.9633 | -1.3633 |  | 2026-06-03 09:20 | 208.299 | 211.107 | 217.3 | 35.1845 | 34.456 | 0.72853 | 206.7358 | 33.4 | 33.9633 | -0.56325 |  | 2026-06-03 09:20 | 153.444 | 155.551 | 159.9 | 25.9252 | 25.5229 | 0.40222 | 153.1377 | 24.6 | 25.158 | -0.55796 |  | 2026-06-03 09:20 | 154.495 | 156.466 | 161.8 | 26.0777 | 25.5229 | 0.55472 | 153.1377 | 24.7 | 25.158 | -0.45796 |  | 2026-06-03 09:20 | 153.403 | 155.345 | 161.2 | 25.8908 | 25.5229 | 0.36789 | 153.1377 | 24.7 | 25.158 | -0.45796 |  | 2026-06-03 09:20 | 154.221 | 158.552 | 163.1 | 26.4253 | 25.5229 | 0.90239 | 153.1377 | 24.9 | 25.158 | -0.25796 |  | 2026-06-03 09:20 | 146.288 | 148.14 | 153.9 | 24.69 | 24.2819 | 0.40808 | 145.6915 | 23.5 | 23.9347 | -0.43469 |  | 2026-06-03 09:20 | 268.8468 | 264.1976 | 4.6493 | 1585.1854 | 254.7 | 260.4195 | -5.7195
2026-06-03 09:10 | 533 | 48.5 | 192.361 | 194.749 | 180.8 | 32.4582 | 31.7734 | 0.68475 | 190.6405 | 30.4 | 31.3191 | -0.91905 |  | 2026-06-03 09:10 | 190.861 | 193.375 | 181.2 | 32.2292 | 31.7734 | 0.45575 | 190.6405 | 30.8 | 31.3191 | -0.51905 |  | 2026-06-03 09:10 | 188.866 | 192.376 | 180 | 32.0627 | 31.7734 | 0.28925 | 190.6405 | 30.4 | 31.3191 | -0.91905 |  | 2026-06-03 09:10 | 193.009 | 195.551 | 183.9 | 32.5918 | 31.7734 | 0.81842 | 190.6405 | 31 | 31.3191 | -0.31905 |  | 2026-06-03 09:10 | 142.255 | 144.041 | 135.3 | 24.0068 | 23.5359 | 0.47097 | 141.2152 | 22.8 | 23.1993 | -0.3993 |  | 2026-06-03 09:10 | 143.146 | 144.929 | 137.1 | 24.1548 | 23.5359 | 0.61897 | 141.2152 | 22.7 | 23.1993 | -0.4993 |  | 2026-06-03 09:10 | 142.299 | 144.071 | 136.5 | 24.0118 | 23.5359 | 0.47597 | 141.2152 | 22.8 | 23.1993 | -0.3993 |  | 2026-06-03 09:10 | 143.693 | 147.525 | 138.2 | 24.5875 | 23.5359 | 1.0516 | 141.2152 | 23 | 23.1993 | -0.1993 |  | 2026-06-03 09:10 | 136.417 | 138.13 | 130.4 | 23.0217 | 22.3915 | 0.63021 | 134.3487 | 21.9 | 22.0713 | -0.17126 |  | 2026-06-03 09:10 | 249.1245 | 243.6286 | 5.4959 | 1461.7714 | 235.8 | 240.1447 | -4.3447
2026-06-03 09:00 | 491 | 48.22 | 177.023 | 179.468 | 150.4 | 29.9113 | 29.3009 | 0.61039 | 175.8057 | 28.2 | 28.8819 | -0.68194 |  | 2026-06-03 09:00 | 175.444 | 177.683 | 150.4 | 29.6138 | 29.3009 | 0.31289 | 175.8057 | 27 | 28.8819 | -1.8819 |  | 2026-06-03 09:00 | 173.443 | 176.43 | 149.6 | 29.405 | 29.3009 | 0.10405 | 175.8057 | 27.4 | 28.8819 | -1.4819 |  | 2026-06-03 09:00 | 177.866 | 180.117 | 152.9 | 30.0195 | 29.3009 | 0.71855 | 175.8057 | 28.5 | 28.8819 | -0.38194 |  | 2026-06-03 09:00 | 131.053 | 132.658 | 112.5 | 22.1097 | 21.7044 | 0.40526 | 130.2264 | 21 | 21.394 | -0.39403 |  | 2026-06-03 09:00 | 132.018 | 133.621 | 114.4 | 22.2702 | 21.7044 | 0.56576 | 130.2264 | 21.2 | 21.394 | -0.19403 |  | 2026-06-03 09:00 | 131.152 | 132.718 | 113.7 | 22.1197 | 21.7044 | 0.41526 | 130.2264 | 20.7 | 21.394 | -0.69403 |  | 2026-06-03 09:00 | 132.281 | 135.74 | 115.2 | 22.6233 | 21.7044 | 0.91893 | 130.2264 | 20.9 | 21.394 | -0.49403 |  | 2026-06-03 09:00 | 125.634 | 127.173 | 108.5 | 21.1955 | 20.6491 | 0.54645 | 123.8943 | 19.9 | 20.3538 | -0.45377 |  | 2026-06-03 09:00 | 229.268 | 224.6705 | 4.5975 | 1348.0228 | 214.8 | 221.4577 | -6.6577
2026-06-03 08:50 | 447 | 47.93 | 158.32 | 160.104 | 122.2 | 26.684 | 26.7047 | -0.020671 | 160.228 | 25.1 | 26.3228 | -1.2228 |  | 2026-06-03 08:50 | 159.905 | 161.88 | 123.4 | 26.98 | 26.7047 | 0.27533 | 160.228 | 26.4 | 26.3228 | 0.077206 |  | 2026-06-03 08:50 | 157.337 | 159.828 | 122.2 | 26.638 | 26.7047 | -0.066671 | 160.228 | 25 | 26.3228 | -1.3228 |  | 2026-06-03 08:50 | 161.311 | 163.303 | 124.4 | 27.2172 | 26.7047 | 0.5125 | 160.228 | 25.3 | 26.3228 | -1.0228 |  | 2026-06-03 08:50 | 118.626 | 120.03 | 91.5 | 20.005 | 19.7812 | 0.22376 | 118.6874 | 18.6 | 19.4984 | -0.89837 |  | 2026-06-03 08:50 | 119.799 | 121.205 | 93.2 | 20.2008 | 19.7812 | 0.4196 | 118.6874 | 18.7 | 19.4984 | -0.79837 |  | 2026-06-03 08:50 | 118.715 | 120.108 | 93 | 20.018 | 19.7812 | 0.23676 | 118.6874 | 18.8 | 19.4984 | -0.69837 |  | 2026-06-03 08:50 | 120.126 | 123.354 | 94.3 | 20.559 | 19.7812 | 0.77776 | 118.6874 | 19.1 | 19.4984 | -0.39837 |  | 2026-06-03 08:50 | 114.008 | 115.369 | 88.6 | 19.2282 | 18.8194 | 0.40877 | 112.9164 | 18 | 18.5503 | -0.55028 |  | 2026-06-03 08:50 | 207.5302 | 204.763 | 2.7671 | 1228.5782 | 195 | 201.8349 | -6.8349
2026-06-03 08:40 | 402 | 45.06 | 142.045 | 143.712 | 97.1 | 23.952 | 24.2786 | -0.32658 | 145.6715 | 22.1 | 23.9314 | -1.8314 |  | 2026-06-03 08:40 | 140.99 | 143.69 | 97 | 23.9483 | 24.2786 | -0.33024 | 145.6715 | 21.3 | 23.9314 | -2.6314 |  | 2026-06-03 08:40 | 140.808 | 142.883 | 97.2 | 23.8138 | 24.2786 | -0.46474 | 145.6715 | 22 | 23.9314 | -1.9314 |  | 2026-06-03 08:40 | 144.337 | 146.046 | 99.1 | 24.341 | 24.2786 | 0.062425 | 145.6715 | 22.6 | 23.9314 | -1.3314 |  | 2026-06-03 08:40 | 105.836 | 107.056 | 72.9 | 17.8427 | 17.9841 | -0.14146 | 107.9048 | 16.5 | 17.727 | -1.227 |  | 2026-06-03 08:40 | 107.342 | 108.558 | 74.5 | 18.093 | 17.9841 | 0.10887 | 107.9048 | 16.8 | 17.727 | -0.92696 |  | 2026-06-03 08:40 | 106.209 | 107.434 | 74.2 | 17.9057 | 17.9841 | -0.078463 | 107.9048 | 16.5 | 17.727 | -1.227 |  | 2026-06-03 08:40 | 107.443 | 110.23 | 75.2 | 18.3717 | 17.9841 | 0.38754 | 107.9048 | 16.6 | 17.727 | -1.127 |  | 2026-06-03 08:40 | 102.001 | 103.177 | 70.6 | 17.1962 | 17.1097 | 0.086495 | 102.658 | 15.9 | 16.865 | -0.965 |  | 2026-06-03 08:40 | 185.4643 | 186.1605 | -0.69616 | 1116.963 | 170.3 | 183.4984 | -13.1984
2026-06-03 08:30 | 357 | 41.04 | 122.451 | 123.363 | 75 | 20.5605 | 21.8871 | -1.3266 | 131.3226 | 34.7 | 21.5741 | 13.1259 |  | 2026-06-03 08:30 | 124.854 | 126.307 | 75.7 | 21.0512 | 21.8871 | -0.83593 | 131.3226 | 35.7 | 21.5741 | 14.1259 |  | 2026-06-03 08:30 | 123.231 | 124.927 | 75.2 | 20.8212 | 21.8871 | -1.0659 | 131.3226 | 35.1 | 21.5741 | 13.5259 |  | 2026-06-03 08:30 | 126.364 | 127.808 | 76.5 | 21.3013 | 21.8871 | -0.58576 | 131.3226 | 36 | 21.5741 | 14.4259 |  | 2026-06-03 08:30 | 92.547 | 93.586 | 56.4 | 15.5977 | 16.2127 | -0.61499 | 97.276 | 26.3 | 15.9808 | 10.3192 |  | 2026-06-03 08:30 | 94.098 | 95.135 | 57.7 | 15.8558 | 16.2127 | -0.35683 | 97.276 | 26.9 | 15.9808 | 10.9192 |  | 2026-06-03 08:30 | 93.562 | 94.612 | 57.7 | 15.7687 | 16.2127 | -0.44399 | 97.276 | 26.7 | 15.9808 | 10.7192 |  | 2026-06-03 08:30 | 94.437 | 97.027 | 58.6 | 16.1712 | 16.2127 | -0.041494 | 97.276 | 27.2 | 15.9808 | 11.2192 |  | 2026-06-03 08:30 | 89.499 | 90.813 | 54.7 | 15.1355 | 15.4243 | -0.28884 | 92.546 | 25.8 | 15.2038 | 10.5962 |  | 2026-06-03 08:30 | 162.263 | 167.8234 | -5.5604 | 1006.9401 | 274.4 | 165.4235 | 108.9765
2026-06-03 08:20 | 312 | 36.74 |  |  |  | 0 | 19.4332 | -19.4332 | 116.5993 | 0 | 19.1553 | -19.1553 | [5 empty] | 0 | 19.4332 | -19.4332 | 116.5993 | 0 | 19.1553 | -19.1553 | [5 empty] | 0 | 19.4332 | -19.4332 | 116.5993 | 0 | 19.1553 | -19.1553 | [5 empty] | 0 | 19.4332 | -19.4332 | 116.5993 | 0 | 19.1553 | -19.1553 | [5 empty] | 0 | 14.395 | -14.395 | 86.3699 | 0 | 14.1891 | -14.1891 | [5 empty] | 0 | 14.395 | -14.395 | 86.3699 | 0 | 14.1891 | -14.1891 | [5 empty] | 0 | 14.395 | -14.395 | 86.3699 | 0 | 14.1891 | -14.1891 | [5 empty] | 0 | 14.395 | -14.395 | 86.3699 | 0 | 14.1891 | -14.1891 | [5 empty] | 0 | 13.695 | -13.695 | 82.1702 | 0 | 13.4992 | -13.4992 |  | 2026-06-03 08:20 | 0 | 149.0078 | -149.0078 | 894.0469 | 0 | 146.877 | -146.877
2026-06-03 08:10 | 267 | 31.86 | 85.814 | 86.751 | 40.3 | 14.4585 | 16.9266 | -2.4681 | 101.5594 | 13.1 | 16.6845 | -3.5845 |  | 2026-06-03 08:10 | 88.577 | 89.544 | 40 | 14.924 | 16.9266 | -2.0026 | 101.5594 | 13.4 | 16.6845 | -3.2845 |  | 2026-06-03 08:10 | 87.444 | 88.55 | 40.1 | 14.7583 | 16.9266 | -2.1682 | 101.5594 | 13 | 16.6845 | -3.6845 |  | 2026-06-03 08:10 | 90.106 | 91.081 | 40.5 | 15.1802 | 16.9266 | -1.7464 | 101.5594 | 13.5 | 16.6845 | -3.1845 |  | 2026-06-03 08:10 | 65.665 | 66.442 | 30.1 | 11.0737 | 12.5382 | -1.4645 | 75.2292 | 10 | 12.3589 | -2.3589 |  | 2026-06-03 08:10 | 67.217 | 68.006 | 30.8 | 11.3343 | 12.5382 | -1.2039 | 75.2292 | 10.2 | 12.3589 | -2.1589 |  | 2026-06-03 08:10 | 66.842 | 67.64 | 31 | 11.2733 | 12.5382 | -1.2649 | 75.2292 | 10.1 | 12.3589 | -2.2589 |  | 2026-06-03 08:10 | 67.478 | 69.425 | 31.4 | 11.5708 | 12.5382 | -0.96736 | 75.2292 | 10.1 | 12.3589 | -2.2589 |  | 2026-06-03 08:10 | 63.955 | 64.725 | 28.9 | 10.7875 | 11.9285 | -1.141 | 71.5713 | 9.5 | 11.758 | -2.258 |  | 2026-06-03 08:10 | 115.3607 | 129.7876 | -14.4269 | 778.7256 | 102.9 | 127.9316 | -25.0316
2026-06-03 08:00 | 222 | 29.56 | 68.633 | 69.424 | 27.2 | 11.5707 | 14.1899 | -2.6192 | 85.1391 | 9.9 | 13.9869 | -4.0869 |  | 2026-06-03 08:00 | 70.654 | 71.49 | 26.6 | 11.915 | 14.1899 | -2.2749 | 85.1391 | 10.2 | 13.9869 | -3.7869 |  | 2026-06-03 08:00 | 69.871 | 70.677 | 27.1 | 11.7795 | 14.1899 | -2.4104 | 85.1391 | 10.2 | 13.9869 | -3.7869 |  | 2026-06-03 08:00 | 71.932 | 72.761 | 27 | 12.1268 | 14.1899 | -2.063 | 85.1391 | 10.5 | 13.9869 | -3.4869 |  | 2026-06-03 08:00 | 52.167 | 52.859 | 20.1 | 8.8098 | 10.511 | -1.7012 | 63.066 | 7.5 | 10.3607 | -2.8607 |  | 2026-06-03 08:00 | 53.747 | 54.433 | 20.6 | 9.0722 | 10.511 | -1.4388 | 63.066 | 7.9 | 10.3607 | -2.4607 |  | 2026-06-03 08:00 | 53.507 | 54.212 | 20.9 | 9.0353 | 10.511 | -1.4757 | 63.066 | 7.9 | 10.3607 | -2.4607 |  | 2026-06-03 08:00 | 54.168 | 55.735 | 21.3 | 9.2892 | 10.511 | -1.2218 | 63.066 | 8 | 10.3607 | -2.3607 |  | 2026-06-03 08:00 | 51.366 | 52.058 | 19.4 | 8.6763 | 9.9999 | -1.3236 | 59.9995 | 7.6 | 9.8569 | -2.2569 |  | 2026-06-03 08:00 | 92.2748 | 108.8034 | -16.5285 | 652.8202 | 79.7 | 107.2475 | -27.5475
2026-06-03 07:50 | 176 | 27.26 | 52.375 | 53.043 | 17.3 | 8.8405 | 11.3416 | -2.5011 | 68.0499 | 7.4 | 11.1795 | -3.7795 |  | 2026-06-03 07:50 | 51.981 | 53.487 | 16.4 | 8.9145 | 11.3416 | -2.4271 | 68.0499 | 7.3 | 11.1795 | -3.8795 |  | 2026-06-03 07:50 | 52.553 | 53.245 | 16.9 | 8.8742 | 11.3416 | -2.4675 | 68.0499 | 7.4 | 11.1795 | -3.7795 |  | 2026-06-03 07:50 | 54.278 | 54.987 | 16.5 | 9.1645 | 11.3416 | -2.1771 | 68.0499 | 7.7 | 11.1795 | -3.4795 |  | 2026-06-03 07:50 | 39.308 | 39.915 | 12.6 | 6.6525 | 8.4012 | -1.7487 | 50.4073 | 5.5 | 8.2811 | -2.7811 |  | 2026-06-03 07:50 | 40.446 | 41.045 | 12.7 | 6.8408 | 8.4012 | -1.5604 | 50.4073 | 5.7 | 8.2811 | -2.5811 |  | 2026-06-03 07:50 | 40.242 | 40.851 | 13 | 6.8085 | 8.4012 | -1.5927 | 50.4073 | 5.6 | 8.2811 | -2.6811 |  | 2026-06-03 07:50 | 40.926 | 42.047 | 13.3 | 7.0078 | 8.4012 | -1.3934 | 50.4073 | 5.7 | 8.2811 | -2.5811 |  | 2026-06-03 07:50 | 38.798 | 39.397 | 11.8 | 6.5662 | 7.9927 | -1.4266 | 47.9563 | 5.4 | 7.8784 | -2.4784 |  | 2026-06-03 07:50 | 69.6695 | 86.9642 | -17.2947 | 521.785 | 57.7 | 85.7206 | -28.0206
2026-06-03 07:40 | 131 | 22.96 | 36.875 | 37.444 | 9.9 | 6.2407 | 8.5699 | -2.3292 | 51.4191 | 5.1 | 8.4473 | -3.3473 |  | 2026-06-03 07:40 | 36.263 | 36.845 | 9.1 | 6.1408 | 8.5699 | -2.429 | 51.4191 | 4.8 | 8.4473 | -3.6473 |  | 2026-06-03 07:40 | 36.485 | 37.041 | 9.5 | 6.1735 | 8.5699 | -2.3964 | 51.4191 | 5 | 8.4473 | -3.4473 |  | 2026-06-03 07:40 | 36.617 | 37.193 | 8.8 | 6.1988 | 8.5699 | -2.371 | 51.4191 | 4.7 | 8.4473 | -3.7473 |  | 2026-06-03 07:40 | 27.124 | 27.606 | 7.1 | 4.601 | 6.348 | -1.747 | 38.0882 | 3.7 | 6.2573 | -2.5573 |  | 2026-06-03 07:40 | 28.331 | 28.811 | 7 | 4.8018 | 6.348 | -1.5462 | 38.0882 | 3.7 | 6.2573 | -2.5573 |  | 2026-06-03 07:40 | 28.157 | 28.659 | 7.4 | 4.7765 | 6.348 | -1.5715 | 38.0882 | 3.8 | 6.2573 | -2.4573 |  | 2026-06-03 07:40 | 28.745 | 29.656 | 7.6 | 4.9427 | 6.348 | -1.4054 | 38.0882 | 3.9 | 6.2573 | -2.3573 |  | 2026-06-03 07:40 | 26.842 | 27.363 | 6.4 | 4.5605 | 6.0394 | -1.4789 | 36.2362 | 3.5 | 5.953 | -2.453 |  | 2026-06-03 07:40 | 48.4363 | 65.7109 | -17.2746 | 394.2657 | 38.2 | 64.7713 | -26.5713
2026-06-03 07:30 | 87 | 20.95 | 23.352 | 23.821 | 4.8 | 3.9702 | 5.7312 | -1.761 | 34.3871 | 2.9 | 5.6492 | -2.7492 |  | 2026-06-03 07:30 | 21.122 | 21.719 | 4.3 | 3.6198 | 5.7312 | -2.1114 | 34.3871 | 2.6 | 5.6492 | -3.0492 |  | 2026-06-03 07:30 | 23.257 | 23.7 | 4.5 | 3.95 | 5.7312 | -1.7812 | 34.3871 | 3 | 5.6492 | -2.6492 |  | 2026-06-03 07:30 | 21.491 | 21.968 | 4.1 | 3.6613 | 5.7312 | -2.0699 | 34.3871 | 2.7 | 5.6492 | -2.9492 |  | 2026-06-03 07:30 | 17.001 | 17.609 | 3.4 | 2.9348 | 4.2453 | -1.3105 | 25.4719 | 2.1 | 4.1846 | -2.0846 |  | 2026-06-03 07:30 | 17.897 | 18.305 | 3.3 | 3.0508 | 4.2453 | -1.1945 | 25.4719 | 2.3 | 4.1846 | -1.8846 |  | 2026-06-03 07:30 | 17.732 | 18.138 | 3.6 | 3.023 | 4.2453 | -1.2223 | 25.4719 | 2.2 | 4.1846 | -1.9846 |  | 2026-06-03 07:30 | 18.179 | 19.029 | 3.7 | 3.1715 | 4.2453 | -1.0738 | 25.4719 | 2.3 | 4.1846 | -1.8846 |  | 2026-06-03 07:30 | 15.895 | 16.276 | 2.9 | 2.7127 | 4.0389 | -1.3262 | 24.2334 | 2 | 3.9811 | -1.9811 |  | 2026-06-03 07:30 | 30.0942 | 43.9449 | -13.8508 | 263.6696 | 22.1 | 43.3165 | -21.2165
2026-06-03 07:20 | 21 | 20.95 | 12.707 | 13.068 | 1.9 | 2.178 | 1.3834 | 0.79461 | 8.3003 | 1.4 | 1.3636 | 0.036393 |  | 2026-06-03 07:20 | 10.427 | 10.901 | 1.7 | 1.8168 | 1.3834 | 0.43344 | 8.3003 | 1.2 | 1.3636 | -0.16361 |  | 2026-06-03 07:20 | 12.291 | 12.669 | 1.5 | 2.1115 | 1.3834 | 0.72811 | 8.3003 | 1.3 | 1.3636 | -0.063607 |  | 2026-06-03 07:20 | 10.752 | 11.428 | 1.4 | 1.9047 | 1.3834 | 0.52128 | 8.3003 | 1.2 | 1.3636 | -0.16361 |  | 2026-06-03 07:20 | 8.968 | 9.553 | 1.3 | 1.5922 | 1.0247 | 0.56743 | 6.1484 | 1 | 1.0101 | -0.010079 |  | 2026-06-03 07:20 | 8.831 | 9.14 | 1 | 1.5233 | 1.0247 | 0.4986 | 6.1484 | 0.9 | 1.0101 | -0.11008 |  | 2026-06-03 07:20 | 9.502 | 9.839 | 1.4 | 1.6398 | 1.0247 | 0.6151 | 6.1484 | 1.1 | 1.0101 | 0.089921 |  | 2026-06-03 07:20 | 9.797 | 10.384 | 1.4 | 1.7307 | 1.0247 | 0.70593 | 6.1484 | 1.1 | 1.0101 | 0.089921 |  | 2026-06-03 07:20 | 7.923 | 8.223 | 0.9 | 1.3705 | 0.97491 | 0.39559 | 5.8494 | 0.8 | 0.96097 | -0.16097 |  | 2026-06-03 07:20 | 15.8675 | 10.6074 | 5.2601 | 63.6444 | 10 | 10.4557 | -0.45571
2026-06-03 07:10 | 11 | 20.38 | 4.896 | 5.117 | 0.5 | 0.85283 | 0.72606 | 0.12678 | 4.3563 | 0.5 | 0.71568 | -0.21568 |  | 2026-06-03 07:10 | 4.74 | 5.24 | 0.5 | 0.87333 | 0.72606 | 0.14728 | 4.3563 | 0.5 | 0.71568 | -0.21568 |  | 2026-06-03 07:10 | 4.675 | 4.889 | 0.2 | 0.81483 | 0.72606 | 0.088775 | 4.3563 | 0.2 | 0.71568 | -0.51568 |  | 2026-06-03 07:10 | 4.513 | 5.421 | 0.2 | 0.9035 | 0.72606 | 0.17744 | 4.3563 | 0.2 | 0.71568 | -0.51568 |  | 2026-06-03 07:10 | 3.495 | 4.179 | 0.3 | 0.6965 | 0.53782 | 0.15868 | 3.2269 | 0.3 | 0.53013 | -0.23013 |  | 2026-06-03 07:10 | 3.323 | 3.483 | 0.1 | 0.5805 | 0.53782 | 0.042679 | 3.2269 | 0.1 | 0.53013 | -0.43013 |  | 2026-06-03 07:10 | 3.587 | 3.759 | 0.3 | 0.6265 | 0.53782 | 0.088679 | 3.2269 | 0.3 | 0.53013 | -0.23013 |  | 2026-06-03 07:10 | 3.689 | 4.165 | 0.3 | 0.69417 | 0.53782 | 0.15635 | 3.2269 | 0.3 | 0.53013 | -0.23013 |  | 2026-06-03 07:10 | 3.134 | 3.287 | 0.1 | 0.54783 | 0.51167 | 0.036163 | 3.07 | 0.1 | 0.50435 | -0.40435 |  | 2026-06-03 07:10 | 6.59 | 5.5672 | 1.0228 | 33.4031 | 2.5 | 5.4876 | -2.9876
2026-06-03 07:00 | 1 | 20.38 | 1.186 | 1.247 | 0 | 0.20783 | 0.066005 | 0.14183 | 0.39603 | 0 | 0.065061 | -0.065061 |  | 2026-06-03 07:00 | 1.347 | 1.916 | 0 | 0.31933 | 0.066005 | 0.25333 | 0.39603 | 0 | 0.065061 | -0.065061 |  | 2026-06-03 07:00 | 0 | 0 | 0 | 0 | 0.066005 | -0.066005 | 0.39603 | 0 | 0.065061 | -0.065061 |  | 2026-06-03 07:00 | 0 | 0 | 0 | 0 | 0.066005 | -0.066005 | 0.39603 | 0 | 0.065061 | -0.065061 |  | 2026-06-03 07:00 | 0.784 | 1.324 | 0 | 0.22067 | 0.048893 | 0.17177 | 0.29336 | 0 | 0.048194 | -0.048194 |  | 2026-06-03 07:00 | 0 | 0 | 0 | 0 | 0.048893 | -0.048893 | 0.29336 | 0 | 0.048194 | -0.048194 |  | 2026-06-03 07:00 | 0.694 | 0.73 | 0 | 0.12167 | 0.048893 | 0.072774 | 0.29336 | 0 | 0.048194 | -0.048194 |  | 2026-06-03 07:00 | 0.895 | 1.309 | 0 | 0.21817 | 0.048893 | 0.16927 | 0.29336 | 0 | 0.048194 | -0.048194 |  | 2026-06-03 07:00 | 0 | 0 | 0 | 0 | 0.046515 | -0.046515 | 0.27909 | 0 | 0.04585 | -0.04585 |  | 2026-06-03 07:00 | 1.0877 | 0.50611 | 0.58156 | 3.0366 | 0 | 0.49887 | -0.49887
[110 empty] | Total: - | 19168.5005 | 20354.0121 | -1185.5116 |  | 19068.7 | 20062.9497 | -994.2497
Sum:- | 44517 |  | 14519.459 |  | 94190 | 2514.773 |  |  |  | 2484.2 | 2616.5586 | -132.3586 | 0.98301 |  | 14778.015 |  | 92563.2 |  |  |  |  | 2505.2 | 2616.5586 | -111.3586 | 0.98285 |  | 14543.426 |  | 93120 |  |  |  |  | 2458.7 | 2616.5586 | -157.8586 | 0.97295 |  | 14739.2 |  | 94540.8 |  |  |  |  | 2492 | 2616.5586 | -124.5586 | 0.983 |  | 10996.526 |  | 70368.1 |  |  |  |  | 1859.3 | 1938.1915 | -78.8915 | 0.98447 |  | 10880.628 |  | 69933.6 |  |  |  |  | 1839.9 | 1938.1915 | -98.2915 | 0.98196 |  | 10867.534 |  | 69785.3 |  |  |  |  | 1837.7 | 1938.1915 | -100.4915 | 0.98121 |  | 10910.34 |  | 70243.2 |  |  |  |  | 1845.7 | 1938.1915 | -92.4915 | 0.9715 |  | 10321.671 |  | 66445.1 |  |  |  |  | 1746 | 1843.9492 | -97.9492 | 0.9848
Formulas:
Time = [Time]

## 7 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-07-03 19:00 | 0 | 38.17 | 0.094 | 0.099 | 2538.8 | 0.0165 | 0 | 0.0165 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.081 | 0.252 | 2566.8 | 0.042 | 0 | 0.042 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.091 | 0.096 | 2532.1 | 0.016 | 0 | 0.016 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.082 | 0.202 | 2545.4 | 0.033667 | 0 | 0.033667 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.088 | 0.093 | 1912.5 | 0.0155 | 0 | 0.0155 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.087 | 0.091 | 1886.1 | 0.015167 | 0 | 0.015167 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.066 | 0.08 | 1886.1 | 0.013333 | 0 | 0.013333 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.061 | 0.087 | 1886.4 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.053 | 0.088 | 1784.3 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 2026-07-03 19:00 | 0.18133 | 0 | 0.18133 | 0 | 0 | 0 | 0 | 1 | 98.24%
2026-07-03 18:50 | 0 | 39.61 | 0.342 | 0.36 | 2538.8 | 0.06 | 0 | 0.06 | 0 | 0.3 | 0 | 0.3 |  | 2026-07-03 18:50 | 0.484 | 0.892 | 2566.8 | 0.14867 | 0 | 0.14867 | 0 | 0.3 | 0 | 0.3 |  | 2026-07-03 18:50 | 0.304 | 0.32 | 2532.1 | 0.053333 | 0 | 0.053333 | 0 | 0.2 | 0 | 0.2 |  | 2026-07-03 18:50 | 0.322 | 0.677 | 2545.4 | 0.11283 | 0 | 0.11283 | 0 | 0.2 | 0 | 0.2 |  | 2026-07-03 18:50 | 0.121 | 0.173 | 1912.5 | 0.028833 | 0 | 0.028833 | 0 | 0.2 | 0 | 0.2 |  | 2026-07-03 18:50 | 0.114 | 0.12 | 1886.1 | 0.02 | 0 | 0.02 | 0 | 0.1 | 0 | 0.1 |  | 2026-07-03 18:50 | 0.002 | 0.07 | 1886.1 | 0.011667 | 0 | 0.011667 | 0 | 0.2 | 0 | 0.2 |  | 2026-07-03 18:50 | 0.152 | 0.626 | 1886.4 | 0.10433 | 0 | 0.10433 | 0 | 0.2 | 0 | 0.2 |  | 2026-07-03 18:50 | 0.028 | 0.085 | 1784.3 | 0.014167 | 0 | 0.014167 | 0 | 0.1 | 0 | 0.1 |  | 2026-07-03 18:50 | 0.55383 | 0 | 0.55383 | 0 | 1.8 | 0 | 1.8 | 2 | 98.39%
2026-07-03 18:40 | 2 | 41.33 | 2.88 | 3.028 | 2538.5 | 0.50467 | 0.12248 | 0.38218 | 0.73491 | 0.7 | 0.12073 | 0.57927 |  | 2026-07-03 18:40 | 3.035 | 3.423 | 2566.5 | 0.5705 | 0.12248 | 0.44802 | 0.73491 | 0.8 | 0.12073 | 0.67927 |  | 2026-07-03 18:40 | 2.64 | 2.776 | 2531.9 | 0.46267 | 0.12248 | 0.34018 | 0.73491 | 0.8 | 0.12073 | 0.67927 |  | 2026-07-03 18:40 | 2.527 | 2.932 | 2545.2 | 0.48867 | 0.12248 | 0.36618 | 0.73491 | 0.8 | 0.12073 | 0.67927 |  | 2026-07-03 18:40 | 1.803 | 1.896 | 1912.3 | 0.316 | 0.09073 | 0.22527 | 0.54438 | 0.5 | 0.089432 | 0.41057 |  | 2026-07-03 18:40 | 1.764 | 1.855 | 1886 | 0.30917 | 0.09073 | 0.21844 | 0.54438 | 0.6 | 0.089432 | 0.51057 |  | 2026-07-03 18:40 | 1.762 | 1.853 | 1885.9 | 0.30883 | 0.09073 | 0.2181 | 0.54438 | 0.5 | 0.089432 | 0.41057 |  | 2026-07-03 18:40 | 1.82 | 2.085 | 1886.2 | 0.3475 | 0.09073 | 0.25677 | 0.54438 | 0.5 | 0.089432 | 0.41057 |  | 2026-07-03 18:40 | 1.631 | 1.715 | 1784.2 | 0.28583 | 0.086318 | 0.19952 | 0.51791 | 0.5 | 0.085084 | 0.41492 |  | 2026-07-03 18:40 | 3.5938 | 0.93918 | 2.6547 | 5.6351 | 5.7 | 0.92575 | 4.7743 | 3 | 97.29%
2026-07-03 18:30 | 13 | 43.34 | 6.156 | 6.44 | 2537.8 | 1.0733 | 0.79021 | 0.28312 | 4.7413 | 1.5 | 0.77891 | 0.72109 |  | 2026-07-03 18:30 | 7.159 | 7.604 | 2565.7 | 1.2673 | 0.79021 | 0.47712 | 4.7413 | 1.7 | 0.77891 | 0.92109 |  | 2026-07-03 18:30 | 6.624 | 6.914 | 2531.1 | 1.1523 | 0.79021 | 0.36212 | 4.7413 | 1.6 | 0.77891 | 0.82109 |  | 2026-07-03 18:30 | 6.96 | 7.264 | 2544.4 | 1.2107 | 0.79021 | 0.42046 | 4.7413 | 1.7 | 0.77891 | 0.92109 |  | 2026-07-03 18:30 | 4.917 | 5.145 | 1911.8 | 0.8575 | 0.58534 | 0.27216 | 3.5121 | 1.2 | 0.57697 | 0.62303 |  | 2026-07-03 18:30 | 4.732 | 4.971 | 1885.4 | 0.8285 | 0.58534 | 0.24316 | 3.5121 | 1.2 | 0.57697 | 0.62303 |  | 2026-07-03 18:30 | 4.702 | 4.926 | 1885.4 | 0.821 | 0.58534 | 0.23566 | 3.5121 | 1.1 | 0.57697 | 0.52303 |  | 2026-07-03 18:30 | 4.103 | 4.514 | 1885.7 | 0.75233 | 0.58534 | 0.16699 | 3.5121 | 0.9 | 0.57697 | 0.32303 |  | 2026-07-03 18:30 | 4.106 | 4.307 | 1783.7 | 0.71783 | 0.55688 | 0.16095 | 3.3413 | 0.9 | 0.54892 | 0.35108 |  | 2026-07-03 18:30 | 8.6808 | 6.0591 | 2.6217 | 36.3546 | 11.8 | 5.9724 | 5.8276 | 4 | 98.32%
2026-07-03 18:20 | 25 | 45.06 | 12.5 | 12.907 | 2536.3 | 2.1512 | 1.5099 | 0.64131 | 9.0592 | 2.8 | 1.4883 | 1.3117 |  | 2026-07-03 18:20 | 14.43 | 14.853 | 2564 | 2.4755 | 1.5099 | 0.96564 | 9.0592 | 3.2 | 1.4883 | 1.7117 |  | 2026-07-03 18:20 | 13.663 | 14.114 | 2529.5 | 2.3523 | 1.5099 | 0.84247 | 9.0592 | 3.1 | 1.4883 | 1.6117 |  | 2026-07-03 18:20 | 14.08 | 14.502 | 2542.7 | 2.417 | 1.5099 | 0.90714 | 9.0592 | 3.1 | 1.4883 | 1.6117 |  | 2026-07-03 18:20 | 10.2 | 10.572 | 1910.6 | 1.762 | 1.1184 | 0.64358 | 6.7105 | 2.3 | 1.1024 | 1.1976 |  | 2026-07-03 18:20 | 9.82 | 10.185 | 1884.2 | 1.6975 | 1.1184 | 0.57908 | 6.7105 | 2.2 | 1.1024 | 1.0976 |  | 2026-07-03 18:20 | 9.806 | 10.167 | 1884.3 | 1.6945 | 1.1184 | 0.57608 | 6.7105 | 2.3 | 1.1024 | 1.1976 |  | 2026-07-03 18:20 | 6.831 | 7.473 | 1884.8 | 1.2455 | 1.1184 | 0.12708 | 6.7105 | 1.5 | 1.1024 | 0.39758 |  | 2026-07-03 18:20 | 8.075 | 8.397 | 1782.8 | 1.3995 | 1.064 | 0.33547 | 6.3842 | 1.9 | 1.0488 | 0.85118 |  | 2026-07-03 18:20 | 17.195 | 11.5771 | 5.6179 | 69.4629 | 22.4 | 11.4116 | 10.9884 | 5 | 98.44%
2026-07-03 18:10 | 36 | 47.07 | 22.093 | 22.595 | 2533.5 | 3.7658 | 2.1578 | 1.6081 | 12.9465 | 4.6 | 2.1269 | 2.4731 |  | 2026-07-03 18:10 | 24.619 | 25.157 | 2560.8 | 4.1928 | 2.1578 | 2.0351 | 12.9465 | 4.9 | 2.1269 | 2.7731 |  | 2026-07-03 18:10 | 23.662 | 24.189 | 2526.4 | 4.0315 | 2.1578 | 1.8737 | 12.9465 | 5 | 2.1269 | 2.8731 |  | 2026-07-03 18:10 | 23.542 | 24.072 | 2539.6 | 4.012 | 2.1578 | 1.8542 | 12.9465 | 5 | 2.1269 | 2.8731 |  | 2026-07-03 18:10 | 17.462 | 17.908 | 1908.3 | 2.9847 | 1.5983 | 1.3863 | 9.59 | 3.7 | 1.5755 | 2.1245 |  | 2026-07-03 18:10 | 16.732 | 17.161 | 1882 | 2.8602 | 1.5983 | 1.2618 | 9.59 | 3.5 | 1.5755 | 1.9245 |  | 2026-07-03 18:10 | 16.969 | 17.402 | 1882 | 2.9003 | 1.5983 | 1.302 | 9.59 | 3.5 | 1.5755 | 1.9245 |  | 2026-07-03 18:10 | 11.88 | 12.585 | 1883.3 | 2.0975 | 1.5983 | 0.49917 | 9.59 | 2.8 | 1.5755 | 1.2245 |  | 2026-07-03 18:10 | 15.232 | 15.523 | 1780.9 | 2.5872 | 1.5206 | 1.0666 | 9.1237 | 3.2 | 1.4989 | 1.7011 |  | 2026-07-03 18:10 | 29.432 | 16.545 | 12.887 | 99.2697 | 36.2 | 16.3084 | 19.8916 | 6 | 98.16%
2026-07-03 18:00 | 47 | 47.64 | 34.639 | 35.252 | 2528.9 | 5.8753 | 2.811 | 3.0644 | 16.8658 | 7.2 | 2.7708 | 4.4292 |  | 2026-07-03 18:00 | 36.896 | 37.546 | 2555.9 | 6.2577 | 2.811 | 3.4467 | 16.8658 | 7.8 | 2.7708 | 5.0292 |  | 2026-07-03 18:00 | 36.542 | 37.178 | 2521.4 | 6.1963 | 2.811 | 3.3854 | 16.8658 | 7.3 | 2.7708 | 4.5292 |  | 2026-07-03 18:00 | 36.101 | 36.729 | 2534.6 | 6.1215 | 2.811 | 3.3105 | 16.8658 | 7.1 | 2.7708 | 4.3292 |  | 2026-07-03 18:00 | 27.363 | 27.913 | 1904.6 | 4.6522 | 2.0822 | 2.57 | 12.4932 | 5.5 | 2.0524 | 3.4476 |  | 2026-07-03 18:00 | 26.025 | 26.615 | 1878.5 | 4.4358 | 2.0822 | 2.3536 | 12.4932 | 5.2 | 2.0524 | 3.1476 |  | 2026-07-03 18:00 | 26.31 | 26.861 | 1878.5 | 4.4768 | 2.0822 | 2.3946 | 12.4932 | 5.3 | 2.0524 | 3.2476 |  | 2026-07-03 18:00 | 23.761 | 24.615 | 1880.5 | 4.1025 | 2.0822 | 2.0203 | 12.4932 | 5 | 2.0524 | 2.9476 |  | 2026-07-03 18:00 | 23.617 | 24.141 | 1777.7 | 4.0235 | 1.981 | 2.0425 | 11.8857 | 4.9 | 1.9526 | 2.9474 |  | 2026-07-03 18:00 | 46.1417 | 21.5537 | 24.588 | 129.3219 | 55.3 | 21.2454 | 34.0546 | 7 | 98.13%
2026-07-03 17:50 | 157 | 47.93 | 49.713 | 50.496 | 2521.7 | 8.416 | 9.3795 | -0.96349 | 56.277 | 9.8 | 9.2454 | 0.55463 |  | 2026-07-03 17:50 | 52.125 | 52.93 | 2548.1 | 8.8217 | 9.3795 | -0.55783 | 56.277 | 9.9 | 9.2454 | 0.65463 |  | 2026-07-03 17:50 | 51.341 | 52.139 | 2514.1 | 8.6898 | 9.3795 | -0.68966 | 56.277 | 9.9 | 9.2454 | 0.65463 |  | 2026-07-03 17:50 | 50.845 | 51.63 | 2527.5 | 8.605 | 9.3795 | -0.77449 | 56.277 | 9.9 | 9.2454 | 0.65463 |  | 2026-07-03 17:50 | 38.394 | 39.054 | 1899.1 | 6.509 | 6.9478 | -0.43877 | 41.6866 | 7.4 | 6.8484 | 0.55158 |  | 2026-07-03 17:50 | 36.826 | 37.47 | 1873.3 | 6.245 | 6.9478 | -0.70277 | 41.6866 | 7.1 | 6.8484 | 0.25158 |  | 2026-07-03 17:50 | 37.062 | 37.699 | 1873.2 | 6.2832 | 6.9478 | -0.66461 | 41.6866 | 7.2 | 6.8484 | 0.35158 |  | 2026-07-03 17:50 | 36.234 | 37.253 | 1875.5 | 6.2088 | 6.9478 | -0.73894 | 41.6866 | 7.1 | 6.8484 | 0.25158 |  | 2026-07-03 17:50 | 33.792 | 34.387 | 1772.8 | 5.7312 | 6.6099 | -0.87878 | 39.6597 | 6.6 | 6.5154 | 0.084577 |  | 2026-07-03 17:50 | 65.5097 | 71.919 | -6.4093 | 431.514 | 74.9 | 70.8906 | 4.0094 | 8 | 97.11%
2026-07-03 17:40 | 213 | 47.93 | 68.021 | 67.775 | 2511.9 | 11.2958 | 12.725 | -1.4292 | 76.3503 | 12 | 12.5431 | -0.54308 |  | 2026-07-03 17:40 | 68.821 | 69.763 | 2538.2 | 11.6272 | 12.725 | -1.0979 | 76.3503 | 12.3 | 12.5431 | -0.24308 |  | 2026-07-03 17:40 | 68.092 | 68.989 | 2504.2 | 11.4982 | 12.725 | -1.2269 | 76.3503 | 12.8 | 12.5431 | 0.25692 |  | 2026-07-03 17:40 | 67.648 | 68.553 | 2517.6 | 11.4255 | 12.725 | -1.2995 | 76.3503 | 12.7 | 12.5431 | 0.15692 |  | 2026-07-03 17:40 | 50.867 | 51.657 | 1891.7 | 8.6095 | 9.426 | -0.81646 | 56.5558 | 9.5 | 9.2912 | 0.20883 |  | 2026-07-03 17:40 | 49.045 | 49.807 | 1866.2 | 8.3012 | 9.426 | -1.1248 | 56.5558 | 9.4 | 9.2912 | 0.10883 |  | 2026-07-03 17:40 | 49.325 | 50.096 | 1866 | 8.3493 | 9.426 | -1.0766 | 56.5558 | 9.3 | 9.2912 | 0.0088323 |  | 2026-07-03 17:40 | 47.851 | 49.113 | 1868.4 | 8.1855 | 9.426 | -1.2405 | 56.5558 | 9 | 9.2912 | -0.29117 |  | 2026-07-03 17:40 | 45.806 | 46.541 | 1766.2 | 7.7568 | 8.9676 | -1.2108 | 53.8058 | 8.5 | 8.8394 | -0.3394 |  | 2026-07-03 17:40 | 87.049 | 97.5716 | -10.5226 | 585.4299 | 95.5 | 96.1764 | -0.67637 | 9 | 98.46%
2026-07-03 17:30 | 259 | 47.64 | 82.981 | 84.014 | 2499.9 | 14.0023 | 15.4903 | -1.4879 | 92.9415 | 15.7 | 15.2687 | 0.43126 |  | 2026-07-03 17:30 | 85.054 | 86.157 | 2525.9 | 14.3595 | 15.4903 | -1.1308 | 92.9415 | 16.5 | 15.2687 | 1.2313 |  | 2026-07-03 17:30 | 84.934 | 86.382 | 2491.4 | 14.397 | 15.4903 | -1.0933 | 92.9415 | 15.5 | 15.2687 | 0.23126 |  | 2026-07-03 17:30 | 84.491 | 85.569 | 2504.9 | 14.2615 | 15.4903 | -1.2288 | 92.9415 | 15.5 | 15.2687 | 0.23126 |  | 2026-07-03 17:30 | 63.359 | 64.233 | 1882.2 | 10.7055 | 11.4743 | -0.76876 | 68.8456 | 11.6 | 11.3102 | 0.28982 |  | 2026-07-03 17:30 | 61.511 | 62.34 | 1856.8 | 10.39 | 11.4743 | -1.0843 | 68.8456 | 11.1 | 11.3102 | -0.21018 |  | 2026-07-03 17:30 | 61.772 | 62.611 | 1856.7 | 10.4352 | 11.4743 | -1.0391 | 68.8456 | 11.2 | 11.3102 | -0.11018 |  | 2026-07-03 17:30 | 60.563 | 62.442 | 1859.4 | 10.407 | 11.4743 | -1.0673 | 68.8456 | 11.1 | 11.3102 | -0.21018 |  | 2026-07-03 17:30 | 56.334 | 57.157 | 1757.7 | 9.5262 | 10.9163 | -1.3902 | 65.498 | 10.4 | 10.7602 | -0.36023 |  | 2026-07-03 17:30 | 108.4842 | 118.7744 | -10.2902 | 712.6463 | 118.6 | 117.0759 | 1.5241
2026-07-03 17:20 | 306 | 47.93 | 101.168 | 102.397 | 2484.2 | 17.0662 | 18.281 | -1.2149 | 109.6863 | 17.8 | 18.0196 | -0.21963 |  | 2026-07-03 17:20 | 103.855 | 105.159 | 2509.4 | 17.5265 | 18.281 | -0.75455 | 109.6863 | 18.9 | 18.0196 | 0.88037 |  | 2026-07-03 17:20 | 102.046 | 103.568 | 2475.9 | 17.2613 | 18.281 | -1.0197 | 109.6863 | 18.3 | 18.0196 | 0.28037 |  | 2026-07-03 17:20 | 101.681 | 102.958 | 2489.4 | 17.1597 | 18.281 | -1.1214 | 109.6863 | 18.5 | 18.0196 | 0.48037 |  | 2026-07-03 17:20 | 76.151 | 77.149 | 1870.6 | 12.8582 | 13.5415 | -0.68335 | 81.2491 | 13.7 | 13.3479 | 0.35213 |  | 2026-07-03 17:20 | 73.82 | 74.75 | 1845.7 | 12.4583 | 13.5415 | -1.0832 | 81.2491 | 13.3 | 13.3479 | -0.047875 |  | 2026-07-03 17:20 | 74.196 | 75.173 | 1845.5 | 12.5288 | 13.5415 | -1.0127 | 81.2491 | 13.5 | 13.3479 | 0.15213 |  | 2026-07-03 17:20 | 73.126 | 75.373 | 1848.3 | 12.5622 | 13.5415 | -0.97935 | 81.2491 | 13.3 | 13.3479 | -0.047875 |  | 2026-07-03 17:20 | 68.805 | 69.74 | 1747.3 | 11.6233 | 12.8831 | -1.2597 | 77.2985 | 12.5 | 12.6988 | -0.19885 |  | 2026-07-03 17:20 | 131.0445 | 140.1734 | -9.1289 | 841.0401 | 139.8 | 138.1689 | 1.6311
2026-07-03 17:10 | 353 | 48.22 | 117.508 | 118.997 | 2466.4 | 19.8328 | 21.0657 | -1.2328 | 126.3939 | 21.2 | 20.7644 | 0.43559 |  | 2026-07-03 17:10 | 121.478 | 123.041 | 2490.5 | 20.5068 | 21.0657 | -0.55882 | 126.3939 | 21.4 | 20.7644 | 0.63559 |  | 2026-07-03 17:10 | 118.631 | 120.658 | 2457.6 | 20.1097 | 21.0657 | -0.95598 | 126.3939 | 21.4 | 20.7644 | 0.63559 |  | 2026-07-03 17:10 | 118.825 | 120.353 | 2470.9 | 20.0588 | 21.0657 | -1.0068 | 126.3939 | 21 | 20.7644 | 0.23559 |  | 2026-07-03 17:10 | 88.838 | 89.972 | 1856.9 | 14.9953 | 15.6042 | -0.60885 | 93.6251 | 15.9 | 15.381 | 0.51895 |  | 2026-07-03 17:10 | 86.236 | 87.336 | 1832.4 | 14.556 | 15.6042 | -1.0482 | 93.6251 | 15.5 | 15.381 | 0.11895 |  | 2026-07-03 17:10 | 86.849 | 87.957 | 1832 | 14.6595 | 15.6042 | -0.94469 | 93.6251 | 15.4 | 15.381 | 0.018954 |  | 2026-07-03 17:10 | 85.744 | 88.307 | 1835 | 14.7178 | 15.6042 | -0.88635 | 93.6251 | 15.2 | 15.381 | -0.18105 |  | 2026-07-03 17:10 | 80.695 | 81.766 | 1734.8 | 13.6277 | 14.8454 | -1.2178 | 89.0727 | 14.4 | 14.6332 | -0.23316 |  | 2026-07-03 17:10 | 153.0645 | 161.5248 | -8.4603 | 969.1488 | 161.4 | 159.215 | 2.185
2026-07-03 17:00 | 401 | 48.5 | 136.816 | 138.548 | 2445.2 | 23.0913 | 23.9046 | -0.81324 | 143.4275 | 23.8 | 23.5627 | 0.23726 |  | 2026-07-03 17:00 | 139.984 | 141.08 | 2469.1 | 23.5133 | 23.9046 | -0.39124 | 143.4275 | 23.6 | 23.5627 | 0.03726 |  | 2026-07-03 17:00 | 136.662 | 139.278 | 2436.2 | 23.213 | 23.9046 | -0.69158 | 143.4275 | 23.9 | 23.5627 | 0.33726 |  | 2026-07-03 17:00 | 136.553 | 138.338 | 2449.9 | 23.0563 | 23.9046 | -0.84824 | 143.4275 | 24 | 23.5627 | 0.43726 |  | 2026-07-03 17:00 | 102.543 | 103.873 | 1841 | 17.3122 | 17.7071 | -0.39493 | 106.2426 | 18 | 17.4539 | 0.54612 |  | 2026-07-03 17:00 | 99.425 | 100.684 | 1816.9 | 16.7807 | 17.7071 | -0.92643 | 106.2426 | 17.7 | 17.4539 | 0.24612 |  | 2026-07-03 17:00 | 99.9 | 101.165 | 1816.6 | 16.8608 | 17.7071 | -0.84626 | 106.2426 | 17.7 | 17.4539 | 0.24612 |  | 2026-07-03 17:00 | 98.578 | 101.239 | 1819.8 | 16.8732 | 17.7071 | -0.83393 | 106.2426 | 17.6 | 17.4539 | 0.14612 |  | 2026-07-03 17:00 | 92.945 | 94.117 | 1720.4 | 15.6862 | 16.8461 | -1.1599 | 101.0766 | 16.6 | 16.6052 | -0.0052067 |  | 2026-07-03 17:00 | 176.387 | 183.2928 | -6.9058 | 1099.7567 | 182.9 | 180.6717 | 2.2283
2026-07-03 16:50 | 445 | 48.5 | 152.794 | 153.96 | 2421.4 | 25.66 | 26.5275 | -0.86752 | 159.1651 | 26.9 | 26.1482 | 0.75182 |  | 2026-07-03 16:50 | 154.666 | 156.309 | 2445.5 | 26.0515 | 26.5275 | -0.47602 | 159.1651 | 27.3 | 26.1482 | 1.1518 |  | 2026-07-03 16:50 | 152.592 | 155.55 | 2412.3 | 25.925 | 26.5275 | -0.60252 | 159.1651 | 27 | 26.1482 | 0.85182 |  | 2026-07-03 16:50 | 152.627 | 154.637 | 2425.9 | 25.7728 | 26.5275 | -0.75469 | 159.1651 | 27 | 26.1482 | 0.85182 |  | 2026-07-03 16:50 | 114.644 | 116.142 | 1823 | 19.357 | 19.65 | -0.29302 | 117.9001 | 20.4 | 19.369 | 1.031 |  | 2026-07-03 16:50 | 110.893 | 112.308 | 1799.2 | 18.718 | 19.65 | -0.93202 | 117.9001 | 19.5 | 19.369 | 0.13098 |  | 2026-07-03 16:50 | 111.767 | 113.193 | 1798.9 | 18.8655 | 19.65 | -0.78452 | 117.9001 | 19.5 | 19.369 | 0.13098 |  | 2026-07-03 16:50 | 110.69 | 113.863 | 1802.2 | 18.9772 | 19.65 | -0.67285 | 117.9001 | 19.3 | 19.369 | -0.069021 |  | 2026-07-03 16:50 | 104.48 | 105.835 | 1703.8 | 17.6392 | 18.6946 | -1.0554 | 112.1673 | 18.2 | 18.4272 | -0.22722 |  | 2026-07-03 16:50 | 196.9662 | 203.4047 | -6.4385 | 1220.4282 | 205.1 | 200.496 | 4.604
2026-07-03 16:40 | 493 | 48.5 | 168.641 | 170.897 | 2394.5 | 28.4828 | 29.3889 | -0.90608 | 176.3335 | 29.3 | 28.9687 | 0.33134 |  | 2026-07-03 16:40 | 0 | 174.007 | 2418.2 | 29.0012 | 29.3889 | -0.38775 | 176.3335 | 30.2 | 28.9687 | 1.2313 |  | 2026-07-03 16:40 | 169.49 | 173.002 | 2385.3 | 28.8337 | 29.3889 | -0.55525 | 176.3335 | 29.4 | 28.9687 | 0.43134 |  | 2026-07-03 16:40 | 169.826 | 172.166 | 2398.9 | 28.6943 | 29.3889 | -0.69458 | 176.3335 | 29.6 | 28.9687 | 0.63134 |  | 2026-07-03 16:40 | 127.633 | 129.323 | 1802.6 | 21.5538 | 21.7696 | -0.21573 | 130.6174 | 22.1 | 21.4583 | 0.64174 |  | 2026-07-03 16:40 | 124.359 | 125.971 | 1779.7 | 20.9952 | 21.7696 | -0.7744 | 130.6174 | 21.9 | 21.4583 | 0.44174 |  | 2026-07-03 16:40 | 124.517 | 126.144 | 1779.4 | 21.024 | 21.7696 | -0.74557 | 130.6174 | 22 | 21.4583 | 0.54174 |  | 2026-07-03 16:40 | 123.624 | 126.822 | 1782.9 | 21.137 | 21.7696 | -0.63257 | 130.6174 | 21.8 | 21.4583 | 0.34174 |  | 2026-07-03 16:40 | 116.513 | 118.048 | 1685.6 | 19.6747 | 20.711 | -1.0364 | 124.2663 | 20.6 | 20.4149 | 0.18512 |  | 2026-07-03 16:40 | 219.3967 | 225.345 | -5.9483 | 1352.0699 | 226.9 | 222.1226 | 4.7774
2026-07-03 16:30 | 542 | 48.5 | 185.96 | 188.505 | 2365.2 | 31.4175 | 32.3099 | -0.89243 | 193.8596 | 32.3 | 31.8479 | 0.45211 |  | 2026-07-03 16:30 | 188.72 | 191.361 | 2388 | 31.8935 | 32.3099 | -0.41643 | 193.8596 | 32.4 | 31.8479 | 0.55211 |  | 2026-07-03 16:30 | 185.935 | 190.071 | 2355.9 | 31.6785 | 32.3099 | -0.63143 | 193.8596 | 32.3 | 31.8479 | 0.45211 |  | 2026-07-03 16:30 | 186.575 | 189.264 | 2369.3 | 31.544 | 32.3099 | -0.76593 | 193.8596 | 32.4 | 31.8479 | 0.55211 |  | 2026-07-03 16:30 | 139.988 | 141.846 | 1780.5 | 23.641 | 23.9333 | -0.29228 | 143.5997 | 24.4 | 23.591 | 0.80897 |  | 2026-07-03 16:30 | 136.56 | 138.359 | 1757.8 | 23.0598 | 23.9333 | -0.87344 | 143.5997 | 23.4 | 23.591 | -0.19103 |  | 2026-07-03 16:30 | 136.399 | 138.245 | 1757.4 | 23.0408 | 23.9333 | -0.89244 | 143.5997 | 23.4 | 23.591 | -0.19103 |  | 2026-07-03 16:30 | 135.405 | 138.95 | 1761.1 | 23.1583 | 23.9333 | -0.77494 | 143.5997 | 23.2 | 23.591 | -0.39103 |  | 2026-07-03 16:30 | 127.824 | 129.534 | 1665 | 21.589 | 22.7695 | -1.1805 | 136.6173 | 22.2 | 22.4439 | -0.24395 |  | 2026-07-03 16:30 | 241.0225 | 247.7424 | -6.7199 | 1486.4542 | 246 | 244.1996 | 1.8004
2026-07-03 16:20 | 581 | 48.79 | 199.378 | 202.147 | 2332.9 | 33.6912 | 34.5965 | -0.90534 | 207.579 | 34.9 | 34.1018 | 0.79823 |  | 2026-07-03 16:20 | 202.177 | 205.089 | 2355.6 | 34.1815 | 34.5965 | -0.415 | 207.579 | 34.9 | 34.1018 | 0.79823 |  | 2026-07-03 16:20 | 199.179 | 203.523 | 2323.6 | 33.9205 | 34.5965 | -0.676 | 207.579 | 34.5 | 34.1018 | 0.39823 |  | 2026-07-03 16:20 | 200.569 | 203.417 | 2336.9 | 33.9028 | 34.5965 | -0.69367 | 207.579 | 35.1 | 34.1018 | 0.99823 |  | 2026-07-03 16:20 | 150.261 | 152.302 | 1756.1 | 25.3837 | 25.627 | -0.24337 | 153.7622 | 26 | 25.2606 | 0.73943 |  | 2026-07-03 16:20 | 146.931 | 148.896 | 1734.4 | 24.816 | 25.627 | -0.81104 | 153.7622 | 25.5 | 25.2606 | 0.23943 |  | 2026-07-03 16:20 | 146.49 | 148.465 | 1734 | 24.7442 | 25.627 | -0.88287 | 153.7622 | 25.4 | 25.2606 | 0.13943 |  | 2026-07-03 16:20 | 145.355 | 149.401 | 1737.9 | 24.9002 | 25.627 | -0.72687 | 153.7622 | 25.3 | 25.2606 | 0.039427 |  | 2026-07-03 16:20 | 137.638 | 139.493 | 1642.8 | 23.2488 | 24.381 | -1.1321 | 146.2857 | 23.5 | 24.0323 | -0.53231 |  | 2026-07-03 16:20 | 258.7888 | 265.2751 | -6.4863 | 1591.6508 | 265.1 | 261.4817 | 3.6183
2026-07-03 16:10 | 624 | 48.79 | 212.842 | 215.999 | 2298 | 35.9998 | 37.157 | -1.1572 | 222.942 | 35.8 | 36.6257 | -0.82566 |  | 2026-07-03 16:10 | 217.162 | 219.701 | 2320.7 | 36.6168 | 37.157 | -0.54017 | 222.942 | 36.4 | 36.6257 | -0.22566 |  | 2026-07-03 16:10 | 213.28 | 218.123 | 2289.1 | 36.3538 | 37.157 | -0.80317 | 222.942 | 37 | 36.6257 | 0.37434 |  | 2026-07-03 16:10 | 214.991 | 218.132 | 2301.8 | 36.3553 | 37.157 | -0.80167 | 222.942 | 36.7 | 36.6257 | 0.074342 |  | 2026-07-03 16:10 | 161.019 | 163.223 | 1730.1 | 27.2038 | 27.5237 | -0.31987 | 165.1422 | 27.8 | 27.1301 | 0.66988 |  | 2026-07-03 16:10 | 157.401 | 159.593 | 1708.9 | 26.5988 | 27.5237 | -0.92487 | 165.1422 | 27.2 | 27.1301 | 0.069883 |  | 2026-07-03 16:10 | 157.24 | 159.497 | 1708.6 | 26.5828 | 27.5237 | -0.94087 | 165.1422 | 27.2 | 27.1301 | 0.069883 |  | 2026-07-03 16:10 | 156.233 | 160.874 | 1712.6 | 26.8123 | 27.5237 | -0.71137 | 165.1422 | 27 | 27.1301 | -0.13012 |  | 2026-07-03 16:10 | 147.615 | 149.65 | 1619.3 | 24.9417 | 26.1854 | -1.2437 | 157.1124 | 25.6 | 25.8109 | -0.21095 |  | 2026-07-03 16:10 | 277.4653 | 284.9082 | -7.4429 | 1709.4494 | 280.7 | 280.834 | -0.13404
2026-07-03 16:00 | 667 | 49.08 | 226.741 | 230.054 | 2262.2 | 38.3423 | 39.6735 | -1.3312 | 238.0412 | 39.7 | 39.1062 | 0.5938 |  | 2026-07-03 16:00 | 230.871 | 234.315 | 2284.3 | 39.0525 | 39.6735 | -0.62103 | 238.0412 | 41.1 | 39.1062 | 1.9938 |  | 2026-07-03 16:00 | 228.227 | 233.424 | 2252.1 | 38.904 | 39.6735 | -0.76953 | 238.0412 | 38.7 | 39.1062 | -0.4062 |  | 2026-07-03 16:00 | 229.084 | 232.478 | 2265.1 | 38.7463 | 39.6735 | -0.92719 | 238.0412 | 39.6 | 39.1062 | 0.4938 |  | 2026-07-03 16:00 | 172.15 | 174.541 | 1702.3 | 29.0902 | 29.3878 | -0.29763 | 176.3268 | 29.7 | 28.9676 | 0.73245 |  | 2026-07-03 16:00 | 168.201 | 170.788 | 1681.7 | 28.4647 | 29.3878 | -0.92313 | 176.3268 | 29 | 28.9676 | 0.032448 |  | 2026-07-03 16:00 | 168.239 | 170.882 | 1681.4 | 28.4803 | 29.3878 | -0.90746 | 176.3268 | 29 | 28.9676 | 0.032448 |  | 2026-07-03 16:00 | 167.297 | 171.996 | 1685.6 | 28.666 | 29.3878 | -0.7218 | 176.3268 | 28.9 | 28.9676 | -0.067552 |  | 2026-07-03 16:00 | 157.941 | 160.212 | 1593.7 | 26.702 | 27.9588 | -1.2568 | 167.7531 | 27.3 | 27.559 | -0.25904 |  | 2026-07-03 16:00 | 296.4483 | 304.2041 | -7.7558 | 1825.2249 | 303 | 299.854 | 3.146
2026-07-03 15:50 | 707 | 49.08 | 240.307 | 243.526 | 2222.5 | 40.5877 | 42.0527 | -1.4651 | 252.3165 | 40.6 | 41.4514 | -0.85139 |  | 2026-07-03 15:50 | 244.671 | 248.447 | 2243.2 | 41.4078 | 42.0527 | -0.64492 | 252.3165 | 41.3 | 41.4514 | -0.15139 |  | 2026-07-03 15:50 | 240.435 | 246.314 | 2213.4 | 41.0523 | 42.0527 | -1.0004 | 252.3165 | 41.2 | 41.4514 | -0.25139 |  | 2026-07-03 15:50 | 242.415 | 246.132 | 2225.5 | 41.022 | 42.0527 | -1.0307 | 252.3165 | 40.8 | 41.4514 | -0.65139 |  | 2026-07-03 15:50 | 181.685 | 184.246 | 1672.6 | 30.7077 | 31.1502 | -0.44252 | 186.9011 | 30.7 | 30.7047 | -0.0047365 |  | 2026-07-03 15:50 | 177.742 | 180.588 | 1652.7 | 30.098 | 31.1502 | -1.0522 | 186.9011 | 30.5 | 30.7047 | -0.20474 |  | 2026-07-03 15:50 | 177.575 | 180.355 | 1652.4 | 30.0592 | 31.1502 | -1.091 | 186.9011 | 30.4 | 30.7047 | -0.30474 |  | 2026-07-03 15:50 | 176.607 | 181.567 | 1656.7 | 30.2612 | 31.1502 | -0.88902 | 186.9011 | 30.2 | 30.7047 | -0.50474 |  | 2026-07-03 15:50 | 166.843 | 169.2 | 1566.4 | 28.2 | 29.6355 | -1.4355 | 177.8133 | 28.5 | 29.2118 | -0.71175 |  | 2026-07-03 15:50 | 313.3958 | 322.4473 | -9.0514 | 1934.6836 | 314.2 | 317.8363 | -3.6363
2026-07-03 15:40 | 744 | 48.79 | 252.272 | 256.166 | 2181.9 | 42.6943 | 44.3026 | -1.6082 | 265.8155 | 43.5 | 43.6691 | -0.16905 |  | 2026-07-03 15:40 | 256.968 | 260.011 | 2201.9 | 43.3352 | 44.3026 | -0.96741 | 265.8155 | 43.4 | 43.6691 | -0.26905 |  | 2026-07-03 15:40 | 252.014 | 258.374 | 2172.2 | 43.0623 | 44.3026 | -1.2402 | 265.8155 | 42.8 | 43.6691 | -0.86905 |  | 2026-07-03 15:40 | 253.721 | 257.768 | 2184.7 | 42.9613 | 44.3026 | -1.3412 | 265.8155 | 43.2 | 43.6691 | -0.46905 |  | 2026-07-03 15:40 | 190.115 | 192.857 | 1641.9 | 32.1428 | 32.8167 | -0.67389 | 196.9004 | 32.7 | 32.3474 | 0.35255 |  | 2026-07-03 15:40 | 186.44 | 189.292 | 1622.2 | 31.5487 | 32.8167 | -1.2681 | 196.9004 | 31.6 | 32.3474 | -0.74745 |  | 2026-07-03 15:40 | 186.07 | 188.838 | 1622 | 31.473 | 32.8167 | -1.3437 | 196.9004 | 31.6 | 32.3474 | -0.74745 |  | 2026-07-03 15:40 | 185.479 | 190.712 | 1626.5 | 31.7853 | 32.8167 | -1.0314 | 196.9004 | 31.5 | 32.3474 | -0.84745 |  | 2026-07-03 15:40 | 175.193 | 177.699 | 1537.9 | 29.6165 | 31.2211 | -1.6046 | 187.3263 | 29.8 | 30.7746 | -0.97459 |  | 2026-07-03 15:40 | 328.6195 | 339.6983 | -11.0788 | 2038.1897 | 330.1 | 334.8406 | -4.7406
2026-07-03 15:30 | 776 | 48.79 | 263.543 | 266.964 | 2138.4 | 44.494 | 46.2081 | -1.7141 | 277.2484 | 44.8 | 45.5473 | -0.74729 |  | 2026-07-03 15:30 | 266.348 | 270.624 | 2158.5 | 45.104 | 46.2081 | -1.1041 | 277.2484 | 44.9 | 45.5473 | -0.64729 |  | 2026-07-03 15:30 | 262.587 | 269.553 | 2129.4 | 44.9255 | 46.2081 | -1.2826 | 277.2484 | 44.7 | 45.5473 | -0.84729 |  | 2026-07-03 15:30 | 264.162 | 268.348 | 2141.5 | 44.7247 | 46.2081 | -1.4834 | 277.2484 | 45 | 45.5473 | -0.54729 |  | 2026-07-03 15:30 | 198.687 | 201.59 | 1609.2 | 33.5983 | 34.2282 | -0.62986 | 205.3692 | 34 | 33.7387 | 0.26127 |  | 2026-07-03 15:30 | 194.339 | 197.522 | 1590.6 | 32.9203 | 34.2282 | -1.3079 | 205.3692 | 33.3 | 33.7387 | -0.43873 |  | 2026-07-03 15:30 | 194.435 | 197.819 | 1590.4 | 32.9698 | 34.2282 | -1.2584 | 205.3692 | 33.2 | 33.7387 | -0.53873 |  | 2026-07-03 15:30 | 193.798 | 199.561 | 1595 | 33.2602 | 34.2282 | -0.96803 | 205.3692 | 33.1 | 33.7387 | -0.63873 |  | 2026-07-03 15:30 | 182.964 | 185.637 | 1508.1 | 30.9395 | 32.5639 | -1.6244 | 195.3833 | 31.4 | 32.0982 | -0.69823 |  | 2026-07-03 15:30 | 342.9363 | 354.309 | -11.3726 | 2125.8537 | 344.4 | 349.2423 | -4.8423
2026-07-03 15:20 | 811 | 48.79 | 272.961 | 277.343 | 2093.6 | 46.2238 | 48.2922 | -2.0684 | 289.7532 | 46.1 | 47.6016 | -1.5016 |  | 2026-07-03 15:20 | 277.263 | 281.8 | 2113.6 | 46.9667 | 48.2922 | -1.3255 | 289.7532 | 48.8 | 47.6016 | 1.1984 |  | 2026-07-03 15:20 | 272.496 | 279.891 | 2084.7 | 46.6485 | 48.2922 | -1.6437 | 289.7532 | 46.2 | 47.6016 | -1.4016 |  | 2026-07-03 15:20 | 274.875 | 279.345 | 2096.5 | 46.5575 | 48.2922 | -1.7347 | 289.7532 | 47.1 | 47.6016 | -0.50162 |  | 2026-07-03 15:20 | 206.765 | 209.888 | 1575.2 | 34.9813 | 35.772 | -0.79066 | 214.632 | 34.9 | 35.2605 | -0.36046 |  | 2026-07-03 15:20 | 202.214 | 205.446 | 1557.3 | 34.241 | 35.772 | -1.531 | 214.632 | 34 | 35.2605 | -1.2605 |  | 2026-07-03 15:20 | 202.644 | 206.119 | 1557.2 | 34.3532 | 35.772 | -1.4188 | 214.632 | 34.1 | 35.2605 | -1.1605 |  | 2026-07-03 15:20 | 202.063 | 207.838 | 1561.9 | 34.6397 | 35.772 | -1.1323 | 214.632 | 34.1 | 35.2605 | -1.1605 |  | 2026-07-03 15:20 | 190.961 | 193.771 | 1476.7 | 32.2952 | 34.0326 | -1.7375 | 204.1957 | 32.1 | 33.546 | -1.446 |  | 2026-07-03 15:20 | 356.9068 | 370.2894 | -13.3826 | 2221.7363 | 357.4 | 364.9942 | -7.5942
2026-07-03 15:10 | 843 | 49.36 | 282.97 | 286.733 | 2047.5 | 47.7888 | 50.0884 | -2.2996 | 300.5306 | 47.2 | 49.3722 | -2.1722 |  | 2026-07-03 15:10 | 287.538 | 292.303 | 2064.8 | 48.7172 | 50.0884 | -1.3713 | 300.5306 | 50.2 | 49.3722 | 0.82782 |  | 2026-07-03 15:10 | 282.152 | 289.539 | 2038.5 | 48.2565 | 50.0884 | -1.8319 | 300.5306 | 47.9 | 49.3722 | -1.4722 |  | 2026-07-03 15:10 | 284.394 | 289.106 | 2049.4 | 48.1843 | 50.0884 | -1.9041 | 300.5306 | 47.7 | 49.3722 | -1.6722 |  | 2026-07-03 15:10 | 213.466 | 216.695 | 1540.3 | 36.1158 | 37.1025 | -0.98672 | 222.6153 | 35.7 | 36.572 | -0.87198 |  | 2026-07-03 15:10 | 209.165 | 212.939 | 1523.3 | 35.4898 | 37.1025 | -1.6127 | 222.6153 | 35.7 | 36.572 | -0.87198 |  | 2026-07-03 15:10 | 209.183 | 212.852 | 1523.1 | 35.4753 | 37.1025 | -1.6272 | 222.6153 | 35.6 | 36.572 | -0.97198 |  | 2026-07-03 15:10 | 209.009 | 214.991 | 1527.8 | 35.8318 | 37.1025 | -1.2707 | 222.6153 | 35.5 | 36.572 | -1.072 |  | 2026-07-03 15:10 | 197.259 | 200.234 | 1444.6 | 33.3723 | 35.2985 | -1.9261 | 211.7909 | 33.6 | 34.7937 | -1.1937 |  | 2026-07-03 15:10 | 369.232 | 384.0624 | -14.8304 | 2304.3747 | 369.1 | 378.5703 | -9.4703
2026-07-03 15:00 | 874 | 49.08 | 292.531 | 297.378 | 2000.3 | 49.563 | 51.986 | -2.423 | 311.916 | 50.5 | 51.2426 | -0.7426 | 0.9837 | 2026-07-03 15:00 | 299.321 | 304.312 | 2014.6 | 50.7187 | 51.986 | -1.2673 | 311.916 | 47.2 | 51.2426 | -4.0426 | 0.9836 | 2026-07-03 15:00 | 291.339 | 299.539 | 1990.6 | 49.9232 | 51.986 | -2.0628 | 311.916 | 49.7 | 51.2426 | -1.5426 | 0.97262 | 2026-07-03 15:00 | 294.49 | 299.4 | 2001.7 | 49.9 | 51.986 | -2.086 | 311.916 | 50.1 | 51.2426 | -1.1426 | 0.9836 | 2026-07-03 15:00 | 220.592 | 223.929 | 1504.6 | 37.3215 | 38.5081 | -1.1866 | 231.0489 | 37.6 | 37.9575 | -0.35748 | 0.9851 | 2026-07-03 15:00 | 216.821 | 220.749 | 1487.6 | 36.7915 | 38.5081 | -1.7166 | 231.0489 | 36.3 | 37.9575 | -1.6575 | 0.98221 | 2026-07-03 15:00 | 216.219 | 220.172 | 1487.5 | 36.6953 | 38.5081 | -1.8128 | 231.0489 | 36.3 | 37.9575 | -1.6575 | 0.98205 | 2026-07-03 15:00 | 216.235 | 222.437 | 1492.3 | 37.0728 | 38.5081 | -1.4353 | 231.0489 | 36.3 | 37.9575 | -1.6575 | 0.97212 | 2026-07-03 15:00 | 204.92 | 207.998 | 1411 | 34.6663 | 36.6357 | -1.9694 | 219.8144 | 34.8 | 36.1118 | -1.3118 | 0.9852 | 2026-07-03 15:00 | 382.6523 | 398.6123 | -15.96 | 2391.674 | 378.8 | 392.9122 | -14.1122
2026-07-03 14:50 | 904 | 49.65 | 301.668 | 306.787 | 1949.8 | 51.1312 | 53.6533 | -2.5221 | 321.9196 | 102.7 | 52.886 | 49.814 | 0.98331 | 2026-07-03 14:50 | 306.638 | 311.846 | 1967.4 | 51.9743 | 53.6533 | -1.6789 | 321.9196 | 51 | 52.886 | -1.886 | 0.9833 | 2026-07-03 14:50 | 301.704 | 309.978 | 1940.9 | 51.663 | 53.6533 | -1.9903 | 321.9196 | 51 | 52.886 | -1.886 | 0.97331 | 2026-07-03 14:50 | 303.379 | 308.531 | 1951.6 | 51.4218 | 53.6533 | -2.2314 | 321.9196 | 51.3 | 52.886 | -1.586 | 0.9833 | 2026-07-03 14:50 | 228.487 | 232.037 | 1467 | 38.6728 | 39.7432 | -1.0703 | 238.459 | 38.6 | 39.1748 | -0.57484 | 0.9847 | 2026-07-03 14:50 | 223.958 | 227.894 | 1451.3 | 37.9823 | 39.7432 | -1.7608 | 238.459 | 37.8 | 39.1748 | -1.3748 | 0.98273 | 2026-07-03 14:50 | 223.758 | 227.893 | 1451.2 | 37.9822 | 39.7432 | -1.761 | 238.459 | 37.7 | 39.1748 | -1.4748 | 0.98186 | 2026-07-03 14:50 | 223.5 | 229.984 | 1456 | 38.3307 | 39.7432 | -1.4125 | 238.459 | 37.7 | 39.1748 | -1.4748 | 0.97181 | 2026-07-03 14:50 | 211.285 | 214.503 | 1376.2 | 35.7505 | 37.8107 | -2.0602 | 226.8642 | 35.2 | 37.27 | -2.07 | 0.985 | 2026-07-03 14:50 | 394.9088 | 411.3964 | -16.4876 | 2468.3787 | 443 | 405.5135 | 37.4865
2026-07-03 14:40 | 931 | 49.08 |  |  |  | 0 | 55.3764 | -55.3764 | 332.2583 | 0 | 54.5845 | -54.5845 |  | 2026-07-03 14:40 | 315.176 | 320.118 | 1916.4 | 53.353 | 55.3764 | -2.0234 | 332.2583 | 54.8 | 54.5845 | 0.21549 | 0.98456 | 2026-07-03 14:40 | 309.777 | 318.467 | 1889.9 | 53.0778 | 55.3764 | -2.2986 | 332.2583 | 51.6 | 54.5845 | -2.9845 | 0.97271 | 2026-07-03 14:40 | 311.798 | 317.158 | 1900.3 | 52.8597 | 55.3764 | -2.5167 | 332.2583 | 52 | 54.5845 | -2.5845 | 0.9831 | 2026-07-03 14:40 | 234.557 | 238.249 | 1428.4 | 39.7082 | 41.0195 | -1.3114 | 246.1173 | 39 | 40.433 | -1.433 | 0.9845 | 2026-07-03 14:40 | 229.632 | 234.157 | 1413.5 | 39.0262 | 41.0195 | -1.9934 | 246.1173 | 38.3 | 40.433 | -2.133 | 0.98068 | 2026-07-03 14:40 | 229.822 | 234.29 | 1413.5 | 39.0483 | 41.0195 | -1.9712 | 246.1173 | 38.4 | 40.433 | -2.033 | 0.98093 | 2026-07-03 14:40 | 228.297 | 235.029 | 1418.3 | 39.1715 | 41.0195 | -1.848 | 246.1173 | 38.2 | 40.433 | -2.233 | 0.97136 | 2026-07-03 14:40 | 216.687 | 220.009 | 1341 | 36.6682 | 39.025 | -2.3569 | 234.1501 | 36.1 | 38.467 | -2.367 | 0.9849 | 2026-07-03 14:40 | 352.9128 | 424.6088 | -71.696 | 2547.6527 | 348.4 | 418.5369 | -70.1369
2026-07-03 14:30 | 950 | 49.08 | 314.029 | 319.395 | 1847.1 | 53.2325 | 56.5065 | -3.274 | 339.0391 | 53.8 | 55.6985 | -1.8985 | 0.9832 | 2026-07-03 14:30 | 319.188 | 324.774 | 1861.6 | 54.129 | 56.5065 | -2.3775 | 339.0391 | 51.8 | 55.6985 | -3.8985 | 0.9828 | 2026-07-03 14:30 | 313.279 | 322.1 | 1838.3 | 53.6833 | 56.5065 | -2.8232 | 339.0391 | 53 | 55.6985 | -2.6985 | 0.97261 | 2026-07-03 14:30 | 316.086 | 321.646 | 1848.3 | 53.6077 | 56.5065 | -2.8989 | 339.0391 | 53.6 | 55.6985 | -2.0985 | 0.98271 | 2026-07-03 14:30 | 237.362 | 241.124 | 1389.4 | 40.1873 | 41.8567 | -1.6693 | 251.1401 | 40.2 | 41.2581 | -1.0581 | 0.9844 | 2026-07-03 14:30 | 233.024 | 237.554 | 1375.2 | 39.5923 | 41.8567 | -2.2643 | 251.1401 | 39.5 | 41.2581 | -1.7581 | 0.98093 | 2026-07-03 14:30 | 232.921 | 237.636 | 1375.1 | 39.606 | 41.8567 | -2.2507 | 251.1401 | 39.5 | 41.2581 | -1.7581 | 0.98016 | 2026-07-03 14:30 | 232.901 | 239.778 | 1380.1 | 39.963 | 41.8567 | -1.8937 | 251.1401 | 39.5 | 41.2581 | -1.7581 | 0.97132 | 2026-07-03 14:30 | 220.102 | 223.522 | 1304.9 | 37.2537 | 39.8214 | -2.5678 | 238.9287 | 37.2 | 39.252 | -2.052 | 0.9847 | 2026-07-03 14:30 | 411.2548 | 433.2743 | -22.0194 | 2599.6456 | 408.1 | 427.0784 | -18.9784
2026-07-03 14:20 | 982 | 49.08 | 320.816 | 326.875 | 1793.3 | 54.4792 | 58.4099 | -3.9307 | 350.4594 | 51.6 | 57.5746 | -5.9746 | 0.98146 | 2026-07-03 14:20 | 326.368 | 332.114 | 1809.8 | 55.3523 | 58.4099 | -3.0576 | 350.4594 | 111.3 | 57.5746 | 53.7254 | 0.9827 | 2026-07-03 14:20 | 319.689 | 328.766 | 1785.3 | 54.7943 | 58.4099 | -3.6156 | 350.4594 | 53.4 | 57.5746 | -4.1746 | 0.97239 | 2026-07-03 14:20 | 323.558 | 329.288 | 1794.7 | 54.8813 | 58.4099 | -3.5286 | 350.4594 | 53.9 | 57.5746 | -3.6746 | 0.9826 | 2026-07-03 14:20 | 242.909 | 246.809 | 1349.2 | 41.1348 | 43.2666 | -2.1318 | 259.5996 | 40.6 | 42.6479 | -2.0479 | 0.9842 | 2026-07-03 14:20 | 238.552 | 243.291 | 1335.7 | 40.5485 | 43.2666 | -2.7181 | 259.5996 | 39.8 | 42.6479 | -2.8479 | 0.98052 | 2026-07-03 14:20 | 238.527 | 243.202 | 1335.6 | 40.5337 | 43.2666 | -2.7329 | 259.5996 | 39.8 | 42.6479 | -2.8479 | 0.98078 | 2026-07-03 14:20 | 238.67 | 245.588 | 1340.6 | 40.9313 | 43.2666 | -2.3353 | 259.5996 | 39.8 | 42.6479 | -2.8479 | 0.97183 | 2026-07-03 14:20 | 225.083 | 228.673 | 1267.7 | 38.1122 | 41.1628 | -3.0506 | 246.9768 | 37.6 | 40.5742 | -2.9742 | 0.9843 | 2026-07-03 14:20 | 420.7677 | 447.8688 | -27.1011 | 2687.2126 | 467.8 | 441.4642 | 26.3358
2026-07-03 14:10 | 993 | 48.79 | 326.071 | 331.778 | 1741.7 | 55.2963 | 59.1297 | -3.8333 | 354.7779 | 55.1 | 58.2841 | -3.1841 | 0.9828 |  |  |  |  | 0 | 59.1297 | -59.1297 | 354.7779 | 0 | 58.2841 | -58.2841 |  | 2026-07-03 14:10 | 323.821 | 333.092 | 1731.9 | 55.5153 | 59.1297 | -3.6143 | 354.7779 | 55 | 58.2841 | -3.2841 | 0.97217 | 2026-07-03 14:10 | 326.871 | 332.693 | 1740.8 | 55.4488 | 59.1297 | -3.6808 | 354.7779 | 54.7 | 58.2841 | -3.5841 | 0.9825 | 2026-07-03 14:10 | 245.439 | 249.43 | 1308.6 | 41.5717 | 43.7997 | -2.2281 | 262.7985 | 41 | 43.1734 | -2.1734 | 0.984 | 2026-07-03 14:10 | 240.777 | 245.91 | 1295.9 | 40.985 | 43.7997 | -2.8147 | 262.7985 | 40.3 | 43.1734 | -2.8734 | 0.97913 | 2026-07-03 14:10 | 241.265 | 245.958 | 1295.8 | 40.993 | 43.7997 | -2.8067 | 262.7985 | 41 | 43.1734 | -2.1734 | 0.98092 | 2026-07-03 14:10 | 241.211 | 248.254 | 1300.8 | 41.3757 | 43.7997 | -2.4241 | 262.7985 | 41 | 43.1734 | -2.1734 | 0.97163 | 2026-07-03 14:10 | 227.504 | 231.18 | 1230.1 | 38.53 | 41.67 | -3.14 | 250.0202 | 38.7 | 41.0741 | -2.3741 | 0.9841 | 2026-07-03 14:10 | 369.7158 | 453.3876 | -83.6718 | 2720.3257 | 366.8 | 446.9042 | -80.1042
2026-07-03 14:00 | 1013 | 49.08 | 329.303 | 335.064 | 1686.6 | 55.844 | 60.2538 | -4.4098 | 361.5228 | 55.8 | 59.3922 | -3.5922 | 0.98281 | 2026-07-03 14:00 | 335.469 | 341.479 | 1698.5 | 56.9132 | 60.2538 | -3.3406 | 361.5228 | 55.1 | 59.3922 | -4.2922 | 0.9824 | 2026-07-03 14:00 | 328.468 | 338.003 | 1676.9 | 56.3338 | 60.2538 | -3.92 | 361.5228 | 54 | 59.3922 | -5.3922 | 0.97179 | 2026-07-03 14:00 | 331.48 | 337.453 | 1686.1 | 56.2422 | 60.2538 | -4.0116 | 361.5228 | 56 | 59.3922 | -3.3922 | 0.9823 | 2026-07-03 14:00 | 248.917 | 253.016 | 1267.6 | 42.1693 | 44.6324 | -2.4631 | 267.7947 | 42.1 | 43.9942 | -1.8942 | 0.9838 | 2026-07-03 14:00 | 244.294 | 249.335 | 1255.6 | 41.5558 | 44.6324 | -3.0766 | 267.7947 | 41.3 | 43.9942 | -2.6942 | 0.97978 | 2026-07-03 14:00 | 244.647 | 249.556 | 1254.8 | 41.5927 | 44.6324 | -3.0398 | 267.7947 | 40.7 | 43.9942 | -3.2942 | 0.98033 | 2026-07-03 14:00 | 244.596 | 251.745 | 1259.8 | 41.9575 | 44.6324 | -2.6749 | 267.7947 | 40.8 | 43.9942 | -3.1942 | 0.9716 | 2026-07-03 14:00 | 231.254 | 234.99 | 1191.4 | 39.165 | 42.4622 | -3.2972 | 254.7734 | 38.5 | 41.855 | -3.355 | 0.9841 | 2026-07-03 14:00 | 431.7735 | 462.0072 | -30.2337 | 2772.0432 | 424.3 | 455.4005 | -31.1005
2026-07-03 13:50 | 1021 | 49.08 | 332.651 | 338.542 | 1630.8 | 56.4237 | 60.7296 | -4.306 | 364.3778 | 55.5 | 59.8612 | -4.3612 | 0.9826 | 2026-07-03 13:50 | 338.149 | 344.312 | 1643.4 | 57.3853 | 60.7296 | -3.3443 | 364.3778 | 57.7 | 59.8612 | -2.1612 | 0.9821 | 2026-07-03 13:50 | 331.245 | 341.158 | 1622.9 | 56.8597 | 60.7296 | -3.87 | 364.3778 | 56.3 | 59.8612 | -3.5612 | 0.97094 | 2026-07-03 13:50 | 332.188 | 337.933 | 1630.1 | 56.3222 | 60.7296 | -4.4075 | 364.3778 | 55.7 | 59.8612 | -4.1612 | 0.983 | 2026-07-03 13:50 | 251.191 | 255.353 | 1225.5 | 42.5588 | 44.9849 | -2.4261 | 269.9095 | 42.1 | 44.3416 | -2.2416 | 0.9837 | 2026-07-03 13:50 | 246.889 | 251.841 | 1214.3 | 41.9735 | 44.9849 | -3.0114 | 269.9095 | 41.4 | 44.3416 | -2.9416 | 0.98034 | 2026-07-03 13:50 | 246.97 | 251.943 | 1214.1 | 41.9905 | 44.9849 | -2.9944 | 269.9095 | 41.3 | 44.3416 | -3.0416 | 0.98026 | 2026-07-03 13:50 | 247.12 | 254.581 | 1219 | 42.4302 | 44.9849 | -2.5548 | 269.9095 | 41.3 | 44.3416 | -3.0416 | 0.97069 | 2026-07-03 13:50 | 233.387 | 237.23 | 1152.9 | 39.5383 | 42.7976 | -3.2592 | 256.7855 | 39.6 | 42.1856 | -2.5856 | 0.9838 | 2026-07-03 13:50 | 435.4822 | 465.6558 | -30.1737 | 2793.9349 | 430.9 | 458.9969 | -28.0969
2026-07-03 13:40 | 1043 | 48.79 | 337.037 | 343.11 | 1575.3 | 57.185 | 62.107 | -4.922 | 372.6419 | 56.6 | 61.2188 | -4.6188 | 0.9823 | 2026-07-03 13:40 | 332.792 | 338.375 | 1585.7 | 56.3958 | 62.107 | -5.7111 | 372.6419 | 55.1 | 61.2188 | -6.1188 | 0.9835 | 2026-07-03 13:40 | 336.748 | 346.732 | 1566.6 | 57.7887 | 62.107 | -4.3183 | 372.6419 | 55.6 | 61.2188 | -5.6188 | 0.97121 | 2026-07-03 13:40 | 334.667 | 340.351 | 1574.4 | 56.7252 | 62.107 | -5.3818 | 372.6419 | 55.8 | 61.2188 | -5.4188 | 0.9833 | 2026-07-03 13:40 | 255.624 | 259.886 | 1183.4 | 43.3143 | 46.0052 | -2.6908 | 276.031 | 42.2 | 45.3473 | -3.1473 | 0.9836 | 2026-07-03 13:40 | 251 | 255.941 | 1172.9 | 42.6568 | 46.0052 | -3.3483 | 276.031 | 42.1 | 45.3473 | -3.2473 | 0.98069 | 2026-07-03 13:40 | 251.173 | 256.305 | 1172.8 | 42.7175 | 46.0052 | -3.2877 | 276.031 | 42.1 | 45.3473 | -3.2473 | 0.97998 | 2026-07-03 13:40 | 250.69 | 258.009 | 1177.7 | 43.0015 | 46.0052 | -3.0037 | 276.031 | 42.1 | 45.3473 | -3.2473 | 0.97163 | 2026-07-03 13:40 | 236.806 | 240.73 | 1113.3 | 40.1217 | 43.7682 | -3.6466 | 262.6093 | 39.3 | 43.1423 | -3.8423 | 0.9837 | 2026-07-03 13:40 | 439.9065 | 476.2168 | -36.3103 | 2857.3008 | 430.9 | 469.4069 | -38.5069
2026-07-03 13:30 | 1053 | 48.79 | 341.075 | 347.221 | 1518.7 | 57.8702 | 62.7024 | -4.8323 | 376.2147 | 55.6 | 61.8058 | -6.2058 | 0.9823 | 2026-07-03 13:30 | 339.159 | 344.954 | 1530.6 | 57.4923 | 62.7024 | -5.2101 | 376.2147 | 55.7 | 61.8058 | -6.1058 | 0.9832 | 2026-07-03 13:30 | 340.417 | 350.551 | 1511 | 58.4252 | 62.7024 | -4.2773 | 376.2147 | 55.9 | 61.8058 | -5.9058 | 0.97109 | 2026-07-03 13:30 | 338.074 | 343.851 | 1518.6 | 57.3085 | 62.7024 | -5.3939 | 376.2147 | 56.6 | 61.8058 | -5.2058 | 0.9832 | 2026-07-03 13:30 | 257.949 | 262.25 | 1141.2 | 43.7083 | 46.4463 | -2.7379 | 278.6775 | 43.5 | 45.7821 | -2.2821 | 0.9836 | 2026-07-03 13:30 | 253.784 | 258.838 | 1130.8 | 43.1397 | 46.4463 | -3.3066 | 278.6775 | 42.3 | 45.7821 | -3.4821 | 0.98047 | 2026-07-03 13:30 | 253.239 | 258.407 | 1130.7 | 43.0678 | 46.4463 | -3.3784 | 278.6775 | 42.2 | 45.7821 | -3.5821 | 0.98 | 2026-07-03 13:30 | 254.029 | 261.548 | 1135.6 | 43.5913 | 46.4463 | -2.8549 | 278.6775 | 42.4 | 45.7821 | -3.3821 | 0.97125 | 2026-07-03 13:30 | 240.521 | 244.432 | 1074 | 40.7387 | 44.1879 | -3.4492 | 265.1271 | 40 | 43.556 | -3.556 | 0.984 | 2026-07-03 13:30 | 445.342 | 480.7826 | -35.4406 | 2884.6958 | 434.2 | 473.9074 | -39.7074
2026-07-03 13:20 | 1059 | 48.5 | 331.973 | 338.987 | 1463.1 | 56.4978 | 63.1295 | -6.6317 | 378.7772 | 60.3 | 62.2268 | -1.9268 | 0.97931 | 2026-07-03 13:20 | 340.671 | 346.15 | 1474.9 | 57.6917 | 63.1295 | -5.4379 | 378.7772 | 56.4 | 62.2268 | -5.8268 | 0.98417 | 2026-07-03 13:20 | 341.466 | 351.856 | 1455.1 | 58.6427 | 63.1295 | -4.4869 | 378.7772 | 57.1 | 62.2268 | -5.1268 | 0.97047 | 2026-07-03 13:20 | 331.946 | 337.412 | 1462 | 56.2353 | 63.1295 | -6.8942 | 378.7772 | 55.8 | 62.2268 | -6.4268 | 0.9838 | 2026-07-03 13:20 | 258.059 | 262.362 | 1097.7 | 43.727 | 46.7626 | -3.0356 | 280.5757 | 43.2 | 46.0939 | -2.8939 | 0.9836 | 2026-07-03 13:20 | 254.611 | 259.843 | 1088.5 | 43.3072 | 46.7626 | -3.4555 | 280.5757 | 42.6 | 46.0939 | -3.4939 | 0.97986 | 2026-07-03 13:20 | 253.986 | 259.446 | 1088.5 | 43.241 | 46.7626 | -3.5216 | 280.5757 | 42.5 | 46.0939 | -3.5939 | 0.97896 | 2026-07-03 13:20 | 254.652 | 262.424 | 1093.2 | 43.7373 | 46.7626 | -3.0253 | 280.5757 | 42.7 | 46.0939 | -3.3939 | 0.97038 | 2026-07-03 13:20 | 240.939 | 244.882 | 1034 | 40.8137 | 44.4888 | -3.6752 | 266.9331 | 40.4 | 43.8527 | -3.4527 | 0.9839 | 2026-07-03 13:20 | 443.8937 | 484.0575 | -40.1638 | 2904.345 | 441 | 477.1355 | -36.1355
2026-07-03 13:10 | 1069 | 48.5 | 335.425 | 344.162 | 1402.8 | 57.3603 | 63.7257 | -6.3653 | 382.354 | 53.8 | 62.8144 | -9.0144 | 0.97461 | 2026-07-03 13:10 | 332.042 | 337.373 | 1418.5 | 56.2288 | 63.7257 | -7.4968 | 382.354 | 60.1 | 62.8144 | -2.7144 | 0.9842 | 2026-07-03 13:10 | 333.99 | 343.806 | 1398 | 57.301 | 63.7257 | -6.4247 | 382.354 | 57.1 | 62.8144 | -5.7144 | 0.97145 | 2026-07-03 13:10 | 328.761 | 334.005 | 1406.2 | 55.6675 | 63.7257 | -8.0582 | 382.354 | 55.9 | 62.8144 | -6.9144 | 0.9843 | 2026-07-03 13:10 | 261.781 | 266.146 | 1054.5 | 44.3577 | 47.2042 | -2.8465 | 283.2252 | 43.6 | 46.5292 | -2.9292 | 0.9836 | 2026-07-03 13:10 | 257.537 | 263.019 | 1045.9 | 43.8365 | 47.2042 | -3.3677 | 283.2252 | 42.9 | 46.5292 | -3.6292 | 0.97916 | 2026-07-03 13:10 | 257.974 | 263.281 | 1046 | 43.8802 | 47.2042 | -3.324 | 283.2252 | 43.1 | 46.5292 | -3.4292 | 0.97984 | 2026-07-03 13:10 | 258.902 | 266.755 | 1050.5 | 44.4592 | 47.2042 | -2.745 | 283.2252 | 43.3 | 46.5292 | -3.2292 | 0.97056 | 2026-07-03 13:10 | 244.112 | 248.132 | 993.6 | 41.3553 | 44.9089 | -3.5536 | 269.4537 | 40.7 | 44.2667 | -3.5667 | 0.9838 | 2026-07-03 13:10 | 444.4465 | 488.6284 | -44.1819 | 2931.7703 | 440.5 | 481.641 | -41.141
2026-07-03 13:00 | 1075 | 48.5 | 342.246 | 351.475 | 1349 | 58.5792 | 64.0833 | -5.5042 | 384.5 | 57.1 | 63.1669 | -6.0669 | 0.97374 | 2026-07-03 13:00 | 347.737 | 353.679 | 1358.4 | 58.9465 | 64.0833 | -5.1368 | 384.5 | 53.9 | 63.1669 | -9.2669 | 0.9832 | 2026-07-03 13:00 | 347.161 | 357.448 | 1340.9 | 59.5747 | 64.0833 | -4.5087 | 384.5 | 57.3 | 63.1669 | -5.8669 | 0.97122 | 2026-07-03 13:00 | 338.407 | 344.014 | 1350.3 | 57.3357 | 64.0833 | -6.7477 | 384.5 | 56.3 | 63.1669 | -6.8669 | 0.9837 | 2026-07-03 13:00 | 262.627 | 267.006 | 1010.9 | 44.501 | 47.4691 | -2.9681 | 284.8148 | 43.8 | 46.7903 | -2.9903 | 0.9836 | 2026-07-03 13:00 | 258.542 | 263.878 | 1003 | 43.9797 | 47.4691 | -3.4895 | 284.8148 | 43.1 | 46.7903 | -3.6903 | 0.97978 | 2026-07-03 13:00 | 258.879 | 264.437 | 1002.9 | 44.0728 | 47.4691 | -3.3963 | 284.8148 | 43.1 | 46.7903 | -3.6903 | 0.97898 | 2026-07-03 13:00 | 259.714 | 267.302 | 1007.2 | 44.5503 | 47.4691 | -2.9188 | 284.8148 | 43.2 | 46.7903 | -3.5903 | 0.97161 | 2026-07-03 13:00 | 244.904 | 248.911 | 952.9 | 41.4852 | 45.161 | -3.6758 | 270.966 | 41.5 | 44.5152 | -3.0152 | 0.9839 | 2026-07-03 13:00 | 453.025 | 491.3709 | -38.3459 | 2948.2255 | 439.3 | 484.3443 | -45.0443
2026-07-03 12:50 | 1074 | 48.5 | 340.552 | 346.16 | 1291.9 | 57.6933 | 64.0237 | -6.3304 | 384.1424 | 56.7 | 63.1082 | -6.4082 | 0.9838 | 2026-07-03 12:50 | 0 | 353.222 | 1304.5 | 58.8703 | 64.0237 | -5.1534 | 384.1424 | 56.5 | 63.1082 | -6.6082 |  | 2026-07-03 12:50 | 345.317 | 355.464 | 1283.6 | 59.244 | 64.0237 | -4.7797 | 384.1424 | 56.5 | 63.1082 | -6.6082 | 0.97145 | 2026-07-03 12:50 | 330.825 | 336.136 | 1294 | 56.0227 | 64.0237 | -8.0011 | 384.1424 | 56 | 63.1082 | -7.1082 | 0.9842 | 2026-07-03 12:50 | 262.755 | 267.136 | 967.1 | 44.5227 | 47.425 | -2.9023 | 284.5499 | 43.8 | 46.7468 | -2.9468 | 0.9836 | 2026-07-03 12:50 | 258.514 | 263.569 | 959.9 | 43.9282 | 47.425 | -3.4968 | 284.5499 | 43.1 | 46.7468 | -3.6468 | 0.98082 | 2026-07-03 12:50 | 258.818 | 264.428 | 959.8 | 44.0713 | 47.425 | -3.3536 | 284.5499 | 43.2 | 46.7468 | -3.5468 | 0.97878 | 2026-07-03 12:50 | 259.446 | 267.583 | 964 | 44.5972 | 47.425 | -2.8278 | 284.5499 | 43.3 | 46.7468 | -3.4468 | 0.96959 | 2026-07-03 12:50 | 244.818 | 248.875 | 911.4 | 41.4792 | 45.119 | -3.6398 | 270.714 | 40.3 | 44.4738 | -4.1738 | 0.9837 | 2026-07-03 12:50 | 450.4288 | 490.9138 | -40.485 | 2945.483 | 439.4 | 483.8938 | -44.4938
2026-07-03 12:40 | 1069 | 48.79 | 343.065 | 348.927 | 1235.2 | 58.1545 | 63.6552 | -5.5007 | 381.9311 | 56.6 | 62.7449 | -6.1449 | 0.9832 | 2026-07-03 12:40 | 340.113 | 345.678 | 1248 | 57.613 | 63.6552 | -6.0422 | 381.9311 | 58.8 | 62.7449 | -3.9449 | 0.9839 | 2026-07-03 12:40 | 338.092 | 345.137 | 1227.1 | 57.5228 | 63.6552 | -6.1324 | 381.9311 | 56.6 | 62.7449 | -6.1449 | 0.97959 | 2026-07-03 12:40 | 340.808 | 346.455 | 1238 | 57.7425 | 63.6552 | -5.9127 | 381.9311 | 56.5 | 62.7449 | -6.2449 | 0.9837 | 2026-07-03 12:40 | 263.321 | 267.684 | 923.3 | 44.614 | 47.152 | -2.538 | 282.9119 | 43.8 | 46.4777 | -2.6777 | 0.9837 | 2026-07-03 12:40 | 258.918 | 263.999 | 916.8 | 43.9998 | 47.152 | -3.1522 | 282.9119 | 43.3 | 46.4777 | -3.1777 | 0.98075 | 2026-07-03 12:40 | 259.428 | 264.699 | 916.6 | 44.1165 | 47.152 | -3.0355 | 282.9119 | 43.2 | 46.4777 | -3.2777 | 0.98009 | 2026-07-03 12:40 | 259.809 | 267.709 | 920.7 | 44.6182 | 47.152 | -2.5338 | 282.9119 | 43.3 | 46.4777 | -3.1777 | 0.97049 | 2026-07-03 12:40 | 245.429 | 249.47 | 871.1 | 41.5783 | 44.8593 | -3.2809 | 269.1557 | 40.9 | 44.2178 | -3.3178 | 0.9838 | 2026-07-03 12:40 | 449.9597 | 488.088 | -38.1283 | 2928.5279 | 443 | 481.1083 | -38.1083
2026-07-03 12:30 | 1072 | 48.79 | 341.088 | 346.74 | 1178.6 | 57.79 | 63.8338 | -6.0438 | 383.003 | 57.5 | 62.921 | -5.421 | 0.9837 | 2026-07-03 12:30 | 346.378 | 352.118 | 1189.2 | 58.6863 | 63.8338 | -5.1475 | 383.003 | 60.9 | 62.921 | -2.021 | 0.9837 | 2026-07-03 12:30 | 338.045 | 348.179 | 1170.5 | 58.0298 | 63.8338 | -5.804 | 383.003 | 57.3 | 62.921 | -5.621 | 0.97089 | 2026-07-03 12:30 | 333.582 | 338.972 | 1181.5 | 56.4953 | 63.8338 | -7.3385 | 383.003 | 57.9 | 62.921 | -5.021 | 0.9841 | 2026-07-03 12:30 | 262.96 | 267.317 | 879.5 | 44.5528 | 47.2843 | -2.7315 | 283.7059 | 43.5 | 46.6081 | -3.1081 | 0.9837 | 2026-07-03 12:30 | 259.269 | 264.582 | 873.5 | 44.097 | 47.2843 | -3.1873 | 283.7059 | 42.7 | 46.6081 | -3.9081 | 0.97992 | 2026-07-03 12:30 | 259.071 | 264.655 | 873.4 | 44.1092 | 47.2843 | -3.1751 | 283.7059 | 43.5 | 46.6081 | -3.1081 | 0.9789 | 2026-07-03 12:30 | 259.245 | 267.485 | 877.4 | 44.5808 | 47.2843 | -2.7035 | 283.7059 | 43.5 | 46.6081 | -3.1081 | 0.96919 | 2026-07-03 12:30 | 245.295 | 249.334 | 830.2 | 41.5557 | 44.9852 | -3.4295 | 269.911 | 41.1 | 44.3419 | -3.2419 | 0.9838 | 2026-07-03 12:30 | 449.897 | 489.4577 | -39.5607 | 2936.7464 | 447.9 | 482.4585 | -34.5585
2026-07-03 12:20 | 1060 | 49.08 | 348.305 | 354.162 | 1121.1 | 59.027 | 63.0494 | -4.0224 | 378.2963 | 58.5 | 62.1478 | -3.6478 | 0.98346 | 2026-07-03 12:20 | 348.733 | 348.049 | 1128.3 | 58.0082 | 63.0494 | -5.0412 | 378.2963 | 54.1 | 62.1478 | -8.0478 | 1.002 | 2026-07-03 12:20 | 345.426 | 355.438 | 1113.2 | 59.2397 | 63.0494 | -3.8097 | 378.2963 | 57.1 | 62.1478 | -5.0478 | 0.97183 | 2026-07-03 12:20 | 348.278 | 354.698 | 1123.6 | 59.1163 | 63.0494 | -3.933 | 378.2963 | 56.7 | 62.1478 | -5.4478 | 0.9819 | 2026-07-03 12:20 | 261.449 | 265.754 | 836 | 44.2923 | 46.7032 | -2.4109 | 280.2195 | 43.7 | 46.0354 | -2.3354 | 0.9838 | 2026-07-03 12:20 | 256.937 | 262.089 | 830.8 | 43.6815 | 46.7032 | -3.0217 | 280.2195 | 43.2 | 46.0354 | -2.8354 | 0.98034 | 2026-07-03 12:20 | 258.178 | 263.433 | 829.9 | 43.9055 | 46.7032 | -2.7977 | 280.2195 | 42.6 | 46.0354 | -3.4354 | 0.98005 | 2026-07-03 12:20 | 258.414 | 266.206 | 833.9 | 44.3677 | 46.7032 | -2.3356 | 280.2195 | 42.7 | 46.0354 | -3.3354 | 0.97073 | 2026-07-03 12:20 | 244.176 | 248.172 | 789.1 | 41.362 | 44.4324 | -3.0704 | 266.5941 | 40.4 | 43.797 | -3.397 | 0.9839 | 2026-07-03 12:20 | 453.0002 | 483.4429 | -30.4427 | 2900.6572 | 439 | 476.5296 | -37.5296
2026-07-03 12:10 | 1055 | 49.08 | 345.931 | 352.116 | 1062.6 | 58.686 | 62.752 | -4.066 | 376.5119 | 58.6 | 61.8546 | -3.2546 | 0.98243 | 2026-07-03 12:10 | 346.102 | 351.944 | 1074.2 | 58.6573 | 62.752 | -4.0946 | 376.5119 | 61.1 | 61.8546 | -0.75463 | 0.9834 | 2026-07-03 12:10 | 343.095 | 353.233 | 1056.1 | 58.8722 | 62.752 | -3.8798 | 376.5119 | 57.5 | 61.8546 | -4.3546 | 0.9713 | 2026-07-03 12:10 | 347.323 | 353.581 | 1066.9 | 58.9302 | 62.752 | -3.8218 | 376.5119 | 58 | 61.8546 | -3.8546 | 0.9823 | 2026-07-03 12:10 | 259.382 | 263.687 | 792.3 | 43.9478 | 46.4829 | -2.5351 | 278.8977 | 42.9 | 45.8182 | -2.9182 | 0.98367 | 2026-07-03 12:10 | 255.872 | 261.193 | 787.6 | 43.5322 | 46.4829 | -2.9508 | 278.8977 | 42.2 | 45.8182 | -3.6182 | 0.97963 | 2026-07-03 12:10 | 256.06 | 261.689 | 787.3 | 43.6148 | 46.4829 | -2.8681 | 278.8977 | 42.2 | 45.8182 | -3.6182 | 0.97849 | 2026-07-03 12:10 | 257.057 | 264.772 | 791.2 | 44.1287 | 46.4829 | -2.3543 | 278.8977 | 43 | 45.8182 | -2.8182 | 0.97086 | 2026-07-03 12:10 | 242.229 | 246.168 | 748.7 | 41.028 | 44.2228 | -3.1948 | 265.3366 | 40.5 | 43.5904 | -3.0904 | 0.984 | 2026-07-03 12:10 | 451.3972 | 481.1625 | -29.7653 | 2886.9749 | 446 | 474.2819 | -28.2819
2026-07-03 12:00 | 1047 | 49.36 | 343.484 | 349.531 | 1004 | 58.2552 | 62.2095 | -3.9543 | 373.2569 | 55.7 | 61.3199 | -5.6199 | 0.9827 | 2026-07-03 12:00 | 348.435 | 354.677 | 1013.1 | 59.1128 | 62.2095 | -3.0967 | 373.2569 | 58.2 | 61.3199 | -3.1199 | 0.9824 | 2026-07-03 12:00 | 342.01 | 351.826 | 998.6 | 58.6377 | 62.2095 | -3.5718 | 373.2569 | 56.1 | 61.3199 | -5.2199 | 0.9721 | 2026-07-03 12:00 | 344.69 | 350.901 | 1008.9 | 58.4835 | 62.2095 | -3.726 | 373.2569 | 56.7 | 61.3199 | -4.6199 | 0.9823 | 2026-07-03 12:00 | 257.989 | 262.237 | 749.4 | 43.7062 | 46.0811 | -2.3749 | 276.4866 | 42.2 | 45.4221 | -3.2221 | 0.9838 | 2026-07-03 12:00 | 253.821 | 258.56 | 745.4 | 43.0933 | 46.0811 | -2.9878 | 276.4866 | 42.5 | 45.4221 | -2.9221 | 0.98167 | 2026-07-03 12:00 | 253.926 | 258.932 | 745.1 | 43.1553 | 46.0811 | -2.9258 | 276.4866 | 42.3 | 45.4221 | -3.1221 | 0.98067 | 2026-07-03 12:00 | 254.512 | 262.237 | 748.2 | 43.7062 | 46.0811 | -2.3749 | 276.4866 | 41.8 | 45.4221 | -3.6221 | 0.97054 | 2026-07-03 12:00 | 240.349 | 244.282 | 708.2 | 40.7137 | 43.8405 | -3.1268 | 263.0428 | 39.6 | 43.2135 | -3.6135 | 0.9839 | 2026-07-03 12:00 | 448.8638 | 477.0028 | -28.139 | 2862.0169 | 435.1 | 470.1817 | -35.0817
2026-07-03 11:50 | 1033 | 49.36 | 338.611 | 344.642 | 948.3 | 57.4403 | 61.3777 | -3.9373 | 368.2659 | 56.8 | 60.5 | -3.7 | 0.9825 | 2026-07-03 11:50 | 345.286 | 351.508 | 954.9 | 58.5847 | 61.3777 | -2.793 | 368.2659 | 54.5 | 60.5 | -6 | 0.9823 | 2026-07-03 11:50 | 336.65 | 346.337 | 942.5 | 57.7228 | 61.3777 | -3.6548 | 368.2659 | 55.9 | 60.5 | -4.6 | 0.97203 | 2026-07-03 11:50 | 340.435 | 346.569 | 952.2 | 57.7615 | 61.3777 | -3.6162 | 368.2659 | 56.3 | 60.5 | -4.2 | 0.9823 | 2026-07-03 11:50 | 253.844 | 258.024 | 707.2 | 43.004 | 45.4649 | -2.4609 | 272.7896 | 42.2 | 44.8148 | -2.6148 | 0.9838 | 2026-07-03 11:50 | 251.563 | 256.253 | 702.9 | 42.7088 | 45.4649 | -2.7561 | 272.7896 | 41.5 | 44.8148 | -3.3148 | 0.9817 | 2026-07-03 11:50 | 250.715 | 255.724 | 702.8 | 42.6207 | 45.4649 | -2.8443 | 272.7896 | 41.5 | 44.8148 | -3.3148 | 0.98041 | 2026-07-03 11:50 | 251.633 | 259.12 | 706.4 | 43.1867 | 45.4649 | -2.2783 | 272.7896 | 41.6 | 44.8148 | -3.2148 | 0.97111 | 2026-07-03 11:50 | 238.559 | 242.371 | 668.6 | 40.3952 | 43.2542 | -2.8591 | 259.5255 | 39.4 | 42.6357 | -3.2357 | 0.98427 | 2026-07-03 11:50 | 443.4247 | 470.6246 | -27.1999 | 2823.7474 | 429.7 | 463.8946 | -34.1946
Average of B45 and B47 | 1017.5 | 49.36 | 332.561 | 338.372 | 891.5 | 56.3953 | 60.4567 | -4.0614 | 362.7401 | 53.5 | 59.5922 | -6.0922 | 0.98283 | 2026-07-03 11:40 | 338.773 | 344.861 | 900.4 | 57.4768 | 60.4567 | -2.9799 | 362.7401 | 56 | 59.5922 | -3.5922 | 0.98235 | 2026-07-03 11:40 | 332.269 | 342.116 | 886.6 | 57.0193 | 60.4567 | -3.4374 | 362.7401 | 55.5 | 59.5922 | -4.0922 | 0.97122 | 2026-07-03 11:40 | 334.175 | 340.196 | 895.9 | 56.6993 | 60.4567 | -3.7574 | 362.7401 | 56.1 | 59.5922 | -3.4922 | 0.9823 | 2026-07-03 11:40 | 250.693 | 254.743 | 665 | 42.4572 | 44.7827 | -2.3256 | 268.6964 | 41.9 | 44.1423 | -2.2423 | 0.9841 | 2026-07-03 11:40 | 247.244 | 251.772 | 661.4 | 41.962 | 44.7827 | -2.8207 | 268.6964 | 41 | 44.1423 | -3.1423 | 0.98202 | 2026-07-03 11:40 | 247.091 | 251.814 | 661.3 | 41.969 | 44.7827 | -2.8137 | 268.6964 | 40.8 | 44.1423 | -3.3423 | 0.98124 | 2026-07-03 11:40 | 247.719 | 255.191 | 664.8 | 42.5318 | 44.7827 | -2.2509 | 268.6964 | 41 | 44.1423 | -3.1423 | 0.97072 | 2026-07-03 11:40 | 234.98 | 238.752 | 629.2 | 39.792 | 42.6052 | -2.8132 | 255.6313 | 38.9 | 41.996 | -3.096 | 0.9842 | Average of B45 and B47 | 436.3028 | 463.5629 | -27.2601 | 2781.3775 | 424.7 | 456.934 | -32.234
2026-07-03 11:30 | 1002 | 49.36 | 330.529 | 336.279 | 838 | 56.0465 | 59.5357 | -3.4892 | 357.2144 | 54.7 | 58.6844 | -3.9844 | 0.9829 | 2026-07-03 11:30 | 334.525 | 341.565 | 844.4 | 56.9275 | 59.5357 | -2.6082 | 357.2144 | 55.4 | 58.6844 | -3.2844 | 0.97939 | 2026-07-03 11:30 | 329.114 | 338.368 | 831.1 | 56.3947 | 59.5357 | -3.1411 | 357.2144 | 53.6 | 58.6844 | -5.0844 | 0.97265 | 2026-07-03 11:30 | 332.505 | 338.428 | 839.8 | 56.4047 | 59.5357 | -3.1311 | 357.2144 | 54.9 | 58.6844 | -3.7844 | 0.9825 | 2026-07-03 11:30 | 248.882 | 252.877 | 623.1 | 42.1462 | 44.1005 | -1.9544 | 264.6032 | 41.2 | 43.4699 | -2.2699 | 0.9842 | 2026-07-03 11:30 | 246.065 | 250.589 | 620.4 | 41.7648 | 44.1005 | -2.3357 | 264.6032 | 40.6 | 43.4699 | -2.8699 | 0.98195 | 2026-07-03 11:30 | 245.917 | 250.496 | 620.5 | 41.7493 | 44.1005 | -2.3512 | 264.6032 | 40.7 | 43.4699 | -2.7699 | 0.98172 | 2026-07-03 11:30 | 246.98 | 254.491 | 623.8 | 42.4152 | 44.1005 | -1.6854 | 264.6032 | 40.9 | 43.4699 | -2.5699 | 0.97049 | 2026-07-03 11:30 | 233.922 | 237.629 | 590.3 | 39.6048 | 41.9562 | -2.3514 | 251.7372 | 38.7 | 41.3562 | -2.6562 | 0.9844 | 2026-07-03 11:30 | 433.4537 | 456.5013 | -23.0476 | 2739.0076 | 420.7 | 449.9733 | -29.2733
2026-07-03 11:20 | 973 | 49.65 | 324.433 | 330.044 | 783.3 | 55.0073 | 57.7485 | -2.7412 | 346.4909 | 55.6 | 56.9227 | -1.3227 | 0.983 | 2026-07-03 11:20 | 328.619 | 334.37 | 789 | 55.7283 | 57.7485 | -2.0202 | 346.4909 | 54 | 56.9227 | -2.9227 | 0.9828 | 2026-07-03 11:20 | 323.379 | 332.356 | 777.5 | 55.3927 | 57.7485 | -2.3558 | 346.4909 | 53.7 | 56.9227 | -3.2227 | 0.97299 | 2026-07-03 11:20 | 326.146 | 331.854 | 784.9 | 55.309 | 57.7485 | -2.4395 | 346.4909 | 53.5 | 56.9227 | -3.4227 | 0.9828 | 2026-07-03 11:20 | 244.075 | 247.993 | 581.9 | 41.3322 | 42.7767 | -1.4445 | 256.6599 | 40 | 42.165 | -2.165 | 0.9842 | 2026-07-03 11:20 | 241.205 | 245.396 | 579.8 | 40.8993 | 42.7767 | -1.8773 | 256.6599 | 39.6 | 42.165 | -2.565 | 0.98292 | 2026-07-03 11:20 | 241.43 | 245.959 | 579.8 | 40.9932 | 42.7767 | -1.7835 | 256.6599 | 40.2 | 42.165 | -1.965 | 0.98159 | 2026-07-03 11:20 | 242.821 | 250.063 | 582.9 | 41.6772 | 42.7767 | -1.0995 | 256.6599 | 40.4 | 42.165 | -1.765 | 0.97104 | 2026-07-03 11:20 | 229.671 | 233.24 | 551.6 | 38.8733 | 40.6967 | -1.8234 | 244.1802 | 38.2 | 40.1147 | -1.9147 | 0.9847 | 2026-07-03 11:20 | 425.2125 | 442.7973 | -17.5848 | 2656.7837 | 415.2 | 436.4653 | -21.2653
2026-07-03 11:10 | 954 | 49.65 | 320.027 | 325.462 | 727.7 | 54.2437 | 56.6208 | -2.3772 | 339.7249 | 51.4 | 55.8111 | -4.4111 | 0.9833 | 2026-07-03 11:10 | 324.193 | 329.766 | 735 | 54.961 | 56.6208 | -1.6598 | 339.7249 | 53.6 | 55.8111 | -2.2111 | 0.9831 | 2026-07-03 11:10 | 318.223 | 327.212 | 723.8 | 54.5353 | 56.6208 | -2.0855 | 339.7249 | 52.7 | 55.8111 | -3.1111 | 0.97253 | 2026-07-03 11:10 | 321.506 | 327.099 | 731.4 | 54.5165 | 56.6208 | -2.1043 | 339.7249 | 53.9 | 55.8111 | -1.9111 | 0.9829 | 2026-07-03 11:10 | 240.286 | 244.069 | 541.9 | 40.6782 | 41.9413 | -1.2632 | 251.6481 | 40.3 | 41.3416 | -1.0416 | 0.9845 | 2026-07-03 11:10 | 238.22 | 242.475 | 540.2 | 40.4125 | 41.9413 | -1.5288 | 251.6481 | 40.5 | 41.3416 | -0.84159 | 0.98245 | 2026-07-03 11:10 | 238.026 | 242.356 | 539.6 | 40.3927 | 41.9413 | -1.5487 | 251.6481 | 39.4 | 41.3416 | -1.9416 | 0.98213 | 2026-07-03 11:10 | 238.545 | 245.834 | 542.5 | 40.9723 | 41.9413 | -0.96901 | 251.6481 | 39.4 | 41.3416 | -1.9416 | 0.97035 | 2026-07-03 11:10 | 226.038 | 229.527 | 513.4 | 38.2545 | 39.902 | -1.6475 | 239.412 | 37.3 | 39.3314 | -2.0314 | 0.9848 | 2026-07-03 11:10 | 418.9667 | 434.1507 | -15.184 | 2604.904 | 408.5 | 427.9423 | -19.4423
2026-07-03 11:00 | 936 | 49.36 | 315.778 | 321.076 | 676.3 | 53.5127 | 55.6142 | -2.1015 | 333.6853 | 52.2 | 54.8189 | -2.6189 | 0.9835 | 2026-07-03 11:00 | 320.532 | 325.976 | 681.4 | 54.3293 | 55.6142 | -1.2849 | 333.6853 | 54.3 | 54.8189 | -0.51893 | 0.9833 | 2026-07-03 11:00 | 315.144 | 323.511 | 671.1 | 53.9185 | 55.6142 | -1.6957 | 333.6853 | 51.9 | 54.8189 | -2.9189 | 0.97414 | 2026-07-03 11:00 | 316.776 | 322.189 | 677.5 | 53.6982 | 55.6142 | -1.916 | 333.6853 | 51.6 | 54.8189 | -3.2189 | 0.9832 | 2026-07-03 11:00 | 236.597 | 240.249 | 501.6 | 40.0415 | 41.1957 | -1.1542 | 247.1743 | 39.1 | 40.6066 | -1.5066 | 0.9848 | 2026-07-03 11:00 | 234.171 | 238.357 | 499.7 | 39.7262 | 41.1957 | -1.4695 | 247.1743 | 38.2 | 40.6066 | -2.4066 | 0.98244 | 2026-07-03 11:00 | 233.928 | 237.909 | 500.2 | 39.6515 | 41.1957 | -1.5442 | 247.1743 | 38.6 | 40.6066 | -2.0066 | 0.98327 | 2026-07-03 11:00 | 234.84 | 242.171 | 503.1 | 40.3618 | 41.1957 | -0.83388 | 247.1743 | 38.8 | 40.6066 | -1.8066 | 0.96973 | 2026-07-03 11:00 | 222.769 | 226.131 | 476.1 | 37.6885 | 39.1926 | -1.5041 | 235.1557 | 36.7 | 38.6322 | -1.9322 | 0.98513 | 2026-07-03 11:00 | 412.9282 | 426.4323 | -13.5042 | 2558.5939 | 401.4 | 420.3343 | -18.9343
2026-07-03 10:50 | 909 | 49.65 | 309.445 | 314.541 | 624.1 | 52.4235 | 53.95 | -1.5265 | 323.7002 | 51.8 | 53.1785 | -1.3785 | 0.9838 | 2026-07-03 10:50 | 312.948 | 318.236 | 627.1 | 53.0393 | 53.95 | -0.91069 | 323.7002 | 50.4 | 53.1785 | -2.7785 | 0.98338 | 2026-07-03 10:50 | 307.649 | 315.983 | 619.2 | 52.6638 | 53.95 | -1.2862 | 323.7002 | 50.9 | 53.1785 | -2.2785 | 0.97363 | 2026-07-03 10:50 | 310.495 | 315.672 | 625.9 | 52.612 | 53.95 | -1.338 | 323.7002 | 51.4 | 53.1785 | -1.7785 | 0.9836 | 2026-07-03 10:50 | 231.392 | 234.94 | 462.5 | 39.1567 | 39.963 | -0.80632 | 239.7779 | 37.7 | 39.3915 | -1.6915 | 0.9849 | 2026-07-03 10:50 | 229.694 | 233.707 | 461.5 | 38.9512 | 39.963 | -1.0118 | 239.7779 | 37.4 | 39.3915 | -1.9915 | 0.98283 | 2026-07-03 10:50 | 229.061 | 233.112 | 461.6 | 38.852 | 39.963 | -1.111 | 239.7779 | 37.3 | 39.3915 | -2.0915 | 0.98262 | 2026-07-03 10:50 | 229.961 | 236.692 | 464.3 | 39.4487 | 39.963 | -0.51432 | 239.7779 | 37.4 | 39.3915 | -1.9915 | 0.97156 | 2026-07-03 10:50 | 217.536 | 220.781 | 439.4 | 36.7968 | 38.0198 | -1.223 | 228.119 | 36 | 37.4761 | -1.4761 | 0.9853 | 2026-07-03 10:50 | 403.944 | 413.6719 | -9.7279 | 2482.0312 | 390.3 | 407.7564 | -17.4564
Average of B51 and B53 | 879 | 49.365 | 302.178 | 307.029 | 572.3 | 51.1715 | 52.2265 | -1.055 | 313.3587 | 49.1 | 51.4796 | -2.3796 | 0.9842 | 2026-07-03 10:40 | 306.065 | 311.073 | 576.7 | 51.8455 | 52.2265 | -0.38095 | 313.3587 | 50.3 | 51.4796 | -1.1796 | 0.9839 | 2026-07-03 10:40 | 300.461 | 308.227 | 568.3 | 51.3712 | 52.2265 | -0.85528 | 313.3587 | 48.9 | 51.4796 | -2.5796 | 0.9748 | 2026-07-03 10:40 | 303.777 | 308.748 | 574.5 | 51.458 | 52.2265 | -0.76845 | 313.3587 | 49.9 | 51.4796 | -1.5796 | 0.9839 | 2026-07-03 10:40 | 225.743 | 229.088 | 424.8 | 38.1813 | 38.6863 | -0.50493 | 232.1176 | 37.1 | 38.133 | -1.033 | 0.9854 | 2026-07-03 10:40 | 224.452 | 228.295 | 424.1 | 38.0492 | 38.6863 | -0.63709 | 232.1176 | 36.9 | 38.133 | -1.233 | 0.98317 | 2026-07-03 10:40 | 223.374 | 227.275 | 424.3 | 37.8792 | 38.6863 | -0.80709 | 232.1176 | 36.8 | 38.133 | -1.333 | 0.98284 | 2026-07-03 10:40 | 224.413 | 231.124 | 426.9 | 38.5207 | 38.6863 | -0.16559 | 232.1176 | 36.9 | 38.133 | -1.233 | 0.97096 | 2026-07-03 10:40 | 212.778 | 215.887 | 403.4 | 35.9812 | 36.8052 | -0.82402 | 220.8311 | 34.4 | 36.2789 | -1.8789 | 0.9856 | Average of B51 and B53 | 394.4577 | 400.456 | -5.9984 | 2402.7361 | 380.3 | 394.7295 | -14.4295
2026-07-03 10:30 | 849 | 49.08 | 292.694 | 297.921 | 523.2 | 49.6535 | 50.499 | -0.84549 | 302.9939 | 47.9 | 49.7769 | -1.8769 | 0.98246 | 2026-07-03 10:30 | 296.024 | 300.776 | 526.4 | 50.1293 | 50.499 | -0.36965 | 302.9939 | 49.7 | 49.7769 | -0.076851 | 0.9842 | 2026-07-03 10:30 | 291.085 | 298.628 | 519.4 | 49.7713 | 50.499 | -0.72765 | 302.9939 | 48 | 49.7769 | -1.7769 | 0.97474 | 2026-07-03 10:30 | 293.732 | 298.478 | 524.6 | 49.7463 | 50.499 | -0.75265 | 302.9939 | 48 | 49.7769 | -1.7769 | 0.9841 | 2026-07-03 10:30 | 218.996 | 222.196 | 387.7 | 37.0327 | 37.4067 | -0.37399 | 224.4399 | 35.8 | 36.8717 | -1.0717 | 0.9856 | 2026-07-03 10:30 | 217.393 | 221.134 | 387.2 | 36.8557 | 37.4067 | -0.55099 | 224.4399 | 35.6 | 36.8717 | -1.2717 | 0.98308 | 2026-07-03 10:30 | 217.089 | 220.625 | 387.5 | 36.7708 | 37.4067 | -0.63582 | 224.4399 | 35.4 | 36.8717 | -1.4717 | 0.98397 | 2026-07-03 10:30 | 217.074 | 223.402 | 390 | 37.2337 | 37.4067 | -0.17299 | 224.4399 | 36.1 | 36.8717 | -0.77174 | 0.97167 | 2026-07-03 10:30 | 205.555 | 208.516 | 369 | 34.7527 | 35.5878 | -0.83513 | 213.5268 | 34.2 | 35.0789 | -0.8789 | 0.9858 | 2026-07-03 10:30 | 381.946 | 387.2104 | -5.2644 | 2323.2622 | 370.7 | 381.6733 | -10.9733
2026-07-03 10:20 | 817 | 49.08 | 284.385 | 288.774 | 475.3 | 48.129 | 48.5956 | -0.46661 | 291.5737 | 47.6 | 47.9007 | -0.30069 | 0.9848 | 2026-07-03 10:20 | 286.671 | 291.214 | 476.7 | 48.5357 | 48.5956 | -0.059942 | 291.5737 | 45.5 | 47.9007 | -2.4007 | 0.9844 | 2026-07-03 10:20 | 282.364 | 289.162 | 471.4 | 48.1937 | 48.5956 | -0.40194 | 291.5737 | 46.1 | 47.9007 | -1.8007 | 0.97649 | 2026-07-03 10:20 | 285.072 | 289.56 | 476.6 | 48.26 | 48.5956 | -0.33561 | 291.5737 | 46.6 | 47.9007 | -1.3007 | 0.9845 | 2026-07-03 10:20 | 212.231 | 215.288 | 351.9 | 35.8813 | 35.9967 | -0.11541 | 215.9805 | 35.1 | 35.482 | -0.38199 | 0.9858 | 2026-07-03 10:20 | 210.593 | 213.666 | 351.6 | 35.611 | 35.9967 | -0.38575 | 215.9805 | 34.9 | 35.482 | -0.58199 | 0.98562 | 2026-07-03 10:20 | 210.447 | 213.627 | 352.1 | 35.6045 | 35.9967 | -0.39225 | 215.9805 | 34.9 | 35.482 | -0.58199 | 0.98511 | 2026-07-03 10:20 | 210.456 | 216.363 | 353.9 | 36.0605 | 35.9967 | 0.063753 | 215.9805 | 34.3 | 35.482 | -1.182 | 0.9727 | 2026-07-03 10:20 | 198.848 | 201.712 | 334.8 | 33.6187 | 34.2464 | -0.62778 | 205.4787 | 32.5 | 33.7567 | -1.2567 | 0.9858 | 2026-07-03 10:20 | 369.8943 | 372.6159 | -2.7215 | 2235.6952 | 357.5 | 367.2875 | -9.7875
2026-07-03 10:10 | 777 | 49.65 | 273.451 | 277.587 | 427.7 | 46.2645 | 46.1157 | 0.1488 | 276.6942 | 44.1 | 45.4562 | -1.3562 | 0.9851 | 2026-07-03 10:10 | 276.395 | 280.633 | 431.2 | 46.7722 | 46.1157 | 0.65647 | 276.6942 | 45.9 | 45.4562 | 0.44376 | 0.9849 | 2026-07-03 10:10 | 272.946 | 279.438 | 425.3 | 46.573 | 46.1157 | 0.4573 | 276.6942 | 44.6 | 45.4562 | -0.85624 | 0.97677 | 2026-07-03 10:10 | 274.02 | 278.825 | 430 | 46.4708 | 46.1157 | 0.35513 | 276.6942 | 45.1 | 45.4562 | -0.35624 | 0.98277 | 2026-07-03 10:10 | 204.899 | 207.737 | 316.8 | 34.6228 | 34.1598 | 0.46306 | 204.9587 | 33.1 | 33.6713 | -0.57129 | 0.98634 | 2026-07-03 10:10 | 203.191 | 206.055 | 316.7 | 34.3425 | 34.1598 | 0.18272 | 204.9587 | 32.9 | 33.6713 | -0.77129 | 0.9861 | 2026-07-03 10:10 | 203.487 | 206.314 | 317.2 | 34.3857 | 34.1598 | 0.22589 | 204.9587 | 32.8 | 33.6713 | -0.87129 | 0.9863 | 2026-07-03 10:10 | 203.704 | 209.324 | 319.6 | 34.8873 | 34.1598 | 0.72756 | 204.9587 | 33.3 | 33.6713 | -0.37129 | 0.97315 | 2026-07-03 10:10 | 192.246 | 194.956 | 302.3 | 32.4927 | 32.4988 | -0.0061306 | 194.9928 | 31.5 | 32.0341 | -0.53406 | 0.9861 | 2026-07-03 10:10 | 356.8115 | 353.6007 | 3.2108 | 2121.6042 | 343.3 | 348.5442 | -5.2442
Average of B55 and B57 | 742.5 | 49.365 | 262.662 | 267.486 | 383.6 | 44.581 | 44.1162 | 0.4648 | 264.6972 | 42.5 | 43.4853 | -0.98534 | 0.98197 | 2026-07-03 10:00 | 265.901 | 269.895 | 385.3 | 44.9825 | 44.1162 | 0.8663 | 264.6972 | 43.6 | 43.4853 | 0.11466 | 0.9852 | 2026-07-03 10:00 | 262.582 | 268.925 | 380.7 | 44.8208 | 44.1162 | 0.70463 | 264.6972 | 42.8 | 43.4853 | -0.68534 | 0.97641 | 2026-07-03 10:00 | 265.06 | 269.069 | 384.9 | 44.8448 | 44.1162 | 0.72863 | 264.6972 | 43.3 | 43.4853 | -0.18534 | 0.9851 | 2026-07-03 10:00 | 197.943 | 200.631 | 283.7 | 33.4385 | 32.6787 | 0.75983 | 196.072 | 32.2 | 32.2114 | -0.011361 | 0.9866 | 2026-07-03 10:00 | 196.61 | 199.301 | 283.8 | 33.2168 | 32.6787 | 0.53817 | 196.072 | 32.1 | 32.2114 | -0.11136 | 0.9865 | 2026-07-03 10:00 | 196.623 | 199.37 | 284.4 | 33.2283 | 32.6787 | 0.54967 | 196.072 | 32 | 32.2114 | -0.21136 | 0.98622 | 2026-07-03 10:00 | 196.592 | 202.291 | 286.3 | 33.7152 | 32.6787 | 1.0365 | 196.072 | 31.7 | 32.2114 | -0.51136 | 0.97183 | 2026-07-03 10:00 | 185.748 | 188.273 | 270.8 | 31.3788 | 31.0897 | 0.28913 | 186.5382 | 30.8 | 30.6451 | 0.15488 | 0.98659 | Average of B55 and B57 | 344.2068 | 338.2692 | 5.9377 | 2029.615 | 331 | 333.4319 | -2.4319
2026-07-03 09:50 | 708 | 49.08 | 252.53 | 256.142 | 341.1 | 42.6903 | 42.1122 | 0.5781 | 252.6734 | 41.3 | 41.51 | -0.21002 |  | 2026-07-03 09:50 | 250.526 | 257.766 | 341.7 | 42.961 | 42.1122 | 0.84877 | 252.6734 | 40.6 | 41.51 | -0.91002 |  | 2026-07-03 09:50 | 251.012 | 256.758 | 337.9 | 42.793 | 42.1122 | 0.68077 | 252.6734 | 40.5 | 41.51 | -1.01 |  | 2026-07-03 09:50 | 252.822 | 256.542 | 341.6 | 42.757 | 42.1122 | 0.64477 | 252.6734 | 41 | 41.51 | -0.51002 |  | 2026-07-03 09:50 | 188.268 | 190.806 | 251.5 | 31.801 | 31.1942 | 0.60676 | 187.1655 | 30.3 | 30.7482 | -0.44817 |  | 2026-07-03 09:50 | 187.289 | 189.814 | 251.7 | 31.6357 | 31.1942 | 0.44142 | 187.1655 | 30.2 | 30.7482 | -0.54817 |  | 2026-07-03 09:50 | 187.307 | 189.893 | 252.4 | 31.6488 | 31.1942 | 0.45459 | 187.1655 | 30.2 | 30.7482 | -0.54817 |  | 2026-07-03 09:50 | 187.457 | 192.893 | 254.6 | 32.1488 | 31.1942 | 0.95459 | 187.1655 | 30.6 | 30.7482 | -0.14817 |  | 2026-07-03 09:50 | 176.455 | 178.998 | 240 | 29.833 | 29.6775 | 0.15554 | 178.0648 | 28.2 | 29.2531 | -1.0531 |  | 2026-07-03 09:50 | 328.2687 | 322.9034 | 5.3653 | 1937.4201 | 312.9 | 318.2858 | -5.3858
2026-07-03 09:40 | 668 | 48.79 | 238.683 | 241.998 | 299.8 | 40.333 | 39.777 | 0.55595 | 238.6623 | 40.5 | 39.2082 | 1.2918 |  | 2026-07-03 09:40 | 240.474 | 243.938 | 301.1 | 40.6563 | 39.777 | 0.87929 | 238.6623 | 39.4 | 39.2082 | 0.19176 |  | 2026-07-03 09:40 | 237.11 | 242.066 | 297.4 | 40.3443 | 39.777 | 0.56729 | 238.6623 | 38.7 | 39.2082 | -0.50824 |  | 2026-07-03 09:40 | 239.874 | 243.305 | 300.6 | 40.5508 | 39.777 | 0.77379 | 238.6623 | 39.2 | 39.2082 | -0.0082361 |  | 2026-07-03 09:40 | 177.634 | 179.974 | 221.2 | 29.9957 | 29.4645 | 0.53119 | 176.7869 | 29 | 29.0431 | -0.043138 |  | 2026-07-03 09:40 | 177.159 | 179.511 | 221.5 | 29.9185 | 29.4645 | 0.45402 | 176.7869 | 28.9 | 29.0431 | -0.14314 |  | 2026-07-03 09:40 | 176.641 | 178.949 | 222.2 | 29.8248 | 29.4645 | 0.36035 | 176.7869 | 28.9 | 29.0431 | -0.14314 |  | 2026-07-03 09:40 | 176.954 | 181.823 | 224 | 30.3038 | 29.4645 | 0.83935 | 176.7869 | 28.5 | 29.0431 | -0.54314 |  | 2026-07-03 09:40 | 167.771 | 169.998 | 211.8 | 28.333 | 28.0318 | 0.3012 | 168.1908 | 27.1 | 27.6309 | -0.53095 |  | 2026-07-03 09:40 | 310.2603 | 304.9979 | 5.2624 | 1829.9875 | 300.2 | 300.6364 | -0.43644
2026-07-03 09:30 | 631 | 48.79 | 225.228 | 228.287 | 259.3 | 38.0478 | 37.5738 | 0.47401 | 225.443 | 34.7 | 37.0365 | -2.3365 |  | 2026-07-03 09:30 | 227.987 | 231.177 | 261.7 | 38.5295 | 37.5738 | 0.95567 | 225.443 | 36.6 | 37.0365 | -0.43652 |  | 2026-07-03 09:30 | 224.275 | 228.898 | 258.7 | 38.1497 | 37.5738 | 0.57584 | 225.443 | 36.1 | 37.0365 | -0.93652 |  | 2026-07-03 09:30 | 226.891 | 230.043 | 261.4 | 38.3405 | 37.5738 | 0.76667 | 225.443 | 36.5 | 37.0365 | -0.53652 |  | 2026-07-03 09:30 | 167.828 | 169.987 | 192.2 | 28.3312 | 27.8325 | 0.4987 | 166.9948 | 27 | 27.4345 | -0.43446 |  | 2026-07-03 09:30 | 166.653 | 168.797 | 192.6 | 28.1328 | 27.8325 | 0.30037 | 166.9948 | 27 | 27.4345 | -0.43446 |  | 2026-07-03 09:30 | 166.202 | 168.34 | 193.3 | 28.0567 | 27.8325 | 0.2242 | 166.9948 | 26.8 | 27.4345 | -0.63446 |  | 2026-07-03 09:30 | 167.698 | 172.338 | 195.5 | 28.723 | 27.8325 | 0.89053 | 166.9948 | 27 | 27.4345 | -0.43446 |  | 2026-07-03 09:30 | 158.867 | 160.943 | 184.7 | 26.8238 | 26.4791 | 0.34469 | 158.8749 | 26 | 26.1005 | -0.10049 |  | 2026-07-03 09:30 | 293.135 | 288.1043 | 5.0307 | 1728.6259 | 277.7 | 283.9844 | -6.2844
2026-07-03 09:20 | 592 | 48.5 | 210.809 | 213.564 | 224.6 | 35.594 | 35.2905 | 0.30345 | 211.7433 | 33.9 | 34.7859 | -0.88589 |  | 2026-07-03 09:20 | 213.667 | 216.569 | 225.1 | 36.0948 | 35.2905 | 0.80429 | 211.7433 | 34.6 | 34.7859 | -0.18589 |  | 2026-07-03 09:20 | 210.443 | 214.76 | 222.6 | 35.7933 | 35.2905 | 0.50279 | 211.7433 | 33.7 | 34.7859 | -1.0859 |  | 2026-07-03 09:20 | 213.449 | 216.304 | 224.9 | 36.0507 | 35.2905 | 0.76012 | 211.7433 | 34.2 | 34.7859 | -0.58589 |  | 2026-07-03 09:20 | 157.888 | 159.87 | 165.2 | 26.645 | 26.1411 | 0.50386 | 156.8469 | 25.3 | 25.7673 | -0.46733 |  | 2026-07-03 09:20 | 157.112 | 159.101 | 165.6 | 26.5168 | 26.1411 | 0.37569 | 156.8469 | 25.1 | 25.7673 | -0.66733 |  | 2026-07-03 09:20 | 157.294 | 159.269 | 166.5 | 26.5448 | 26.1411 | 0.40369 | 156.8469 | 25.1 | 25.7673 | -0.66733 |  | 2026-07-03 09:20 | 158.105 | 162.371 | 168.5 | 27.0618 | 26.1411 | 0.92069 | 156.8469 | 25.3 | 25.7673 | -0.46733 |  | 2026-07-03 09:20 | 149.82 | 151.701 | 158.7 | 25.2835 | 24.8701 | 0.41344 | 149.2204 | 23.6 | 24.5144 | -0.91442 |  | 2026-07-03 09:20 | 275.5848 | 270.5968 | 4.988 | 1623.5809 | 260.8 | 266.7273 | -5.9273
2026-07-03 09:10 | 550 | 48.22 | 195.537 | 198.072 | 190.7 | 33.012 | 32.8218 | 0.19016 | 196.931 | 30.5 | 32.3525 | -1.8525 |  | 2026-07-03 09:10 | 197.224 | 199.822 | 190.5 | 33.3037 | 32.8218 | 0.48183 | 196.931 | 31.7 | 32.3525 | -0.65248 |  | 2026-07-03 09:10 | 194.665 | 198.192 | 188.9 | 33.032 | 32.8218 | 0.21016 | 196.931 | 31.3 | 32.3525 | -1.0525 |  | 2026-07-03 09:10 | 197.643 | 200.226 | 190.7 | 33.371 | 32.8218 | 0.54916 | 196.931 | 31.6 | 32.3525 | -0.75248 |  | 2026-07-03 09:10 | 145.9 | 147.702 | 139.9 | 24.617 | 24.3125 | 0.30453 | 145.8748 | 23.3 | 23.9648 | -0.6648 |  | 2026-07-03 09:10 | 145.408 | 147.204 | 140.5 | 24.534 | 24.3125 | 0.22153 | 145.8748 | 23.3 | 23.9648 | -0.6648 |  | 2026-07-03 09:10 | 145.164 | 146.957 | 141.4 | 24.4928 | 24.3125 | 0.18036 | 145.8748 | 23.3 | 23.9648 | -0.6648 |  | 2026-07-03 09:10 | 146.293 | 150.177 | 143.2 | 25.0295 | 24.3125 | 0.71703 | 145.8748 | 23.4 | 23.9648 | -0.5648 |  | 2026-07-03 09:10 | 138.848 | 140.658 | 135.1 | 23.443 | 23.1303 | 0.3127 | 138.7818 | 22.2 | 22.7995 | -0.59954 |  | 2026-07-03 09:10 | 254.835 | 251.6675 | 3.1675 | 1510.0052 | 240.6 | 248.0687 | -7.4687
2026-07-03 09:00 | 507 | 47.64 | 180.844 | 183.115 | 160.2 | 30.5192 | 30.3226 | 0.19655 | 181.9357 | 29.2 | 29.889 | -0.689 |  | 2026-07-03 09:00 | 180.875 | 183.202 | 158.8 | 30.5337 | 30.3226 | 0.21105 | 181.9357 | 28.5 | 29.889 | -1.389 |  | 2026-07-03 09:00 | 179.495 | 182.568 | 157.6 | 30.428 | 30.3226 | 0.10538 | 181.9357 | 28 | 29.889 | -1.889 |  | 2026-07-03 09:00 | 181.457 | 183.773 | 159.1 | 30.6288 | 30.3226 | 0.30622 | 181.9357 | 28.6 | 29.889 | -1.289 |  | 2026-07-03 09:00 | 133.939 | 135.572 | 116.6 | 22.5953 | 22.4612 | 0.13414 | 134.7672 | 21.2 | 22.14 | -0.94 |  | 2026-07-03 09:00 | 133.359 | 134.968 | 117.2 | 22.4947 | 22.4612 | 0.033469 | 134.7672 | 21.3 | 22.14 | -0.84 |  | 2026-07-03 09:00 | 133.652 | 135.289 | 118.1 | 22.5482 | 22.4612 | 0.086969 | 134.7672 | 21.1 | 22.14 | -1.04 |  | 2026-07-03 09:00 | 134.158 | 137.77 | 119.8 | 22.9617 | 22.4612 | 0.50047 | 134.7672 | 21.4 | 22.14 | -0.74 |  | 2026-07-03 09:00 | 127.36 | 128.92 | 112.9 | 21.4867 | 21.369 | 0.11762 | 128.2143 | 20.3 | 21.0635 | -0.76347 |  | 2026-07-03 09:00 | 234.1962 | 232.5043 | 1.6919 | 1395.0258 | 219.6 | 229.1795 | -9.5795
2026-07-03 08:50 | 460 | 47.35 | 163.88 | 165.836 | 131 | 27.6393 | 27.542 | 0.097362 | 165.2518 | 25.6 | 27.1481 | -1.5481 |  | 2026-07-03 08:50 | 163.898 | 165.956 | 130.3 | 27.6593 | 27.542 | 0.11736 | 165.2518 | 25.9 | 27.1481 | -1.2481 |  | 2026-07-03 08:50 | 162.515 | 165.117 | 129.6 | 27.5195 | 27.542 | -0.022472 | 165.2518 | 25.8 | 27.1481 | -1.3481 |  | 2026-07-03 08:50 | 164.606 | 166.639 | 130.5 | 27.7732 | 27.542 | 0.23119 | 165.2518 | 26.1 | 27.1481 | -1.0481 |  | 2026-07-03 08:50 | 120.958 | 122.415 | 95.4 | 20.4025 | 20.4015 | 0.0010394 | 122.4088 | 19.3 | 20.1097 | -0.80972 |  | 2026-07-03 08:50 | 120.6 | 122.015 | 95.9 | 20.3358 | 20.4015 | -0.065627 | 122.4088 | 19.2 | 20.1097 | -0.90972 |  | 2026-07-03 08:50 | 120.715 | 122.144 | 97 | 20.3573 | 20.4015 | -0.044127 | 122.4088 | 19.2 | 20.1097 | -0.90972 |  | 2026-07-03 08:50 | 121.974 | 125.364 | 98.4 | 20.894 | 20.4015 | 0.49254 | 122.4088 | 19.4 | 20.1097 | -0.70972 |  | 2026-07-03 08:50 | 115.804 | 117.199 | 92.6 | 19.5332 | 19.4095 | 0.1237 | 116.4568 | 18.5 | 19.1319 | -0.63191 |  | 2026-07-03 08:50 | 212.1142 | 211.1832 | 0.93097 | 1267.0992 | 199 | 208.1633 | -9.1633
2026-07-03 08:40 | 417 | 47.35 | 147.649 | 149.382 | 105.4 | 24.897 | 24.9674 | -0.070396 | 149.8044 | 23.6 | 24.6104 | -1.0104 |  | 2026-07-03 08:40 | 148.264 | 150.292 | 104.4 | 25.0487 | 24.9674 | 0.08127 | 149.8044 | 23.7 | 24.6104 | -0.91036 |  | 2026-07-03 08:40 | 146.286 | 148.429 | 103.8 | 24.7382 | 24.9674 | -0.22923 | 149.8044 | 23.1 | 24.6104 | -1.5104 |  | 2026-07-03 08:40 | 148.465 | 150.253 | 104.4 | 25.0422 | 24.9674 | 0.07477 | 149.8044 | 23.5 | 24.6104 | -1.1104 |  | 2026-07-03 08:40 | 108.787 | 110.053 | 76.1 | 18.3422 | 18.4944 | -0.1522 | 110.9662 | 16.8 | 18.2299 | -1.4299 |  | 2026-07-03 08:40 | 108.525 | 109.754 | 76.7 | 18.2923 | 18.4944 | -0.20203 | 110.9662 | 17.1 | 18.2299 | -1.1299 |  | 2026-07-03 08:40 | 108.737 | 109.969 | 77.8 | 18.3282 | 18.4944 | -0.1662 | 110.9662 | 16.9 | 18.2299 | -1.3299 |  | 2026-07-03 08:40 | 110.064 | 113.034 | 79 | 18.839 | 18.4944 | 0.34463 | 110.9662 | 17.2 | 18.2299 | -1.0299 |  | 2026-07-03 08:40 | 104.387 | 105.601 | 74.1 | 17.6002 | 17.5951 | 0.0050665 | 105.5706 | 16.4 | 17.3435 | -0.94349 |  | 2026-07-03 08:40 | 191.1278 | 191.4422 | -0.31432 | 1148.6529 | 178.3 | 188.7045 | -10.4045
2026-07-03 08:30 | 373 | 43.05 | 130.148 | 131.622 | 81.8 | 21.937 | 22.6976 | -0.76058 | 136.1855 | 20.2 | 22.373 | -2.173 |  | 2026-07-03 08:30 | 128.548 | 132.629 | 80.7 | 22.1048 | 22.6976 | -0.59275 | 136.1855 | 20.2 | 22.373 | -2.173 |  | 2026-07-03 08:30 | 129.147 | 130.867 | 80.7 | 21.8112 | 22.6976 | -0.88641 | 136.1855 | 20.1 | 22.373 | -2.273 |  | 2026-07-03 08:30 | 131.448 | 132.964 | 80.9 | 22.1607 | 22.6976 | -0.53691 | 136.1855 | 20.3 | 22.373 | -2.073 |  | 2026-07-03 08:30 | 95.756 | 96.841 | 59.3 | 16.1402 | 16.813 | -0.67286 | 100.8781 | 14.8 | 16.5726 | -1.7726 |  | 2026-07-03 08:30 | 96.079 | 97.148 | 59.6 | 16.1913 | 16.813 | -0.62169 | 100.8781 | 15 | 16.5726 | -1.5726 |  | 2026-07-03 08:30 | 96.43 | 97.512 | 60.9 | 16.252 | 16.813 | -0.56102 | 100.8781 | 15 | 16.5726 | -1.5726 |  | 2026-07-03 08:30 | 97.458 | 100.067 | 61.8 | 16.6778 | 16.813 | -0.13519 | 100.8781 | 15.1 | 16.5726 | -1.4726 |  | 2026-07-03 08:30 | 92.433 | 93.48 | 57.7 | 15.58 | 15.9955 | -0.41551 | 95.9731 | 14.3 | 15.7668 | -1.4668 |  | 2026-07-03 08:30 | 168.855 | 174.0379 | -5.1829 | 1044.2276 | 155 | 171.5492 | -16.5492
2026-07-03 08:20 | 327 | 37.6 | 111.072 | 113.437 | 61.6 | 18.9062 | 20.3036 | -1.3974 | 121.8214 | 17.2 | 20.0132 | -2.8132 |  | 2026-07-03 08:20 | 112.085 | 114.105 | 60.5 | 19.0175 | 20.3036 | -1.2861 | 121.8214 | 17.5 | 20.0132 | -2.5132 |  | 2026-07-03 08:20 | 111.433 | 112.72 | 60.6 | 18.7867 | 20.3036 | -1.5169 | 121.8214 | 17 | 20.0132 | -3.0132 |  | 2026-07-03 08:20 | 113.391 | 114.652 | 60.6 | 19.1087 | 20.3036 | -1.1949 | 121.8214 | 17.2 | 20.0132 | -2.8132 |  | 2026-07-03 08:20 | 81.958 | 82.911 | 44.5 | 13.8185 | 15.0397 | -1.2212 | 90.2381 | 12.5 | 14.8246 | -2.3246 |  | 2026-07-03 08:20 | 83.953 | 84.84 | 44.6 | 14.14 | 15.0397 | -0.89968 | 90.2381 | 12.9 | 14.8246 | -1.9246 |  | 2026-07-03 08:20 | 83.17 | 84.121 | 45.9 | 14.0202 | 15.0397 | -1.0195 | 90.2381 | 12.7 | 14.8246 | -2.1246 |  | 2026-07-03 08:20 | 84.32 | 86.665 | 46.7 | 14.4442 | 15.0397 | -0.59552 | 90.2381 | 12.9 | 14.8246 | -1.9246 |  | 2026-07-03 08:20 | 79.954 | 81.072 | 43.4 | 13.512 | 14.3084 | -0.7964 | 85.8504 | 12.3 | 14.1038 | -1.8038 |  | 2026-07-03 08:20 | 145.7538 | 155.6814 | -9.9276 | 934.0886 | 132.2 | 153.4552 | -21.2552
2026-07-03 08:10 | 281 | 32.72 | 93.382 | 94.354 | 44.4 | 15.7257 | 17.7592 | -2.0335 | 106.555 | 14 | 17.5052 | -3.5052 |  | 2026-07-03 08:10 | 94.491 | 95.479 | 43 | 15.9132 | 17.7592 | -1.846 | 106.555 | 14.5 | 17.5052 | -3.0052 |  | 2026-07-03 08:10 | 92.998 | 93.987 | 43.6 | 15.6645 | 17.7592 | -2.0947 | 106.555 | 13.9 | 17.5052 | -3.6052 |  | 2026-07-03 08:10 | 93.985 | 94.982 | 43.4 | 15.8303 | 17.7592 | -1.9288 | 106.555 | 14.1 | 17.5052 | -3.4052 |  | 2026-07-03 08:10 | 68.819 | 69.62 | 32 | 11.6033 | 13.1549 | -1.5516 | 78.9296 | 10.3 | 12.9668 | -2.6668 |  | 2026-07-03 08:10 | 70.339 | 71.129 | 31.7 | 11.8548 | 13.1549 | -1.3001 | 78.9296 | 10.3 | 12.9668 | -2.6668 |  | 2026-07-03 08:10 | 69.752 | 70.547 | 33.2 | 11.7578 | 13.1549 | -1.3971 | 78.9296 | 10.5 | 12.9668 | -2.4668 |  | 2026-07-03 08:10 | 70.745 | 72.637 | 33.8 | 12.1062 | 13.1549 | -1.0488 | 78.9296 | 10.8 | 12.9668 | -2.1668 |  | 2026-07-03 08:10 | 67.055 | 67.817 | 31.1 | 11.3028 | 12.5153 | -1.2125 | 75.0918 | 10.1 | 12.3363 | -2.2363 |  | 2026-07-03 08:10 | 121.7587 | 136.1717 | -14.413 | 817.0301 | 108.5 | 134.2244 | -25.7244
2026-07-03 08:00 | 234 | 25.83 | 75.346 | 76.153 | 30.4 | 12.6922 | 15.1553 | -2.4631 | 90.9318 | 10.8 | 14.9386 | -4.1386 |  | 2026-07-03 08:00 | 75.257 | 76.097 | 28.5 | 12.6828 | 15.1553 | -2.4725 | 90.9318 | 10.7 | 14.9386 | -4.2386 |  | 2026-07-03 08:00 | 74.655 | 75.47 | 29.7 | 12.5783 | 15.1553 | -2.577 | 90.9318 | 11 | 14.9386 | -3.9386 |  | 2026-07-03 08:00 | 75.287 | 76.14 | 29.3 | 12.69 | 15.1553 | -2.4653 | 90.9318 | 11.2 | 14.9386 | -3.7386 |  | 2026-07-03 08:00 | 55.078 | 55.775 | 21.7 | 9.2958 | 11.2262 | -1.9303 | 67.3569 | 8 | 11.0656 | -3.0656 |  | 2026-07-03 08:00 | 53.775 | 54.445 | 21.4 | 9.0742 | 11.2262 | -2.152 | 67.3569 | 8 | 11.0656 | -3.0656 |  | 2026-07-03 08:00 | 56.051 | 56.738 | 22.7 | 9.4563 | 11.2262 | -1.7698 | 67.3569 | 8.3 | 11.0656 | -2.7656 |  | 2026-07-03 08:00 | 56.836 | 58.673 | 23 | 9.7788 | 11.2262 | -1.4473 | 67.3569 | 8.2 | 11.0656 | -2.8656 |  | 2026-07-03 08:00 | 54.102 | 54.782 | 21 | 9.1303 | 10.6803 | -1.55 | 64.0818 | 7.9 | 10.5276 | -2.6276 |  | 2026-07-03 08:00 | 97.3788 | 116.2061 | -18.8273 | 697.2367 | 84.1 | 114.5444 | -30.4444
2026-07-03 07:50 | 187 | 16.65 | 57.717 | 58.4 | 19.6 | 9.7333 | 12.5016 | -2.7682 | 75.0094 | 8.3 | 12.3228 | -4.0228 |  | 2026-07-03 07:50 | 56.635 | 57.311 | 17.8 | 9.5518 | 12.5016 | -2.9497 | 75.0094 | 13.2 | 12.3228 | 0.87721 |  | 2026-07-03 07:50 | 56.531 | 57.2 | 18.7 | 9.5333 | 12.5016 | -2.9682 | 75.0094 | 8 | 12.3228 | -4.3228 |  | 2026-07-03 07:50 | 57.832 | 58.517 | 18.1 | 9.7528 | 12.5016 | -2.7487 | 75.0094 | 8.1 | 12.3228 | -4.2228 |  | 2026-07-03 07:50 | 41.604 | 42.252 | 13.7 | 7.042 | 9.2604 | -2.2184 | 55.5625 | 6 | 9.128 | -3.128 |  | 2026-07-03 07:50 | 40.906 | 41.607 | 13.4 | 6.9345 | 9.2604 | -2.3259 | 55.5625 | 5.8 | 9.128 | -3.328 |  | 2026-07-03 07:50 | 42.814 | 43.409 | 14.4 | 7.2348 | 9.2604 | -2.0256 | 55.5625 | 6.1 | 9.128 | -3.028 |  | 2026-07-03 07:50 | 43.503 | 44.887 | 14.8 | 7.4812 | 9.2604 | -1.7792 | 55.5625 | 6.3 | 9.128 | -2.828 |  | 2026-07-03 07:50 | 41.407 | 41.991 | 13.1 | 6.9985 | 8.8101 | -1.8116 | 52.8608 | 5.9 | 8.6842 | -2.7842 |  | 2026-07-03 07:50 | 74.2623 | 95.858 | -21.5957 | 575.1482 | 67.7 | 94.4873 | -26.7873
2026-07-03 07:40 | 141 | 10.62 | 40.127 | 40.693 | 11.3 | 6.7822 | 9.6196 | -2.8374 | 57.7176 | 5.5 | 9.482 | -3.982 | [5 empty] | 0 | 9.6196 | -9.6196 | 57.7176 | 0 | 9.482 | -9.482 |  | 2026-07-03 07:40 | 40.254 | 40.789 | 10.7 | 6.7982 | 9.6196 | -2.8214 | 57.7176 | 5.5 | 9.482 | -3.982 |  | 2026-07-03 07:40 | 40.179 | 40.749 | 10 | 6.7915 | 9.6196 | -2.8281 | 57.7176 | 5.4 | 9.482 | -4.082 |  | 2026-07-03 07:40 | 29.341 | 29.932 | 7.7 | 4.9887 | 7.1256 | -2.137 | 42.7538 | 3.9 | 7.0237 | -3.1237 |  | 2026-07-03 07:40 | 29.173 | 29.635 | 7.6 | 4.9392 | 7.1256 | -2.1865 | 42.7538 | 4 | 7.0237 | -3.0237 |  | 2026-07-03 07:40 | 30.446 | 30.903 | 8.3 | 5.1505 | 7.1256 | -1.9751 | 42.7538 | 4.1 | 7.0237 | -2.9237 |  | 2026-07-03 07:40 | 31.06 | 32.096 | 8.5 | 5.3493 | 7.1256 | -1.7763 | 42.7538 | 4.2 | 7.0237 | -2.8237 |  | 2026-07-03 07:40 | 29.189 | 29.667 | 7.2 | 4.9445 | 6.7792 | -1.8347 | 40.6749 | 3.8 | 6.6822 | -2.8822 |  | 2026-07-03 07:40 | 45.744 | 73.7601 | -28.0161 | 442.5606 | 36.4 | 72.7053 | -36.3053
2026-07-03 07:30 | 99 | 8.9 | 26.15 | 26.6 | 5.8 | 4.4333 | 6.7929 | -2.3596 | 40.7574 | 3.5 | 6.6958 | -3.1958 |  | 2026-07-03 07:30 | 23.514 | 24.356 | 4.6 | 4.0593 | 6.7929 | -2.7336 | 40.7574 | 2.9 | 6.6958 | -3.7958 |  | 2026-07-03 07:30 | 25.737 | 26.198 | 5.2 | 4.3663 | 6.7929 | -2.4266 | 40.7574 | 3.3 | 6.6958 | -3.3958 |  | 2026-07-03 07:30 | 23.871 | 24.555 | 4.6 | 4.0925 | 6.7929 | -2.7004 | 40.7574 | 2.9 | 6.6958 | -3.7958 |  | 2026-07-03 07:30 | 18.696 | 19.337 | 3.8 | 3.2228 | 5.0318 | -1.8089 | 30.1907 | 2.4 | 4.9598 | -2.5598 |  | 2026-07-03 07:30 | 18.798 | 19.193 | 3.6 | 3.1988 | 5.0318 | -1.8329 | 30.1907 | 2.4 | 4.9598 | -2.5598 |  | 2026-07-03 07:30 | 19.65 | 20.065 | 4.2 | 3.3442 | 5.0318 | -1.6876 | 30.1907 | 2.5 | 4.9598 | -2.4598 |  | 2026-07-03 07:30 | 20.202 | 21.26 | 4.3 | 3.5433 | 5.0318 | -1.4884 | 30.1907 | 2.6 | 4.9598 | -2.3598 |  | 2026-07-03 07:30 | 17.581 | 17.971 | 3.4 | 2.9952 | 4.7871 | -1.7919 | 28.7227 | 2.2 | 4.7187 | -2.5187 |  | 2026-07-03 07:30 | 33.2558 | 52.0858 | -18.83 | 312.515 | 24.7 | 51.341 | -26.641
2026-07-03 07:20 | 23 | 8.04 | 14.839 | 15.281 | 2.3 | 2.5468 | 1.5826 | 0.96419 | 9.4959 | 1.7 | 1.56 | 0.13999 |  | 2026-07-03 07:20 | 11.845 | 12.546 | 1.7 | 2.091 | 1.5826 | 0.50835 | 9.4959 | 1.4 | 1.56 | -0.16001 |  | 2026-07-03 07:20 | 14.331 | 14.692 | 1.9 | 2.4487 | 1.5826 | 0.86602 | 9.4959 | 1.6 | 1.56 | 0.039986 |  | 2026-07-03 07:20 | 12.132 | 12.774 | 1.7 | 2.129 | 1.5826 | 0.54635 | 9.4959 | 1.4 | 1.56 | -0.16001 |  | 2026-07-03 07:20 | 10.37 | 11.139 | 1.4 | 1.8565 | 1.1723 | 0.68417 | 7.034 | 1.2 | 1.1556 | 0.044434 |  | 2026-07-03 07:20 | 9.904 | 10.216 | 1.2 | 1.7027 | 1.1723 | 0.53034 | 7.034 | 1 | 1.1556 | -0.15557 |  | 2026-07-03 07:20 | 11.021 | 11.358 | 1.7 | 1.893 | 1.1723 | 0.72067 | 7.034 | 1.3 | 1.1556 | 0.14443 |  | 2026-07-03 07:20 | 11.312 | 12.275 | 1.7 | 2.0458 | 1.1723 | 0.8735 | 7.034 | 1.3 | 1.1556 | 0.14443 |  | 2026-07-03 07:20 | 9.163 | 9.474 | 1.2 | 1.579 | 1.1153 | 0.46367 | 6.692 | 1 | 1.0994 | -0.099378 |  | 2026-07-03 07:20 | 18.2925 | 12.1352 | 6.1573 | 72.8114 | 11.9 | 11.9617 | -0.061696
2026-07-03 07:10 | 13 | 7.17 | 6.122 | 6.368 | 0.6 | 1.0613 | 0.89711 | 0.16422 | 5.3827 | 0.6 | 0.88428 | -0.28428 |  | 2026-07-03 07:10 | 5.406 | 5.992 | 0.3 | 0.99867 | 0.89711 | 0.10156 | 5.3827 | 0.3 | 0.88428 | -0.58428 |  | 2026-07-03 07:10 | 5.572 | 5.807 | 0.3 | 0.96783 | 0.89711 | 0.070723 | 5.3827 | 0.3 | 0.88428 | -0.58428 |  | 2026-07-03 07:10 | 5.282 | 6.199 | 0.3 | 1.0332 | 0.89711 | 0.13606 | 5.3827 | 0.3 | 0.88428 | -0.58428 |  | 2026-07-03 07:10 | 4.336 | 4.797 | 0.2 | 0.7995 | 0.66453 | 0.13497 | 3.9872 | 0.2 | 0.65502 | -0.45502 |  | 2026-07-03 07:10 | 3.675 | 3.83 | 0.2 | 0.63833 | 0.66453 | -0.026193 | 3.9872 | 0.2 | 0.65502 | -0.45502 |  | 2026-07-03 07:10 | 4.433 | 4.625 | 0.4 | 0.77083 | 0.66453 | 0.10631 | 3.9872 | 0.4 | 0.65502 | -0.25502 |  | 2026-07-03 07:10 | 4.415 | 4.805 | 0.4 | 0.80083 | 0.66453 | 0.13631 | 3.9872 | 0.4 | 0.65502 | -0.25502 |  | 2026-07-03 07:10 | 3.6 | 3.765 | 0.2 | 0.6275 | 0.63221 | -0.0047142 | 3.7933 | 0.2 | 0.62317 | -0.42317 |  | 2026-07-03 07:10 | 7.698 | 6.8788 | 0.81924 | 41.2726 | 2.9 | 6.7804 | -3.8804
2026-07-03 07:00 | 4 | 7.75 | 1.587 | 1.669 | 0 | 0.27817 | 0.27551 | 0.0026602 | 1.653 | 0 | 0.27157 | -0.27157 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.27551 | -0.27551 | 1.653 | 0 | 0.27157 | -0.27157 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.27551 | -0.27551 | 1.653 | 0 | 0.27157 | -0.27157 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.27551 | -0.27551 | 1.653 | 0 | 0.27157 | -0.27157 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.20408 | -0.20408 | 1.2245 | 0 | 0.20116 | -0.20116 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.20408 | -0.20408 | 1.2245 | 0 | 0.20116 | -0.20116 |  | 2026-07-03 07:00 | 0.934 | 0.982 | 0 | 0.16367 | 0.20408 | -0.040412 | 1.2245 | 0 | 0.20116 | -0.20116 |  | 2026-07-03 07:00 | 1.085 | 1.47 | 0 | 0.245 | 0.20408 | 0.040921 | 1.2245 | 0 | 0.20116 | -0.20116 |  | 2026-07-03 07:00 | 0 | 0 | 0 | 0 | 0.19416 | -0.19416 | 1.1649 | 0 | 0.19138 | -0.19138 |  | 2026-07-03 07:00 | 0.68683 | 2.1125 | -1.4257 | 12.675 | 0 | 2.0823 | -2.0823
[110 empty] | Total: - | 19792.8807 | 20817.7713 | -1024.8906 |  | 19538.5 | 20520.0772 | -981.5772
Sum:- | 45493 |  | 14918.974 |  | 94133.1 |  |  |  |  | 2538.8 | 2676.176 | -137.376 | 0.98239 |  | 14513.504 |  | 95138.3 |  |  |  |  | 2566.8 | 2676.176 | -109.376 | 0.98394 |  | 15203.033 |  | 95602.6 |  |  |  |  | 2532.1 | 2676.176 | -144.076 | 0.97289 |  | 15256.42 |  | 96191.3 |  |  |  |  | 2545.4 | 2676.176 | -130.776 | 0.98322 |  | 11484.61 |  | 72114 |  |  |  |  | 1912.5 | 1982.3526 | -69.8526 | 0.98435 |  | 11316.242 |  | 71345.9 |  |  |  |  | 1886.1 | 1982.3526 | -96.2526 | 0.98162 |  | 11325.742 |  | 71355.4 |  |  |  |  | 1886.1 | 1982.3526 | -96.2526 | 0.98127 |  | 11323.641 |  | 71558.9 |  |  |  |  | 1886.4 | 1982.3526 | -95.9526 | 0.97111 |  | 10708.596 |  | 67659.8 |  |  |  |  | 1784.3 | 1885.963 | -101.663 | 0.98455
Formulas:
Time = [Time]

## 8 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-08-03 19:00 | 0 | 36.16 | 0.051 | 0.07 | 2495 | 0.011667 | 0 | 0.011667 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.05 | 0.251 | 2516.8 | 0.041833 | 0 | 0.041833 | 0 | 0.1 | 0 | 0.1 |  | 2026-08-03 19:00 | 0.093 | 0.098 | 2474.3 | 0.016333 | 0 | 0.016333 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.086 | 0.217 | 2494.1 | 0.036167 | 0 | 0.036167 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.096 | 0.101 | 1862.6 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.095 | 0.1 | 1845.9 | 0.016667 | 0 | 0.016667 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.081 | 0.085 | 1844.3 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.077 | 0.083 | 1855.9 | 0.013833 | 0 | 0.013833 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.085 | 0.089 | 1756.7 | 0.014833 | 0 | 0.014833 | 0 | 0 | 0 | 0 |  | 2026-08-03 19:00 | 0.18233 | 0 | 0.18233 | 0 | 0.1 | 0 | 0.1 | 1 | 98.28%
2026-08-03 18:50 | 0 | 37.88 | 0.284 | 0.299 | 2495 | 0.049833 | 0 | 0.049833 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.455 | 0.957 | 2516.7 | 0.1595 | 0 | 0.1595 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.347 | 0.365 | 2474.3 | 0.060833 | 0 | 0.060833 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.338 | 0.762 | 2494.1 | 0.127 | 0 | 0.127 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.133 | 0.268 | 1862.6 | 0.044667 | 0 | 0.044667 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.043 | 0.087 | 1845.9 | 0.0145 | 0 | 0.0145 | 0 | 0.1 | 0 | 0.1 |  | 2026-08-03 18:50 | 0.02 | 0.089 | 1844.3 | 0.014833 | 0 | 0.014833 | 0 | 0.2 | 0 | 0.2 |  | 2026-08-03 18:50 | 0.144 | 0.433 | 1855.9 | 0.072167 | 0 | 0.072167 | 0 | 0.1 | 0 | 0.1 |  | 2026-08-03 18:50 | 0.025 | 0.079 | 1756.7 | 0.013167 | 0 | 0.013167 | 0 | 0.1 | 0 | 0.1 |  | 2026-08-03 18:50 | 0.5565 | 0 | 0.5565 | 0 | 1.5 | 0 | 1.5 | 2 | 98.24%
2026-08-03 18:40 | 1 | 40.47 | 2.769 | 2.808 | 2494.8 | 0.468 | 0.061438 | 0.40656 | 0.36863 | 0.8 | 0.060559 | 0.73944 |  | 2026-08-03 18:40 | 3.033 | 3.222 | 2516.5 | 0.537 | 0.061438 | 0.47556 | 0.36863 | 0.8 | 0.060559 | 0.73944 |  | 2026-08-03 18:40 | 2.589 | 2.722 | 2474.1 | 0.45367 | 0.061438 | 0.39223 | 0.36863 | 0.8 | 0.060559 | 0.73944 |  | 2026-08-03 18:40 | 2.445 | 2.996 | 2493.9 | 0.49933 | 0.061438 | 0.4379 | 0.36863 | 0.8 | 0.060559 | 0.73944 |  | 2026-08-03 18:40 | 1.748 | 1.949 | 1862.4 | 0.32483 | 0.04551 | 0.27932 | 0.27306 | 0.5 | 0.044859 | 0.45514 |  | 2026-08-03 18:40 | 1.614 | 1.697 | 1845.8 | 0.28283 | 0.04551 | 0.23732 | 0.27306 | 0.5 | 0.044859 | 0.45514 |  | 2026-08-03 18:40 | 1.725 | 1.814 | 1844.1 | 0.30233 | 0.04551 | 0.25682 | 0.27306 | 0.5 | 0.044859 | 0.45514 |  | 2026-08-03 18:40 | 1.778 | 2.172 | 1855.8 | 0.362 | 0.04551 | 0.31649 | 0.27306 | 0.5 | 0.044859 | 0.45514 |  | 2026-08-03 18:40 | 1.589 | 1.671 | 1756.6 | 0.2785 | 0.043297 | 0.2352 | 0.25978 | 0.5 | 0.042678 | 0.45732 |  | 2026-08-03 18:40 | 3.5085 | 0.47109 | 3.0374 | 2.8265 | 5.7 | 0.46435 | 5.2356 | 3 | 97.22%
2026-08-03 18:30 | 13 | 43.05 | 6.456 | 6.747 | 2494 | 1.1245 | 0.79107 | 0.33343 | 4.7464 | 1.5 | 0.77976 | 0.72024 |  | 2026-08-03 18:30 | 7.5 | 7.819 | 2515.7 | 1.3032 | 0.79107 | 0.5121 | 4.7464 | 1.7 | 0.77976 | 0.92024 |  | 2026-08-03 18:30 | 6.705 | 6.999 | 2473.3 | 1.1665 | 0.79107 | 0.37543 | 4.7464 | 1.6 | 0.77976 | 0.82024 |  | 2026-08-03 18:30 | 6.901 | 7.204 | 2493.1 | 1.2007 | 0.79107 | 0.4096 | 4.7464 | 1.7 | 0.77976 | 0.92024 |  | 2026-08-03 18:30 | 4.926 | 5.204 | 1861.9 | 0.86733 | 0.58598 | 0.28136 | 3.5159 | 1.2 | 0.5776 | 0.6224 |  | 2026-08-03 18:30 | 4.798 | 5.026 | 1845.3 | 0.83767 | 0.58598 | 0.25169 | 3.5159 | 1.2 | 0.5776 | 0.6224 |  | 2026-08-03 18:30 | 4.689 | 4.916 | 1843.6 | 0.81933 | 0.58598 | 0.23336 | 3.5159 | 1.2 | 0.5776 | 0.6224 |  | 2026-08-03 18:30 | 4.383 | 4.81 | 1855.3 | 0.80167 | 0.58598 | 0.21569 | 3.5159 | 1 | 0.5776 | 0.4224 |  | 2026-08-03 18:30 | 4.239 | 4.449 | 1756.1 | 0.7415 | 0.55748 | 0.18402 | 3.3449 | 1 | 0.54951 | 0.45049 |  | 2026-08-03 18:30 | 8.8623 | 6.0657 | 2.7967 | 36.394 | 12.1 | 5.9789 | 6.1211 | 4 | 98.29%
2026-08-03 18:20 | 26 | 45.35 | 13.141 | 13.572 | 2492.5 | 2.262 | 1.5685 | 0.69346 | 9.4113 | 3 | 1.5461 | 1.4539 |  | 2026-08-03 18:20 | 14.619 | 15.049 | 2514 | 2.5082 | 1.5685 | 0.93962 | 9.4113 | 3.4 | 1.5461 | 1.8539 |  | 2026-08-03 18:20 | 13.964 | 14.393 | 2471.7 | 2.3988 | 1.5685 | 0.83029 | 9.4113 | 3.2 | 1.5461 | 1.6539 |  | 2026-08-03 18:20 | 14.341 | 14.765 | 2491.4 | 2.4608 | 1.5685 | 0.89229 | 9.4113 | 3.2 | 1.5461 | 1.6539 |  | 2026-08-03 18:20 | 10.496 | 10.871 | 1860.7 | 1.8118 | 1.1619 | 0.64995 | 6.9713 | 2.4 | 1.1453 | 1.2547 |  | 2026-08-03 18:20 | 10.127 | 10.507 | 1844.1 | 1.7512 | 1.1619 | 0.58928 | 6.9713 | 2.3 | 1.1453 | 1.1547 |  | 2026-08-03 18:20 | 10.051 | 10.424 | 1842.4 | 1.7373 | 1.1619 | 0.57545 | 6.9713 | 2.2 | 1.1453 | 1.0547 |  | 2026-08-03 18:20 | 7.441 | 7.901 | 1854.3 | 1.3168 | 1.1619 | 0.15495 | 6.9713 | 1.6 | 1.1453 | 0.45473 |  | 2026-08-03 18:20 | 8.385 | 8.717 | 1755.1 | 1.4528 | 1.1054 | 0.34745 | 6.6323 | 1.9 | 1.0896 | 0.81042 |  | 2026-08-03 18:20 | 17.6998 | 12.0271 | 5.6727 | 72.1625 | 23.2 | 11.8551 | 11.3449 | 5 | 98.41%
2026-08-03 18:10 | 38 | 46.78 | 22.956 | 23.48 | 2489.5 | 3.9133 | 2.2801 | 1.6332 | 13.6808 | 4.8 | 2.2475 | 2.5525 |  | 2026-08-03 18:10 | 25.1 | 25.649 | 2510.6 | 4.2748 | 2.2801 | 1.9947 | 13.6808 | 5.1 | 2.2475 | 2.8525 |  | 2026-08-03 18:10 | 24.177 | 24.711 | 2468.5 | 4.1185 | 2.2801 | 1.8384 | 13.6808 | 5.3 | 2.2475 | 3.0525 |  | 2026-08-03 18:10 | 24.377 | 24.928 | 2488.2 | 4.1547 | 2.2801 | 1.8745 | 13.6808 | 5 | 2.2475 | 2.7525 |  | 2026-08-03 18:10 | 18.078 | 18.534 | 1858.3 | 3.089 | 1.689 | 1.4 | 10.1339 | 3.8 | 1.6648 | 2.1352 |  | 2026-08-03 18:10 | 17.377 | 17.821 | 1841.8 | 2.9702 | 1.689 | 1.2812 | 10.1339 | 3.6 | 1.6648 | 1.9352 |  | 2026-08-03 18:10 | 17.543 | 17.991 | 1840.2 | 2.9985 | 1.689 | 1.3095 | 10.1339 | 3.7 | 1.6648 | 2.0352 |  | 2026-08-03 18:10 | 12.654 | 13.321 | 1852.7 | 2.2202 | 1.689 | 0.53118 | 10.1339 | 3 | 1.6648 | 1.3352 |  | 2026-08-03 18:10 | 15.725 | 16.143 | 1753.2 | 2.6905 | 1.6069 | 1.0836 | 9.6412 | 3.4 | 1.5839 | 1.8161 |  | 2026-08-03 18:10 | 30.4297 | 17.4833 | 12.9463 | 104.9 | 37.7 | 17.2333 | 20.4667 | 6 | 98.12%
2026-08-03 18:00 | 51 | 47.93 | 35.528 | 36.153 | 2484.7 | 6.0255 | 3.0468 | 2.9787 | 18.281 | 7.3 | 3.0033 | 4.2967 |  | 2026-08-03 18:00 | 37.522 | 38.19 | 2505.5 | 6.365 | 3.0468 | 3.3182 | 18.281 | 7.4 | 3.0033 | 4.3967 |  | 2026-08-03 18:00 | 37.582 | 38.236 | 2463.2 | 6.3727 | 3.0468 | 3.3258 | 18.281 | 7.1 | 3.0033 | 4.0967 |  | 2026-08-03 18:00 | 36.493 | 37.143 | 2483.2 | 6.1905 | 3.0468 | 3.1437 | 18.281 | 7.3 | 3.0033 | 4.2967 |  | 2026-08-03 18:00 | 27.706 | 28.252 | 1854.5 | 4.7087 | 2.2569 | 2.4517 | 13.5415 | 5.4 | 2.2246 | 3.1754 |  | 2026-08-03 18:00 | 26.38 | 26.935 | 1838.2 | 4.4892 | 2.2569 | 2.2322 | 13.5415 | 5.2 | 2.2246 | 2.9754 |  | 2026-08-03 18:00 | 26.618 | 27.172 | 1836.5 | 4.5287 | 2.2569 | 2.2717 | 13.5415 | 5.3 | 2.2246 | 3.0754 |  | 2026-08-03 18:00 | 24.31 | 25.249 | 1849.7 | 4.2082 | 2.2569 | 1.9512 | 13.5415 | 5.1 | 2.2246 | 2.8754 |  | 2026-08-03 18:00 | 24.616 | 25.161 | 1749.8 | 4.1935 | 2.1472 | 2.0463 | 12.8831 | 4.9 | 2.1165 | 2.7835 |  | 2026-08-03 18:00 | 47.0818 | 23.3622 | 23.7196 | 140.1734 | 55 | 23.0281 | 31.9719 | 7 | 98.03%
2026-08-03 17:50 | 155 | 47.93 | 49.742 | 50.535 | 2477.4 | 8.4225 | 9.26 | -0.83751 | 55.5601 | 22 | 9.1276 | 12.8724 |  | 2026-08-03 17:50 | 51.967 | 52.785 | 2498.1 | 8.7975 | 9.26 | -0.46251 | 55.5601 | 9.6 | 9.1276 | 0.47241 |  | 2026-08-03 17:50 | 51.036 | 51.829 | 2456.1 | 8.6382 | 9.26 | -0.62184 | 55.5601 | 9.7 | 9.1276 | 0.57241 |  | 2026-08-03 17:50 | 50.326 | 51.124 | 2475.9 | 8.5207 | 9.26 | -0.73934 | 55.5601 | 9.7 | 9.1276 | 0.57241 |  | 2026-08-03 17:50 | 37.984 | 38.645 | 1849.1 | 6.4408 | 6.8593 | -0.41843 | 41.1556 | 7.4 | 6.7612 | 0.63882 |  | 2026-08-03 17:50 | 36.473 | 37.119 | 1833 | 6.1865 | 6.8593 | -0.67277 | 41.1556 | 7.1 | 6.7612 | 0.33882 |  | 2026-08-03 17:50 | 36.689 | 37.339 | 1831.2 | 6.2232 | 6.8593 | -0.6361 | 41.1556 | 7.1 | 6.7612 | 0.33882 |  | 2026-08-03 17:50 | 36.472 | 37.303 | 1844.6 | 6.2172 | 6.8593 | -0.6421 | 41.1556 | 7.1 | 6.7612 | 0.33882 |  | 2026-08-03 17:50 | 34.277 | 34.873 | 1744.9 | 5.8122 | 6.5257 | -0.71358 | 39.1545 | 6.6 | 6.4324 | 0.16758 |  | 2026-08-03 17:50 | 65.2587 | 71.0028 | -5.7442 | 426.017 | 86.3 | 69.9875 | 16.3125 | 8 | 97.15%
2026-08-03 17:40 | 211 | 47.93 |  |  |  | 0 | 12.6056 | -12.6056 | 75.6334 | 0 | 12.4253 | -12.4253 |  | 2026-08-03 17:40 | 67.412 | 68.341 | 2488.5 | 11.3902 | 12.6056 | -1.2154 | 75.6334 | 12.8 | 12.4253 | 0.3747 |  | 2026-08-03 17:40 | 67.919 | 68.583 | 2446.4 | 11.4305 | 12.6056 | -1.1751 | 75.6334 | 12.7 | 12.4253 | 0.2747 |  | 2026-08-03 17:40 | 66.982 | 67.899 | 2466.2 | 11.3165 | 12.6056 | -1.2891 | 75.6334 | 12.5 | 12.4253 | 0.074699 |  | 2026-08-03 17:40 | 50.423 | 51.212 | 1841.7 | 8.5353 | 9.3375 | -0.80212 | 56.0247 | 9.3 | 9.2039 | 0.096073 |  | 2026-08-03 17:40 | 48.56 | 49.315 | 1825.9 | 8.2192 | 9.3375 | -1.1183 | 56.0247 | 9.1 | 9.2039 | -0.10393 |  | 2026-08-03 17:40 | 48.944 | 49.725 | 1824.1 | 8.2875 | 9.3375 | -1.05 | 56.0247 | 9.1 | 9.2039 | -0.10393 |  | 2026-08-03 17:40 | 48.748 | 50.181 | 1837.5 | 8.3635 | 9.3375 | -0.97395 | 56.0247 | 9 | 9.2039 | -0.20393 |  | 2026-08-03 17:40 | 45.69 | 46.423 | 1738.3 | 7.7372 | 8.8834 | -1.1463 | 53.3006 | 8.5 | 8.7564 | -0.2564 |  | 2026-08-03 17:40 | 75.2798 | 96.6555 | -21.3756 | 579.9329 | 83 | 95.2733 | -12.2733 | 9 | 98.44%
2026-08-03 17:30 | 257 | 47.35 | 83.813 | 84.044 | 2455.4 | 14.0073 | 15.3876 | -1.3802 | 92.3255 | 15 | 15.1675 | -0.16754 |  | 2026-08-03 17:30 | 84.126 | 85.234 | 2475.7 | 14.2057 | 15.3876 | -1.1819 | 92.3255 | 15.7 | 15.1675 | 0.53246 |  | 2026-08-03 17:30 | 84.083 | 85.454 | 2433.7 | 14.2423 | 15.3876 | -1.1452 | 92.3255 | 15.3 | 15.1675 | 0.13246 |  | 2026-08-03 17:30 | 83.378 | 84.468 | 2453.7 | 14.078 | 15.3876 | -1.3096 | 92.3255 | 15.2 | 15.1675 | 0.032462 |  | 2026-08-03 17:30 | 62.546 | 63.415 | 1832.4 | 10.5692 | 11.3982 | -0.82904 | 68.3892 | 11.5 | 11.2352 | 0.26479 |  | 2026-08-03 17:30 | 60.644 | 61.486 | 1816.8 | 10.2477 | 11.3982 | -1.1505 | 68.3892 | 11.1 | 11.2352 | -0.13521 |  | 2026-08-03 17:30 | 60.984 | 61.831 | 1815 | 10.3052 | 11.3982 | -1.093 | 68.3892 | 11.3 | 11.2352 | 0.064787 |  | 2026-08-03 17:30 | 60.778 | 62.419 | 1828.5 | 10.4032 | 11.3982 | -0.99504 | 68.3892 | 11.3 | 11.2352 | 0.064787 |  | 2026-08-03 17:30 | 57.329 | 57.973 | 1729.8 | 9.6622 | 10.844 | -1.1818 | 65.0639 | 10.6 | 10.6889 | -0.088914 |  | 2026-08-03 17:30 | 107.7207 | 117.9871 | -10.2665 | 707.9228 | 117 | 116.2999 | 0.70008
2026-08-03 17:20 | 288 | 47.64 | 101.269 | 100.451 | 2440.4 | 16.7418 | 17.2247 | -0.48285 | 103.3481 | 18.2 | 16.9784 | 1.2216 |  | 2026-08-03 17:20 | 100.721 | 102.006 | 2460 | 17.001 | 17.2247 | -0.22368 | 103.3481 | 17.9 | 16.9784 | 0.92163 |  | 2026-08-03 17:20 | 100.139 | 102.257 | 2418.4 | 17.0428 | 17.2247 | -0.18185 | 103.3481 | 18 | 16.9784 | 1.0216 |  | 2026-08-03 17:20 | 99.705 | 100.977 | 2438.5 | 16.8295 | 17.2247 | -0.39518 | 103.3481 | 18.1 | 16.9784 | 1.1216 |  | 2026-08-03 17:20 | 74.518 | 75.538 | 1820.9 | 12.5897 | 12.759 | -0.16936 | 76.5541 | 13.7 | 12.5766 | 1.1234 |  | 2026-08-03 17:20 | 72.717 | 73.604 | 1805.7 | 12.2673 | 12.759 | -0.49169 | 76.5541 | 13.3 | 12.5766 | 0.72343 |  | 2026-08-03 17:20 | 72.947 | 73.923 | 1803.7 | 12.3205 | 12.759 | -0.43852 | 76.5541 | 13.2 | 12.5766 | 0.62343 |  | 2026-08-03 17:20 | 72.827 | 74.693 | 1817.2 | 12.4488 | 12.759 | -0.31019 | 76.5541 | 13.2 | 12.5766 | 0.62343 |  | 2026-08-03 17:20 | 68.613 | 69.552 | 1719.2 | 11.592 | 12.1386 | -0.54663 | 72.8318 | 12.5 | 11.965 | 0.53495 |  | 2026-08-03 17:20 | 128.8335 | 132.0735 | -3.24 | 792.4407 | 138.1 | 130.1848 | 7.9152
2026-08-03 17:10 | 352 | 47.93 | 117.608 | 119.085 | 2422.2 | 19.8475 | 21.0292 | -1.1817 | 126.1751 | 21.3 | 20.7285 | 0.57154 |  | 2026-08-03 17:10 | 118.235 | 119.768 | 2442.1 | 19.9613 | 21.0292 | -1.0678 | 126.1751 | 21.1 | 20.7285 | 0.37154 |  | 2026-08-03 17:10 | 117.95 | 120.312 | 2400.4 | 20.052 | 21.0292 | -0.97718 | 126.1751 | 21 | 20.7285 | 0.27154 |  | 2026-08-03 17:10 | 117.637 | 119.174 | 2420.4 | 19.8623 | 21.0292 | -1.1668 | 126.1751 | 20.9 | 20.7285 | 0.17154 |  | 2026-08-03 17:10 | 88.33 | 89.484 | 1807.2 | 14.914 | 15.5772 | -0.66317 | 93.463 | 15.5 | 15.3544 | 0.14558 |  | 2026-08-03 17:10 | 86.025 | 87.14 | 1792.4 | 14.5233 | 15.5772 | -1.0538 | 93.463 | 15.4 | 15.3544 | 0.045582 |  | 2026-08-03 17:10 | 86.318 | 87.455 | 1790.5 | 14.5758 | 15.5772 | -1.0013 | 93.463 | 15.4 | 15.3544 | 0.045582 |  | 2026-08-03 17:10 | 86.165 | 88.643 | 1804 | 14.7738 | 15.5772 | -0.80334 | 93.463 | 15.3 | 15.3544 | -0.054418 |  | 2026-08-03 17:10 | 81.147 | 82.241 | 1706.7 | 13.7068 | 14.8197 | -1.1129 | 88.9185 | 14.4 | 14.6078 | -0.20783 |  | 2026-08-03 17:10 | 152.217 | 161.2452 | -9.0282 | 967.471 | 160.3 | 158.9394 | 1.3606
2026-08-03 17:00 | 394 | 48.22 | 133.712 | 135.432 | 2400.9 | 22.572 | 23.5124 | -0.94037 | 141.0742 | 23.4 | 23.1761 | 0.22386 |  | 2026-08-03 17:00 | 136.81 | 137.295 | 2421 | 22.8825 | 23.5124 | -0.62987 | 141.0742 | 24.4 | 23.1761 | 1.2239 |  | 2026-08-03 17:00 | 133.51 | 136.448 | 2379.4 | 22.7413 | 23.5124 | -0.77104 | 141.0742 | 23.7 | 23.1761 | 0.52386 |  | 2026-08-03 17:00 | 133.554 | 135.327 | 2399.5 | 22.5545 | 23.5124 | -0.95787 | 141.0742 | 23.7 | 23.1761 | 0.52386 |  | 2026-08-03 17:00 | 100.103 | 101.444 | 1791.7 | 16.9073 | 17.4166 | -0.50924 | 104.4994 | 17.7 | 17.1675 | 0.53249 |  | 2026-08-03 17:00 | 97.984 | 99.239 | 1777 | 16.5398 | 17.4166 | -0.87674 | 104.4994 | 17.3 | 17.1675 | 0.13249 |  | 2026-08-03 17:00 | 98.137 | 99.409 | 1775.1 | 16.5682 | 17.4166 | -0.8484 | 104.4994 | 17.3 | 17.1675 | 0.13249 |  | 2026-08-03 17:00 | 98.203 | 100.88 | 1788.7 | 16.8133 | 17.4166 | -0.60324 | 104.4994 | 17.4 | 17.1675 | 0.23249 |  | 2026-08-03 17:00 | 92.633 | 93.834 | 1692.3 | 15.639 | 16.5697 | -0.93071 | 99.4183 | 16.4 | 16.3328 | 0.067238 |  | 2026-08-03 17:00 | 173.218 | 180.2855 | -7.0675 | 1081.7128 | 181.3 | 177.7074 | 3.5926
2026-08-03 16:50 | 439 | 48.22 | 150.045 | 152.021 | 2377.5 | 25.3368 | 26.1978 | -0.86096 | 157.1868 | 26 | 25.8232 | 0.17684 |  | 2026-08-03 16:50 | 151.638 | 153.713 | 2396.6 | 25.6188 | 26.1978 | -0.57896 | 157.1868 | 26.7 | 25.8232 | 0.87684 |  | 2026-08-03 16:50 | 149.762 | 153.174 | 2355.7 | 25.529 | 26.1978 | -0.66879 | 157.1868 | 26.4 | 25.8232 | 0.57684 |  | 2026-08-03 16:50 | 149.759 | 151.762 | 2375.8 | 25.2937 | 26.1978 | -0.90413 | 157.1868 | 26.4 | 25.8232 | 0.57684 |  | 2026-08-03 16:50 | 112.382 | 113.874 | 1774 | 18.979 | 19.4058 | -0.42677 | 116.4346 | 19.8 | 19.1283 | 0.67173 |  | 2026-08-03 16:50 | 109.963 | 111.389 | 1759.7 | 18.5648 | 19.4058 | -0.84094 | 116.4346 | 19.1 | 19.1283 | -0.028269 |  | 2026-08-03 16:50 | 110.144 | 111.583 | 1757.8 | 18.5972 | 19.4058 | -0.80861 | 116.4346 | 19.2 | 19.1283 | 0.071731 |  | 2026-08-03 16:50 | 110.232 | 113.199 | 1771.3 | 18.8665 | 19.4058 | -0.53927 | 116.4346 | 19.4 | 19.1283 | 0.27173 |  | 2026-08-03 16:50 | 103.822 | 105.189 | 1675.9 | 17.5315 | 18.4622 | -0.93069 | 110.7731 | 18.4 | 18.1982 | 0.20182 |  | 2026-08-03 16:50 | 194.3173 | 200.8764 | -6.5591 | 1205.2587 | 201.4 | 198.0039 | 3.3961
2026-08-03 16:40 | 482 | 48.5 | 165.883 | 168.102 | 2351.5 | 28.017 | 28.7332 | -0.71618 | 172.3991 | 28.6 | 28.3223 | 0.2777 |  | 2026-08-03 16:40 | 168.414 | 169.131 | 2369.9 | 28.1885 | 28.7332 | -0.54468 | 172.3991 | 29 | 28.3223 | 0.6777 |  | 2026-08-03 16:40 | 164.532 | 168.329 | 2329.3 | 28.0548 | 28.7332 | -0.67835 | 172.3991 | 28.5 | 28.3223 | 0.1777 |  | 2026-08-03 16:40 | 164.68 | 166.951 | 2349.4 | 27.8252 | 28.7332 | -0.90801 | 172.3991 | 29 | 28.3223 | 0.6777 |  | 2026-08-03 16:40 | 123.645 | 125.299 | 1754.2 | 20.8832 | 21.2838 | -0.40067 | 127.703 | 21.8 | 20.9795 | 0.82052 |  | 2026-08-03 16:40 | 120.799 | 122.454 | 1740.6 | 20.409 | 21.2838 | -0.87484 | 127.703 | 21.3 | 20.9795 | 0.32052 |  | 2026-08-03 16:40 | 120.999 | 122.593 | 1738.6 | 20.4322 | 21.2838 | -0.85167 | 127.703 | 21.4 | 20.9795 | 0.42052 |  | 2026-08-03 16:40 | 121.426 | 124.644 | 1751.9 | 20.774 | 21.2838 | -0.50984 | 127.703 | 21.1 | 20.9795 | 0.12052 |  | 2026-08-03 16:40 | 114.507 | 116.027 | 1657.5 | 19.3378 | 20.2489 | -0.9111 | 121.4936 | 19.8 | 19.9594 | -0.15938 |  | 2026-08-03 16:40 | 213.9217 | 220.317 | -6.3953 | 1321.9021 | 220.5 | 217.1665 | 3.3335
2026-08-03 16:30 | 530 | 49.08 | 180.706 | 183.197 | 2322.9 | 30.5328 | 31.5247 | -0.99186 | 189.1481 | 31.9 | 31.0739 | 0.82611 |  | 2026-08-03 16:30 | 183.086 | 185.686 | 2340.9 | 30.9477 | 31.5247 | -0.57702 | 189.1481 | 31.4 | 31.0739 | 0.32611 |  | 2026-08-03 16:30 | 180.237 | 184.419 | 2300.8 | 30.7365 | 31.5247 | -0.78819 | 189.1481 | 31.4 | 31.0739 | 0.32611 |  | 2026-08-03 16:30 | 180.95 | 183.502 | 2320.4 | 30.5837 | 31.5247 | -0.94102 | 189.1481 | 31 | 31.0739 | -0.073888 |  | 2026-08-03 16:30 | 135.331 | 137.169 | 1732.4 | 22.8615 | 23.3516 | -0.49012 | 140.1097 | 23.2 | 23.0177 | 0.18231 |  | 2026-08-03 16:30 | 132.479 | 134.265 | 1719.3 | 22.3775 | 23.3516 | -0.97412 | 140.1097 | 22.8 | 23.0177 | -0.21769 |  | 2026-08-03 16:30 | 132.521 | 134.335 | 1717.2 | 22.3892 | 23.3516 | -0.96246 | 140.1097 | 22.7 | 23.0177 | -0.31769 |  | 2026-08-03 16:30 | 132.67 | 136.146 | 1730.8 | 22.691 | 23.3516 | -0.66062 | 140.1097 | 23.2 | 23.0177 | 0.18231 |  | 2026-08-03 16:30 | 125.414 | 127.117 | 1637.7 | 21.1862 | 22.2162 | -1.03 | 133.2971 | 21.9 | 21.8985 | 0.0015141 |  | 2026-08-03 16:30 | 234.306 | 241.7214 | -7.4154 | 1450.3286 | 239.5 | 238.2648 | 1.2352
2026-08-03 16:20 | 568 | 48.79 | 0 | 0 | 2291 | 0 | 33.8224 | -33.8224 | 202.9344 | 34.2 | 33.3387 | 0.86126 |  | 2026-08-03 16:20 | 196.779 | 199.634 | 2309.5 | 33.2723 | 33.8224 | -0.55007 | 202.9344 | 70 | 33.3387 | 36.6613 |  | 2026-08-03 16:20 | 194.183 | 199.017 | 2269.4 | 33.1695 | 33.8224 | -0.6529 | 202.9344 | 33.5 | 33.3387 | 0.16126 |  | 2026-08-03 16:20 | 194.576 | 197.379 | 2289.4 | 32.8965 | 33.8224 | -0.9259 | 202.9344 | 33.7 | 33.3387 | 0.36126 |  | 2026-08-03 16:20 | 146.067 | 148.066 | 1709.2 | 24.6777 | 25.0536 | -0.37596 | 150.3218 | 25.3 | 24.6954 | 0.60464 |  | 2026-08-03 16:20 | 143.044 | 145.144 | 1696.5 | 24.1907 | 25.0536 | -0.86296 | 150.3218 | 24.7 | 24.6954 | 0.0046373 |  | 2026-08-03 16:20 | 143.295 | 145.271 | 1694.5 | 24.2118 | 25.0536 | -0.8418 | 150.3218 | 24.8 | 24.6954 | 0.10464 |  | 2026-08-03 16:20 | 143.572 | 147.524 | 1707.6 | 24.5873 | 25.0536 | -0.4663 | 150.3218 | 24.8 | 24.6954 | 0.10464 |  | 2026-08-03 16:20 | 135.676 | 137.519 | 1615.8 | 22.9198 | 23.8354 | -0.91559 | 143.0126 | 23.4 | 23.4946 | -0.094579 |  | 2026-08-03 16:20 | 219.9257 | 259.3395 | -39.4139 | 1556.0373 | 294.4 | 255.631 | 38.769
2026-08-03 16:10 | 613 | 48.5 | 209.441 | 212.458 | 2256.8 | 35.4097 | 36.5424 | -1.1327 | 219.2544 | 35.6 | 36.0198 | -0.41985 | [5 empty] | 0 | 36.5424 | -36.5424 | 219.2544 | 0 | 36.0198 | -36.0198 |  | 2026-08-03 16:10 | 208.132 | 213.358 | 2235.9 | 35.5597 | 36.5424 | -0.98274 | 219.2544 | 36.1 | 36.0198 | 0.08015 |  | 2026-08-03 16:10 | 208.707 | 211.778 | 2255.7 | 35.2963 | 36.5424 | -1.2461 | 219.2544 | 36.1 | 36.0198 | 0.08015 |  | 2026-08-03 16:10 | 156.435 | 158.608 | 1683.9 | 26.4347 | 27.0684 | -0.63378 | 162.4107 | 27.1 | 26.6814 | 0.41863 |  | 2026-08-03 16:10 | 153.507 | 155.943 | 1671.8 | 25.9905 | 27.0684 | -1.0779 | 162.4107 | 26.6 | 26.6814 | -0.08137 |  | 2026-08-03 16:10 | 153.367 | 156.042 | 1669.7 | 26.007 | 27.0684 | -1.0614 | 162.4107 | 26.5 | 26.6814 | -0.18137 |  | 2026-08-03 16:10 | 153.829 | 158.189 | 1682.8 | 26.3648 | 27.0684 | -0.70362 | 162.4107 | 26.2 | 26.6814 | -0.48137 |  | 2026-08-03 16:10 | 145.357 | 147.391 | 1592.4 | 24.5652 | 25.7523 | -1.1871 | 154.5137 | 25.6 | 25.384 | 0.21598 |  | 2026-08-03 16:10 | 235.6278 | 280.1957 | -44.5679 | 1681.1742 | 239.8 | 276.1889 | -36.3889
2026-08-03 16:00 | 655 | 48.5 | 223.468 | 226.756 | 2221.2 | 37.7927 | 39.0461 | -1.2535 | 234.2768 | 39.9 | 38.4878 | 1.4122 |  | 2026-08-03 16:00 | 225.611 | 229.047 | 2239.5 | 38.1745 | 39.0461 | -0.87163 | 234.2768 | 38.6 | 38.4878 | 0.11223 |  | 2026-08-03 16:00 | 222.532 | 227.916 | 2199.8 | 37.986 | 39.0461 | -1.0601 | 234.2768 | 37.4 | 38.4878 | -1.0878 |  | 2026-08-03 16:00 | 223.046 | 226.408 | 2219.6 | 37.7347 | 39.0461 | -1.3115 | 234.2768 | 37.6 | 38.4878 | -0.88777 |  | 2026-08-03 16:00 | 167.409 | 169.786 | 1656.8 | 28.2977 | 28.9231 | -0.62539 | 173.5383 | 28.2 | 28.5095 | -0.30946 |  | 2026-08-03 16:00 | 163.942 | 166.523 | 1645.2 | 27.7538 | 28.9231 | -1.1692 | 173.5383 | 28 | 28.5095 | -0.50946 |  | 2026-08-03 16:00 | 164.199 | 167.085 | 1643.2 | 27.8475 | 28.9231 | -1.0756 | 173.5383 | 28.1 | 28.5095 | -0.40946 |  | 2026-08-03 16:00 | 164.524 | 169.033 | 1656.6 | 28.1722 | 28.9231 | -0.75089 | 173.5383 | 28.2 | 28.5095 | -0.30946 |  | 2026-08-03 16:00 | 155.457 | 157.638 | 1566.8 | 26.273 | 27.5167 | -1.2437 | 165.1002 | 25.9 | 27.1232 | -1.2232 |  | 2026-08-03 16:00 | 290.032 | 299.3934 | -9.3614 | 1796.3607 | 291.9 | 295.1121 | -3.2121
2026-08-03 15:50 | 687 | 48.5 | 234.351 | 237.951 | 2181.3 | 39.6585 | 40.9537 | -1.2952 | 245.7223 | 37.2 | 40.3681 | -3.1681 |  | 2026-08-03 15:50 | 236.308 | 239.98 | 2200.9 | 39.9967 | 40.9537 | -0.95706 | 245.7223 | 40.2 | 40.3681 | -0.16809 |  | 2026-08-03 15:50 | 232.567 | 238.228 | 2162.4 | 39.7047 | 40.9537 | -1.2491 | 245.7223 | 40.2 | 40.3681 | -0.16809 |  | 2026-08-03 15:50 | 233.659 | 237.265 | 2182 | 39.5442 | 40.9537 | -1.4096 | 245.7223 | 40.9 | 40.3681 | 0.53191 |  | 2026-08-03 15:50 | 175.494 | 178.022 | 1628.6 | 29.6703 | 30.3361 | -0.66576 | 182.0166 | 30.3 | 29.9023 | 0.39771 |  | 2026-08-03 15:50 | 171.906 | 174.913 | 1617.2 | 29.1522 | 30.3361 | -1.1839 | 182.0166 | 29.4 | 29.9023 | -0.50229 |  | 2026-08-03 15:50 | 172.228 | 175.262 | 1615.1 | 29.2103 | 30.3361 | -1.1258 | 182.0166 | 29.4 | 29.9023 | -0.50229 |  | 2026-08-03 15:50 | 172.942 | 177.934 | 1628.4 | 29.6557 | 30.3361 | -0.68043 | 182.0166 | 29.6 | 29.9023 | -0.30229 |  | 2026-08-03 15:50 | 163.227 | 165.561 | 1540.9 | 27.5935 | 28.861 | -1.2675 | 173.1662 | 27.9 | 28.4483 | -0.54832 |  | 2026-08-03 15:50 | 304.186 | 314.0203 | -9.8343 | 1884.1218 | 305.1 | 309.5298 | -4.4298
2026-08-03 15:40 | 735 | 48.5 | 249.209 | 253.133 | 2144.1 | 42.1888 | 43.8151 | -1.6263 | 262.8907 | 43.2 | 43.1886 | 0.011436 |  | 2026-08-03 15:40 | 250.643 | 254.641 | 2160.7 | 42.4402 | 43.8151 | -1.375 | 262.8907 | 43.2 | 43.1886 | 0.011436 |  | 2026-08-03 15:40 | 246.644 | 252.768 | 2122.2 | 42.128 | 43.8151 | -1.6871 | 262.8907 | 41.9 | 43.1886 | -1.2886 |  | 2026-08-03 15:40 | 248.705 | 252.698 | 2141.1 | 42.1163 | 43.8151 | -1.6988 | 262.8907 | 41.6 | 43.1886 | -1.5886 |  | 2026-08-03 15:40 | 186.051 | 188.808 | 1598.3 | 31.468 | 32.4556 | -0.98764 | 194.7339 | 31.6 | 31.9915 | -0.39153 |  | 2026-08-03 15:40 | 182.928 | 185.875 | 1587.8 | 30.9792 | 32.4556 | -1.4765 | 194.7339 | 31 | 31.9915 | -0.99153 |  | 2026-08-03 15:40 | 182.785 | 185.738 | 1585.7 | 30.9563 | 32.4556 | -1.4993 | 194.7339 | 31 | 31.9915 | -0.99153 |  | 2026-08-03 15:40 | 183.889 | 189.284 | 1598.8 | 31.5473 | 32.4556 | -0.90831 | 194.7339 | 31.1 | 31.9915 | -0.89153 |  | 2026-08-03 15:40 | 173.608 | 176.127 | 1513 | 29.3545 | 30.8775 | -1.523 | 185.2652 | 29.9 | 30.436 | -0.53598 |  | 2026-08-03 15:40 | 323.1787 | 335.9606 | -12.7819 | 2015.7635 | 324.5 | 331.1563 | -6.6563
2026-08-03 15:30 | 754 | 48.79 | 254.095 | 258.095 | 2100.9 | 43.0158 | 44.898 | -1.8822 | 269.3883 | 43 | 44.256 | -1.256 |  | 2026-08-03 15:30 | 256.847 | 261.023 | 2117.5 | 43.5038 | 44.898 | -1.3942 | 269.3883 | 43.5 | 44.256 | -0.756 |  | 2026-08-03 15:30 | 252.865 | 259.656 | 2080.3 | 43.276 | 44.898 | -1.622 | 269.3883 | 42.6 | 44.256 | -1.656 |  | 2026-08-03 15:30 | 254.135 | 258.241 | 2099.5 | 43.0402 | 44.898 | -1.8579 | 269.3883 | 42.9 | 44.256 | -1.356 |  | 2026-08-03 15:30 | 191.743 | 194.564 | 1566.7 | 32.4273 | 33.2578 | -0.83048 | 199.5469 | 32.3 | 32.7822 | -0.48222 |  | 2026-08-03 15:30 | 188.37 | 191.706 | 1556.8 | 31.951 | 33.2578 | -1.3068 | 199.5469 | 31.8 | 32.7822 | -0.98222 |  | 2026-08-03 15:30 | 189.084 | 192.077 | 1554.7 | 32.0128 | 33.2578 | -1.245 | 199.5469 | 31.9 | 32.7822 | -0.88222 |  | 2026-08-03 15:30 | 190.294 | 195.586 | 1567.7 | 32.5977 | 33.2578 | -0.66014 | 199.5469 | 32 | 32.7822 | -0.78222 |  | 2026-08-03 15:30 | 179.425 | 182.083 | 1483.1 | 30.3472 | 31.6407 | -1.2935 | 189.8441 | 29.7 | 31.1882 | -1.4882 |  | 2026-08-03 15:30 | 332.1718 | 344.2641 | -12.0923 | 2065.5847 | 329.7 | 339.3411 | -9.6411
2026-08-03 15:20 | 778 | 49.36 | 260.374 | 264.673 | 2057.9 | 44.1122 | 46.2263 | -2.1142 | 277.3581 | 42.9 | 45.5653 | -2.6653 |  | 2026-08-03 15:20 | 263.868 | 268.213 | 2074 | 44.7022 | 46.2263 | -1.5242 | 277.3581 | 45.2 | 45.5653 | -0.36531 |  | 2026-08-03 15:20 | 257.882 | 265.236 | 2037.7 | 44.206 | 46.2263 | -2.0203 | 277.3581 | 44.3 | 45.5653 | -1.2653 |  | 2026-08-03 15:20 | 260.47 | 264.786 | 2056.6 | 44.131 | 46.2263 | -2.0953 | 277.3581 | 44.2 | 45.5653 | -1.3653 |  | 2026-08-03 15:20 | 195.236 | 198.189 | 1534.4 | 33.0315 | 34.2417 | -1.2102 | 205.4504 | 33.1 | 33.7521 | -0.65208 |  | 2026-08-03 15:20 | 192.734 | 195.896 | 1525 | 32.6493 | 34.2417 | -1.5924 | 205.4504 | 32.6 | 33.7521 | -1.1521 |  | 2026-08-03 15:20 | 192.757 | 195.862 | 1522.8 | 32.6437 | 34.2417 | -1.5981 | 205.4504 | 32.6 | 33.7521 | -1.1521 |  | 2026-08-03 15:20 | 193.581 | 198.962 | 1535.7 | 33.1603 | 34.2417 | -1.0814 | 205.4504 | 32.7 | 33.7521 | -1.0521 |  | 2026-08-03 15:20 | 183.334 | 186.118 | 1453.4 | 31.0197 | 32.5768 | -1.5571 | 195.4606 | 31 | 32.1109 | -1.1109 |  | 2026-08-03 15:20 | 339.6558 | 354.4491 | -14.7933 | 2126.6945 | 338.6 | 349.3805 | -10.7805
2026-08-03 15:10 | 810 | 48.79 | 270.117 | 274.081 | 2015 | 45.6802 | 48.2326 | -2.5525 | 289.3959 | 46.6 | 47.5429 | -0.94292 |  | 2026-08-03 15:10 | 274.042 | 278.64 | 2028.8 | 46.44 | 48.2326 | -1.7926 | 289.3959 | 46.7 | 47.5429 | -0.84292 |  | 2026-08-03 15:10 | 267.331 | 274.682 | 1993.4 | 45.7803 | 48.2326 | -2.4523 | 289.3959 | 44.4 | 47.5429 | -3.1429 |  | 2026-08-03 15:10 | 270.196 | 274.729 | 2012.4 | 45.7882 | 48.2326 | -2.4445 | 289.3959 | 45.3 | 47.5429 | -2.2429 |  | 2026-08-03 15:10 | 201.276 | 204.383 | 1501.3 | 34.0638 | 35.7279 | -1.6641 | 214.3673 | 34.3 | 35.217 | -0.91698 |  | 2026-08-03 15:10 | 198.63 | 201.963 | 1492.4 | 33.6605 | 35.7279 | -2.0674 | 214.3673 | 33.8 | 35.217 | -1.417 |  | 2026-08-03 15:10 | 198.431 | 202.341 | 1490.2 | 33.7235 | 35.7279 | -2.0044 | 214.3673 | 33.8 | 35.217 | -1.417 |  | 2026-08-03 15:10 | 199.543 | 205.317 | 1503 | 34.2195 | 35.7279 | -1.5084 | 214.3673 | 34.1 | 35.217 | -1.117 |  | 2026-08-03 15:10 | 188.747 | 191.621 | 1422.4 | 31.9368 | 33.9907 | -2.0538 | 203.944 | 32.2 | 33.5046 | -1.3046 |  | 2026-08-03 15:10 | 351.2928 | 369.8328 | -18.54 | 2218.9968 | 351.2 | 364.5442 | -13.3442
2026-08-03 15:00 | 838 | 49.08 | 279.194 | 283.073 | 1968.4 | 47.1788 | 49.8447 | -2.6659 | 299.0682 | 47 | 49.1319 | -2.1319 | 0.9863 | 2026-08-03 15:00 | 282.41 | 287.148 | 1982.1 | 47.858 | 49.8447 | -1.9867 | 299.0682 | 48.3 | 49.1319 | -0.83192 | 0.9835 | 2026-08-03 15:00 | 276.626 | 284.108 | 1949 | 47.3513 | 49.8447 | -2.4934 | 299.0682 | 47.3 | 49.1319 | -1.8319 | 0.97366 | 2026-08-03 15:00 | 278.883 | 283.619 | 1967.1 | 47.2698 | 49.8447 | -2.5749 | 299.0682 | 48.4 | 49.1319 | -0.73192 | 0.9833 | 2026-08-03 15:00 | 208.863 | 212.108 | 1467 | 35.3513 | 36.922 | -1.5707 | 221.532 | 35.8 | 36.394 | -0.59402 | 0.9847 | 2026-08-03 15:00 | 205.384 | 209.203 | 1458.6 | 34.8672 | 36.922 | -2.0548 | 221.532 | 35.2 | 36.394 | -1.194 | 0.98175 | 2026-08-03 15:00 | 205.403 | 209.511 | 1456.4 | 34.9185 | 36.922 | -2.0035 | 221.532 | 35.2 | 36.394 | -1.194 | 0.98039 | 2026-08-03 15:00 | 206.161 | 212.277 | 1468.9 | 35.3795 | 36.922 | -1.5425 | 221.532 | 35.3 | 36.394 | -1.094 | 0.97119 | 2026-08-03 15:00 | 195.203 | 198.196 | 1390.2 | 33.0327 | 35.1267 | -2.094 | 210.7603 | 33.4 | 34.6244 | -1.2244 | 0.9849 | 2026-08-03 15:00 | 363.2072 | 382.1935 | -18.9863 | 2293.1611 | 365.9 | 376.7281 | -10.8281
2026-08-03 14:50 | 879 | 49.36 | 291.751 | 296.623 | 1921.4 | 49.4372 | 52.2274 | -2.7903 | 313.3647 | 49 | 51.4806 | -2.4806 | 0.98358 | 2026-08-03 14:50 | 293.731 | 299.293 | 1933.8 | 49.8822 | 52.2274 | -2.3453 | 313.3647 | 99.8 | 51.4806 | 48.3194 | 0.98142 | 2026-08-03 14:50 | 289.271 | 297.288 | 1901.7 | 49.548 | 52.2274 | -2.6794 | 313.3647 | 49.1 | 51.4806 | -2.3806 | 0.97303 | 2026-08-03 14:50 | 290.471 | 295.464 | 1918.7 | 49.244 | 52.2274 | -2.9834 | 313.3647 | 48.8 | 51.4806 | -2.6806 | 0.9831 | 2026-08-03 14:50 | 217.774 | 221.18 | 1431.2 | 36.8633 | 38.687 | -1.8237 | 232.122 | 36.5 | 38.1338 | -1.6338 | 0.9846 | 2026-08-03 14:50 | 213.972 | 218.035 | 1423.4 | 36.3392 | 38.687 | -2.3478 | 232.122 | 35.9 | 38.1338 | -2.2338 | 0.98137 | 2026-08-03 14:50 | 214.033 | 218.004 | 1421.2 | 36.334 | 38.687 | -2.353 | 232.122 | 35.9 | 38.1338 | -2.2338 | 0.98178 | 2026-08-03 14:50 | 214.73 | 220.77 | 1433.6 | 36.795 | 38.687 | -1.892 | 232.122 | 36.1 | 38.1338 | -2.0338 | 0.97264 | 2026-08-03 14:50 | 202.765 | 205.895 | 1356.8 | 34.3158 | 36.8059 | -2.4901 | 220.8353 | 34.1 | 36.2796 | -2.1796 | 0.9848 | 2026-08-03 14:50 | 378.7587 | 400.4637 | -21.705 | 2402.7821 | 425.2 | 394.7371 | 30.4629
2026-08-03 14:40 | 899 | 49.36 | 298.315 | 303.381 | 1872.4 | 50.5635 | 53.4158 | -2.8523 | 320.4947 | 51.2 | 52.6519 | -1.4519 | 0.9833 |  |  |  |  | 0 | 53.4158 | -53.4158 | 320.4947 | 0 | 52.6519 | -52.6519 |  | 2026-08-03 14:40 | 295.276 | 303.905 | 1852.6 | 50.6508 | 53.4158 | -2.765 | 320.4947 | 49.4 | 52.6519 | -3.2519 | 0.97161 | 2026-08-03 14:40 | 293.83 | 298.972 | 1869.9 | 49.8287 | 53.4158 | -3.5871 | 320.4947 | 49.7 | 52.6519 | -2.9519 | 0.9828 | 2026-08-03 14:40 | 222.469 | 226.04 | 1394.7 | 37.6733 | 39.5672 | -1.8939 | 237.4035 | 37.3 | 39.0014 | -1.7014 | 0.9842 | 2026-08-03 14:40 | 218.674 | 222.964 | 1387.5 | 37.1607 | 39.5672 | -2.4066 | 237.4035 | 36.7 | 39.0014 | -2.3014 | 0.98076 | 2026-08-03 14:40 | 219.135 | 223.376 | 1385.3 | 37.2293 | 39.5672 | -2.3379 | 237.4035 | 37.2 | 39.0014 | -1.8014 | 0.98101 | 2026-08-03 14:40 | 220.164 | 226.497 | 1397.5 | 37.7495 | 39.5672 | -1.8177 | 237.4035 | 37.4 | 39.0014 | -1.6014 | 0.97204 | 2026-08-03 14:40 | 208.415 | 211.696 | 1322.7 | 35.2827 | 37.6433 | -2.3607 | 225.86 | 35.4 | 37.105 | -1.705 | 0.9845 | 2026-08-03 14:40 | 336.1385 | 409.5755 | -73.437 | 2457.4529 | 334.3 | 403.7186 | -69.4186
2026-08-03 14:30 | 935 | 49.08 | 307.243 | 312.62 | 1821.2 | 52.1033 | 55.6143 | -3.511 | 333.6859 | 53.6 | 54.819 | -1.219 | 0.9828 | 2026-08-03 14:30 | 310.251 | 315.777 | 1834 | 52.6295 | 55.6143 | -2.9848 | 333.6859 | 53.5 | 54.819 | -1.319 | 0.9825 | 2026-08-03 14:30 | 304.267 | 312.715 | 1803.2 | 52.1192 | 55.6143 | -3.4951 | 333.6859 | 51.6 | 54.819 | -3.219 | 0.97298 | 2026-08-03 14:30 | 305.48 | 310.953 | 1820.2 | 51.8255 | 55.6143 | -3.7888 | 333.6859 | 51.8 | 54.819 | -3.019 | 0.9824 | 2026-08-03 14:30 | 229.636 | 233.37 | 1357.4 | 38.895 | 41.1958 | -2.3008 | 247.1747 | 38.9 | 40.6067 | -1.7067 | 0.984 | 2026-08-03 14:30 | 225.577 | 229.844 | 1350.8 | 38.3073 | 41.1958 | -2.8885 | 247.1747 | 38.3 | 40.6067 | -2.3067 | 0.98144 | 2026-08-03 14:30 | 225.982 | 230.396 | 1348.1 | 38.3993 | 41.1958 | -2.7965 | 247.1747 | 38 | 40.6067 | -2.6067 | 0.98084 | 2026-08-03 14:30 | 226.92 | 233.428 | 1360.1 | 38.9047 | 41.1958 | -2.2911 | 247.1747 | 38.2 | 40.6067 | -2.4067 | 0.97212 | 2026-08-03 14:30 | 214.62 | 218.043 | 1287.3 | 36.3405 | 39.1927 | -2.8522 | 235.1561 | 35.9 | 38.6322 | -2.7322 | 0.9843 | 2026-08-03 14:30 | 399.5243 | 426.4331 | -26.9088 | 2558.5986 | 399.8 | 420.3351 | -20.5351
2026-08-03 14:20 | 956 | 49.36 | 313.098 | 318.61 | 1767.6 | 53.1017 | 56.8026 | -3.7009 | 340.8153 | 51.7 | 55.9903 | -4.2903 | 0.9827 | 2026-08-03 14:20 | 316.196 | 321.854 | 1780.5 | 53.6423 | 56.8026 | -3.1602 | 340.8153 | 52.5 | 55.9903 | -3.4903 | 0.98242 | 2026-08-03 14:20 | 309.555 | 318.995 | 1751.6 | 53.1658 | 56.8026 | -3.6367 | 340.8153 | 52 | 55.9903 | -3.9903 | 0.97041 | 2026-08-03 14:20 | 311.93 | 317.518 | 1768.4 | 52.9197 | 56.8026 | -3.8829 | 340.8153 | 52.5 | 55.9903 | -3.4903 | 0.9824 | 2026-08-03 14:20 | 233.849 | 237.7 | 1318.5 | 39.6167 | 42.076 | -2.4593 | 252.4558 | 39.3 | 41.4743 | -2.1743 | 0.9838 | 2026-08-03 14:20 | 230.208 | 234.845 | 1312.5 | 39.1408 | 42.076 | -2.9351 | 252.4558 | 38.6 | 41.4743 | -2.8743 | 0.98026 | 2026-08-03 14:20 | 230.646 | 235.663 | 1310.1 | 39.2772 | 42.076 | -2.7988 | 252.4558 | 38.8 | 41.4743 | -2.6743 | 0.97871 | 2026-08-03 14:20 | 232.285 | 238.866 | 1321.9 | 39.811 | 42.076 | -2.265 | 252.4558 | 39.1 | 41.4743 | -2.3743 | 0.97245 | 2026-08-03 14:20 | 219.658 | 223.021 | 1251.4 | 37.1702 | 40.0301 | -2.8599 | 240.1804 | 37.4 | 39.4576 | -2.0576 | 0.98492 | 2026-08-03 14:20 | 407.8453 | 435.5441 | -27.6988 | 2613.2647 | 401.9 | 429.3158 | -27.4158
2026-08-03 14:10 | 968 | 49.08 | 317.03 | 322.642 | 1715.9 | 53.7737 | 57.5772 | -3.8035 | 345.463 | 51.6 | 56.7538 | -5.1538 | 0.98261 | 2026-08-03 14:10 | 320.251 | 326.022 | 1728 | 54.337 | 57.5772 | -3.2402 | 345.463 | 55.2 | 56.7538 | -1.5538 | 0.9823 | 2026-08-03 14:10 | 313.745 | 322.813 | 1699.6 | 53.8022 | 57.5772 | -3.775 | 345.463 | 53.2 | 56.7538 | -3.5538 | 0.97191 | 2026-08-03 14:10 | 315.67 | 321.325 | 1715.9 | 53.5542 | 57.5772 | -4.023 | 345.463 | 53.7 | 56.7538 | -3.0538 | 0.9824 | 2026-08-03 14:10 | 237.03 | 240.958 | 1279.2 | 40.1597 | 42.6498 | -2.4901 | 255.8985 | 40.1 | 42.0399 | -1.9399 | 0.9837 | 2026-08-03 14:10 | 232.937 | 237.645 | 1273.9 | 39.6075 | 42.6498 | -3.0423 | 255.8985 | 39.5 | 42.0399 | -2.5399 | 0.98019 | 2026-08-03 14:10 | 234.537 | 239.317 | 1271.3 | 39.8862 | 42.6498 | -2.7636 | 255.8985 | 39.5 | 42.0399 | -2.5399 | 0.98003 | 2026-08-03 14:10 | 235.887 | 242.74 | 1282.8 | 40.4567 | 42.6498 | -2.1931 | 255.8985 | 39.7 | 42.0399 | -2.3399 | 0.97177 | 2026-08-03 14:10 | 222.105 | 225.671 | 1214 | 37.6118 | 40.576 | -2.9641 | 243.4558 | 37 | 39.9957 | -2.9957 | 0.9842 | 2026-08-03 14:10 | 413.1888 | 441.4837 | -28.2948 | 2648.9021 | 409.5 | 435.1705 | -25.6705
2026-08-03 14:00 | 1000 | 49.36 | 327.182 | 333.01 | 1664.3 | 55.5017 | 59.4169 | -3.9152 | 356.5014 | 56.1 | 58.5672 | -2.4672 | 0.9825 | 2026-08-03 14:00 | 331.976 | 337.439 | 1672.8 | 56.2398 | 59.4169 | -3.1771 | 356.5014 | 54.4 | 58.5672 | -4.1672 | 0.98381 | 2026-08-03 14:00 | 323.969 | 333.514 | 1646.4 | 55.5857 | 59.4169 | -3.8312 | 356.5014 | 54 | 58.5672 | -4.5672 | 0.97138 | 2026-08-03 14:00 | 326.669 | 332.651 | 1662.2 | 55.4418 | 59.4169 | -3.9751 | 356.5014 | 55.2 | 58.5672 | -3.3672 | 0.98202 | 2026-08-03 14:00 | 243.9 | 247.967 | 1239.1 | 41.3278 | 44.0125 | -2.6847 | 264.0751 | 40.8 | 43.3831 | -2.5831 | 0.9836 | 2026-08-03 14:00 | 240.821 | 245.512 | 1234.4 | 40.9187 | 44.0125 | -3.0938 | 264.0751 | 40.3 | 43.3831 | -3.0831 | 0.98089 | 2026-08-03 14:00 | 240.386 | 245.542 | 1231.8 | 40.9237 | 44.0125 | -3.0888 | 264.0751 | 40.2 | 43.3831 | -3.1831 | 0.979 | 2026-08-03 14:00 | 242.904 | 249.933 | 1243.1 | 41.6555 | 44.0125 | -2.357 | 264.0751 | 40.6 | 43.3831 | -2.7831 | 0.97188 | 2026-08-03 14:00 | 229.209 | 233.005 | 1177 | 38.8342 | 41.8725 | -3.0383 | 251.2347 | 38.3 | 41.2737 | -2.9737 | 0.98371 | 2026-08-03 14:00 | 426.4288 | 455.5901 | -29.1613 | 2733.5405 | 419.9 | 449.0751 | -29.1751
2026-08-03 13:50 | 1015 | 48.5 | 329.861 | 335.825 | 1608.2 | 55.9708 | 60.5066 | -4.5358 | 363.0396 | 54.8 | 59.6413 | -4.8413 | 0.98224 | 2026-08-03 13:50 | 335.074 | 341.146 | 1618.4 | 56.8577 | 60.5066 | -3.6489 | 363.0396 | 56.3 | 59.6413 | -3.3413 | 0.9822 | 2026-08-03 13:50 | 327.421 | 337.355 | 1592.4 | 56.2258 | 60.5066 | -4.2808 | 363.0396 | 55.2 | 59.6413 | -4.4413 | 0.97055 | 2026-08-03 13:50 | 331.396 | 337.436 | 1607 | 56.2393 | 60.5066 | -4.2673 | 363.0396 | 55.1 | 59.6413 | -4.5413 | 0.9821 | 2026-08-03 13:50 | 247.291 | 251.383 | 1198.3 | 41.8972 | 44.8197 | -2.9225 | 268.9182 | 41.5 | 44.1788 | -2.6788 | 0.98372 | 2026-08-03 13:50 | 244.264 | 249.573 | 1194.1 | 41.5955 | 44.8197 | -3.2242 | 268.9182 | 40.9 | 44.1788 | -3.2788 | 0.97873 | 2026-08-03 13:50 | 243.686 | 249.072 | 1191.6 | 41.512 | 44.8197 | -3.3077 | 268.9182 | 40.9 | 44.1788 | -3.2788 | 0.97838 | 2026-08-03 13:50 | 246.064 | 253.053 | 1202.5 | 42.1755 | 44.8197 | -2.6442 | 268.9182 | 41.7 | 44.1788 | -2.4788 | 0.97238 | 2026-08-03 13:50 | 233.027 | 236.606 | 1138.7 | 39.4343 | 42.6404 | -3.2061 | 255.8424 | 39.5 | 42.0306 | -2.5306 | 0.98487 | 2026-08-03 13:50 | 431.9082 | 463.9456 | -32.0374 | 2783.6734 | 425.9 | 457.3111 | -31.4111
2026-08-03 13:40 | 1032 | 48.5 | 335.81 | 341.861 | 1553.4 | 56.9768 | 61.52 | -4.5432 | 369.12 | 56.2 | 60.6403 | -4.4403 | 0.9823 | 2026-08-03 13:40 | 340.016 | 346.487 | 1562.1 | 57.7478 | 61.52 | -3.7722 | 369.12 | 169.1 | 60.6403 | 108.4597 | 0.98132 | 2026-08-03 13:40 | 332.773 | 342.734 | 1537.2 | 57.1223 | 61.52 | -4.3977 | 369.12 | 55.7 | 60.6403 | -4.9403 | 0.97094 | 2026-08-03 13:40 | 335.153 | 341.262 | 1551.9 | 56.877 | 61.52 | -4.643 | 369.12 | 55.8 | 60.6403 | -4.8403 | 0.9821 | 2026-08-03 13:40 | 250.352 | 254.526 | 1156.8 | 42.421 | 45.5704 | -3.1494 | 273.4222 | 42 | 44.9187 | -2.9187 | 0.9836 | 2026-08-03 13:40 | 246.876 | 251.932 | 1153.2 | 41.9887 | 45.5704 | -3.5817 | 273.4222 | 41.5 | 44.9187 | -3.4187 | 0.97993 | 2026-08-03 13:40 | 247.028 | 252.622 | 1150.7 | 42.1037 | 45.5704 | -3.4667 | 273.4222 | 41.5 | 44.9187 | -3.4187 | 0.97786 | 2026-08-03 13:40 | 248.594 | 255.78 | 1160.8 | 42.63 | 45.5704 | -2.9404 | 273.4222 | 41.8 | 44.9187 | -3.1187 | 0.97191 | 2026-08-03 13:40 | 234.748 | 238.638 | 1099.2 | 39.773 | 43.3546 | -3.5816 | 260.1274 | 39.5 | 42.7346 | -3.2346 | 0.9837 | 2026-08-03 13:40 | 437.6403 | 471.7161 | -34.0758 | 2830.2965 | 543.1 | 464.9705 | 78.1295
2026-08-03 13:30 | 1048 | 47.64 | 338.431 | 344.529 | 1497.2 | 57.4215 | 62.6787 | -5.2572 | 376.0722 | 57.5 | 61.7824 | -4.2824 | 0.9823 |  |  |  |  | 0 | 62.6787 | -62.6787 | 376.0722 | 0 | 61.7824 | -61.7824 |  | 2026-08-03 13:30 | 334.624 | 344.542 | 1481.5 | 57.4237 | 62.6787 | -5.255 | 376.0722 | 56.1 | 61.7824 | -5.6824 | 0.97121 | 2026-08-03 13:30 | 338.04 | 344.236 | 1496.1 | 57.3727 | 62.6787 | -5.306 | 376.0722 | 55.9 | 61.7824 | -5.8824 | 0.982 | 2026-08-03 13:30 | 252.623 | 256.861 | 1114.8 | 42.8102 | 46.4287 | -3.6185 | 278.572 | 42.4 | 45.7647 | -3.3647 | 0.9835 | 2026-08-03 13:30 | 250.039 | 254.919 | 1111.7 | 42.4865 | 46.4287 | -3.9422 | 278.572 | 41.9 | 45.7647 | -3.8647 | 0.98086 | 2026-08-03 13:30 | 249.965 | 255.595 | 1109.2 | 42.5992 | 46.4287 | -3.8295 | 278.572 | 41.9 | 45.7647 | -3.8647 | 0.97797 | 2026-08-03 13:30 | 251.918 | 259.053 | 1119 | 43.1755 | 46.4287 | -3.2532 | 278.572 | 42.2 | 45.7647 | -3.5647 | 0.97246 | 2026-08-03 13:30 | 238.318 | 242.267 | 1059.7 | 40.3778 | 44.1711 | -3.7933 | 265.0268 | 39.9 | 43.5395 | -3.6395 | 0.9837 | 2026-08-03 13:30 | 383.667 | 480.6006 | -96.9336 | 2883.6037 | 377.8 | 473.728 | -95.928
2026-08-03 13:20 | 1055 | 47.93 | 341.016 | 347.273 | 1439.7 | 57.8788 | 63.0278 | -5.149 | 378.1668 | 55.5 | 62.1265 | -6.6265 | 0.98198 |  |  |  |  | 0 | 63.0278 | -63.0278 | 378.1668 | 0 | 62.1265 | -62.1265 |  | 2026-08-03 13:20 | 338.68 | 348.561 | 1425.4 | 58.0935 | 63.0278 | -4.9343 | 378.1668 | 57.4 | 62.1265 | -4.7265 | 0.97165 | 2026-08-03 13:20 | 340.452 | 346.446 | 1440.2 | 57.741 | 63.0278 | -5.2868 | 378.1668 | 56.4 | 62.1265 | -5.7265 | 0.9827 | 2026-08-03 13:20 | 255.759 | 260.05 | 1072.4 | 43.3417 | 46.6873 | -3.3456 | 280.1236 | 42.9 | 46.0196 | -3.1196 | 0.9835 | 2026-08-03 13:20 | 252.326 | 257.574 | 1069.8 | 42.929 | 46.6873 | -3.7583 | 280.1236 | 42.4 | 46.0196 | -3.6196 | 0.97963 | 2026-08-03 13:20 | 252.897 | 258.276 | 1067.3 | 43.046 | 46.6873 | -3.6413 | 280.1236 | 42.3 | 46.0196 | -3.7196 | 0.97917 | 2026-08-03 13:20 | 254.945 | 262.7 | 1076.8 | 43.7833 | 46.6873 | -2.9039 | 280.1236 | 42.1 | 46.0196 | -3.9196 | 0.97048 | 2026-08-03 13:20 | 241.116 | 245.062 | 1019.8 | 40.8437 | 44.4171 | -3.5735 | 266.5029 | 39.8 | 43.782 | -3.982 | 0.9839 | 2026-08-03 13:20 | 387.657 | 483.2774 | -95.6204 | 2899.6644 | 378.8 | 476.3665 | -97.5665
2026-08-03 13:10 | 1064 | 47.93 | 343.277 | 349.534 | 1384.2 | 58.2557 | 63.5655 | -5.3098 | 381.3929 | 57.5 | 62.6565 | -5.1565 | 0.9821 | 2026-08-03 13:10 | 332.483 | 340.78 | 1393 | 56.7967 | 63.5655 | -6.7688 | 381.3929 | 57.7 | 62.6565 | -4.9565 | 0.97565 | 2026-08-03 13:10 | 339.339 | 350.188 | 1368 | 58.3647 | 63.5655 | -5.2008 | 381.3929 | 55.2 | 62.6565 | -7.4565 | 0.96902 | 2026-08-03 13:10 | 340.142 | 346.024 | 1383.8 | 57.6707 | 63.5655 | -5.8948 | 381.3929 | 56.8 | 62.6565 | -5.8565 | 0.983 | 2026-08-03 13:10 | 256.225 | 260.577 | 1029.5 | 43.4295 | 47.0855 | -3.656 | 282.5132 | 42.3 | 46.4122 | -4.1122 | 0.9833 | 2026-08-03 13:10 | 253.555 | 258.643 | 1027.4 | 43.1072 | 47.0855 | -3.9784 | 282.5132 | 42.6 | 46.4122 | -3.8122 | 0.98033 | 2026-08-03 13:10 | 252.601 | 257.77 | 1025 | 42.9617 | 47.0855 | -4.1239 | 282.5132 | 42.6 | 46.4122 | -3.8122 | 0.97995 | 2026-08-03 13:10 | 254.244 | 261.678 | 1034.7 | 43.613 | 47.0855 | -3.4725 | 282.5132 | 42.9 | 46.4122 | -3.5122 | 0.97159 | 2026-08-03 13:10 | 241.087 | 245.107 | 980 | 40.8512 | 44.7961 | -3.9449 | 268.7764 | 40.7 | 44.1555 | -3.4555 | 0.9836 | 2026-08-03 13:10 | 445.0502 | 487.4001 | -42.35 | 2924.4009 | 438.3 | 480.4303 | -42.1303
2026-08-03 13:00 | 1058 | 47.93 | 342.64 | 348.885 | 1326.7 | 58.1475 | 63.207 | -5.0595 | 379.2422 | 58.5 | 62.3032 | -3.8032 | 0.9821 | 2026-08-03 13:00 | 348.151 | 354.569 | 1335.3 | 59.0948 | 63.207 | -4.1122 | 379.2422 | 57.8 | 62.3032 | -4.5032 | 0.9819 | 2026-08-03 13:00 | 339.207 | 349.725 | 1312.8 | 58.2875 | 63.207 | -4.9195 | 379.2422 | 56.5 | 62.3032 | -5.8032 | 0.96992 | 2026-08-03 13:00 | 343.021 | 349.309 | 1327 | 58.2182 | 63.207 | -4.9889 | 379.2422 | 57 | 62.3032 | -5.3032 | 0.982 | 2026-08-03 13:00 | 256.789 | 261.096 | 987.2 | 43.516 | 46.82 | -3.304 | 280.9201 | 43.4 | 46.1505 | -2.7505 | 0.9835 | 2026-08-03 13:00 | 254.362 | 259.896 | 984.8 | 43.316 | 46.82 | -3.504 | 280.9201 | 42.3 | 46.1505 | -3.8505 | 0.97871 | 2026-08-03 13:00 | 254.39 | 260.07 | 982.4 | 43.345 | 46.82 | -3.475 | 280.9201 | 42.2 | 46.1505 | -3.9505 | 0.97816 | 2026-08-03 13:00 | 256.728 | 264.197 | 991.8 | 44.0328 | 46.82 | -2.7872 | 280.9201 | 42.7 | 46.1505 | -3.4505 | 0.97173 | 2026-08-03 13:00 | 242.853 | 246.852 | 939.3 | 41.142 | 44.5435 | -3.4015 | 267.2607 | 40.3 | 43.9065 | -3.6065 | 0.9838 | 2026-08-03 13:00 | 449.0998 | 484.6517 | -35.5518 | 2907.9099 | 440.7 | 477.7211 | -37.0211
2026-08-03 12:50 | 1066 | 47.64 | 342.647 | 348.963 | 1268.2 | 58.1605 | 63.7552 | -5.5947 | 382.5315 | 55.4 | 62.8435 | -7.4435 | 0.9819 | 2026-08-03 12:50 | 345.503 | 351.585 | 1277.5 | 58.5975 | 63.7552 | -5.1577 | 382.5315 | 57.9 | 62.8435 | -4.9435 | 0.9827 | 2026-08-03 12:50 | 339.059 | 349.088 | 1256.3 | 58.1813 | 63.7552 | -5.5739 | 382.5315 | 56.1 | 62.8435 | -6.7435 | 0.97127 | 2026-08-03 12:50 | 336.46 | 342.209 | 1270 | 57.0348 | 63.7552 | -6.7204 | 382.5315 | 56.7 | 62.8435 | -6.1435 | 0.9832 | 2026-08-03 12:50 | 256.618 | 260.976 | 943.8 | 43.496 | 47.2261 | -3.7301 | 283.3566 | 41.8 | 46.5508 | -4.7508 | 0.9833 | 2026-08-03 12:50 | 255.136 | 260.196 | 942.5 | 43.366 | 47.2261 | -3.8601 | 283.3566 | 42 | 46.5508 | -4.5508 | 0.98055 | 2026-08-03 12:50 | 254.095 | 259.333 | 940.2 | 43.2222 | 47.2261 | -4.0039 | 283.3566 | 42 | 46.5508 | -4.5508 | 0.9798 | 2026-08-03 12:50 | 256.826 | 264.525 | 949.1 | 44.0875 | 47.2261 | -3.1386 | 283.3566 | 42.4 | 46.5508 | -4.1508 | 0.9709 | 2026-08-03 12:50 | 243.435 | 247.494 | 899 | 41.249 | 44.9298 | -3.6808 | 269.5788 | 40.2 | 44.2873 | -4.0873 | 0.9836 | 2026-08-03 12:50 | 447.3948 | 488.8552 | -41.4604 | 2933.1312 | 434.5 | 481.8646 | -47.3646
2026-08-03 12:40 | 1056 | 47.93 | 340.549 | 346.721 | 1212.8 | 57.7868 | 63.0875 | -5.3007 | 378.5253 | 56.4 | 62.1854 | -5.7854 | 0.9822 | 2026-08-03 12:40 | 345.567 | 351.937 | 1219.6 | 58.6562 | 63.0875 | -4.4314 | 378.5253 | 55.4 | 62.1854 | -6.7854 | 0.9819 | 2026-08-03 12:40 | 335.885 | 346.059 | 1200.2 | 57.6765 | 63.0875 | -5.411 | 378.5253 | 56.6 | 62.1854 | -5.5854 | 0.9706 | 2026-08-03 12:40 | 341.56 | 347.856 | 1213.3 | 57.976 | 63.0875 | -5.1115 | 378.5253 | 57 | 62.1854 | -5.1854 | 0.9819 | 2026-08-03 12:40 | 253.023 | 257.32 | 902 | 42.8867 | 46.7315 | -3.8448 | 280.3891 | 42.8 | 46.0633 | -3.2633 | 0.9833 | 2026-08-03 12:40 | 251.272 | 256.228 | 900.5 | 42.7047 | 46.7315 | -4.0268 | 280.3891 | 41.9 | 46.0633 | -4.1633 | 0.98066 | 2026-08-03 12:40 | 249.71 | 255.035 | 898.2 | 42.5058 | 46.7315 | -4.2257 | 280.3891 | 41.8 | 46.0633 | -4.2633 | 0.97912 | 2026-08-03 12:40 | 252.012 | 259.638 | 906.7 | 43.273 | 46.7315 | -3.4585 | 280.3891 | 42.1 | 46.0633 | -3.9633 | 0.97063 | 2026-08-03 12:40 | 239.91 | 243.885 | 858.8 | 40.6475 | 44.4592 | -3.8117 | 266.7555 | 39.9 | 43.8235 | -3.9235 | 0.9837 | 2026-08-03 12:40 | 444.1132 | 483.7355 | -39.6223 | 2902.4129 | 433.9 | 476.8181 | -42.9181
2026-08-03 12:30 | 1056 | 48.22 | 340.506 | 346.747 | 1156.4 | 57.7912 | 63.0179 | -5.2268 | 378.1075 | 60.2 | 62.1168 | -1.9168 | 0.982 | 2026-08-03 12:30 | 343.365 | 349.481 | 1164.2 | 58.2468 | 63.0179 | -4.7711 | 378.1075 | 59.9 | 62.1168 | -2.2168 | 0.9825 | 2026-08-03 12:30 | 337.391 | 347.491 | 1143.6 | 57.9152 | 63.0179 | -5.1028 | 378.1075 | 55.6 | 62.1168 | -6.5168 | 0.97093 | 2026-08-03 12:30 | 342.242 | 348.622 | 1156.3 | 58.1037 | 63.0179 | -4.9143 | 378.1075 | 55.7 | 62.1168 | -6.4168 | 0.9817 | 2026-08-03 12:30 | 255.261 | 259.596 | 859.2 | 43.266 | 46.6799 | -3.4139 | 280.0797 | 42.2 | 46.0124 | -3.8124 | 0.9833 | 2026-08-03 12:30 | 253.364 | 258.574 | 858.6 | 43.0957 | 46.6799 | -3.5843 | 280.0797 | 42.5 | 46.0124 | -3.5124 | 0.97985 | 2026-08-03 12:30 | 252.954 | 258.524 | 856.4 | 43.0873 | 46.6799 | -3.5926 | 280.0797 | 42.4 | 46.0124 | -3.6124 | 0.97845 | 2026-08-03 12:30 | 255.095 | 262.878 | 864.6 | 43.813 | 46.6799 | -2.8669 | 280.0797 | 42.7 | 46.0124 | -3.3124 | 0.97039 | 2026-08-03 12:30 | 241.453 | 245.454 | 818.9 | 40.909 | 44.4102 | -3.5012 | 266.4611 | 40.5 | 43.7751 | -3.2751 | 0.9837 | 2026-08-03 12:30 | 446.2278 | 483.2017 | -36.9738 | 2899.2099 | 441.7 | 476.2919 | -34.5919
2026-08-03 12:20 | 1057 | 48.5 | 341.955 | 348.231 | 1096.2 | 58.0385 | 63.0103 | -4.9718 | 378.0619 | 54.3 | 62.1093 | -7.8093 | 0.98198 | 2026-08-03 12:20 | 335.045 | 340.631 | 1104.3 | 56.7718 | 63.0103 | -6.2385 | 378.0619 | 55.2 | 62.1093 | -6.9093 | 0.9836 | 2026-08-03 12:20 | 338.617 | 348.855 | 1088 | 58.1425 | 63.0103 | -4.8678 | 378.0619 | 56.8 | 62.1093 | -5.3093 | 0.97065 | 2026-08-03 12:20 | 327.49 | 332.815 | 1100.6 | 55.4692 | 63.0103 | -7.5411 | 378.0619 | 57.1 | 62.1093 | -5.0093 | 0.984 | 2026-08-03 12:20 | 256.05 | 260.399 | 817 | 43.3998 | 46.6743 | -3.2745 | 280.0458 | 43 | 46.0069 | -3.0069 | 0.9833 | 2026-08-03 12:20 | 253.646 | 258.861 | 816.1 | 43.1435 | 46.6743 | -3.5308 | 280.0458 | 41.9 | 46.0069 | -4.1069 | 0.97985 | 2026-08-03 12:20 | 253.359 | 258.977 | 814 | 43.1628 | 46.6743 | -3.5115 | 280.0458 | 41.9 | 46.0069 | -4.1069 | 0.97831 | 2026-08-03 12:20 | 255.355 | 262.952 | 821.9 | 43.8253 | 46.6743 | -2.849 | 280.0458 | 42.3 | 46.0069 | -3.7069 | 0.97111 | 2026-08-03 12:20 | 241.466 | 245.492 | 778.4 | 40.9153 | 44.4048 | -3.4895 | 266.4289 | 40 | 43.7698 | -3.7698 | 0.9836 | 2026-08-03 12:20 | 442.8688 | 483.1433 | -40.2745 | 2898.8599 | 432.5 | 476.2344 | -43.7344
2026-08-03 12:10 | 1047 | 48.5 | 340.549 | 346.721 | 1041.9 | 57.7868 | 62.4142 | -4.6274 | 374.4851 | 56.4 | 61.5217 | -5.1217 | 0.9822 | 2026-08-03 12:10 | 341.101 | 347 | 1049.1 | 57.8333 | 62.4142 | -4.5809 | 374.4851 | 56.1 | 61.5217 | -5.4217 | 0.983 | 2026-08-03 12:10 | 337.125 | 347.336 | 1031.2 | 57.8893 | 62.4142 | -4.5249 | 374.4851 | 55.8 | 61.5217 | -5.7217 | 0.9706 | 2026-08-03 12:10 | 335.164 | 340.822 | 1043.5 | 56.8037 | 62.4142 | -5.6105 | 374.4851 | 56.7 | 61.5217 | -4.8217 | 0.9834 | 2026-08-03 12:10 | 254.721 | 258.958 | 774 | 43.1597 | 46.2327 | -3.0731 | 277.3964 | 42.1 | 45.5716 | -3.4716 | 0.98364 | 2026-08-03 12:10 | 253.181 | 258.429 | 774.2 | 43.0715 | 46.2327 | -3.1612 | 277.3964 | 41.9 | 45.5716 | -3.6716 | 0.97969 | 2026-08-03 12:10 | 252.337 | 257.878 | 772.1 | 42.9797 | 46.2327 | -3.2531 | 277.3964 | 41.7 | 45.5716 | -3.8716 | 0.97851 | 2026-08-03 12:10 | 254.707 | 262.244 | 779.6 | 43.7073 | 46.2327 | -2.5254 | 277.3964 | 42.7 | 45.5716 | -2.8716 | 0.97126 | 2026-08-03 12:10 | 241.696 | 245.676 | 738.4 | 40.946 | 43.9847 | -3.0387 | 263.9083 | 40.6 | 43.3557 | -2.7557 | 0.9838 | 2026-08-03 12:10 | 444.1773 | 478.5724 | -34.3951 | 2871.4345 | 434 | 471.7288 | -37.7288
2026-08-03 12:00 | 1032 | 48.5 | 338.367 | 344.429 | 985.5 | 57.4048 | 61.52 | -4.1152 | 369.12 | 56.9 | 60.6403 | -3.7403 | 0.9824 | 2026-08-03 12:00 | 343.141 | 349.36 | 993 | 58.2267 | 61.52 | -3.2933 | 369.12 | 56.6 | 60.6403 | -4.0403 | 0.9822 | 2026-08-03 12:00 | 334.334 | 344.016 | 975.4 | 57.336 | 61.52 | -4.184 | 369.12 | 55.7 | 60.6403 | -4.9403 | 0.97186 | 2026-08-03 12:00 | 339.314 | 345.498 | 986.8 | 57.583 | 61.52 | -3.937 | 369.12 | 56.4 | 60.6403 | -4.2403 | 0.9821 | 2026-08-03 12:00 | 252.314 | 256.521 | 731.9 | 42.7535 | 45.5704 | -2.8169 | 273.4222 | 42 | 44.9187 | -2.9187 | 0.9836 | 2026-08-03 12:00 | 251.069 | 255.776 | 732.3 | 42.6293 | 45.5704 | -2.941 | 273.4222 | 41.7 | 44.9187 | -3.2187 | 0.9816 | 2026-08-03 12:00 | 249.939 | 255.003 | 730.4 | 42.5005 | 45.5704 | -3.0699 | 273.4222 | 41.6 | 44.9187 | -3.3187 | 0.98014 | 2026-08-03 12:00 | 251.996 | 259.323 | 736.9 | 43.2205 | 45.5704 | -2.3499 | 273.4222 | 41.2 | 44.9187 | -3.7187 | 0.97175 | 2026-08-03 12:00 | 239.649 | 243.546 | 697.8 | 40.591 | 43.3546 | -2.7636 | 260.1274 | 39.2 | 42.7346 | -3.5346 | 0.984 | 2026-08-03 12:00 | 442.2453 | 471.7161 | -29.4708 | 2830.2965 | 431.3 | 464.9705 | -33.6705
2026-08-03 11:50 | 1023 | 48.22 | 335.495 | 341.471 | 928.6 | 56.9118 | 61.0486 | -4.1368 | 366.2917 | 56.6 | 60.1756 | -3.5756 | 0.9825 | 2026-08-03 11:50 | 339.39 | 346.214 | 936.4 | 57.7023 | 61.0486 | -3.3463 | 366.2917 | 57.2 | 60.1756 | -2.9756 | 0.98029 | 2026-08-03 11:50 | 331.744 | 341.248 | 919.7 | 56.8747 | 61.0486 | -4.1739 | 366.2917 | 55.1 | 60.1756 | -5.0756 | 0.97215 | 2026-08-03 11:50 | 336.074 | 342.199 | 930.4 | 57.0332 | 61.0486 | -4.0154 | 366.2917 | 55.7 | 60.1756 | -4.4756 | 0.9821 | 2026-08-03 11:50 | 250.065 | 254.234 | 689.9 | 42.3723 | 45.2212 | -2.8489 | 271.3272 | 41.6 | 44.5745 | -2.9745 | 0.9836 | 2026-08-03 11:50 | 248.452 | 253.476 | 690.6 | 42.246 | 45.2212 | -2.9752 | 271.3272 | 41.3 | 44.5745 | -3.2745 | 0.98018 | 2026-08-03 11:50 | 247.519 | 252.728 | 688.8 | 42.1213 | 45.2212 | -3.0999 | 271.3272 | 41.2 | 44.5745 | -3.3745 | 0.97939 | 2026-08-03 11:50 | 249.409 | 256.873 | 695.7 | 42.8122 | 45.2212 | -2.409 | 271.3272 | 42.1 | 44.5745 | -2.4745 | 0.97094 | 2026-08-03 11:50 | 236.564 | 240.435 | 658.6 | 40.0725 | 43.0224 | -2.9499 | 258.1342 | 39.3 | 42.4071 | -3.1071 | 0.9839 | 2026-08-03 11:50 | 438.1463 | 468.1016 | -29.9553 | 2808.6096 | 430.1 | 461.4077 | -31.3077
2026-08-03 11:40 | 1008 | 48.22 | 332.267 | 338.151 | 872 | 56.3585 | 60.1535 | -3.795 | 360.9208 | 53.8 | 59.2933 | -5.4933 | 0.9826 | 2026-08-03 11:40 | 337.218 | 342.961 | 879.2 | 57.1602 | 60.1535 | -2.9933 | 360.9208 | 56.6 | 59.2933 | -2.6933 | 0.98325 | 2026-08-03 11:40 | 329.815 | 339.246 | 864.6 | 56.541 | 60.1535 | -3.6125 | 360.9208 | 54.9 | 59.2933 | -4.3933 | 0.9722 | 2026-08-03 11:40 | 333.444 | 339.418 | 874.7 | 56.5697 | 60.1535 | -3.5838 | 360.9208 | 55.3 | 59.2933 | -3.9933 | 0.9824 | 2026-08-03 11:40 | 248.717 | 252.787 | 648.3 | 42.1312 | 44.5581 | -2.427 | 267.3488 | 41.3 | 43.9209 | -2.6209 | 0.9839 | 2026-08-03 11:40 | 246.593 | 251.381 | 649.3 | 41.8968 | 44.5581 | -2.6613 | 267.3488 | 40.8 | 43.9209 | -3.1209 | 0.98095 | 2026-08-03 11:40 | 246.264 | 251.579 | 647.6 | 41.9298 | 44.5581 | -2.6283 | 267.3488 | 40.8 | 43.9209 | -3.1209 | 0.97887 | 2026-08-03 11:40 | 247.922 | 255.099 | 653.6 | 42.5165 | 44.5581 | -2.0416 | 267.3488 | 40.5 | 43.9209 | -3.4209 | 0.97187 | 2026-08-03 11:40 | 234.655 | 238.446 | 619.3 | 39.741 | 42.3915 | -2.6505 | 254.3492 | 38.8 | 41.7853 | -2.9853 | 0.9841 | 2026-08-03 11:40 | 434.8447 | 461.2379 | -26.3933 | 2767.4276 | 422.8 | 454.6422 | -31.8422
2026-08-03 11:30 | 990 | 48.5 | 328.394 | 334.141 | 818.2 | 55.6902 | 59.0163 | -3.3261 | 354.0977 | 53.7 | 58.1724 | -4.4724 | 0.9828 | 2026-08-03 11:30 | 331.78 | 337.627 | 822.6 | 56.2712 | 59.0163 | -2.7451 | 354.0977 | 53.6 | 58.1724 | -4.5724 | 0.98268 | 2026-08-03 11:30 | 325.242 | 334.702 | 809.7 | 55.7837 | 59.0163 | -3.2326 | 354.0977 | 53.2 | 58.1724 | -4.9724 | 0.97174 | 2026-08-03 11:30 | 327.837 | 333.642 | 819.4 | 55.607 | 59.0163 | -3.4093 | 354.0977 | 53.6 | 58.1724 | -4.5724 | 0.9826 | 2026-08-03 11:30 | 244.734 | 248.688 | 607 | 41.448 | 43.7158 | -2.2678 | 262.2946 | 40.6 | 43.0906 | -2.4906 | 0.9841 | 2026-08-03 11:30 | 242.143 | 247.05 | 608.5 | 41.175 | 43.7158 | -2.5408 | 262.2946 | 40.2 | 43.0906 | -2.8906 | 0.98014 | 2026-08-03 11:30 | 241.631 | 246.474 | 606.8 | 41.079 | 43.7158 | -2.6368 | 262.2946 | 40.1 | 43.0906 | -2.9906 | 0.98035 | 2026-08-03 11:30 | 243.304 | 250.635 | 613.1 | 41.7725 | 43.7158 | -1.9433 | 262.2946 | 40.3 | 43.0906 | -2.7906 | 0.97075 | 2026-08-03 11:30 | 230.206 | 233.902 | 580.5 | 38.9837 | 41.5901 | -2.6065 | 249.5408 | 38.3 | 40.9954 | -2.6954 | 0.9842 | 2026-08-03 11:30 | 427.8102 | 452.5183 | -24.7082 | 2715.11 | 413.6 | 446.0473 | -32.4473
2026-08-03 11:20 | 966 | 48.5 | 321.137 | 326.973 | 764.5 | 54.4955 | 57.5856 | -3.0901 | 345.5135 | 54.2 | 56.7621 | -2.5621 | 0.98215 | 2026-08-03 11:20 | 325.375 | 331.103 | 769 | 55.1838 | 57.5856 | -2.4018 | 345.5135 | 54 | 56.7621 | -2.7621 | 0.9827 | 2026-08-03 11:20 | 319.076 | 328.145 | 756.5 | 54.6908 | 57.5856 | -2.8948 | 345.5135 | 53 | 56.7621 | -3.7621 | 0.97236 | 2026-08-03 11:20 | 321.833 | 327.609 | 765.8 | 54.6015 | 57.5856 | -2.9841 | 345.5135 | 54.2 | 56.7621 | -2.5621 | 0.98237 | 2026-08-03 11:20 | 239.929 | 243.731 | 566.4 | 40.6218 | 42.656 | -2.0342 | 255.9359 | 39.5 | 42.046 | -2.546 | 0.9844 | 2026-08-03 11:20 | 237.844 | 242.179 | 568.3 | 40.3632 | 42.656 | -2.2928 | 255.9359 | 39.2 | 42.046 | -2.846 | 0.9821 | 2026-08-03 11:20 | 236.996 | 241.587 | 566.7 | 40.2645 | 42.656 | -2.3915 | 255.9359 | 39.1 | 42.046 | -2.946 | 0.981 | 2026-08-03 11:20 | 238.743 | 246.119 | 572.8 | 41.0198 | 42.656 | -1.6362 | 255.9359 | 39.5 | 42.046 | -2.546 | 0.97003 | 2026-08-03 11:20 | 226.164 | 229.748 | 542.2 | 38.2913 | 40.5819 | -2.2906 | 243.4913 | 37.6 | 40.0016 | -2.4016 | 0.9844 | 2026-08-03 11:20 | 419.5323 | 441.5482 | -22.0159 | 2649.2892 | 410.3 | 435.2341 | -24.9341
2026-08-03 11:10 | 943 | 48.5 | 315.012 | 321.193 | 710.3 | 53.5322 | 56.2145 | -2.6823 | 337.287 | 51.8 | 55.4106 | -3.6106 | 0.98076 | 2026-08-03 11:10 | 318.229 | 324.329 | 715 | 54.0548 | 56.2145 | -2.1597 | 337.287 | 53.9 | 55.4106 | -1.5106 | 0.98119 | 2026-08-03 11:10 | 312.903 | 321.591 | 703.5 | 53.5985 | 56.2145 | -2.616 | 337.287 | 51.5 | 55.4106 | -3.9106 | 0.97298 | 2026-08-03 11:10 | 315.544 | 321.034 | 711.6 | 53.5057 | 56.2145 | -2.7088 | 337.287 | 51.4 | 55.4106 | -4.0106 | 0.9829 | 2026-08-03 11:10 | 236.062 | 239.796 | 526.9 | 39.966 | 41.6404 | -1.6744 | 249.8422 | 38.8 | 41.0449 | -2.2449 | 0.98443 | 2026-08-03 11:10 | 233.762 | 237.991 | 529.1 | 39.6652 | 41.6404 | -1.9752 | 249.8422 | 38.5 | 41.0449 | -2.5449 | 0.98223 | 2026-08-03 11:10 | 234.404 | 238.868 | 527.6 | 39.8113 | 41.6404 | -1.829 | 249.8422 | 39 | 41.0449 | -2.0449 | 0.98131 | 2026-08-03 11:10 | 236.35 | 243.167 | 533.3 | 40.5278 | 41.6404 | -1.1125 | 249.8422 | 39.2 | 41.0449 | -1.8449 | 0.97197 | 2026-08-03 11:10 | 223.523 | 227.019 | 504.6 | 37.8365 | 39.6157 | -1.7792 | 237.6939 | 36.7 | 39.0492 | -2.3492 | 0.9846 | 2026-08-03 11:10 | 412.498 | 431.0351 | -18.5371 | 2586.2109 | 400.8 | 424.8713 | -24.0713
2026-08-03 11:00 | 917 | 48.79 | 309.607 | 315.199 | 658.5 | 52.5332 | 54.6041 | -2.071 | 327.6247 | 50.1 | 53.8233 | -3.7233 | 0.98226 | 2026-08-03 11:00 | 312.11 | 317.443 | 661.1 | 52.9072 | 54.6041 | -1.697 | 327.6247 | 49.2 | 53.8233 | -4.6233 | 0.9832 | 2026-08-03 11:00 | 307.282 | 316.043 | 652 | 52.6738 | 54.6041 | -1.9303 | 327.6247 | 50.9 | 53.8233 | -2.9233 | 0.97228 | 2026-08-03 11:00 | 309.827 | 315.153 | 660.2 | 52.5255 | 54.6041 | -2.0786 | 327.6247 | 51.4 | 53.8233 | -2.4233 | 0.9831 | 2026-08-03 11:00 | 231.846 | 235.496 | 488.1 | 39.2493 | 40.4475 | -1.1982 | 242.685 | 38.3 | 39.8691 | -1.5691 | 0.9845 | 2026-08-03 11:00 | 229.784 | 233.862 | 490.6 | 38.977 | 40.4475 | -1.4705 | 242.685 | 38.1 | 39.8691 | -1.7691 | 0.98256 | 2026-08-03 11:00 | 230.155 | 234.281 | 488.6 | 39.0468 | 40.4475 | -1.4007 | 242.685 | 37.6 | 39.8691 | -2.2691 | 0.98239 | 2026-08-03 11:00 | 231.714 | 238.53 | 494.1 | 39.755 | 40.4475 | -0.6925 | 242.685 | 37.9 | 39.8691 | -1.9691 | 0.97142 | 2026-08-03 11:00 | 218.643 | 221.973 | 467.9 | 36.9955 | 38.4808 | -1.4853 | 230.8847 | 36.4 | 37.9305 | -1.5305 | 0.985 | 2026-08-03 11:00 | 404.6633 | 418.6873 | -14.0239 | 2512.1235 | 389.9 | 412.7 | -22.8
2026-08-03 10:50 | 895 | 48.79 | 302.131 | 307.163 | 608.4 | 51.1938 | 53.2941 | -2.1003 | 319.7646 | 50.2 | 52.532 | -2.332 | 0.98362 | 2026-08-03 10:50 | 306.594 | 311.738 | 611.9 | 51.9563 | 53.2941 | -1.3378 | 319.7646 | 51.6 | 52.532 | -0.93199 | 0.9835 | 2026-08-03 10:50 | 299.53 | 307.52 | 601.1 | 51.2533 | 53.2941 | -2.0408 | 319.7646 | 49.1 | 52.532 | -3.432 | 0.97402 | 2026-08-03 10:50 | 303.322 | 308.442 | 608.8 | 51.407 | 53.2941 | -1.8871 | 319.7646 | 49.8 | 52.532 | -2.732 | 0.9834 | 2026-08-03 10:50 | 225.654 | 229.137 | 449.8 | 38.1895 | 39.4771 | -1.2876 | 236.8627 | 37 | 38.9126 | -1.9126 | 0.9848 | 2026-08-03 10:50 | 224.331 | 228.137 | 452.5 | 38.0228 | 39.4771 | -1.4543 | 236.8627 | 36.8 | 38.9126 | -2.1126 | 0.98332 | 2026-08-03 10:50 | 224.146 | 228.198 | 451 | 38.033 | 39.4771 | -1.4441 | 236.8627 | 36.8 | 38.9126 | -2.1126 | 0.98224 | 2026-08-03 10:50 | 226.035 | 232.881 | 456.2 | 38.8135 | 39.4771 | -0.66361 | 236.8627 | 37.2 | 38.9126 | -1.7126 | 0.9706 | 2026-08-03 10:50 | 213.889 | 217.168 | 431.5 | 36.1947 | 37.5576 | -1.3629 | 225.3455 | 34.7 | 37.0205 | -2.3205 | 0.9849 | 2026-08-03 10:50 | 395.064 | 408.6424 | -13.5784 | 2451.8545 | 383.2 | 402.7988 | -19.5988
2026-08-03 10:40 | 865 | 48.79 | 295.139 | 299.999 | 558.2 | 49.9998 | 51.5077 | -1.5079 | 309.0462 | 48.1 | 50.7711 | -2.6711 | 0.9838 | 2026-08-03 10:40 | 297.657 | 302.589 | 560.3 | 50.4315 | 51.5077 | -1.0762 | 309.0462 | 49 | 50.7711 | -1.7711 | 0.9837 | 2026-08-03 10:40 | 292.368 | 300.208 | 552 | 50.0347 | 51.5077 | -1.473 | 309.0462 | 48.1 | 50.7711 | -2.6711 | 0.97388 | 2026-08-03 10:40 | 295.412 | 300.307 | 559 | 50.0512 | 51.5077 | -1.4565 | 309.0462 | 49.3 | 50.7711 | -1.4711 | 0.9837 | 2026-08-03 10:40 | 220.453 | 223.742 | 412.8 | 37.2903 | 38.1539 | -0.86352 | 228.9231 | 36.3 | 37.6083 | -1.3083 | 0.9853 | 2026-08-03 10:40 | 218.927 | 222.63 | 415.7 | 37.105 | 38.1539 | -1.0489 | 228.9231 | 36.2 | 37.6083 | -1.4083 | 0.98337 | 2026-08-03 10:40 | 219.454 | 223.337 | 414.2 | 37.2228 | 38.1539 | -0.93102 | 228.9231 | 36.2 | 37.6083 | -1.4083 | 0.98261 | 2026-08-03 10:40 | 221.354 | 227.98 | 419 | 37.9967 | 38.1539 | -0.15719 | 228.9231 | 36.4 | 37.6083 | -1.2083 | 0.97094 | 2026-08-03 10:40 | 208.839 | 211.955 | 396.8 | 35.3258 | 36.2987 | -0.97283 | 217.792 | 34.4 | 35.7796 | -1.3796 | 0.9853 | 2026-08-03 10:40 | 385.4578 | 394.9449 | -9.4871 | 2369.6694 | 374 | 389.2972 | -15.2972
2026-08-03 10:30 | 834 | 48.79 | 287.183 | 291.793 | 510.1 | 48.6322 | 49.6618 | -1.0296 | 297.9706 | 47.4 | 48.9516 | -1.5516 | 0.9842 | 2026-08-03 10:30 | 287.931 | 292.613 | 511.3 | 48.7688 | 49.6618 | -0.89293 | 297.9706 | 48.6 | 48.9516 | -0.3516 | 0.984 | 2026-08-03 10:30 | 283.783 | 291.219 | 503.9 | 48.5365 | 49.6618 | -1.1253 | 297.9706 | 46.4 | 48.9516 | -2.5516 | 0.97447 | 2026-08-03 10:30 | 287.015 | 291.712 | 509.7 | 48.6187 | 49.6618 | -1.0431 | 297.9706 | 46.3 | 48.9516 | -2.6516 | 0.9839 | 2026-08-03 10:30 | 213.698 | 216.864 | 376.5 | 36.144 | 36.7865 | -0.64249 | 220.7189 | 34.9 | 36.2604 | -1.3604 | 0.9854 | 2026-08-03 10:30 | 212.579 | 216.192 | 379.5 | 36.032 | 36.7865 | -0.75449 | 220.7189 | 34.7 | 36.2604 | -1.5604 | 0.98329 | 2026-08-03 10:30 | 212.575 | 216.199 | 378 | 36.0332 | 36.7865 | -0.75332 | 220.7189 | 34.6 | 36.2604 | -1.6604 | 0.98324 | 2026-08-03 10:30 | 214.16 | 220.37 | 382.6 | 36.7283 | 36.7865 | -0.058158 | 220.7189 | 35 | 36.2604 | -1.2604 | 0.97182 | 2026-08-03 10:30 | 202.632 | 205.613 | 362.4 | 34.2688 | 34.9978 | -0.72896 | 209.9867 | 33.6 | 34.4973 | -0.89732 | 0.9855 | 2026-08-03 10:30 | 373.7625 | 380.7908 | -7.0283 | 2284.7449 | 361.5 | 375.3455 | -13.8455
2026-08-03 10:20 | 804 | 49.65 | 277.941 | 282.346 | 462.7 | 47.0577 | 47.7182 | -0.66051 | 286.3091 | 46.4 | 47.0358 | -0.63581 | 0.9844 | 2026-08-03 10:20 | 0 | 284.239 | 462.7 | 47.3732 | 47.7182 | -0.34501 | 286.3091 | 45.9 | 47.0358 | -1.1358 |  | 2026-08-03 10:20 | 274.952 | 282.111 | 457.5 | 47.0185 | 47.7182 | -0.69968 | 286.3091 | 45.1 | 47.0358 | -1.9358 | 0.97462 | 2026-08-03 10:20 | 278.132 | 282.626 | 463.4 | 47.1043 | 47.7182 | -0.61384 | 286.3091 | 45.6 | 47.0358 | -1.4358 | 0.9841 | 2026-08-03 10:20 | 206.501 | 209.518 | 341.6 | 34.9197 | 35.3468 | -0.42713 | 212.0808 | 33.9 | 34.8413 | -0.94134 | 0.9856 | 2026-08-03 10:20 | 205.881 | 209.402 | 344.8 | 34.9003 | 35.3468 | -0.44646 | 212.0808 | 33.8 | 34.8413 | -1.0413 | 0.98319 | 2026-08-03 10:20 | 205.641 | 209.093 | 343.4 | 34.8488 | 35.3468 | -0.49796 | 212.0808 | 33.8 | 34.8413 | -1.0413 | 0.98349 | 2026-08-03 10:20 | 207.249 | 213.148 | 347.6 | 35.5247 | 35.3468 | 0.17787 | 212.0808 | 34 | 34.8413 | -0.84134 | 0.97232 | 2026-08-03 10:20 | 196.222 | 199.089 | 328.8 | 33.1815 | 33.6281 | -0.4466 | 201.7686 | 31.8 | 33.1472 | -1.3472 | 0.9856 | 2026-08-03 10:20 | 361.9287 | 365.888 | -3.9593 | 2195.3279 | 350.3 | 360.6558 | -10.3558
2026-08-03 10:10 | 768 | 49.65 | 267.832 | 271.966 | 416.3 | 45.3277 | 45.5815 | -0.25387 | 273.4892 | 45.9 | 44.9297 | 0.97028 | 0.9848 | 2026-08-03 10:10 | 269.348 | 273.589 | 416.8 | 45.5982 | 45.5815 | 0.016626 | 273.4892 | 42 | 44.9297 | -2.9297 | 0.9845 | 2026-08-03 10:10 | 264.857 | 271.453 | 412.4 | 45.2422 | 45.5815 | -0.33937 | 273.4892 | 43 | 44.9297 | -1.9297 | 0.9757 | 2026-08-03 10:10 | 268.131 | 272.352 | 417.8 | 45.392 | 45.5815 | -0.18954 | 273.4892 | 43.6 | 44.9297 | -1.3297 | 0.9845 | 2026-08-03 10:10 | 198.928 | 201.793 | 307.7 | 33.6322 | 33.7641 | -0.13194 | 202.5846 | 32.7 | 33.2813 | -0.58128 | 0.9858 | 2026-08-03 10:10 | 198.72 | 201.925 | 311 | 33.6542 | 33.7641 | -0.10994 | 202.5846 | 32.7 | 33.2813 | -0.58128 | 0.98413 | 2026-08-03 10:10 | 198.123 | 201.515 | 309.6 | 33.5858 | 33.7641 | -0.17827 | 202.5846 | 32.5 | 33.2813 | -0.78128 | 0.98317 | 2026-08-03 10:10 | 200.045 | 205.681 | 313.6 | 34.2802 | 33.7641 | 0.51606 | 202.5846 | 32.9 | 33.2813 | -0.38128 | 0.9726 | 2026-08-03 10:10 | 189.73 | 192.463 | 297 | 32.0772 | 32.1224 | -0.045197 | 192.7342 | 31.2 | 31.663 | -0.46301 | 0.9858 | 2026-08-03 10:10 | 348.7895 | 349.5049 | -0.71544 | 2097.0297 | 336.5 | 344.507 | -8.007
2026-08-03 10:00 | 732 | 49.65 | 256.255 | 260.635 | 370.4 | 43.4392 | 43.4449 | -0.0057393 | 260.6694 | 39.8 | 42.8236 | -3.0236 | 0.98319 | 2026-08-03 10:00 | 258.902 | 263.149 | 374.8 | 43.8582 | 43.4449 | 0.41326 | 260.6694 | 42.6 | 42.8236 | -0.22364 | 0.98386 | 2026-08-03 10:00 | 254.655 | 260.369 | 369.4 | 43.3948 | 43.4449 | -0.050073 | 260.6694 | 41.9 | 42.8236 | -0.92364 | 0.97805 | 2026-08-03 10:00 | 257.669 | 261.593 | 374.2 | 43.5988 | 43.4449 | 0.15393 | 260.6694 | 42.2 | 42.8236 | -0.62364 | 0.985 | 2026-08-03 10:00 | 190.667 | 193.355 | 275 | 32.2258 | 32.1814 | 0.044422 | 193.0885 | 30.8 | 31.7212 | -0.92122 | 0.9861 | 2026-08-03 10:00 | 190.77 | 193.63 | 278.3 | 32.2717 | 32.1814 | 0.090255 | 193.0885 | 30.9 | 31.7212 | -0.82122 | 0.98523 | 2026-08-03 10:00 | 190.01 | 193.155 | 277.1 | 32.1925 | 32.1814 | 0.011088 | 193.0885 | 30.8 | 31.7212 | -0.92122 | 0.98372 | 2026-08-03 10:00 | 191.96 | 197.711 | 280.7 | 32.9518 | 32.1814 | 0.77042 | 193.0885 | 31.1 | 31.7212 | -0.62122 | 0.97091 | 2026-08-03 10:00 | 182.357 | 184.801 | 265.8 | 30.8002 | 30.6166 | 0.18354 | 183.6998 | 29.5 | 30.1788 | -0.67881 | 0.98677 | 2026-08-03 10:00 | 334.733 | 333.1219 | 1.6111 | 1998.7314 | 319.6 | 328.3583 | -8.7583
2026-08-03 09:50 | 694 | 49.36 | 245.338 | 248.923 | 330.6 | 41.4872 | 41.2353 | 0.25184 | 247.4119 | 39.1 | 40.6457 | -1.5457 |  | 2026-08-03 09:50 | 246.252 | 249.977 | 332.2 | 41.6628 | 41.2353 | 0.42751 | 247.4119 | 40.5 | 40.6457 | -0.14566 |  | 2026-08-03 09:50 | 242.525 | 248.093 | 327.5 | 41.3488 | 41.2353 | 0.11351 | 247.4119 | 39.2 | 40.6457 | -1.4457 |  | 2026-08-03 09:50 | 245.359 | 249.02 | 332 | 41.5033 | 41.2353 | 0.26801 | 247.4119 | 39.7 | 40.6457 | -0.94566 |  | 2026-08-03 09:50 | 181.641 | 184.145 | 244.2 | 30.6908 | 30.5447 | 0.14615 | 183.2681 | 29.4 | 30.1079 | -0.7079 |  | 2026-08-03 09:50 | 181.997 | 184.484 | 247.4 | 30.7473 | 30.5447 | 0.20265 | 183.2681 | 29.4 | 30.1079 | -0.7079 |  | 2026-08-03 09:50 | 181.459 | 184.047 | 246.3 | 30.6745 | 30.5447 | 0.12982 | 183.2681 | 29.8 | 30.1079 | -0.3079 |  | 2026-08-03 09:50 | 183.247 | 188.206 | 249.6 | 31.3677 | 30.5447 | 0.82298 | 183.2681 | 30 | 30.1079 | -0.1079 |  | 2026-08-03 09:50 | 173.713 | 176.126 | 236.3 | 29.3543 | 29.0595 | 0.29485 | 174.3569 | 28.5 | 28.6439 | -0.14393 |  | 2026-08-03 09:50 | 318.8368 | 316.1795 | 2.6573 | 1897.0771 | 305.6 | 311.6582 | -6.0582
2026-08-03 09:40 | 656 | 48.5 | 233.184 | 236.543 | 291.5 | 39.4238 | 39.1057 | 0.31809 | 234.6344 | 37.9 | 38.5465 | -0.64653 |  | 2026-08-03 09:40 | 233.886 | 237.327 | 291.7 | 39.5545 | 39.1057 | 0.44876 | 234.6344 | 39.5 | 38.5465 | 0.95347 |  | 2026-08-03 09:40 | 230.237 | 235.354 | 288.3 | 39.2257 | 39.1057 | 0.11993 | 234.6344 | 37.3 | 38.5465 | -1.2465 |  | 2026-08-03 09:40 | 233.239 | 236.624 | 292.3 | 39.4373 | 39.1057 | 0.33159 | 234.6344 | 37.9 | 38.5465 | -0.64653 |  | 2026-08-03 09:40 | 172.305 | 174.645 | 214.8 | 29.1075 | 28.9672 | 0.14029 | 173.8033 | 28 | 28.553 | -0.55298 |  | 2026-08-03 09:40 | 173.054 | 175.422 | 218 | 29.237 | 28.9672 | 0.26979 | 173.8033 | 28.1 | 28.553 | -0.45298 |  | 2026-08-03 09:40 | 171.998 | 174.334 | 216.5 | 29.0557 | 28.9672 | 0.088452 | 173.8033 | 27.6 | 28.553 | -0.95298 |  | 2026-08-03 09:40 | 173.632 | 178.451 | 219.6 | 29.7418 | 28.9672 | 0.77462 | 173.8033 | 28.3 | 28.553 | -0.25298 |  | 2026-08-03 09:40 | 165.015 | 167.256 | 207.8 | 27.876 | 27.5587 | 0.31728 | 165.3523 | 26.8 | 27.1646 | -0.36463 |  | 2026-08-03 09:40 | 302.6593 | 299.8505 | 2.8088 | 1799.1032 | 291.4 | 295.5627 | -4.1627
2026-08-03 09:30 | 617 | 48.79 | 219.592 | 222.595 | 253.6 | 37.0992 | 36.7402 | 0.35899 | 220.4411 | 36 | 36.2148 | -0.21479 |  | 2026-08-03 09:30 | 217.702 | 220.569 | 252.2 | 36.7615 | 36.7402 | 0.021323 | 220.4411 | 33.7 | 36.2148 | -2.5148 |  | 2026-08-03 09:30 | 216.944 | 221.652 | 251 | 36.942 | 36.7402 | 0.20182 | 220.4411 | 35.2 | 36.2148 | -1.0148 |  | 2026-08-03 09:30 | 220.027 | 223.129 | 254.4 | 37.1882 | 36.7402 | 0.44799 | 220.4411 | 35.7 | 36.2148 | -0.51479 |  | 2026-08-03 09:30 | 162.339 | 164.511 | 186.8 | 27.4185 | 27.2149 | 0.20355 | 163.2897 | 26.3 | 26.8258 | -0.52577 |  | 2026-08-03 09:30 | 163.199 | 165.382 | 189.9 | 27.5637 | 27.2149 | 0.34872 | 163.2897 | 26.5 | 26.8258 | -0.32577 |  | 2026-08-03 09:30 | 162.406 | 164.562 | 188.9 | 27.427 | 27.2149 | 0.21205 | 163.2897 | 26.3 | 26.8258 | -0.52577 |  | 2026-08-03 09:30 | 164.002 | 168.793 | 191.3 | 28.1322 | 27.2149 | 0.91722 | 163.2897 | 26.2 | 26.8258 | -0.62577 |  | 2026-08-03 09:30 | 155.537 | 157.602 | 181 | 26.267 | 25.8917 | 0.37535 | 155.3499 | 24.9 | 25.5214 | -0.6214 |  | 2026-08-03 09:30 | 284.7992 | 281.7121 | 3.087 | 1690.2729 | 270.8 | 277.6837 | -6.8837
2026-08-03 09:20 | 576 | 48.5 | 205.287 | 208.033 | 217.6 | 34.6722 | 34.3367 | 0.33542 | 206.0205 | 33.1 | 33.8457 | -0.74573 |  | 2026-08-03 09:20 | 205.822 | 208.66 | 218.5 | 34.7767 | 34.3367 | 0.43992 | 206.0205 | 34.2 | 33.8457 | 0.35427 |  | 2026-08-03 09:20 | 203.356 | 207.511 | 215.8 | 34.5852 | 34.3367 | 0.24842 | 206.0205 | 32.8 | 33.8457 | -1.0457 |  | 2026-08-03 09:20 | 206.187 | 209.009 | 218.7 | 34.8348 | 34.3367 | 0.49809 | 206.0205 | 33.2 | 33.8457 | -0.64573 |  | 2026-08-03 09:20 | 152.186 | 154.159 | 160.5 | 25.6932 | 25.4346 | 0.25854 | 152.6078 | 24.6 | 25.0709 | -0.47091 |  | 2026-08-03 09:20 | 153.079 | 155.048 | 163.4 | 25.8413 | 25.4346 | 0.40671 | 152.6078 | 24.7 | 25.0709 | -0.37091 |  | 2026-08-03 09:20 | 152.466 | 154.443 | 162.6 | 25.7405 | 25.4346 | 0.30587 | 152.6078 | 24.6 | 25.0709 | -0.47091 |  | 2026-08-03 09:20 | 154.167 | 158.301 | 165.1 | 26.3835 | 25.4346 | 0.94887 | 152.6078 | 24.9 | 25.0709 | -0.17091 |  | 2026-08-03 09:20 | 145.962 | 147.979 | 156.1 | 24.6632 | 24.1979 | 0.46527 | 145.1874 | 23.8 | 23.8519 | -0.051868 |  | 2026-08-03 09:20 | 267.1905 | 263.2834 | 3.9071 | 1579.7004 | 255.9 | 259.5184 | -3.6184
2026-08-03 09:10 | 535 | 47.93 | 190.924 | 193.394 | 184.5 | 32.2323 | 31.962 | 0.27037 | 191.7718 | 29.9 | 31.5049 | -1.6049 |  | 2026-08-03 09:10 | 192.136 | 194.686 | 184.3 | 32.4477 | 31.962 | 0.4857 | 191.7718 | 31.2 | 31.5049 | -0.30491 |  | 2026-08-03 09:10 | 189.44 | 192.81 | 183 | 32.135 | 31.962 | 0.17303 | 191.7718 | 30.4 | 31.5049 | -1.1049 |  | 2026-08-03 09:10 | 192.397 | 194.931 | 185.5 | 32.4885 | 31.962 | 0.52653 | 191.7718 | 30.8 | 31.5049 | -0.70491 |  | 2026-08-03 09:10 | 141.738 | 143.438 | 135.9 | 23.9063 | 23.6755 | 0.2308 | 142.0532 | 22.7 | 23.337 | -0.63697 |  | 2026-08-03 09:10 | 142.922 | 144.716 | 138.7 | 24.1193 | 23.6755 | 0.4438 | 142.0532 | 22.9 | 23.337 | -0.43697 |  | 2026-08-03 09:10 | 142.133 | 143.903 | 138 | 23.9838 | 23.6755 | 0.3083 | 142.0532 | 22.8 | 23.337 | -0.53697 |  | 2026-08-03 09:10 | 143.814 | 147.676 | 140.2 | 24.6127 | 23.6755 | 0.93714 | 142.0532 | 23.1 | 23.337 | -0.23697 |  | 2026-08-03 09:10 | 136.546 | 138.26 | 132.3 | 23.0433 | 22.5243 | 0.519 | 135.146 | 21.6 | 22.2022 | -0.60224 |  | 2026-08-03 09:10 | 248.969 | 245.0743 | 3.8947 | 1470.4459 | 235.4 | 241.5698 | -6.1698
2026-08-03 09:00 | 492 | 47.64 | 175.827 | 178.531 | 154.6 | 29.7552 | 29.4255 | 0.32967 | 176.553 | 28.8 | 29.0047 | -0.20471 |  | 2026-08-03 09:00 | 176.162 | 178.428 | 153.1 | 29.738 | 29.4255 | 0.3125 | 176.553 | 26.7 | 29.0047 | -2.3047 |  | 2026-08-03 09:00 | 174.553 | 177.408 | 152.6 | 29.568 | 29.4255 | 0.1425 | 176.553 | 27.4 | 29.0047 | -1.6047 |  | 2026-08-03 09:00 | 177.097 | 179.375 | 154.7 | 29.8958 | 29.4255 | 0.47034 | 176.553 | 27.9 | 29.0047 | -1.1047 |  | 2026-08-03 09:00 | 130.324 | 131.92 | 113.2 | 21.9867 | 21.7967 | 0.19 | 130.78 | 20.7 | 21.485 | -0.78497 |  | 2026-08-03 09:00 | 131.751 | 133.351 | 115.8 | 22.2252 | 21.7967 | 0.4285 | 130.78 | 21 | 21.485 | -0.48497 |  | 2026-08-03 09:00 | 131.08 | 132.686 | 115.2 | 22.1143 | 21.7967 | 0.31767 | 130.78 | 20.9 | 21.485 | -0.58497 |  | 2026-08-03 09:00 | 132.642 | 136.055 | 117.1 | 22.6758 | 21.7967 | 0.87917 | 130.78 | 21.1 | 21.485 | -0.38497 |  | 2026-08-03 09:00 | 125.771 | 127.311 | 110.7 | 21.2185 | 20.7368 | 0.48167 | 124.421 | 20.1 | 20.4403 | -0.34029 |  | 2026-08-03 09:00 | 229.1775 | 225.6255 | 3.552 | 1353.7529 | 214.6 | 222.399 | -7.799
2026-08-03 08:50 | 449 | 47.64 | 159.427 | 161.347 | 125.8 | 26.8912 | 26.8538 | 0.037409 | 161.1225 | 24.4 | 26.4697 | -2.0697 |  | 2026-08-03 08:50 | 160.306 | 162.286 | 126.4 | 27.0477 | 26.8538 | 0.19391 | 161.1225 | 25.7 | 26.4697 | -0.76975 |  | 2026-08-03 08:50 | 158.272 | 160.708 | 125.2 | 26.7847 | 26.8538 | -0.069091 | 161.1225 | 25.4 | 26.4697 | -1.0697 |  | 2026-08-03 08:50 | 161.258 | 163.233 | 126.8 | 27.2055 | 26.8538 | 0.35174 | 161.1225 | 25.7 | 26.4697 | -0.76975 |  | 2026-08-03 08:50 | 118.103 | 119.513 | 92.5 | 19.9188 | 19.8917 | 0.027161 | 119.35 | 18.6 | 19.6072 | -1.0072 |  | 2026-08-03 08:50 | 119.745 | 121.114 | 94.8 | 20.1857 | 19.8917 | 0.29399 | 119.35 | 18.9 | 19.6072 | -0.70722 |  | 2026-08-03 08:50 | 119.046 | 120.431 | 94.3 | 20.0718 | 19.8917 | 0.18016 | 119.35 | 18.8 | 19.6072 | -0.80722 |  | 2026-08-03 08:50 | 120.736 | 123.75 | 96 | 20.625 | 19.8917 | 0.73333 | 119.35 | 19.1 | 19.6072 | -0.50722 |  | 2026-08-03 08:50 | 114.418 | 115.773 | 90.6 | 19.2955 | 18.9245 | 0.37104 | 113.5468 | 18 | 18.6538 | -0.65384 |  | 2026-08-03 08:50 | 208.0258 | 205.9062 | 2.1197 | 1235.4371 | 194.6 | 202.9617 | -8.3617
2026-08-03 08:40 | 402 | 45.06 | 142.235 | 143.904 | 101.4 | 23.984 | 24.2786 | -0.29458 | 145.6715 | 22.5 | 23.9314 | -1.4314 |  | 2026-08-03 08:40 | 144.029 | 145.764 | 100.7 | 24.294 | 24.2786 | 0.015425 | 145.6715 | 23 | 23.9314 | -0.93139 |  | 2026-08-03 08:40 | 141.621 | 143.741 | 99.8 | 23.9568 | 24.2786 | -0.32174 | 145.6715 | 22 | 23.9314 | -1.9314 |  | 2026-08-03 08:40 | 143.925 | 145.614 | 101.1 | 24.269 | 24.2786 | -0.0095752 | 145.6715 | 22.3 | 23.9314 | -1.6314 |  | 2026-08-03 08:40 | 105.512 | 106.729 | 73.9 | 17.7882 | 17.9841 | -0.19596 | 107.9048 | 16.6 | 17.727 | -1.127 |  | 2026-08-03 08:40 | 107.208 | 108.433 | 75.9 | 18.0722 | 17.9841 | 0.088037 | 107.9048 | 16.9 | 17.727 | -0.82696 |  | 2026-08-03 08:40 | 106.478 | 107.693 | 75.5 | 17.9488 | 17.9841 | -0.035296 | 107.9048 | 16.8 | 17.727 | -0.92696 |  | 2026-08-03 08:40 | 108.029 | 111.069 | 76.9 | 18.5115 | 17.9841 | 0.52737 | 107.9048 | 17 | 17.727 | -0.72696 |  | 2026-08-03 08:40 | 102.659 | 103.853 | 72.6 | 17.3088 | 17.1097 | 0.19916 | 102.658 | 16.2 | 16.865 | -0.665 |  | 2026-08-03 08:40 | 186.1333 | 186.1605 | -0.027159 | 1116.963 | 173.3 | 183.4984 | -10.1984
2026-08-03 08:30 | 359 | 41.33 | 125.333 | 126.753 | 78.9 | 21.1255 | 21.986 | -0.86054 | 131.9162 | 19.7 | 21.6716 | -1.9716 |  | 2026-08-03 08:30 | 126.637 | 128.097 | 77.7 | 21.3495 | 21.986 | -0.63654 | 131.9162 | 19.5 | 21.6716 | -2.1716 |  | 2026-08-03 08:30 | 125.436 | 127.424 | 77.8 | 21.2373 | 21.986 | -0.74871 | 131.9162 | 19.4 | 21.6716 | -2.2716 |  | 2026-08-03 08:30 | 127.278 | 128.746 | 78.8 | 21.4577 | 21.986 | -0.52837 | 131.9162 | 19.9 | 21.6716 | -1.7716 |  | 2026-08-03 08:30 | 92.796 | 93.847 | 57.3 | 15.6412 | 16.286 | -0.64479 | 97.7157 | 14.4 | 16.0531 | -1.6531 |  | 2026-08-03 08:30 | 94.617 | 95.66 | 59 | 15.9433 | 16.286 | -0.34262 | 97.7157 | 14.7 | 16.0531 | -1.3531 |  | 2026-08-03 08:30 | 93.983 | 95.038 | 58.7 | 15.8397 | 16.286 | -0.44629 | 97.7157 | 14.6 | 16.0531 | -1.4531 |  | 2026-08-03 08:30 | 95.136 | 97.626 | 59.9 | 16.271 | 16.286 | -0.014956 | 97.7157 | 14.8 | 16.0531 | -1.2531 |  | 2026-08-03 08:30 | 90.461 | 91.486 | 56.4 | 15.2477 | 15.4941 | -0.2464 | 92.9644 | 14.1 | 15.2725 | -1.1725 |  | 2026-08-03 08:30 | 164.1128 | 168.5821 | -4.4692 | 1011.4923 | 151.1 | 166.1713 | -15.0713
2026-08-03 08:20 | 314 | 33.87 | 108.452 | 109.625 | 59.2 | 18.2708 | 19.7627 | -1.4918 | 118.576 | 16.4 | 19.4801 | -3.0801 |  | 2026-08-03 08:20 | 109.317 | 110.555 | 58.2 | 18.4258 | 19.7627 | -1.3368 | 118.576 | 16.6 | 19.4801 | -2.8801 |  | 2026-08-03 08:20 | 107.697 | 109.122 | 58.4 | 18.187 | 19.7627 | -1.5757 | 118.576 | 16.4 | 19.4801 | -3.0801 |  | 2026-08-03 08:20 | 109.69 | 110.91 | 58.9 | 18.485 | 19.7627 | -1.2777 | 118.576 | 16.8 | 19.4801 | -2.6801 |  | 2026-08-03 08:20 | 79.668 | 80.603 | 42.9 | 13.4338 | 14.639 | -1.2052 | 87.8341 | 12.1 | 14.4297 | -2.3297 |  | 2026-08-03 08:20 | 81.716 | 82.633 | 44.3 | 13.7722 | 14.639 | -0.86685 | 87.8341 | 12.3 | 14.4297 | -2.1297 |  | 2026-08-03 08:20 | 81.125 | 82.069 | 44.1 | 13.6782 | 14.639 | -0.96085 | 87.8341 | 12.2 | 14.4297 | -2.2297 |  | 2026-08-03 08:20 | 82.523 | 84.755 | 45.1 | 14.1258 | 14.639 | -0.51318 | 87.8341 | 12.5 | 14.4297 | -1.9297 |  | 2026-08-03 08:20 | 78.363 | 79.291 | 42.3 | 13.2152 | 13.9272 | -0.71204 | 83.5632 | 12 | 13.728 | -1.728 |  | 2026-08-03 08:20 | 141.5938 | 151.5339 | -9.9401 | 909.2035 | 127.3 | 149.367 | -22.067
2026-08-03 08:10 | 266 | 29.85 | 90.165 | 91.12 | 42.8 | 15.1867 | 16.9847 | -1.7981 | 101.9083 | 13.5 | 16.7418 | -3.2418 |  | 2026-08-03 08:10 | 88.548 | 89.515 | 41.6 | 14.9192 | 16.9847 | -2.0656 | 101.9083 | 13.6 | 16.7418 | -3.1418 |  | 2026-08-03 08:10 | 88.746 | 89.886 | 42 | 14.981 | 16.9847 | -2.0037 | 101.9083 | 13.4 | 16.7418 | -3.3418 |  | 2026-08-03 08:10 | 90.813 | 91.795 | 42.1 | 15.2992 | 16.9847 | -1.6856 | 101.9083 | 13.7 | 16.7418 | -3.0418 |  | 2026-08-03 08:10 | 65.835 | 66.628 | 30.8 | 11.1047 | 12.5813 | -1.4766 | 75.4877 | 9.9 | 12.4014 | -2.5014 |  | 2026-08-03 08:10 | 67.867 | 68.621 | 32 | 11.4368 | 12.5813 | -1.1444 | 75.4877 | 10.3 | 12.4014 | -2.1014 |  | 2026-08-03 08:10 | 67.249 | 68.052 | 31.9 | 11.342 | 12.5813 | -1.2393 | 75.4877 | 10.2 | 12.4014 | -2.2014 |  | 2026-08-03 08:10 | 68.491 | 70.583 | 32.6 | 11.7638 | 12.5813 | -0.81744 | 75.4877 | 10.3 | 12.4014 | -2.1014 |  | 2026-08-03 08:10 | 64.959 | 65.748 | 30.3 | 10.958 | 11.9695 | -1.0115 | 71.8172 | 9.7 | 11.7984 | -2.0984 |  | 2026-08-03 08:10 | 116.9913 | 130.2335 | -13.2422 | 781.4011 | 104.6 | 128.3712 | -23.7712
2026-08-03 08:00 | 222 | 27.26 | 72.784 | 73.586 | 29.3 | 12.2643 | 14.3059 | -2.0416 | 85.8356 | 11.1 | 14.1014 | -3.0014 |  | 2026-08-03 08:00 | 71.705 | 72.563 | 28 | 12.0938 | 14.3059 | -2.2121 | 85.8356 | 10.5 | 14.1014 | -3.6014 |  | 2026-08-03 08:00 | 71.595 | 72.399 | 28.6 | 12.0665 | 14.3059 | -2.2394 | 85.8356 | 10.5 | 14.1014 | -3.6014 |  | 2026-08-03 08:00 | 73.063 | 73.898 | 28.4 | 12.3163 | 14.3059 | -1.9896 | 85.8356 | 10.7 | 14.1014 | -3.4014 |  | 2026-08-03 08:00 | 52.89 | 53.587 | 20.9 | 8.9312 | 10.597 | -1.6658 | 63.5819 | 7.7 | 10.4455 | -2.7455 |  | 2026-08-03 08:00 | 54.709 | 55.407 | 21.7 | 9.2345 | 10.597 | -1.3625 | 63.5819 | 8 | 10.4455 | -2.4455 |  | 2026-08-03 08:00 | 54.268 | 54.977 | 21.7 | 9.1628 | 10.597 | -1.4342 | 63.5819 | 8 | 10.4455 | -2.4455 |  | 2026-08-03 08:00 | 55.273 | 56.669 | 22.3 | 9.4448 | 10.597 | -1.1522 | 63.5819 | 8.2 | 10.4455 | -2.2455 |  | 2026-08-03 08:00 | 52.624 | 53.328 | 20.6 | 8.888 | 10.0817 | -1.1937 | 60.4903 | 7.8 | 9.9376 | -2.1376 |  | 2026-08-03 08:00 | 94.4023 | 109.6934 | -15.2911 | 658.1606 | 82.5 | 108.1248 | -25.6248
2026-08-03 07:50 | 176 | 23.53 | 55.092 | 55.761 | 18.2 | 9.2935 | 11.4909 | -2.1974 | 68.9453 | 7.7 | 11.3266 | -3.6266 |  | 2026-08-03 07:50 | 54.792 | 55.573 | 17.5 | 9.2622 | 11.4909 | -2.2287 | 68.9453 | 7.9 | 11.3266 | -3.4266 |  | 2026-08-03 07:50 | 54.596 | 55.258 | 18.1 | 9.2097 | 11.4909 | -2.2812 | 68.9453 | 7.8 | 11.3266 | -3.5266 |  | 2026-08-03 07:50 | 55.622 | 56.326 | 17.7 | 9.3877 | 11.4909 | -2.1032 | 68.9453 | 7.8 | 11.3266 | -3.5266 |  | 2026-08-03 07:50 | 40.23 | 41.004 | 13.2 | 6.834 | 8.5118 | -1.6778 | 51.0706 | 5.7 | 8.3901 | -2.6901 |  | 2026-08-03 07:50 | 41.844 | 42.397 | 13.7 | 7.0662 | 8.5118 | -1.4456 | 51.0706 | 5.9 | 8.3901 | -2.4901 |  | 2026-08-03 07:50 | 41.522 | 42.129 | 13.7 | 7.0215 | 8.5118 | -1.4903 | 51.0706 | 5.8 | 8.3901 | -2.5901 |  | 2026-08-03 07:50 | 42.446 | 43.763 | 14.1 | 7.2938 | 8.5118 | -1.2179 | 51.0706 | 6.1 | 8.3901 | -2.2901 |  | 2026-08-03 07:50 | 40.322 | 40.919 | 12.8 | 6.8198 | 8.0979 | -1.2781 | 48.5874 | 5.7 | 7.9821 | -2.2821 |  | 2026-08-03 07:50 | 72.1883 | 88.1085 | -15.9202 | 528.6512 | 60.4 | 86.8486 | -26.4486
2026-08-03 07:40 | 132 | 20.95 | 39.363 | 39.934 | 10.5 | 6.6557 | 8.6956 | -2.0399 | 52.1735 | 5.3 | 8.5712 | -3.2712 |  | 2026-08-03 07:40 | 36.74 | 38.619 | 9.6 | 6.4365 | 8.6956 | -2.2591 | 52.1735 | 4.9 | 8.5712 | -3.6712 |  | 2026-08-03 07:40 | 38.745 | 39.307 | 10.3 | 6.5512 | 8.6956 | -2.1444 | 52.1735 | 5.2 | 8.5712 | -3.3712 |  | 2026-08-03 07:40 | 38.814 | 39.363 | 9.9 | 6.5605 | 8.6956 | -2.1351 | 52.1735 | 5.2 | 8.5712 | -3.3712 |  | 2026-08-03 07:40 | 28.434 | 29.076 | 7.5 | 4.846 | 6.4412 | -1.5952 | 38.6471 | 3.8 | 6.3491 | -2.5491 |  | 2026-08-03 07:40 | 29.839 | 30.327 | 7.8 | 5.0545 | 6.4412 | -1.3867 | 38.6471 | 4.1 | 6.3491 | -2.2491 |  | 2026-08-03 07:40 | 29.587 | 30.071 | 7.9 | 5.0118 | 6.4412 | -1.4293 | 38.6471 | 4.1 | 6.3491 | -2.2491 |  | 2026-08-03 07:40 | 30.248 | 31.262 | 8 | 5.2103 | 6.4412 | -1.2308 | 38.6471 | 4.1 | 6.3491 | -2.2491 |  | 2026-08-03 07:40 | 28.478 | 28.959 | 7.1 | 4.8265 | 6.128 | -1.3015 | 36.7679 | 3.8 | 6.0404 | -2.2404 |  | 2026-08-03 07:40 | 51.153 | 66.6751 | -15.5221 | 400.0504 | 40.5 | 65.7216 | -25.2216
2026-08-03 07:30 | 90 | 19.23 | 25.251 | 25.716 | 5.2 | 4.286 | 5.964 | -1.678 | 35.784 | 3.2 | 5.8787 | -2.6787 |  | 2026-08-03 07:30 | 22.899 | 24.129 | 4.7 | 4.0215 | 5.964 | -1.9425 | 35.784 | 2.9 | 5.8787 | -2.9787 |  | 2026-08-03 07:30 | 24.803 | 25.253 | 5.1 | 4.2088 | 5.964 | -1.7552 | 35.784 | 3.2 | 5.8787 | -2.6787 |  | 2026-08-03 07:30 | 23.635 | 24.243 | 4.7 | 4.0405 | 5.964 | -1.9235 | 35.784 | 2.9 | 5.8787 | -2.9787 |  | 2026-08-03 07:30 | 17.979 | 18.757 | 3.7 | 3.1262 | 4.4178 | -1.2916 | 26.5067 | 2.3 | 4.3546 | -2.0546 |  | 2026-08-03 07:30 | 18.004 | 18.411 | 3.7 | 3.0685 | 4.4178 | -1.3493 | 26.5067 | 2.3 | 4.3546 | -2.0546 |  | 2026-08-03 07:30 | 18.782 | 19.195 | 3.8 | 3.1992 | 4.4178 | -1.2186 | 26.5067 | 2.4 | 4.3546 | -1.9546 |  | 2026-08-03 07:30 | 19.372 | 20.253 | 3.9 | 3.3755 | 4.4178 | -1.0423 | 26.5067 | 2.4 | 4.3546 | -1.9546 |  | 2026-08-03 07:30 | 17.078 | 17.473 | 3.3 | 2.9122 | 4.203 | -1.2908 | 25.2178 | 2.1 | 4.1429 | -2.0429 |  | 2026-08-03 07:30 | 32.2383 | 45.7301 | -13.4918 | 274.3807 | 23.7 | 45.0762 | -21.3762
2026-08-03 07:20 | 26 | 17.22 | 13.7 | 14.073 | 2 | 2.3455 | 1.7348 | 0.61068 | 10.4089 | 1.6 | 1.71 | -0.11001 |  | 2026-08-03 07:20 | 11.991 | 12.667 | 1.8 | 2.1112 | 1.7348 | 0.37635 | 10.4089 | 1.4 | 1.71 | -0.31001 |  | 2026-08-03 07:20 | 13.727 | 14.101 | 1.9 | 2.3502 | 1.7348 | 0.61535 | 10.4089 | 1.5 | 1.71 | -0.21001 |  | 2026-08-03 07:20 | 12.164 | 12.83 | 1.8 | 2.1383 | 1.7348 | 0.40352 | 10.4089 | 1.5 | 1.71 | -0.21001 |  | 2026-08-03 07:20 | 9.917 | 10.653 | 1.4 | 1.7755 | 1.285 | 0.49045 | 7.7103 | 1.2 | 1.2667 | -0.066672 |  | 2026-08-03 07:20 | 9.521 | 9.847 | 1.4 | 1.6412 | 1.285 | 0.35612 | 7.7103 | 1 | 1.2667 | -0.26667 |  | 2026-08-03 07:20 | 10.363 | 10.707 | 1.4 | 1.7845 | 1.285 | 0.49945 | 7.7103 | 1.2 | 1.2667 | -0.066672 |  | 2026-08-03 07:20 | 10.725 | 11.264 | 1.5 | 1.8773 | 1.285 | 0.59228 | 7.7103 | 1.3 | 1.2667 | 0.033328 |  | 2026-08-03 07:20 | 8.986 | 9.297 | 1.2 | 1.5495 | 1.2226 | 0.32694 | 7.3354 | 1 | 1.2051 | -0.20508 |  | 2026-08-03 07:20 | 17.5732 | 13.302 | 4.2711 | 79.8121 | 11.7 | 13.1118 | -1.4118
2026-08-03 07:10 | 13 | 14.92 | 6.097 | 6.353 | 0.4 | 1.0588 | 0.87421 | 0.18463 | 5.2452 | 0.4 | 0.8617 | -0.4617 |  | 2026-08-03 07:10 | 5.371 | 6.004 | 0.4 | 1.0007 | 0.87421 | 0.12646 | 5.2452 | 0.4 | 0.8617 | -0.4617 |  | 2026-08-03 07:10 | 5.771 | 6.016 | 0.4 | 1.0027 | 0.87421 | 0.12846 | 5.2452 | 0.4 | 0.8617 | -0.4617 |  | 2026-08-03 07:10 | 5.444 | 6.215 | 0.3 | 1.0358 | 0.87421 | 0.16163 | 5.2452 | 0.3 | 0.8617 | -0.5617 |  | 2026-08-03 07:10 | 4.179 | 4.81 | 0.2 | 0.80167 | 0.64756 | 0.15411 | 3.8854 | 0.2 | 0.6383 | -0.4383 |  | 2026-08-03 07:10 | 3.793 | 3.966 | 0.4 | 0.661 | 0.64756 | 0.01344 | 3.8854 | 0.4 | 0.6383 | -0.2383 |  | 2026-08-03 07:10 | 4.331 | 4.527 | 0.2 | 0.7545 | 0.64756 | 0.10694 | 3.8854 | 0.2 | 0.6383 | -0.4383 |  | 2026-08-03 07:10 | 4.322 | 4.762 | 0.2 | 0.79367 | 0.64756 | 0.14611 | 3.8854 | 0.2 | 0.6383 | -0.4383 |  | 2026-08-03 07:10 | 3.759 | 3.932 | 0.2 | 0.65533 | 0.61607 | 0.039261 | 3.6964 | 0.2 | 0.60726 | -0.40726 |  | 2026-08-03 07:10 | 7.7642 | 6.7031 | 1.061 | 40.2188 | 2.7 | 6.6073 | -3.9073
2026-08-03 07:00 | 3 | 15.5 | 0 | 0 | 0 | 0 | 0.20134 | -0.20134 | 1.2081 | 0 | 0.19846 | -0.19846 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.20134 | -0.20134 | 1.2081 | 0 | 0.19846 | -0.19846 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.20134 | -0.20134 | 1.2081 | 0 | 0.19846 | -0.19846 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.20134 | -0.20134 | 1.2081 | 0 | 0.19846 | -0.19846 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.14914 | -0.14914 | 0.89486 | 0 | 0.14701 | -0.14701 |  | 2026-08-03 07:00 | 1.005 | 1.047 | 0 | 0.1745 | 0.14914 | 0.025356 | 0.89486 | 0 | 0.14701 | -0.14701 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.14914 | -0.14914 | 0.89486 | 0 | 0.14701 | -0.14701 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.14914 | -0.14914 | 0.89486 | 0 | 0.14701 | -0.14701 |  | 2026-08-03 07:00 | 0 | 0 | 0 | 0 | 0.14189 | -0.14189 | 0.85135 | 0 | 0.13986 | -0.13986 |  | 2026-08-03 07:00 | 0.1745 | 1.5438 | -1.3693 | 9.2631 | 0 | 1.5218 | -1.5218
[110 empty] | Total: - | 19257.8195 | 20463.0478 | -1205.2283 |  | 19145.6 | 20170.4262 | -1024.8262
Sum:- | 44665 |  | 14710.883 |  | 91847.8 |  |  |  |  | 2495 | 2630.5754 | -135.5754 | 0.98279 |  | 13607.876 |  | 87886.9 |  |  |  |  | 2516.8 | 2630.5754 | -113.7754 | 0.98244 |  | 14848.196 |  | 93424.9 |  |  |  |  | 2474.3 | 2630.5754 | -156.2754 | 0.97221 |  | 14949.065 |  | 94296.1 |  |  |  |  | 2494.1 | 2630.5754 | -136.4754 | 0.98286 |  | 11172.033 |  | 70269.5 |  |  |  |  | 1862.6 | 1948.5744 | -85.9744 | 0.98413 |  | 11073.458 |  | 69922.5 |  |  |  |  | 1845.9 | 1948.5744 | -102.6744 | 0.98122 |  | 11062.833 |  | 69806.3 |  |  |  |  | 1844.3 | 1948.5744 | -104.2744 | 0.9803 |  | 11135.067 |  | 70392.7 |  |  |  |  | 1855.9 | 1948.5744 | -92.6744 | 0.97151 |  | 10541.735 |  | 66618.7 |  |  |  |  | 1756.7 | 1853.8272 | -97.1272 | 0.98443
Formulas:
Time = [Time]

## 9 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-09-03 19:00 | 0 | 33.29 | 0.089 | 0.094 | 2097.1 | 0.015667 | 0 | 0.015667 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.092 | 0.256 | 2117.3 | 0.042667 | 0 | 0.042667 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.065 | 0.092 | 2090.3 | 0.015333 | 0 | 0.015333 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.058 | 0.14 | 2096.5 | 0.023333 | 0 | 0.023333 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.102 | 0.107 | 1580.8 | 0.017833 | 0 | 0.017833 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.06 | 0.075 | 1558.8 | 0.0125 | 0 | 0.0125 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.052 | 0.069 | 1560.9 | 0.0115 | 0 | 0.0115 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.082 | 0.087 | 1571 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.094 | 0.099 | 1485.6 | 0.0165 | 0 | 0.0165 | 0 | 0 | 0 | 0 |  | 2026-09-03 19:00 | 0.16983 | 0 | 0.16983 | 0 | 0 | 0 | 0 | 1 | 98.36%
2026-09-03 18:50 | 0 | 35.59 | 0.372 | 0.391 | 2097.1 | 0.065167 | 0 | 0.065167 | 0 | 0.2 | 0 | 0.2 |  | 2026-09-03 18:50 | 0.638 | 1.073 | 2117.3 | 0.17883 | 0 | 0.17883 | 0 | 0.2 | 0 | 0.2 |  | 2026-09-03 18:50 | 0.435 | 0.466 | 2090.3 | 0.077667 | 0 | 0.077667 | 0 | 0.2 | 0 | 0.2 |  | 2026-09-03 18:50 | 0.414 | 0.768 | 2096.4 | 0.128 | 0 | 0.128 | 0 | 0.2 | 0 | 0.2 |  | 2026-09-03 18:50 | 0.164 | 0.262 | 1580.8 | 0.043667 | 0 | 0.043667 | 0 | 0.1 | 0 | 0.1 |  | 2026-09-03 18:50 | 0.14 | 0.147 | 1558.8 | 0.0245 | 0 | 0.0245 | 0 | 0.1 | 0 | 0.1 |  | 2026-09-03 18:50 | 0.15 | 0.158 | 1560.9 | 0.026333 | 0 | 0.026333 | 0 | 0.1 | 0 | 0.1 |  | 2026-09-03 18:50 | 0.227 | 0.531 | 1571 | 0.0885 | 0 | 0.0885 | 0 | 0.1 | 0 | 0.1 |  | 2026-09-03 18:50 | 0.093 | 0.101 | 1485.6 | 0.016833 | 0 | 0.016833 | 0 | 0.1 | 0 | 0.1 |  | 2026-09-03 18:50 | 0.6495 | 0 | 0.6495 | 0 | 1.3 | 0 | 1.3 | 2 | 98.2%
2026-09-03 18:40 | 0 | 37.88 | 2.492 | 2.62 | 2096.9 | 0.43667 | 0 | 0.43667 | 0 | 0.7 | 0 | 0.7 |  | 2026-09-03 18:40 | 2.86 | 3.211 | 2117.1 | 0.53517 | 0 | 0.53517 | 0 | 0.8 | 0 | 0.8 |  | 2026-09-03 18:40 | 2.472 | 2.599 | 2090.1 | 0.43317 | 0 | 0.43317 | 0 | 0.7 | 0 | 0.7 |  | 2026-09-03 18:40 | 2.334 | 2.819 | 2096.2 | 0.46983 | 0 | 0.46983 | 0 | 0.7 | 0 | 0.7 |  | 2026-09-03 18:40 | 1.67 | 1.885 | 1580.7 | 0.31417 | 0 | 0.31417 | 0 | 0.5 | 0 | 0.5 |  | 2026-09-03 18:40 | 1.555 | 1.635 | 1558.7 | 0.2725 | 0 | 0.2725 | 0 | 0.5 | 0 | 0.5 |  | 2026-09-03 18:40 | 1.677 | 1.763 | 1560.8 | 0.29383 | 0 | 0.29383 | 0 | 0.5 | 0 | 0.5 |  | 2026-09-03 18:40 | 1.744 | 1.976 | 1570.9 | 0.32933 | 0 | 0.32933 | 0 | 0.5 | 0 | 0.5 |  | 2026-09-03 18:40 | 1.55 | 1.63 | 1485.5 | 0.27167 | 0 | 0.27167 | 0 | 0.5 | 0 | 0.5 |  | 2026-09-03 18:40 | 3.3563 | 0 | 3.3563 | 0 | 5.4 | 0 | 5.4 | 3 | 97.16%
2026-09-03 18:30 | 11 | 40.75 | 6.199 | 6.482 | 2096.2 | 1.0803 | 0.67512 | 0.40522 | 4.0507 | 1.5 | 0.66546 | 0.83454 |  | 2026-09-03 18:30 | 7.024 | 7.156 | 2116.3 | 1.1927 | 0.67512 | 0.51755 | 4.0507 | 1.7 | 0.66546 | 1.0345 |  | 2026-09-03 18:30 | 6.48 | 6.766 | 2089.4 | 1.1277 | 0.67512 | 0.45255 | 4.0507 | 1.6 | 0.66546 | 0.93454 |  | 2026-09-03 18:30 | 6.701 | 7.011 | 2095.5 | 1.1685 | 0.67512 | 0.49338 | 4.0507 | 1.6 | 0.66546 | 0.93454 |  | 2026-09-03 18:30 | 4.832 | 5.059 | 1580.2 | 0.84317 | 0.50009 | 0.34308 | 3.0005 | 1.2 | 0.49294 | 0.70706 |  | 2026-09-03 18:30 | 4.456 | 4.668 | 1558.2 | 0.778 | 0.50009 | 0.27791 | 3.0005 | 1.1 | 0.49294 | 0.60706 |  | 2026-09-03 18:30 | 4.608 | 4.827 | 1560.3 | 0.8045 | 0.50009 | 0.30441 | 3.0005 | 1.2 | 0.49294 | 0.70706 |  | 2026-09-03 18:30 | 4.254 | 4.65 | 1570.4 | 0.775 | 0.50009 | 0.27491 | 3.0005 | 0.9 | 0.49294 | 0.40706 |  | 2026-09-03 18:30 | 4.102 | 4.305 | 1485 | 0.7175 | 0.47577 | 0.24173 | 2.8546 | 0.9 | 0.46897 | 0.43103 |  | 2026-09-03 18:30 | 8.4873 | 5.1766 | 3.3107 | 31.0595 | 11.7 | 5.1026 | 6.5974 | 4 | 98.33%
2026-09-03 18:20 | 22 | 43.91 | 12.409 | 12.579 | 2094.7 | 2.0965 | 1.3344 | 0.76207 | 8.0066 | 2.7 | 1.3153 | 1.3847 |  | 2026-09-03 18:20 | 14.014 | 14.446 | 2114.6 | 2.4077 | 1.3344 | 1.0732 | 8.0066 | 3 | 1.3153 | 1.6847 |  | 2026-09-03 18:20 | 13.049 | 13.46 | 2087.8 | 2.2433 | 1.3344 | 0.9089 | 8.0066 | 2.9 | 1.3153 | 1.5847 |  | 2026-09-03 18:20 | 13.275 | 13.69 | 2093.9 | 2.2817 | 1.3344 | 0.94724 | 8.0066 | 3 | 1.3153 | 1.6847 |  | 2026-09-03 18:20 | 9.714 | 10.076 | 1579 | 1.6793 | 0.98847 | 0.69087 | 5.9308 | 2.2 | 0.97433 | 1.2257 |  | 2026-09-03 18:20 | 8.858 | 9.2 | 1557.1 | 1.5333 | 0.98847 | 0.54487 | 5.9308 | 2 | 0.97433 | 1.0257 |  | 2026-09-03 18:20 | 9.322 | 9.677 | 1559.1 | 1.6128 | 0.98847 | 0.62437 | 5.9308 | 2.1 | 0.97433 | 1.1257 |  | 2026-09-03 18:20 | 7.142 | 7.569 | 1569.5 | 1.2615 | 0.98847 | 0.27303 | 5.9308 | 1.6 | 0.97433 | 0.62567 |  | 2026-09-03 18:20 | 7.854 | 8.172 | 1484.1 | 1.362 | 0.9404 | 0.4216 | 5.6424 | 1.8 | 0.92696 | 0.87304 |  | 2026-09-03 18:20 | 16.4782 | 10.232 | 6.2462 | 61.3919 | 21.3 | 10.0857 | 11.2143 | 5 | 98.41%
2026-09-03 18:10 | 35 | 46.49 | 21.417 | 21.936 | 2092 | 3.656 | 2.1024 | 1.5536 | 12.6146 | 4.5 | 2.0724 | 2.4276 |  | 2026-09-03 18:10 | 23.147 | 23.673 | 2111.6 | 3.9455 | 2.1024 | 1.8431 | 12.6146 | 4.8 | 2.0724 | 2.7276 |  | 2026-09-03 18:10 | 22.609 | 23.134 | 2084.9 | 3.8557 | 2.1024 | 1.7532 | 12.6146 | 4.8 | 2.0724 | 2.7276 |  | 2026-09-03 18:10 | 22.499 | 22.983 | 2090.9 | 3.8305 | 2.1024 | 1.7281 | 12.6146 | 4.6 | 2.0724 | 2.5276 |  | 2026-09-03 18:10 | 16.466 | 16.899 | 1576.8 | 2.8165 | 1.5574 | 1.2591 | 9.3441 | 3.5 | 1.5351 | 1.9649 |  | 2026-09-03 18:10 | 15.222 | 15.63 | 1555.1 | 2.605 | 1.5574 | 1.0476 | 9.3441 | 3.3 | 1.5351 | 1.7649 |  | 2026-09-03 18:10 | 16.268 | 16.697 | 1557 | 2.7828 | 1.5574 | 1.2255 | 9.3441 | 3.4 | 1.5351 | 1.8649 |  | 2026-09-03 18:10 | 11.959 | 12.584 | 1567.9 | 2.0973 | 1.5574 | 0.53998 | 9.3441 | 2.8 | 1.5351 | 1.2649 |  | 2026-09-03 18:10 | 14.558 | 14.98 | 1482.3 | 2.4967 | 1.4816 | 1.015 | 8.8898 | 3.2 | 1.4604 | 1.7396 |  | 2026-09-03 18:10 | 28.086 | 16.1208 | 11.9652 | 96.7245 | 34.9 | 15.8902 | 19.0098 | 6 | 98.14%
2026-09-03 18:00 | 48 | 47.64 | 33.89 | 34.497 | 2087.5 | 5.7495 | 2.8708 | 2.8787 | 17.2247 | 6.7 | 2.8297 | 3.8703 |  | 2026-09-03 18:00 | 35.52 | 36.16 | 2106.8 | 6.0267 | 2.8708 | 3.1559 | 17.2247 | 7.1 | 2.8297 | 4.2703 |  | 2026-09-03 18:00 | 34.781 | 35.401 | 2080.1 | 5.9002 | 2.8708 | 3.0294 | 17.2247 | 7 | 2.8297 | 4.1703 |  | 2026-09-03 18:00 | 34.173 | 34.792 | 2086.3 | 5.7987 | 2.8708 | 2.9279 | 17.2247 | 6.9 | 2.8297 | 4.0703 |  | 2026-09-03 18:00 | 25.939 | 26.475 | 1573.3 | 4.4125 | 2.1265 | 2.286 | 12.759 | 5.2 | 2.0961 | 3.1039 |  | 2026-09-03 18:00 | 24.791 | 25.36 | 1551.8 | 4.2267 | 2.1265 | 2.1002 | 12.759 | 5 | 2.0961 | 2.9039 |  | 2026-09-03 18:00 | 24.99 | 25.555 | 1553.6 | 4.2592 | 2.1265 | 2.1327 | 12.759 | 5 | 2.0961 | 2.9039 |  | 2026-09-03 18:00 | 22.554 | 23.345 | 1565.1 | 3.8908 | 2.1265 | 1.7643 | 12.759 | 4.8 | 2.0961 | 2.7039 |  | 2026-09-03 18:00 | 23.028 | 23.541 | 1479.1 | 3.9235 | 2.0231 | 1.9004 | 12.1386 | 4.6 | 1.9942 | 2.6058 |  | 2026-09-03 18:00 | 44.1877 | 22.0122 | 22.1754 | 132.0735 | 52.3 | 21.6975 | 30.6025 | 7 | 98.02%
2026-09-03 17:50 | 147 | 47.93 | 47.629 | 48.399 | 2080.8 | 8.0665 | 8.7821 | -0.71557 | 52.6924 | 9.9 | 8.6565 | 1.2435 |  | 2026-09-03 17:50 | 50.782 | 50.683 | 2099.7 | 8.4472 | 8.7821 | -0.33491 | 52.6924 | 9.8 | 8.6565 | 1.1435 |  | 2026-09-03 17:50 | 49.522 | 50.302 | 2073.1 | 8.3837 | 8.7821 | -0.39841 | 52.6924 | 9.7 | 8.6565 | 1.0435 |  | 2026-09-03 17:50 | 48.907 | 49.682 | 2079.4 | 8.2803 | 8.7821 | -0.50174 | 52.6924 | 9.6 | 8.6565 | 0.94351 |  | 2026-09-03 17:50 | 36.947 | 37.597 | 1568.1 | 6.2662 | 6.5052 | -0.23907 | 39.0314 | 7.1 | 6.4122 | 0.68779 |  | 2026-09-03 17:50 | 35.102 | 35.731 | 1546.8 | 5.9552 | 6.5052 | -0.55007 | 39.0314 | 6.9 | 6.4122 | 0.48779 |  | 2026-09-03 17:50 | 35.783 | 36.413 | 1548.6 | 6.0688 | 6.5052 | -0.43641 | 39.0314 | 7 | 6.4122 | 0.58779 |  | 2026-09-03 17:50 | 35.327 | 36.328 | 1560.3 | 6.0547 | 6.5052 | -0.45057 | 39.0314 | 7 | 6.4122 | 0.58779 |  | 2026-09-03 17:50 | 33.164 | 33.758 | 1474.5 | 5.6263 | 6.1889 | -0.5626 | 37.1336 | 6.6 | 6.1004 | 0.49957 |  | 2026-09-03 17:50 | 63.1488 | 67.3382 | -4.1893 | 404.0291 | 73.6 | 66.3752 | 7.2248 | 8 | 97.11%
2026-09-03 17:40 | 207 | 47.93 | 65.464 | 66.333 | 2070.9 | 11.0555 | 12.3666 | -1.3111 | 74.1996 | 11.9 | 12.1898 | -0.28975 |  | 2026-09-03 17:40 | 67.339 | 67.84 | 2089.9 | 11.3067 | 12.3666 | -1.0599 | 74.1996 | 12.2 | 12.1898 | 0.01025 |  | 2026-09-03 17:40 | 66.496 | 67.53 | 2063.4 | 11.255 | 12.3666 | -1.1116 | 74.1996 | 12.5 | 12.1898 | 0.31025 |  | 2026-09-03 17:40 | 65.497 | 66.395 | 2069.8 | 11.0658 | 12.3666 | -1.3008 | 74.1996 | 12.3 | 12.1898 | 0.11025 |  | 2026-09-03 17:40 | 49.303 | 50.084 | 1561 | 8.3473 | 9.1604 | -0.81311 | 54.9626 | 9.3 | 9.0294 | 0.27056 |  | 2026-09-03 17:40 | 47.188 | 47.946 | 1539.9 | 7.991 | 9.1604 | -1.1694 | 54.9626 | 9 | 9.0294 | -0.029445 |  | 2026-09-03 17:40 | 48.185 | 48.944 | 1541.6 | 8.1573 | 9.1604 | -1.0031 | 54.9626 | 9.1 | 9.0294 | 0.070555 |  | 2026-09-03 17:40 | 47.727 | 49.193 | 1553.3 | 8.1988 | 9.1604 | -0.96161 | 54.9626 | 9 | 9.0294 | -0.029445 |  | 2026-09-03 17:40 | 44.92 | 45.646 | 1467.9 | 7.6077 | 8.715 | -1.1074 | 52.2901 | 8.4 | 8.5904 | -0.1904 |  | 2026-09-03 17:40 | 84.9852 | 94.8231 | -9.838 | 568.9389 | 93.7 | 93.4672 | 0.23282 | 9 | 98.43%
2026-09-03 17:30 | 255 | 47.93 | 82.023 | 83.053 | 2059 | 13.8422 | 15.2342 | -1.392 | 91.4052 | 15.7 | 15.0164 | 0.68364 |  | 2026-09-03 17:30 | 84.436 | 85.213 | 2077.7 | 14.2022 | 15.2342 | -1.032 | 91.4052 | 15.8 | 15.0164 | 0.78364 |  | 2026-09-03 17:30 | 83.448 | 85.008 | 2050.9 | 14.168 | 15.2342 | -1.0662 | 91.4052 | 15.4 | 15.0164 | 0.38364 |  | 2026-09-03 17:30 | 82.636 | 83.729 | 2057.5 | 13.9548 | 15.2342 | -1.2794 | 91.4052 | 15.4 | 15.0164 | 0.38364 |  | 2026-09-03 17:30 | 61.952 | 62.806 | 1551.7 | 10.4677 | 11.2846 | -0.81693 | 67.7076 | 11.5 | 11.1232 | 0.37677 |  | 2026-09-03 17:30 | 60.153 | 60.995 | 1530.9 | 10.1658 | 11.2846 | -1.1188 | 67.7076 | 11.2 | 11.1232 | 0.076771 |  | 2026-09-03 17:30 | 60.944 | 61.644 | 1532.5 | 10.274 | 11.2846 | -1.0106 | 67.7076 | 11.2 | 11.1232 | 0.076771 |  | 2026-09-03 17:30 | 60.411 | 62.358 | 1544.3 | 10.393 | 11.2846 | -0.8916 | 67.7076 | 11.2 | 11.1232 | 0.076771 |  | 2026-09-03 17:30 | 56.834 | 57.676 | 1459.5 | 9.6127 | 10.7359 | -1.1232 | 64.4154 | 10.6 | 10.5824 | 0.017625 |  | 2026-09-03 17:30 | 107.0803 | 116.8111 | -9.7308 | 700.8668 | 118 | 115.1407 | 2.8593
2026-09-03 17:20 | 309 | 48.22 | 101.865 | 103.113 | 2043.3 | 17.1855 | 18.4399 | -1.2544 | 110.6394 | 18 | 18.1762 | -0.17621 |  | 2026-09-03 17:20 | 103.53 | 104.841 | 2061.9 | 17.4735 | 18.4399 | -0.9664 | 110.6394 | 18.7 | 18.1762 | 0.52379 |  | 2026-09-03 17:20 | 102.684 | 104.563 | 2035.5 | 17.4272 | 18.4399 | -1.0127 | 110.6394 | 18.4 | 18.1762 | 0.22379 |  | 2026-09-03 17:20 | 102.133 | 103.426 | 2042.1 | 17.2377 | 18.4399 | -1.2022 | 110.6394 | 18.5 | 18.1762 | 0.32379 |  | 2026-09-03 17:20 | 76.51 | 77.526 | 1540.2 | 12.921 | 13.6592 | -0.73819 | 81.9551 | 13.7 | 13.4639 | 0.23614 |  | 2026-09-03 17:20 | 74.185 | 75.177 | 1519.7 | 12.5295 | 13.6592 | -1.1297 | 81.9551 | 13.3 | 13.4639 | -0.16386 |  | 2026-09-03 17:20 | 75.137 | 76.142 | 1521.3 | 12.6903 | 13.6592 | -0.96885 | 81.9551 | 13.4 | 13.4639 | -0.063862 |  | 2026-09-03 17:20 | 75.153 | 77.135 | 1533.1 | 12.8558 | 13.6592 | -0.80335 | 81.9551 | 13.4 | 13.4639 | -0.063862 |  | 2026-09-03 17:20 | 70.671 | 71.631 | 1448.9 | 11.9385 | 12.995 | -1.0565 | 77.9702 | 12.6 | 12.8092 | -0.2092 |  | 2026-09-03 17:20 | 132.259 | 141.3914 | -9.1324 | 848.3484 | 140 | 139.3695 | 0.6305
2026-09-03 17:10 | 349 | 48.5 | 116.762 | 118.216 | 2025.3 | 19.7027 | 20.8047 | -1.1021 | 124.8284 | 20.6 | 20.5072 | 0.092777 |  | 2026-09-03 17:10 | 118.8 | 120.34 | 2043.2 | 20.0567 | 20.8047 | -0.74806 | 124.8284 | 21 | 20.5072 | 0.49278 |  | 2026-09-03 17:10 | 117.202 | 119.5 | 2017.1 | 19.9167 | 20.8047 | -0.88806 | 124.8284 | 21 | 20.5072 | 0.49278 |  | 2026-09-03 17:10 | 117.101 | 118.595 | 2023.6 | 19.7658 | 20.8047 | -1.0389 | 124.8284 | 20.7 | 20.5072 | 0.19278 |  | 2026-09-03 17:10 | 87.14 | 88.288 | 1526.5 | 14.7147 | 15.4109 | -0.69624 | 92.4655 | 15.6 | 15.1905 | 0.40946 |  | 2026-09-03 17:10 | 85.236 | 86.341 | 1506.4 | 14.3902 | 15.4109 | -1.0207 | 92.4655 | 15.5 | 15.1905 | 0.30946 |  | 2026-09-03 17:10 | 84.591 | 85.688 | 1507.9 | 14.2813 | 15.4109 | -1.1296 | 92.4655 | 15.4 | 15.1905 | 0.20946 |  | 2026-09-03 17:10 | 85.645 | 88.078 | 1519.7 | 14.6797 | 15.4109 | -0.73124 | 92.4655 | 15.5 | 15.1905 | 0.30946 |  | 2026-09-03 17:10 | 80.68 | 81.759 | 1436.3 | 13.6265 | 14.6616 | -1.0351 | 87.9694 | 14.6 | 14.4519 | 0.14809 |  | 2026-09-03 17:10 | 151.1342 | 159.5241 | -8.39 | 957.1448 | 159.9 | 157.2429 | 2.6571
2026-09-03 17:00 | 394 | 48.5 | 133.876 | 134.874 | 2004.7 | 22.479 | 23.4873 | -1.0083 | 140.9237 | 23.5 | 23.1514 | 0.34858 |  | 2026-09-03 17:00 | 135.375 | 137.172 | 2022.2 | 22.862 | 23.4873 | -0.62529 | 140.9237 | 24.2 | 23.1514 | 1.0486 |  | 2026-09-03 17:00 | 134.133 | 136.945 | 1996.1 | 22.8242 | 23.4873 | -0.66312 | 140.9237 | 23.7 | 23.1514 | 0.54858 |  | 2026-09-03 17:00 | 133.826 | 135.589 | 2002.9 | 22.5982 | 23.4873 | -0.88912 | 140.9237 | 23.6 | 23.1514 | 0.44858 |  | 2026-09-03 17:00 | 100.37 | 101.692 | 1510.9 | 16.9487 | 17.398 | -0.44933 | 104.388 | 17.8 | 17.1492 | 0.6508 |  | 2026-09-03 17:00 | 98.069 | 99.32 | 1490.9 | 16.5533 | 17.398 | -0.84466 | 104.388 | 17 | 17.1492 | -0.1492 |  | 2026-09-03 17:00 | 98.223 | 99.476 | 1492.5 | 16.5793 | 17.398 | -0.81866 | 104.388 | 17.3 | 17.1492 | 0.1508 |  | 2026-09-03 17:00 | 98.522 | 101.229 | 1504.2 | 16.8715 | 17.398 | -0.52649 | 104.388 | 17.3 | 17.1492 | 0.1508 |  | 2026-09-03 17:00 | 92.893 | 94.088 | 1421.7 | 15.6813 | 16.552 | -0.8707 | 99.3122 | 16.6 | 16.3153 | 0.28466 |  | 2026-09-03 17:00 | 173.3975 | 180.0932 | -6.6957 | 1080.5589 | 181 | 177.5178 | 3.4822
2026-09-03 16:50 | 443 | 48.79 | 150.685 | 152.639 | 1981.2 | 25.4398 | 26.3791 | -0.93926 | 158.2745 | 56 | 26.0019 | 29.9981 |  | 2026-09-03 16:50 | 155.597 | 157.71 | 1998 | 26.285 | 26.3791 | -0.09409 | 158.2745 | 26.7 | 26.0019 | 0.69813 |  | 2026-09-03 16:50 | 151.267 | 154.56 | 1972.4 | 25.76 | 26.3791 | -0.61909 | 158.2745 | 26.7 | 26.0019 | 0.69813 |  | 2026-09-03 16:50 | 151.231 | 153.269 | 1979.3 | 25.5448 | 26.3791 | -0.83426 | 158.2745 | 26.7 | 26.0019 | 0.69813 |  | 2026-09-03 16:50 | 113.147 | 114.626 | 1493.1 | 19.1043 | 19.5401 | -0.43573 | 117.2404 | 19.9 | 19.2606 | 0.63936 |  | 2026-09-03 16:50 | 110.582 | 112.076 | 1473.9 | 18.6793 | 19.5401 | -0.86073 | 117.2404 | 19.5 | 19.2606 | 0.23936 |  | 2026-09-03 16:50 | 110.837 | 112.308 | 1475.2 | 18.718 | 19.5401 | -0.82207 | 117.2404 | 19.5 | 19.2606 | 0.23936 |  | 2026-09-03 16:50 | 111.337 | 114.305 | 1486.9 | 19.0508 | 19.5401 | -0.48923 | 117.2404 | 19.9 | 19.2606 | 0.63936 |  | 2026-09-03 16:50 | 105.234 | 106.62 | 1405.1 | 17.77 | 18.59 | -0.81995 | 111.5397 | 18.5 | 18.3241 | 0.17588 |  | 2026-09-03 16:50 | 196.3522 | 202.2666 | -5.9144 | 1213.5995 | 233.4 | 199.3742 | 34.0258
2026-09-03 16:40 | 491 | 48.79 | 168.084 | 170.332 | 1954.2 | 28.3887 | 29.2373 | -0.84865 | 175.4239 | 0 | 28.8192 | -28.8192 |  | 2026-09-03 16:40 | 170.218 | 172.582 | 1971.3 | 28.7637 | 29.2373 | -0.47365 | 175.4239 | 29.8 | 28.8192 | 0.98077 |  | 2026-09-03 16:40 | 168.417 | 172.287 | 1945.7 | 28.7145 | 29.2373 | -0.52282 | 175.4239 | 29.1 | 28.8192 | 0.28077 |  | 2026-09-03 16:40 | 168 | 170.299 | 1952.6 | 28.3832 | 29.2373 | -0.85415 | 175.4239 | 29 | 28.8192 | 0.18077 |  | 2026-09-03 16:40 | 126.039 | 127.686 | 1473.2 | 21.281 | 21.6573 | -0.37627 | 129.9436 | 21.8 | 21.3476 | 0.45242 |  | 2026-09-03 16:40 | 123.056 | 124.677 | 1454.4 | 20.7795 | 21.6573 | -0.87777 | 129.9436 | 21.3 | 21.3476 | -0.047576 |  | 2026-09-03 16:40 | 123.393 | 125.238 | 1455.7 | 20.873 | 21.6573 | -0.78427 | 129.9436 | 21.7 | 21.3476 | 0.35242 |  | 2026-09-03 16:40 | 123.706 | 126.865 | 1467 | 21.1442 | 21.6573 | -0.51311 | 129.9436 | 21.5 | 21.3476 | 0.15242 |  | 2026-09-03 16:40 | 116.796 | 118.346 | 1386.6 | 19.7243 | 20.6042 | -0.87988 | 123.6253 | 20.2 | 20.3096 | -0.10957 |  | 2026-09-03 16:40 | 218.052 | 224.1826 | -6.1306 | 1345.0956 | 194.4 | 220.9768 | -26.5768
2026-09-03 16:30 | 535 | 49.08 | 183.795 | 185.468 | 1925.2 | 30.9113 | 31.8221 | -0.91076 | 190.9326 | 32.2 | 31.367 | 0.83296 |  | 2026-09-03 16:30 | 185.644 | 188.261 | 1941.5 | 31.3768 | 31.8221 | -0.44526 | 190.9326 | 32.2 | 31.367 | 0.83296 |  | 2026-09-03 16:30 | 182.744 | 187.203 | 1916.6 | 31.2005 | 31.8221 | -0.62159 | 190.9326 | 31.7 | 31.367 | 0.33296 |  | 2026-09-03 16:30 | 183.171 | 185.734 | 1923.6 | 30.9557 | 31.8221 | -0.86643 | 190.9326 | 31.8 | 31.367 | 0.43296 |  | 2026-09-03 16:30 | 136.849 | 138.68 | 1451.4 | 23.1133 | 23.5719 | -0.45859 | 141.4315 | 23.8 | 23.2348 | 0.56516 |  | 2026-09-03 16:30 | 134.109 | 135.971 | 1433.1 | 22.6618 | 23.5719 | -0.91009 | 141.4315 | 23.3 | 23.2348 | 0.065157 |  | 2026-09-03 16:30 | 134.538 | 136.533 | 1434 | 22.7555 | 23.5719 | -0.81642 | 141.4315 | 23.1 | 23.2348 | -0.13484 |  | 2026-09-03 16:30 | 135.418 | 139.339 | 1445.5 | 23.2232 | 23.5719 | -0.34875 | 141.4315 | 23.5 | 23.2348 | 0.26516 |  | 2026-09-03 16:30 | 127.72 | 129.442 | 1366.4 | 21.5737 | 22.4258 | -0.8521 | 134.5546 | 22.2 | 22.1051 | 0.094925 |  | 2026-09-03 16:30 | 237.7718 | 244.0018 | -6.23 | 1464.011 | 243.8 | 240.5126 | 3.2874
2026-09-03 16:20 | 574 | 49.08 | 197.755 | 200.522 | 1893 | 33.4203 | 34.1418 | -0.7215 | 204.851 | 33.5 | 33.6536 | -0.15361 |  | 2026-09-03 16:20 | 199.897 | 202.756 | 1909.3 | 33.7927 | 34.1418 | -0.34917 | 204.851 | 35.3 | 33.6536 | 1.6464 |  | 2026-09-03 16:20 | 196.972 | 201.927 | 1884.9 | 33.6545 | 34.1418 | -0.48734 | 204.851 | 33.9 | 33.6536 | 0.24639 |  | 2026-09-03 16:20 | 197.014 | 199.811 | 1891.8 | 33.3018 | 34.1418 | -0.84 | 204.851 | 33.9 | 33.6536 | 0.24639 |  | 2026-09-03 16:20 | 147.996 | 150.021 | 1427.6 | 25.0035 | 25.2902 | -0.28675 | 151.7415 | 25.5 | 24.9286 | 0.5714 |  | 2026-09-03 16:20 | 144.648 | 146.638 | 1409.8 | 24.4397 | 25.2902 | -0.85058 | 151.7415 | 25.2 | 24.9286 | 0.2714 |  | 2026-09-03 16:20 | 145.2 | 147.172 | 1410.9 | 24.5287 | 25.2902 | -0.76158 | 151.7415 | 25.3 | 24.9286 | 0.3714 |  | 2026-09-03 16:20 | 146.03 | 150.119 | 1422 | 25.0198 | 25.2902 | -0.27042 | 151.7415 | 25.1 | 24.9286 | 0.1714 |  | 2026-09-03 16:20 | 137.508 | 139.376 | 1344.2 | 23.2293 | 24.0605 | -0.83121 | 144.3632 | 23.7 | 23.7165 | -0.016473 |  | 2026-09-03 16:20 | 256.3903 | 261.7889 | -5.3985 | 1570.7332 | 261.4 | 258.0453 | 3.3547
2026-09-03 16:10 | 615 | 49.36 | 210.133 | 213.138 | 1859.5 | 35.523 | 36.5414 | -1.0184 | 219.2483 | 35.7 | 36.0188 | -0.31885 |  | 2026-09-03 16:10 | 215.273 | 217.172 | 1874 | 36.1953 | 36.5414 | -0.34606 | 219.2483 | 35.2 | 36.0188 | -0.81885 |  | 2026-09-03 16:10 | 209.632 | 214.796 | 1851 | 35.7993 | 36.5414 | -0.74206 | 219.2483 | 36.1 | 36.0188 | 0.081152 |  | 2026-09-03 16:10 | 210.502 | 213.599 | 1857.9 | 35.5998 | 36.5414 | -0.94156 | 219.2483 | 36.2 | 36.0188 | 0.18115 |  | 2026-09-03 16:10 | 157.719 | 159.91 | 1402.1 | 26.6517 | 27.0677 | -0.41603 | 162.4062 | 27.6 | 26.6806 | 0.91937 |  | 2026-09-03 16:10 | 154.935 | 157.106 | 1384.6 | 26.1843 | 27.0677 | -0.88336 | 162.4062 | 26.8 | 26.6806 | 0.11937 |  | 2026-09-03 16:10 | 155.313 | 157.791 | 1385.6 | 26.2985 | 27.0677 | -0.7692 | 162.4062 | 26.8 | 26.6806 | 0.11937 |  | 2026-09-03 16:10 | 156.209 | 160.57 | 1396.9 | 26.7617 | 27.0677 | -0.30603 | 162.4062 | 26.9 | 26.6806 | 0.21937 |  | 2026-09-03 16:10 | 147.373 | 149.405 | 1320.5 | 24.9008 | 25.7516 | -0.85073 | 154.5094 | 25.4 | 25.3833 | 0.016687 |  | 2026-09-03 16:10 | 273.9145 | 280.1879 | -6.2734 | 1681.1274 | 276.7 | 276.1812 | 0.51878
2026-09-03 16:00 | 656 | 49.08 | 224.414 | 227.693 | 1823.8 | 37.9488 | 39.0192 | -1.0704 | 234.1154 | 38.9 | 38.4613 | 0.43873 |  | 2026-09-03 16:00 | 227.437 | 230.898 | 1838.8 | 38.483 | 39.0192 | -0.53624 | 234.1154 | 39.5 | 38.4613 | 1.0387 |  | 2026-09-03 16:00 | 223.497 | 229.064 | 1814.9 | 38.1773 | 39.0192 | -0.84191 | 234.1154 | 38.4 | 38.4613 | -0.061265 |  | 2026-09-03 16:00 | 223.869 | 227.232 | 1821.7 | 37.872 | 39.0192 | -1.1472 | 234.1154 | 38.5 | 38.4613 | 0.038735 |  | 2026-09-03 16:00 | 168.16 | 170.548 | 1374.5 | 28.4247 | 28.9031 | -0.47847 | 173.4188 | 28.4 | 28.4898 | -0.089826 |  | 2026-09-03 16:00 | 164.756 | 167.292 | 1357.8 | 27.882 | 28.9031 | -1.0211 | 173.4188 | 27.9 | 28.4898 | -0.58983 |  | 2026-09-03 16:00 | 165.079 | 167.569 | 1358.8 | 27.9282 | 28.9031 | -0.97497 | 173.4188 | 27.9 | 28.4898 | -0.58983 |  | 2026-09-03 16:00 | 165.651 | 170.089 | 1370 | 28.3482 | 28.9031 | -0.55497 | 173.4188 | 28.1 | 28.4898 | -0.38983 |  | 2026-09-03 16:00 | 156.571 | 158.778 | 1295.1 | 26.463 | 27.4978 | -1.0348 | 164.9866 | 26.8 | 27.1045 | -0.30454 |  | 2026-09-03 16:00 | 291.5272 | 299.1873 | -7.6601 | 1795.1237 | 294.4 | 294.9089 | -0.50891
2026-09-03 15:50 | 701 | 49.08 | 237.49 | 241.107 | 1784.9 | 40.1845 | 41.6959 | -1.5114 | 250.1752 | 40.1 | 41.0996 | -0.99961 |  | 2026-09-03 15:50 | 241.122 | 244.868 | 1799.3 | 40.8113 | 41.6959 | -0.88453 | 250.1752 | 40.6 | 41.0996 | -0.49961 |  | 2026-09-03 15:50 | 237.188 | 243.06 | 1776.5 | 40.51 | 41.6959 | -1.1859 | 250.1752 | 40 | 41.0996 | -1.0996 |  | 2026-09-03 15:50 | 238.23 | 241.932 | 1783.2 | 40.322 | 41.6959 | -1.3739 | 250.1752 | 40.6 | 41.0996 | -0.49961 |  | 2026-09-03 15:50 | 178.543 | 181.096 | 1346.1 | 30.1827 | 30.8858 | -0.70316 | 185.315 | 30.4 | 30.4442 | -0.044159 |  | 2026-09-03 15:50 | 175.076 | 177.887 | 1329.9 | 29.6478 | 30.8858 | -1.238 | 185.315 | 29.8 | 30.4442 | -0.64416 |  | 2026-09-03 15:50 | 175.465 | 178.284 | 1330.9 | 29.714 | 30.8858 | -1.1718 | 185.315 | 30 | 30.4442 | -0.44416 |  | 2026-09-03 15:50 | 176.087 | 180.891 | 1341.9 | 30.1485 | 30.8858 | -0.73733 | 185.315 | 30.1 | 30.4442 | -0.34416 |  | 2026-09-03 15:50 | 166.38 | 168.725 | 1268.3 | 28.1208 | 29.384 | -1.2632 | 176.3042 | 28.1 | 28.9638 | -0.86385 |  | 2026-09-03 15:50 | 309.6417 | 319.7108 | -10.0691 | 1918.2648 | 309.7 | 315.1389 | -5.4389
2026-09-03 15:40 | 735 | 48.79 | 251.32 | 254.299 | 1744.8 | 42.3832 | 43.7667 | -1.3835 | 262.6 | 42.4 | 43.1408 | -0.7408 |  | 2026-09-03 15:40 | 252.798 | 256.804 | 1758.7 | 42.8007 | 43.7667 | -0.966 | 262.6 | 43 | 43.1408 | -0.1408 |  | 2026-09-03 15:40 | 248.594 | 254.703 | 1736.5 | 42.4505 | 43.7667 | -1.3162 | 262.6 | 42.8 | 43.1408 | -0.3408 |  | 2026-09-03 15:40 | 249.386 | 253.338 | 1742.6 | 42.223 | 43.7667 | -1.5437 | 262.6 | 42.4 | 43.1408 | -0.7408 |  | 2026-09-03 15:40 | 187.012 | 189.777 | 1315.7 | 31.6295 | 32.4197 | -0.79025 | 194.5185 | 31.9 | 31.9561 | -0.056147 |  | 2026-09-03 15:40 | 183.409 | 186.553 | 1300.1 | 31.0922 | 32.4197 | -1.3276 | 194.5185 | 31.2 | 31.9561 | -0.75615 |  | 2026-09-03 15:40 | 183.682 | 186.726 | 1300.9 | 31.121 | 32.4197 | -1.2987 | 194.5185 | 31.8 | 31.9561 | -0.15615 |  | 2026-09-03 15:40 | 184.626 | 189.992 | 1311.8 | 31.6653 | 32.4197 | -0.75442 | 194.5185 | 31.9 | 31.9561 | -0.056147 |  | 2026-09-03 15:40 | 174.376 | 176.888 | 1240.2 | 29.4813 | 30.8434 | -1.362 | 185.0603 | 30.1 | 30.4023 | -0.30232 |  | 2026-09-03 15:40 | 324.8467 | 335.589 | -10.7424 | 2013.5341 | 327.5 | 330.7901 | -3.2901
2026-09-03 15:30 | 775 | 49.36 | 261.798 | 265.883 | 1702.4 | 44.3138 | 46.0481 | -1.7343 | 276.2886 | 46.7 | 45.3896 | 1.3104 |  | 2026-09-03 15:30 | 267.3 | 271.591 | 1715.7 | 45.2652 | 46.0481 | -0.78293 | 276.2886 | 45.5 | 45.3896 | 0.1104 |  | 2026-09-03 15:30 | 262.293 | 269.367 | 1693.7 | 44.8945 | 46.0481 | -1.1536 | 276.2886 | 45.4 | 45.3896 | 0.010395 |  | 2026-09-03 15:30 | 263.353 | 267.62 | 1700.2 | 44.6033 | 46.0481 | -1.4448 | 276.2886 | 45.6 | 45.3896 | 0.2104 |  | 2026-09-03 15:30 | 198.041 | 200.934 | 1283.8 | 33.489 | 34.1097 | -0.6207 | 204.6582 | 34.2 | 33.6219 | 0.57807 |  | 2026-09-03 15:30 | 194.199 | 197.397 | 1268.9 | 32.8995 | 34.1097 | -1.2102 | 204.6582 | 33.5 | 33.6219 | -0.12193 |  | 2026-09-03 15:30 | 194.882 | 198.468 | 1269.1 | 33.078 | 34.1097 | -1.0317 | 204.6582 | 33.1 | 33.6219 | -0.52193 |  | 2026-09-03 15:30 | 196.157 | 201.476 | 1279.9 | 33.5793 | 34.1097 | -0.53036 | 204.6582 | 33.3 | 33.6219 | -0.32193 |  | 2026-09-03 15:30 | 185.002 | 187.705 | 1210.1 | 31.2842 | 32.4512 | -1.167 | 194.7069 | 31.4 | 31.9871 | -0.5871 |  | 2026-09-03 15:30 | 343.4068 | 353.0823 | -9.6755 | 2118.4939 | 348.7 | 348.0332 | 0.66676
2026-09-03 15:20 | 829 | 49.08 | 279.701 | 284.202 | 1655.7 | 47.367 | 49.3094 | -1.9424 | 295.8563 | 45 | 48.6043 | -3.6043 |  | 2026-09-03 15:20 | 284.07 | 288.718 | 1670.2 | 48.1197 | 49.3094 | -1.1897 | 295.8563 | 47.5 | 48.6043 | -1.1043 |  | 2026-09-03 15:20 | 277.806 | 285.147 | 1648.3 | 47.5245 | 49.3094 | -1.7849 | 295.8563 | 46 | 48.6043 | -2.6043 |  | 2026-09-03 15:20 | 279.236 | 283.887 | 1654.6 | 47.3145 | 49.3094 | -1.9949 | 295.8563 | 46.2 | 48.6043 | -2.4043 |  | 2026-09-03 15:20 | 209.013 | 212.153 | 1249.6 | 35.3588 | 36.5255 | -1.1666 | 219.1528 | 34.6 | 36.0031 | -1.4031 |  | 2026-09-03 15:20 | 205.15 | 208.94 | 1235.4 | 34.8233 | 36.5255 | -1.7021 | 219.1528 | 34 | 36.0031 | -2.0031 |  | 2026-09-03 15:20 | 205.249 | 209.199 | 1236 | 34.8665 | 36.5255 | -1.659 | 219.1528 | 34 | 36.0031 | -2.0031 |  | 2026-09-03 15:20 | 206.487 | 212.131 | 1246.6 | 35.3552 | 36.5255 | -1.1703 | 219.1528 | 34.3 | 36.0031 | -1.7031 |  | 2026-09-03 15:20 | 195.28 | 198.173 | 1178.7 | 33.0288 | 34.7495 | -1.7206 | 208.4967 | 32.9 | 34.2525 | -1.3525 |  | 2026-09-03 15:20 | 363.7583 | 378.0888 | -14.3305 | 2268.5329 | 354.5 | 372.6821 | -18.1821
2026-09-03 15:10 | 842 | 49.36 | 282.484 | 287.077 | 1610.7 | 47.8462 | 50.029 | -2.1829 | 300.1741 | 48.2 | 49.3136 | -1.1136 |  | 2026-09-03 15:10 | 286.969 | 291.724 | 1622.7 | 48.6207 | 50.029 | -1.4084 | 300.1741 | 48.8 | 49.3136 | -0.51361 |  | 2026-09-03 15:10 | 280.99 | 288.798 | 1602.3 | 48.133 | 50.029 | -1.896 | 300.1741 | 47.5 | 49.3136 | -1.8136 |  | 2026-09-03 15:10 | 283.916 | 288.621 | 1608.4 | 48.1035 | 50.029 | -1.9255 | 300.1741 | 47.7 | 49.3136 | -1.6136 |  | 2026-09-03 15:10 | 211.665 | 214.867 | 1215 | 35.8112 | 37.0585 | -1.2474 | 222.3512 | 35.8 | 36.5286 | -0.7286 |  | 2026-09-03 15:10 | 208.364 | 212.078 | 1201.4 | 35.3463 | 37.0585 | -1.7122 | 222.3512 | 35.1 | 36.5286 | -1.4286 |  | 2026-09-03 15:10 | 208.546 | 212.799 | 1202 | 35.4665 | 37.0585 | -1.592 | 222.3512 | 35.3 | 36.5286 | -1.2286 |  | 2026-09-03 15:10 | 209.583 | 215.377 | 1212.3 | 35.8962 | 37.0585 | -1.1624 | 222.3512 | 35.9 | 36.5286 | -0.6286 |  | 2026-09-03 15:10 | 200.211 | 203.219 | 1145.8 | 33.8698 | 35.2566 | -1.3868 | 211.5396 | 33.3 | 34.7524 | -1.4524 |  | 2026-09-03 15:10 | 369.0933 | 383.6069 | -14.5135 | 2301.6411 | 367.6 | 378.1213 | -10.5213
2026-09-03 15:00 | 867 | 49.08 | 289.266 | 294.029 | 1562.5 | 49.0048 | 51.5696 | -2.5648 | 309.4178 | 48.8 | 50.8322 | -2.0322 | 0.9838 | 2026-09-03 15:00 | 293.513 | 298.437 | 1573.9 | 49.7395 | 51.5696 | -1.8301 | 309.4178 | 50.4 | 50.8322 | -0.43219 | 0.9835 | 2026-09-03 15:00 | 287.342 | 295.532 | 1554.8 | 49.2553 | 51.5696 | -2.3143 | 309.4178 | 49.3 | 50.8322 | -1.5322 | 0.97229 | 2026-09-03 15:00 | 289.825 | 294.717 | 1560.7 | 49.1195 | 51.5696 | -2.4501 | 309.4178 | 50.3 | 50.8322 | -0.53219 | 0.9834 | 2026-09-03 15:00 | 217.116 | 220.4 | 1179.2 | 36.7333 | 38.1997 | -1.4664 | 229.1984 | 37.7 | 37.6535 | 0.046525 | 0.9851 | 2026-09-03 15:00 | 213.172 | 216.921 | 1166.3 | 36.1535 | 38.1997 | -2.0462 | 229.1984 | 37 | 37.6535 | -0.65347 | 0.98272 | 2026-09-03 15:00 | 213.825 | 217.65 | 1166.7 | 36.275 | 38.1997 | -1.9247 | 229.1984 | 37.1 | 37.6535 | -0.55347 | 0.98243 | 2026-09-03 15:00 | 215.796 | 221.485 | 1176.4 | 36.9142 | 38.1997 | -1.2856 | 229.1984 | 36.9 | 37.6535 | -0.75347 | 0.97431 | 2026-09-03 15:00 | 203.81 | 206.893 | 1112.5 | 34.4822 | 36.3423 | -1.8601 | 218.0539 | 34.8 | 35.8226 | -1.0226 | 0.9851 | 2026-09-03 15:00 | 377.6773 | 395.4198 | -17.7424 | 2372.5187 | 382.3 | 389.7653 | -7.4653
2026-09-03 14:50 | 918 | 49.08 | 306.253 | 311.391 | 1513.7 | 51.8985 | 54.6031 | -2.7046 | 327.6189 | 51.5 | 53.8223 | -2.3223 | 0.9835 | 2026-09-03 14:50 | 309.471 | 314.759 | 1523.5 | 52.4598 | 54.6031 | -2.1433 | 327.6189 | 52.8 | 53.8223 | -1.0223 | 0.9832 | 2026-09-03 14:50 | 304.871 | 313.83 | 1505.5 | 52.305 | 54.6031 | -2.2981 | 327.6189 | 51.2 | 53.8223 | -2.6223 | 0.97145 | 2026-09-03 14:50 | 305.366 | 310.615 | 1510.4 | 51.7692 | 54.6031 | -2.834 | 327.6189 | 51.4 | 53.8223 | -2.4223 | 0.9831 | 2026-09-03 14:50 | 229.765 | 233.359 | 1141.5 | 38.8932 | 40.4468 | -1.5536 | 242.6806 | 38.1 | 39.8684 | -1.7684 | 0.9846 | 2026-09-03 14:50 | 224.735 | 229.202 | 1129.3 | 38.2003 | 40.4468 | -2.2464 | 242.6806 | 38 | 39.8684 | -1.8684 | 0.98051 | 2026-09-03 14:50 | 226.46 | 230.913 | 1129.6 | 38.4855 | 40.4468 | -1.9613 | 242.6806 | 38.1 | 39.8684 | -1.7684 | 0.98072 | 2026-09-03 14:50 | 227.972 | 234.642 | 1139.5 | 39.107 | 40.4468 | -1.3398 | 242.6806 | 38.4 | 39.8684 | -1.4684 | 0.97157 | 2026-09-03 14:50 | 214.235 | 217.542 | 1077.7 | 36.257 | 38.4801 | -2.2231 | 230.8806 | 36.1 | 37.9298 | -1.8298 | 0.9848 | 2026-09-03 14:50 | 399.3755 | 418.6798 | -19.3043 | 2512.0786 | 395.6 | 412.6926 | -17.0926
2026-09-03 14:40 | 935 | 49.08 | 308.699 | 313.974 | 1462.2 | 52.329 | 55.6143 | -3.2853 | 333.6859 | 53.2 | 54.819 | -1.619 | 0.9832 | 2026-09-03 14:40 | 0 | 0 | 1470.7 | 0 | 55.6143 | -55.6143 | 333.6859 | 51.9 | 54.819 | -2.919 |  | 2026-09-03 14:40 | 307.474 | 316.347 | 1454.3 | 52.7245 | 55.6143 | -2.8898 | 333.6859 | 52.2 | 54.819 | -2.619 | 0.97195 | 2026-09-03 14:40 | 309.264 | 314.676 | 1459 | 52.446 | 55.6143 | -3.1683 | 333.6859 | 51.9 | 54.819 | -2.919 | 0.9828 | 2026-09-03 14:40 | 232.062 | 235.716 | 1103.4 | 39.286 | 41.1958 | -1.9098 | 247.1747 | 39.4 | 40.6067 | -1.2067 | 0.9845 | 2026-09-03 14:40 | 227.407 | 231.693 | 1091.3 | 38.6155 | 41.1958 | -2.5803 | 247.1747 | 38.1 | 40.6067 | -2.5067 | 0.9815 | 2026-09-03 14:40 | 228.598 | 233.118 | 1091.5 | 38.853 | 41.1958 | -2.3428 | 247.1747 | 38.2 | 40.6067 | -2.4067 | 0.98061 | 2026-09-03 14:40 | 230.366 | 237.214 | 1101.1 | 39.5357 | 41.1958 | -1.6601 | 247.1747 | 39.6 | 40.6067 | -1.0067 | 0.97113 | 2026-09-03 14:40 | 216.607 | 219.995 | 1041.6 | 36.6658 | 39.1927 | -2.5269 | 235.1561 | 36.9 | 38.6322 | -1.7322 | 0.9846 | 2026-09-03 14:40 | 350.4555 | 426.4331 | -75.9776 | 2558.5986 | 401.4 | 420.3351 | -18.9351
2026-09-03 14:30 | 964 | 49.36 | 317.406 | 322.928 | 1409 | 53.8213 | 57.2779 | -3.4566 | 343.6673 | 51.7 | 56.4588 | -4.7588 | 0.9829 | 2026-09-03 14:30 | 322.04 | 327.736 | 1418.8 | 54.6227 | 57.2779 | -2.6552 | 343.6673 | 53.1 | 56.4588 | -3.3588 | 0.98262 | 2026-09-03 14:30 | 315.629 | 324.81 | 1402.1 | 54.135 | 57.2779 | -3.1429 | 343.6673 | 52.2 | 56.4588 | -4.2588 | 0.97173 | 2026-09-03 14:30 | 317.767 | 323.394 | 1407.1 | 53.899 | 57.2779 | -3.3789 | 343.6673 | 53.3 | 56.4588 | -3.1588 | 0.9826 | 2026-09-03 14:30 | 237.822 | 241.664 | 1064 | 40.2773 | 42.4281 | -2.1507 | 254.5684 | 39.9 | 41.8213 | -1.9213 | 0.9841 | 2026-09-03 14:30 | 234.133 | 238.52 | 1053.2 | 39.7533 | 42.4281 | -2.6747 | 254.5684 | 39.2 | 41.8213 | -2.6213 | 0.98161 | 2026-09-03 14:30 | 234.618 | 239.439 | 1053.3 | 39.9065 | 42.4281 | -2.5216 | 254.5684 | 39.4 | 41.8213 | -2.4213 | 0.97987 | 2026-09-03 14:30 | 237.089 | 243.809 | 1061.5 | 40.6348 | 42.4281 | -1.7932 | 254.5684 | 38.6 | 41.8213 | -3.2213 | 0.97244 | 2026-09-03 14:30 | 223.334 | 226.831 | 1004.7 | 37.8052 | 40.365 | -2.5599 | 242.1903 | 36.8 | 39.7878 | -2.9878 | 0.98458 | 2026-09-03 14:30 | 414.8552 | 439.1888 | -24.3337 | 2635.1331 | 404.2 | 432.9084 | -28.7084
2026-09-03 14:20 | 970 | 49.65 | 318.131 | 323.6 | 1357.3 | 53.9333 | 57.5704 | -3.6371 | 345.4226 | 54.2 | 56.7472 | -2.5472 | 0.9831 | 2026-09-03 14:20 | 322.924 | 328.609 | 1365.7 | 54.7682 | 57.5704 | -2.8023 | 345.4226 | 56.7 | 56.7472 | -0.047178 | 0.9827 | 2026-09-03 14:20 | 316.175 | 325.313 | 1349.9 | 54.2188 | 57.5704 | -3.3516 | 345.4226 | 54.1 | 56.7472 | -2.6472 | 0.97191 | 2026-09-03 14:20 | 319.52 | 325.145 | 1353.8 | 54.1908 | 57.5704 | -3.3796 | 345.4226 | 53.7 | 56.7472 | -3.0472 | 0.9827 | 2026-09-03 14:20 | 238.875 | 242.71 | 1024.1 | 40.4517 | 42.6448 | -2.1931 | 255.8686 | 40.2 | 42.0349 | -1.8349 | 0.9842 | 2026-09-03 14:20 | 234.802 | 239.432 | 1014 | 39.9053 | 42.6448 | -2.7394 | 255.8686 | 39.5 | 42.0349 | -2.5349 | 0.98066 | 2026-09-03 14:20 | 235.463 | 240.247 | 1013.9 | 40.0412 | 42.6448 | -2.6036 | 255.8686 | 39.6 | 42.0349 | -2.4349 | 0.98009 | 2026-09-03 14:20 | 237.296 | 244.038 | 1022.9 | 40.673 | 42.6448 | -1.9718 | 255.8686 | 39.9 | 42.0349 | -2.1349 | 0.97237 | 2026-09-03 14:20 | 223.474 | 226.969 | 967.9 | 37.8282 | 40.5712 | -2.743 | 243.4273 | 37.6 | 39.991 | -2.391 | 0.9846 | 2026-09-03 14:20 | 416.0105 | 441.432 | -25.4215 | 2648.5921 | 415.5 | 435.1195 | -19.6195
2026-09-03 14:10 | 989 | 49.36 | 323.529 | 329.191 | 1303.1 | 54.8652 | 58.7633 | -3.8981 | 352.5798 | 54.4 | 57.923 | -3.523 | 0.9828 | 2026-09-03 14:10 | 328.232 | 334.112 | 1309 | 55.6853 | 58.7633 | -3.078 | 352.5798 | 56 | 57.923 | -1.923 | 0.9824 | 2026-09-03 14:10 | 321.625 | 331.124 | 1295.8 | 55.1873 | 58.7633 | -3.576 | 352.5798 | 54.1 | 57.923 | -3.823 | 0.97131 | 2026-09-03 14:10 | 324.273 | 330.049 | 1300.1 | 55.0082 | 58.7633 | -3.7551 | 352.5798 | 54.6 | 57.923 | -3.323 | 0.9825 | 2026-09-03 14:10 | 242.492 | 246.435 | 983.9 | 41.0725 | 43.5284 | -2.4559 | 261.1703 | 40.8 | 42.9059 | -2.1059 | 0.984 | 2026-09-03 14:10 | 238.664 | 243.523 | 974.5 | 40.5872 | 43.5284 | -2.9412 | 261.1703 | 40.7 | 42.9059 | -2.2059 | 0.98005 | 2026-09-03 14:10 | 239.196 | 244.201 | 974.3 | 40.7002 | 43.5284 | -2.8282 | 261.1703 | 40.8 | 42.9059 | -2.1059 | 0.9795 | 2026-09-03 14:10 | 240.826 | 247.817 | 983 | 41.3028 | 43.5284 | -2.2255 | 261.1703 | 41.1 | 42.9059 | -1.8059 | 0.97179 | 2026-09-03 14:10 | 227.115 | 230.784 | 930.3 | 38.464 | 41.4119 | -2.9479 | 248.4712 | 38.7 | 40.8197 | -2.1197 | 0.9841 | 2026-09-03 14:10 | 422.8727 | 450.5786 | -27.7059 | 2703.4716 | 421.2 | 444.1353 | -22.9353
2026-09-03 14:00 | 1019 | 49.36 | 334.371 | 340.257 | 1248.7 | 56.7095 | 60.5458 | -3.8363 | 363.2749 | 55.5 | 59.68 | -4.18 | 0.9827 | 2026-09-03 14:00 | 338.457 | 344.486 | 1253 | 57.4143 | 60.5458 | -3.1315 | 363.2749 | 55.3 | 59.68 | -4.38 | 0.9825 | 2026-09-03 14:00 | 331.363 | 340.719 | 1241.7 | 56.7865 | 60.5458 | -3.7593 | 363.2749 | 55.9 | 59.68 | -3.78 | 0.97254 | 2026-09-03 14:00 | 334.969 | 340.97 | 1245.5 | 56.8283 | 60.5458 | -3.7175 | 363.2749 | 56.4 | 59.68 | -3.28 | 0.9824 | 2026-09-03 14:00 | 249.906 | 253.97 | 943.1 | 42.3283 | 44.8488 | -2.5204 | 269.0925 | 42.3 | 44.2074 | -1.9074 | 0.984 | 2026-09-03 14:00 | 246.274 | 251.319 | 933.8 | 41.8865 | 44.8488 | -2.9623 | 269.0925 | 41 | 44.2074 | -3.2074 | 0.97993 | 2026-09-03 14:00 | 246.166 | 250.988 | 933.5 | 41.8313 | 44.8488 | -3.0174 | 269.0925 | 41.1 | 44.2074 | -3.1074 | 0.98079 | 2026-09-03 14:00 | 247.943 | 255.385 | 941.9 | 42.5642 | 44.8488 | -2.2846 | 269.0925 | 41.4 | 44.2074 | -2.8074 | 0.97086 | 2026-09-03 14:00 | 234.302 | 238.088 | 891.6 | 39.6813 | 42.668 | -2.9867 | 256.0082 | 39.1 | 42.0579 | -2.9579 | 0.9841 | 2026-09-03 14:00 | 436.0303 | 464.2463 | -28.216 | 2785.4778 | 428 | 457.6076 | -29.6076
2026-09-03 13:50 | 1028 | 49.36 | 334.907 | 340.838 | 1193.2 | 56.8063 | 61.0806 | -4.2742 | 366.4834 | 56.9 | 60.2071 | -3.3071 | 0.9826 | 2026-09-03 13:50 | 339.074 | 345.219 | 1197.7 | 57.5365 | 61.0806 | -3.5441 | 366.4834 | 55.8 | 60.2071 | -4.4071 | 0.9822 | 2026-09-03 13:50 | 332.375 | 342.027 | 1185.8 | 57.0045 | 61.0806 | -4.0761 | 366.4834 | 55.6 | 60.2071 | -4.6071 | 0.97178 | 2026-09-03 13:50 | 335.436 | 341.515 | 1189.1 | 56.9192 | 61.0806 | -4.1614 | 366.4834 | 55.9 | 60.2071 | -4.3071 | 0.9822 | 2026-09-03 13:50 | 251.204 | 255.291 | 900.8 | 42.5485 | 45.2449 | -2.6964 | 271.4692 | 42 | 44.5979 | -2.5979 | 0.98399 | 2026-09-03 13:50 | 247.01 | 252.029 | 892.8 | 42.0048 | 45.2449 | -3.24 | 271.4692 | 41.4 | 44.5979 | -3.1979 | 0.98009 | 2026-09-03 13:50 | 247.338 | 252.431 | 892.4 | 42.0718 | 45.2449 | -3.173 | 271.4692 | 42.1 | 44.5979 | -2.4979 | 0.97982 | 2026-09-03 13:50 | 249.296 | 256.56 | 900.5 | 42.76 | 45.2449 | -2.4849 | 271.4692 | 43 | 44.5979 | -1.5979 | 0.97169 | 2026-09-03 13:50 | 235.37 | 239.221 | 852.5 | 39.8702 | 43.0449 | -3.1747 | 258.2693 | 40.1 | 42.4293 | -2.3293 | 0.9839 | 2026-09-03 13:50 | 437.5218 | 468.3466 | -30.8248 | 2810.0797 | 432.8 | 461.6493 | -28.8493
2026-09-03 13:40 | 1045 | 49.36 | 339.41 | 345.526 | 1136.3 | 57.5877 | 62.0907 | -4.503 | 372.5439 | 59 | 61.2028 | -2.2028 | 0.9823 | 2026-09-03 13:40 | 333.032 | 338.276 | 1141.9 | 56.3793 | 62.0907 | -5.7113 | 372.5439 | 60.1 | 61.2028 | -1.1028 | 0.9845 | 2026-09-03 13:40 | 336.973 | 346.704 | 1130.2 | 57.784 | 62.0907 | -4.3067 | 372.5439 | 56.3 | 61.2028 | -4.9028 | 0.97193 | 2026-09-03 13:40 | 336.449 | 342.337 | 1133.2 | 57.0562 | 62.0907 | -5.0345 | 372.5439 | 56.3 | 61.2028 | -4.9028 | 0.9828 | 2026-09-03 13:40 | 254.639 | 258.858 | 858.8 | 43.143 | 45.9931 | -2.8501 | 275.9585 | 42.6 | 45.3354 | -2.7354 | 0.9837 | 2026-09-03 13:40 | 250.611 | 255.534 | 851.4 | 42.589 | 45.9931 | -3.4041 | 275.9585 | 41.9 | 45.3354 | -3.4354 | 0.98073 | 2026-09-03 13:40 | 251.787 | 257.046 | 850.3 | 42.841 | 45.9931 | -3.1521 | 275.9585 | 41.5 | 45.3354 | -3.8354 | 0.97954 | 2026-09-03 13:40 | 253.994 | 261.414 | 857.5 | 43.569 | 45.9931 | -2.4241 | 275.9585 | 41.7 | 45.3354 | -3.6354 | 0.97162 | 2026-09-03 13:40 | 239.36 | 243.277 | 812.4 | 40.5462 | 43.7567 | -3.2105 | 262.5403 | 39.8 | 43.131 | -3.331 | 0.9839 | 2026-09-03 13:40 | 441.4953 | 476.0916 | -34.5963 | 2856.5498 | 439.2 | 469.2835 | -30.0835
2026-09-03 13:30 | 1046 | 49.36 | 339.97 | 346.166 | 1077.3 | 57.6943 | 62.1501 | -4.4557 | 372.9004 | 56.3 | 61.2613 | -4.9613 | 0.9821 | 2026-09-03 13:30 | 338.118 | 343.826 | 1081.8 | 57.3043 | 62.1501 | -4.8457 | 372.9004 | 110.3 | 61.2613 | 49.0387 | 0.9834 | 2026-09-03 13:30 | 338.224 | 348.677 | 1073.9 | 58.1128 | 62.1501 | -4.0372 | 372.9004 | 56.6 | 61.2613 | -4.6613 | 0.97002 | 2026-09-03 13:30 | 339.126 | 345.131 | 1076.9 | 57.5218 | 62.1501 | -4.6282 | 372.9004 | 55.7 | 61.2613 | -5.5613 | 0.9826 | 2026-09-03 13:30 | 255.643 | 259.905 | 816.2 | 43.3175 | 46.0371 | -2.7196 | 276.2225 | 42.9 | 45.3788 | -2.4788 | 0.9836 | 2026-09-03 13:30 | 251.314 | 256.51 | 809.5 | 42.7517 | 46.0371 | -3.2854 | 276.2225 | 42.2 | 45.3788 | -3.1788 | 0.97974 | 2026-09-03 13:30 | 252.404 | 257.833 | 808.8 | 42.9722 | 46.0371 | -3.0649 | 276.2225 | 42.3 | 45.3788 | -3.0788 | 0.97894 | 2026-09-03 13:30 | 254.421 | 261.941 | 815.8 | 43.6568 | 46.0371 | -2.3803 | 276.2225 | 42.8 | 45.3788 | -2.5788 | 0.97129 | 2026-09-03 13:30 | 240.24 | 244.196 | 772.6 | 40.6993 | 43.7986 | -3.0993 | 262.7915 | 40.4 | 43.1723 | -2.7723 | 0.9838 | 2026-09-03 13:30 | 444.0308 | 476.5472 | -32.5164 | 2859.2834 | 489.5 | 469.7326 | 19.7674
2026-09-03 13:20 | 1063 | 49.08 | 340.879 | 343.081 | 1021 | 57.1802 | 63.2278 | -6.0477 | 379.3669 | 54.8 | 62.3237 | -7.5237 | 0.99358 |  |  |  |  | 0 | 63.2278 | -63.2278 | 379.3669 | 0 | 62.3237 | -62.3237 |  | 2026-09-03 13:20 | 341.898 | 352.612 | 1017.3 | 58.7687 | 63.2278 | -4.4592 | 379.3669 | 57.1 | 62.3237 | -5.2237 | 0.96962 | 2026-09-03 13:20 | 338.839 | 344.454 | 1021.2 | 57.409 | 63.2278 | -5.8188 | 379.3669 | 56.4 | 62.3237 | -5.9237 | 0.9837 | 2026-09-03 13:20 | 259.146 | 263.44 | 773.3 | 43.9067 | 46.8354 | -2.9288 | 281.0126 | 43.7 | 46.1657 | -2.4657 | 0.9837 | 2026-09-03 13:20 | 254.709 | 259.713 | 767.3 | 43.2855 | 46.8354 | -3.5499 | 281.0126 | 43 | 46.1657 | -3.1657 | 0.98073 | 2026-09-03 13:20 | 255.555 | 261.428 | 766.5 | 43.5713 | 46.8354 | -3.2641 | 281.0126 | 43.1 | 46.1657 | -3.0657 | 0.97753 | 2026-09-03 13:20 | 257.808 | 265.35 | 773 | 44.225 | 46.8354 | -2.6104 | 281.0126 | 43 | 46.1657 | -3.1657 | 0.97158 | 2026-09-03 13:20 | 243.199 | 247.179 | 732.2 | 41.1965 | 44.5581 | -3.3616 | 267.3486 | 40.6 | 43.9209 | -3.3209 | 0.9839 | 2026-09-03 13:20 | 389.5428 | 484.8111 | -95.2683 | 2908.8666 | 381.7 | 477.8783 | -96.1783
2026-09-03 13:10 | 1062 | 49.36 | 345.662 | 351.89 | 966.2 | 58.6483 | 63.1007 | -4.4524 | 378.6044 | 58.6 | 62.1984 | -3.5984 | 0.9823 | 2026-09-03 13:10 | 336.335 | 349.058 | 971.5 | 58.1763 | 63.1007 | -4.9244 | 378.6044 | 56.2 | 62.1984 | -5.9984 | 0.96355 | 2026-09-03 13:10 | 342.839 | 353.511 | 960.2 | 58.9185 | 63.1007 | -4.1822 | 378.6044 | 56.4 | 62.1984 | -5.7984 | 0.96981 | 2026-09-03 13:10 | 337.988 | 343.693 | 964.8 | 57.2822 | 63.1007 | -5.8186 | 378.6044 | 56.3 | 62.1984 | -5.8984 | 0.9834 | 2026-09-03 13:10 | 259.405 | 263.73 | 729.6 | 43.955 | 46.7413 | -2.7863 | 280.4477 | 42.8 | 46.0729 | -3.2729 | 0.9836 | 2026-09-03 13:10 | 255.27 | 260.258 | 724.3 | 43.3763 | 46.7413 | -3.365 | 280.4477 | 42.2 | 46.0729 | -3.8729 | 0.98083 | 2026-09-03 13:10 | 255.828 | 261.017 | 723.4 | 43.5028 | 46.7413 | -3.2385 | 280.4477 | 42.8 | 46.0729 | -3.2729 | 0.98012 | 2026-09-03 13:10 | 258.68 | 266.06 | 730 | 44.3433 | 46.7413 | -2.398 | 280.4477 | 43.2 | 46.0729 | -2.8729 | 0.97226 | 2026-09-03 13:10 | 245.166 | 249.152 | 691.6 | 41.5253 | 44.4685 | -2.9432 | 266.8113 | 40.9 | 43.8326 | -2.9326 | 0.984 | 2026-09-03 13:10 | 449.7282 | 483.8367 | -34.1085 | 2903.02 | 439.4 | 476.9178 | -37.5178
2026-09-03 13:00 | 1071 | 49.08 | 348.925 | 355.212 | 907.6 | 59.202 | 63.7037 | -4.5017 | 382.222 | 55.7 | 62.7927 | -7.0927 | 0.9823 | 2026-09-03 13:00 | 347.909 | 353.818 | 915.3 | 58.9697 | 63.7037 | -4.734 | 382.222 | 57.9 | 62.7927 | -4.8927 | 0.9833 | 2026-09-03 13:00 | 346.333 | 356.948 | 903.8 | 59.4913 | 63.7037 | -4.2123 | 382.222 | 56.8 | 62.7927 | -5.9927 | 0.97026 | 2026-09-03 13:00 | 349.8 | 356.28 | 908.5 | 59.38 | 63.7037 | -4.3237 | 382.222 | 56.7 | 62.7927 | -6.0927 | 0.98181 | 2026-09-03 13:00 | 262.283 | 266.602 | 686.8 | 44.4337 | 47.1879 | -2.7542 | 283.1274 | 43.6 | 46.5131 | -2.9131 | 0.9838 | 2026-09-03 13:00 | 258.187 | 263.407 | 682.1 | 43.9012 | 47.1879 | -3.2867 | 283.1274 | 43 | 46.5131 | -3.5131 | 0.98018 | 2026-09-03 13:00 | 259.335 | 264.929 | 680.6 | 44.1548 | 47.1879 | -3.0331 | 283.1274 | 43.1 | 46.5131 | -3.4131 | 0.97888 | 2026-09-03 13:00 | 261.017 | 268.889 | 686.8 | 44.8148 | 47.1879 | -2.3731 | 283.1274 | 43.3 | 46.5131 | -3.2131 | 0.97072 | 2026-09-03 13:00 | 246.278 | 250.333 | 650.7 | 41.7222 | 44.8934 | -3.1713 | 269.3607 | 40.9 | 44.2515 | -3.3515 | 0.9838 | 2026-09-03 13:00 | 456.0697 | 488.4597 | -32.3901 | 2930.7584 | 441 | 481.4748 | -40.4748
2026-09-03 12:50 | 1064 | 49.08 | 334.968 | 340.449 | 851.9 | 56.7415 | 63.2873 | -6.5458 | 379.7238 | 57.4 | 62.3823 | -4.9823 | 0.9839 | 2026-09-03 12:50 | 337.226 | 342.779 | 857.4 | 57.1298 | 63.2873 | -6.1575 | 379.7238 | 56.8 | 62.3823 | -5.5823 | 0.9838 | 2026-09-03 12:50 | 337.38 | 348.119 | 847 | 58.0198 | 63.2873 | -5.2675 | 379.7238 | 56.8 | 62.3823 | -5.5823 | 0.96915 | 2026-09-03 12:50 | 337.511 | 343.208 | 851.8 | 57.2013 | 63.2873 | -6.086 | 379.7238 | 56.4 | 62.3823 | -5.9823 | 0.9834 | 2026-09-03 12:50 | 259.723 | 264.027 | 643.2 | 44.0045 | 46.8795 | -2.875 | 281.2769 | 43.7 | 46.2091 | -2.5091 | 0.9837 | 2026-09-03 12:50 | 256.185 | 261.191 | 639.1 | 43.5318 | 46.8795 | -3.3477 | 281.2769 | 43.1 | 46.2091 | -3.1091 | 0.98083 | 2026-09-03 12:50 | 256.357 | 261.891 | 637.5 | 43.6485 | 46.8795 | -3.231 | 281.2769 | 42.6 | 46.2091 | -3.6091 | 0.97887 | 2026-09-03 12:50 | 258.295 | 265.796 | 643.5 | 44.2993 | 46.8795 | -2.5802 | 281.2769 | 43 | 46.2091 | -3.2091 | 0.97178 | 2026-09-03 12:50 | 243.948 | 247.965 | 609.8 | 41.3275 | 44.6 | -3.2725 | 267.6001 | 40.6 | 43.9622 | -3.3622 | 0.9838 | 2026-09-03 12:50 | 445.9042 | 485.2672 | -39.363 | 2911.6031 | 440.4 | 478.3279 | -37.9279
2026-09-03 12:40 | 1071 | 49.08 | 338.461 | 343.805 | 794.5 | 57.3008 | 63.7037 | -6.4028 | 382.222 | 56.4 | 62.7927 | -6.3927 | 0.98446 | 2026-09-03 12:40 | 340.02 | 345.328 | 800.6 | 57.5547 | 63.7037 | -6.149 | 382.222 | 55 | 62.7927 | -7.7927 | 0.98463 | 2026-09-03 12:40 | 339.919 | 350.656 | 790.2 | 58.4427 | 63.7037 | -5.261 | 382.222 | 55.7 | 62.7927 | -7.0927 | 0.96938 | 2026-09-03 12:40 | 333.191 | 338.609 | 795.4 | 56.4348 | 63.7037 | -7.2688 | 382.222 | 55.6 | 62.7927 | -7.1927 | 0.984 | 2026-09-03 12:40 | 261.786 | 266.124 | 599.5 | 44.354 | 47.1879 | -2.8339 | 283.1274 | 43.9 | 46.5131 | -2.6131 | 0.9837 | 2026-09-03 12:40 | 258.599 | 263.831 | 596 | 43.9718 | 47.1879 | -3.2161 | 283.1274 | 43.4 | 46.5131 | -3.1131 | 0.98017 | 2026-09-03 12:40 | 258.714 | 264.629 | 594.9 | 44.1048 | 47.1879 | -3.0831 | 283.1274 | 43.3 | 46.5131 | -3.2131 | 0.97765 | 2026-09-03 12:40 | 260.977 | 268.928 | 600.5 | 44.8213 | 47.1879 | -2.3666 | 283.1274 | 43.8 | 46.5131 | -2.7131 | 0.97043 | 2026-09-03 12:40 | 246.606 | 250.667 | 569.2 | 41.7778 | 44.8934 | -3.1156 | 269.3607 | 41.4 | 44.2515 | -2.8515 | 0.9838 | 2026-09-03 12:40 | 448.7628 | 488.4597 | -39.6969 | 2930.7584 | 438.5 | 481.4748 | -42.9748
2026-09-03 12:30 | 1073 | 49.08 | 340.72 | 346.295 | 738.1 | 57.7158 | 63.8226 | -6.1068 | 382.9358 | 55.7 | 62.91 | -7.21 | 0.9839 | 2026-09-03 12:30 | 335.21 | 344.271 | 745.6 | 57.3785 | 63.8226 | -6.4441 | 382.9358 | 58.6 | 62.91 | -4.31 | 0.97368 | 2026-09-03 12:30 | 340.353 | 351.097 | 734.5 | 58.5162 | 63.8226 | -5.3065 | 382.9358 | 55.4 | 62.91 | -7.51 | 0.9694 | 2026-09-03 12:30 | 337.082 | 342.633 | 739.8 | 57.1055 | 63.8226 | -6.7171 | 382.9358 | 55.2 | 62.91 | -7.71 | 0.9838 | 2026-09-03 12:30 | 262.079 | 266.395 | 555.6 | 44.3992 | 47.276 | -2.8769 | 283.6561 | 43.4 | 46.6 | -3.2 | 0.9838 | 2026-09-03 12:30 | 258.938 | 263.995 | 552.6 | 43.9992 | 47.276 | -3.2769 | 283.6561 | 42.9 | 46.6 | -3.7 | 0.98084 | 2026-09-03 12:30 | 259.028 | 264.592 | 551.6 | 44.0987 | 47.276 | -3.1774 | 283.6561 | 43 | 46.6 | -3.6 | 0.97897 | 2026-09-03 12:30 | 261.226 | 268.828 | 556.7 | 44.8047 | 47.276 | -2.4714 | 283.6561 | 43.2 | 46.6 | -3.4 | 0.97172 | 2026-09-03 12:30 | 246.914 | 250.98 | 527.8 | 41.83 | 44.9773 | -3.1473 | 269.8637 | 40.8 | 44.3341 | -3.5341 | 0.9838 | 2026-09-03 12:30 | 449.8477 | 489.3719 | -39.5242 | 2936.2313 | 438.2 | 482.3739 | -44.1739
2026-09-03 12:20 | 1066 | 49.36 | 333.875 | 339.269 | 682.4 | 56.5448 | 63.3384 | -6.7936 | 380.0305 | 55.8 | 62.4327 | -6.6327 | 0.9841 | 2026-09-03 12:20 | 0 | 0 | 687 | 0 | 63.3384 | -63.3384 | 380.0305 | 53.7 | 62.4327 | -8.7327 |  | 2026-09-03 12:20 | 333.638 | 344.064 | 679.1 | 57.344 | 63.3384 | -5.9944 | 380.0305 | 56.6 | 62.4327 | -5.8327 | 0.9697 | 2026-09-03 12:20 | 333.564 | 339.091 | 684.6 | 56.5152 | 63.3384 | -6.8232 | 380.0305 | 56.2 | 62.4327 | -6.2327 | 0.9837 | 2026-09-03 12:20 | 258.659 | 262.998 | 512.2 | 43.833 | 46.9173 | -3.0843 | 281.504 | 42.9 | 46.2464 | -3.3464 | 0.9835 | 2026-09-03 12:20 | 256.275 | 261.641 | 509.7 | 43.6068 | 46.9173 | -3.3105 | 281.504 | 42.4 | 46.2464 | -3.8464 | 0.97949 | 2026-09-03 12:20 | 255.821 | 261.368 | 508.6 | 43.5613 | 46.9173 | -3.356 | 281.504 | 42.4 | 46.2464 | -3.8464 | 0.97878 | 2026-09-03 12:20 | 257.395 | 265.447 | 513.5 | 44.2412 | 46.9173 | -2.6762 | 281.504 | 42.8 | 46.2464 | -3.4464 | 0.96967 | 2026-09-03 12:20 | 243.541 | 247.603 | 487 | 41.2672 | 44.636 | -3.3689 | 267.8162 | 40.4 | 43.9977 | -3.5977 | 0.98359 | 2026-09-03 12:20 | 386.9135 | 485.659 | -98.7455 | 2913.9542 | 433.2 | 478.7141 | -45.5141
2026-09-03 12:10 | 1056 | 49.08 | 340.552 | 346.265 | 626.6 | 57.7108 | 62.8115 | -5.1006 | 376.8688 | 55.7 | 61.9133 | -6.2133 | 0.9835 | 2026-09-03 12:10 | 333.579 | 338.969 | 633.3 | 56.4948 | 62.8115 | -6.3166 | 376.8688 | 56.2 | 61.9133 | -5.7133 | 0.9841 | 2026-09-03 12:10 | 335.027 | 345.345 | 622.5 | 57.5575 | 62.8115 | -5.254 | 376.8688 | 56.1 | 61.9133 | -5.8133 | 0.97012 | 2026-09-03 12:10 | 335.335 | 340.857 | 628.4 | 56.8095 | 62.8115 | -6.002 | 376.8688 | 56.3 | 61.9133 | -5.6133 | 0.9838 | 2026-09-03 12:10 | 258.152 | 262.479 | 469.3 | 43.7465 | 46.527 | -2.7805 | 279.162 | 42.6 | 45.8617 | -3.2617 | 0.98351 | 2026-09-03 12:10 | 255.392 | 260.705 | 467.3 | 43.4508 | 46.527 | -3.0762 | 279.162 | 42.2 | 45.8617 | -3.6617 | 0.97962 | 2026-09-03 12:10 | 255.703 | 261.328 | 466.2 | 43.5547 | 46.527 | -2.9723 | 279.162 | 42.3 | 45.8617 | -3.5617 | 0.97848 | 2026-09-03 12:10 | 257.478 | 265.181 | 470.7 | 44.1968 | 46.527 | -2.3302 | 279.162 | 42.5 | 45.8617 | -3.3617 | 0.97095 | 2026-09-03 12:10 | 243.311 | 247.292 | 446.6 | 41.2153 | 44.2647 | -3.0494 | 265.5881 | 40.3 | 43.6317 | -3.3317 | 0.9839 | 2026-09-03 12:10 | 444.7368 | 481.6186 | -36.8817 | 2889.7113 | 434.2 | 474.7314 | -40.5314
2026-09-03 12:00 | 1042 | 49.08 | 340.116 | 346.201 | 570.9 | 57.7002 | 61.9787 | -4.2786 | 371.8724 | 56.7 | 61.0924 | -4.3924 | 0.98242 | 2026-09-03 12:00 | 343.037 | 349.076 | 577.1 | 58.1793 | 61.9787 | -3.7994 | 371.8724 | 58.6 | 61.0924 | -2.4924 | 0.9827 | 2026-09-03 12:00 | 337.124 | 347.108 | 566.4 | 57.8513 | 61.9787 | -4.1274 | 371.8724 | 55.6 | 61.0924 | -5.4924 | 0.97124 | 2026-09-03 12:00 | 341.125 | 347.342 | 572.1 | 57.8903 | 61.9787 | -4.0884 | 371.8724 | 55.6 | 61.0924 | -5.4924 | 0.9821 | 2026-09-03 12:00 | 253.922 | 258.156 | 426.7 | 43.026 | 45.9102 | -2.8842 | 275.461 | 42.5 | 45.2537 | -2.7537 | 0.9836 | 2026-09-03 12:00 | 251.727 | 256.954 | 425.1 | 42.8257 | 45.9102 | -3.0845 | 275.461 | 42.1 | 45.2537 | -3.1537 | 0.97966 | 2026-09-03 12:00 | 251.481 | 256.799 | 423.9 | 42.7998 | 45.9102 | -3.1103 | 275.461 | 42.1 | 45.2537 | -3.1537 | 0.97929 | 2026-09-03 12:00 | 253.482 | 261.088 | 428.2 | 43.5147 | 45.9102 | -2.3955 | 275.461 | 42.4 | 45.2537 | -2.8537 | 0.97087 | 2026-09-03 12:00 | 240.285 | 244.209 | 406.3 | 40.7015 | 43.6778 | -2.9763 | 262.0671 | 40.2 | 43.0532 | -2.8532 | 0.98393 | 2026-09-03 12:00 | 444.4888 | 475.2335 | -30.7446 | 2851.4008 | 435.8 | 468.4376 | -32.6376
2026-09-03 11:50 | 1033 | 48.79 | 338.242 | 344.225 | 514.2 | 57.3708 | 61.5115 | -4.1407 | 369.0691 | 55.5 | 60.6319 | -5.1319 | 0.98262 | 2026-09-03 11:50 | 342.906 | 349.095 | 518.5 | 58.1825 | 61.5115 | -3.329 | 369.0691 | 56.2 | 60.6319 | -4.4319 | 0.98227 | 2026-09-03 11:50 | 335.07 | 344.874 | 510.8 | 57.479 | 61.5115 | -4.0325 | 369.0691 | 55.2 | 60.6319 | -5.4319 | 0.97157 | 2026-09-03 11:50 | 323.905 | 329.105 | 516.5 | 54.8508 | 61.5115 | -6.6607 | 369.0691 | 56.5 | 60.6319 | -4.1319 | 0.9842 | 2026-09-03 11:50 | 252.374 | 256.53 | 384.2 | 42.755 | 45.5641 | -2.8091 | 273.3845 | 41.5 | 44.9125 | -3.4125 | 0.9838 | 2026-09-03 11:50 | 250.184 | 255.091 | 383 | 42.5152 | 45.5641 | -3.0489 | 273.3845 | 41.2 | 44.9125 | -3.7125 | 0.98076 | 2026-09-03 11:50 | 250.018 | 255.302 | 381.8 | 42.5503 | 45.5641 | -3.0138 | 273.3845 | 41.1 | 44.9125 | -3.8125 | 0.9793 | 2026-09-03 11:50 | 252.296 | 259.859 | 385.8 | 43.3098 | 45.5641 | -2.2543 | 273.3845 | 41.5 | 44.9125 | -3.4125 | 0.9709 | 2026-09-03 11:50 | 239.194 | 243.083 | 366.1 | 40.5138 | 43.3486 | -2.8347 | 260.0915 | 39.3 | 42.7287 | -3.4287 | 0.984 | 2026-09-03 11:50 | 439.5273 | 471.651 | -32.1236 | 2829.9058 | 428 | 464.9064 | -36.9064
2026-09-03 11:40 | 1010 | 49.08 | 330.562 | 336.381 | 458.7 | 56.0635 | 60.0754 | -4.0119 | 360.4521 | 57.4 | 59.2163 | -1.8163 | 0.9827 | 2026-09-03 11:40 | 335.48 | 341.431 | 462.3 | 56.9052 | 60.0754 | -3.1702 | 360.4521 | 55.1 | 59.2163 | -4.1163 | 0.98257 | 2026-09-03 11:40 | 329.007 | 338.937 | 455.6 | 56.4895 | 60.0754 | -3.5859 | 360.4521 | 54.8 | 59.2163 | -4.4163 | 0.9707 | 2026-09-03 11:40 | 332.525 | 338.457 | 460 | 56.4095 | 60.0754 | -3.6659 | 360.4521 | 54.7 | 59.2163 | -4.5163 | 0.98247 | 2026-09-03 11:40 | 247.677 | 251.73 | 342.7 | 41.955 | 44.5003 | -2.5453 | 267.0016 | 40.8 | 43.8639 | -3.0639 | 0.9839 | 2026-09-03 11:40 | 246.404 | 251.042 | 341.8 | 41.8403 | 44.5003 | -2.6599 | 267.0016 | 40.5 | 43.8639 | -3.3639 | 0.98153 | 2026-09-03 11:40 | 245.331 | 250.24 | 340.7 | 41.7067 | 44.5003 | -2.7936 | 267.0016 | 40.3 | 43.8639 | -3.5639 | 0.98038 | 2026-09-03 11:40 | 247.67 | 254.945 | 344.3 | 42.4908 | 44.5003 | -2.0094 | 267.0016 | 41.2 | 43.8639 | -2.6639 | 0.97146 | 2026-09-03 11:40 | 234.817 | 238.611 | 326.8 | 39.7685 | 42.3365 | -2.568 | 254.0189 | 39.1 | 41.7311 | -2.6311 | 0.9841 | 2026-09-03 11:40 | 433.629 | 460.639 | -27.01 | 2763.8338 | 423.9 | 454.0518 | -30.1518
2026-09-03 11:30 | 996 | 49.08 | 325.472 | 331.565 | 401.3 | 55.2608 | 59.2426 | -3.9818 | 355.4558 | 51.7 | 58.3955 | -6.6955 | 0.98162 | 2026-09-03 11:30 | 331.075 | 336.972 | 407.2 | 56.162 | 59.2426 | -3.0806 | 355.4558 | 53.1 | 58.3955 | -5.2955 | 0.9825 | 2026-09-03 11:30 | 323.657 | 333.191 | 400.8 | 55.5318 | 59.2426 | -3.7108 | 355.4558 | 53.4 | 58.3955 | -4.9955 | 0.97139 | 2026-09-03 11:30 | 328.671 | 334.49 | 405.3 | 55.7483 | 59.2426 | -3.4943 | 355.4558 | 54.1 | 58.3955 | -4.2955 | 0.9826 | 2026-09-03 11:30 | 243.58 | 247.541 | 301.9 | 41.2568 | 43.8834 | -2.6266 | 263.3006 | 40.2 | 43.2559 | -3.0559 | 0.984 | 2026-09-03 11:30 | 242.234 | 246.881 | 301.3 | 41.1468 | 43.8834 | -2.7366 | 263.3006 | 40.6 | 43.2559 | -2.6559 | 0.98118 | 2026-09-03 11:30 | 241.129 | 246.249 | 300.4 | 41.0415 | 43.8834 | -2.8419 | 263.3006 | 40.5 | 43.2559 | -2.7559 | 0.97921 | 2026-09-03 11:30 | 243.331 | 250.884 | 303.1 | 41.814 | 43.8834 | -2.0694 | 263.3006 | 40.4 | 43.2559 | -2.8559 | 0.96989 | 2026-09-03 11:30 | 231.08 | 234.79 | 287.7 | 39.1317 | 41.7496 | -2.618 | 250.4979 | 38.3 | 41.1526 | -2.8526 | 0.9842 | 2026-09-03 11:30 | 427.0938 | 454.2539 | -27.16 | 2725.5232 | 412.3 | 447.758 | -35.458
2026-09-03 11:20 | 973 | 48.79 | 321.347 | 326.971 | 349.6 | 54.4952 | 57.9387 | -3.4436 | 347.6323 | 53.3 | 57.1102 | -3.8102 | 0.9828 | 2026-09-03 11:20 | 326.298 | 332.042 | 354.1 | 55.3403 | 57.9387 | -2.5984 | 347.6323 | 54 | 57.1102 | -3.1102 | 0.9827 | 2026-09-03 11:20 | 319.257 | 328.453 | 347.4 | 54.7422 | 57.9387 | -3.1966 | 347.6323 | 53 | 57.1102 | -4.1102 | 0.972 | 2026-09-03 11:20 | 323.324 | 328.983 | 351.2 | 54.8305 | 57.9387 | -3.1082 | 347.6323 | 54.4 | 57.1102 | -2.7102 | 0.9828 | 2026-09-03 11:20 | 240.017 | 243.87 | 261.7 | 40.645 | 42.9176 | -2.2726 | 257.5054 | 40.5 | 42.3039 | -1.8039 | 0.9842 | 2026-09-03 11:20 | 239.017 | 243.441 | 260.7 | 40.5735 | 42.9176 | -2.3441 | 257.5054 | 39.5 | 42.3039 | -2.8039 | 0.98183 | 2026-09-03 11:20 | 238.239 | 243.204 | 259.9 | 40.534 | 42.9176 | -2.3836 | 257.5054 | 39.5 | 42.3039 | -2.8039 | 0.97959 | 2026-09-03 11:20 | 241.082 | 248.336 | 262.7 | 41.3893 | 42.9176 | -1.5282 | 257.5054 | 40 | 42.3039 | -2.3039 | 0.97079 | 2026-09-03 11:20 | 228.892 | 232.519 | 249.4 | 38.7532 | 40.8308 | -2.0776 | 244.9845 | 37.9 | 40.2469 | -2.3469 | 0.9844 | 2026-09-03 11:20 | 421.3032 | 444.2559 | -22.9528 | 2665.5357 | 412.1 | 437.9031 | -25.8031
2026-09-03 11:10 | 956 | 48.79 | 318.001 | 323.501 | 296.3 | 53.9168 | 56.9264 | -3.0096 | 341.5586 | 52.2 | 56.1124 | -3.9124 | 0.983 | 2026-09-03 11:10 | 322.513 | 328.091 | 300.1 | 54.6818 | 56.9264 | -2.2446 | 341.5586 | 105.4 | 56.1124 | 49.2876 | 0.983 | 2026-09-03 11:10 | 315.839 | 324.787 | 294.4 | 54.1312 | 56.9264 | -2.7953 | 341.5586 | 52.6 | 56.1124 | -3.5124 | 0.97245 | 2026-09-03 11:10 | 318.495 | 323.97 | 296.8 | 53.995 | 56.9264 | -2.9314 | 341.5586 | 52.3 | 56.1124 | -3.8124 | 0.9831 | 2026-09-03 11:10 | 237.237 | 240.972 | 221.2 | 40.162 | 42.1677 | -2.0057 | 253.0064 | 38.9 | 41.5647 | -2.6647 | 0.9845 | 2026-09-03 11:10 | 235.654 | 239.904 | 221.2 | 39.984 | 42.1677 | -2.1837 | 253.0064 | 39.8 | 41.5647 | -1.7647 | 0.98228 | 2026-09-03 11:10 | 235.53 | 240.4 | 220.4 | 40.0667 | 42.1677 | -2.1011 | 253.0064 | 38.8 | 41.5647 | -2.7647 | 0.97974 | 2026-09-03 11:10 | 237.872 | 244.809 | 222.7 | 40.8015 | 42.1677 | -1.3662 | 253.0064 | 39.1 | 41.5647 | -2.4647 | 0.97166 | 2026-09-03 11:10 | 225.526 | 229.03 | 211.5 | 38.1717 | 40.1174 | -1.9457 | 240.7042 | 37.1 | 39.5437 | -2.4437 | 0.9847 | 2026-09-03 11:10 | 415.9107 | 436.494 | -20.5834 | 2618.9641 | 456.2 | 430.2522 | 25.9478
2026-09-03 11:00 | 931 | 48.5 | 312.289 | 317.561 | 244.1 | 52.9268 | 55.4992 | -2.5723 | 332.9949 | 52 | 54.7055 | -2.7055 | 0.9834 |  |  |  |  | 0 | 55.4992 | -55.4992 | 332.9949 | 0 | 54.7055 | -54.7055 |  | 2026-09-03 11:00 | 309.911 | 318.574 | 241.8 | 53.0957 | 55.4992 | -2.4035 | 332.9949 | 50.4 | 54.7055 | -4.3055 | 0.97281 | 2026-09-03 11:00 | 313.56 | 318.885 | 244.5 | 53.1475 | 55.4992 | -2.3517 | 332.9949 | 51.2 | 54.7055 | -3.5055 | 0.9833 | 2026-09-03 11:00 | 232.846 | 236.464 | 182.3 | 39.4107 | 41.1105 | -1.6998 | 246.6629 | 38.4 | 40.5226 | -2.1226 | 0.9847 | 2026-09-03 11:00 | 231.883 | 235.82 | 181.4 | 39.3033 | 41.1105 | -1.8071 | 246.6629 | 37.5 | 40.5226 | -3.0226 | 0.98331 | 2026-09-03 11:00 | 231.245 | 235.612 | 181.6 | 39.2687 | 41.1105 | -1.8418 | 246.6629 | 38.1 | 40.5226 | -2.4226 | 0.98147 | 2026-09-03 11:00 | 233.553 | 240.842 | 183.6 | 40.1403 | 41.1105 | -0.97015 | 246.6629 | 38.6 | 40.5226 | -1.9226 | 0.96974 | 2026-09-03 11:00 | 221.314 | 224.638 | 174.4 | 37.4397 | 39.1115 | -1.6719 | 234.6692 | 36.6 | 38.5522 | -1.9522 | 0.9852 | 2026-09-03 11:00 | 354.7327 | 425.5501 | -70.8174 | 2553.3004 | 342.8 | 419.4647 | -76.6647
2026-09-03 10:50 | 905 | 48.79 | 302.331 | 307.517 | 192.1 | 51.2528 | 53.8896 | -2.6367 | 323.3374 | 49.5 | 53.1189 | -3.6189 | 0.98314 | 2026-09-03 10:50 | 307.117 | 312.333 | 194.7 | 52.0555 | 53.8896 | -1.8341 | 323.3374 | 52.1 | 53.1189 | -1.0189 | 0.9833 | 2026-09-03 10:50 | 299.965 | 308.181 | 191.4 | 51.3635 | 53.8896 | -2.5261 | 323.3374 | 49.7 | 53.1189 | -3.4189 | 0.97334 | 2026-09-03 10:50 | 305.04 | 310.221 | 193.3 | 51.7035 | 53.8896 | -2.1861 | 323.3374 | 50.3 | 53.1189 | -2.8189 | 0.9833 | 2026-09-03 10:50 | 225.036 | 228.533 | 143.9 | 38.0888 | 39.9182 | -1.8294 | 239.5092 | 36.7 | 39.3474 | -2.6474 | 0.9847 | 2026-09-03 10:50 | 226.135 | 230.044 | 143.9 | 38.3407 | 39.9182 | -1.5775 | 239.5092 | 36.6 | 39.3474 | -2.7474 | 0.98301 | 2026-09-03 10:50 | 223.932 | 228.093 | 143.5 | 38.0155 | 39.9182 | -1.9027 | 239.5092 | 36.5 | 39.3474 | -2.8474 | 0.98176 | 2026-09-03 10:50 | 227.157 | 233.893 | 145 | 38.9822 | 39.9182 | -0.93603 | 239.5092 | 36.9 | 39.3474 | -2.4474 | 0.9712 | 2026-09-03 10:50 | 215.858 | 219.145 | 137.8 | 36.5242 | 37.9772 | -1.4531 | 227.8633 | 35.6 | 37.4341 | -1.8341 | 0.985 | 2026-09-03 10:50 | 396.3267 | 413.2083 | -16.8816 | 2479.2495 | 383.9 | 407.2994 | -23.3994
2026-09-03 10:40 | 873 | 49.36 | 295.003 | 299.898 | 142.6 | 49.983 | 51.8709 | -1.8879 | 311.2257 | 48.9 | 51.1292 | -2.2292 | 0.98368 | 2026-09-03 10:40 | 298.22 | 303.171 | 142.6 | 50.5285 | 51.8709 | -1.3424 | 311.2257 | 47.4 | 51.1292 | -3.7292 | 0.98367 | 2026-09-03 10:40 | 292.589 | 300.444 | 141.7 | 50.074 | 51.8709 | -1.7969 | 311.2257 | 47.9 | 51.1292 | -3.2292 | 0.97386 | 2026-09-03 10:40 | 295.365 | 300.29 | 143 | 50.0483 | 51.8709 | -1.8226 | 311.2257 | 48.3 | 51.1292 | -2.8292 | 0.9836 | 2026-09-03 10:40 | 219.434 | 222.764 | 107.2 | 37.1273 | 38.4229 | -1.2956 | 230.5375 | 36.4 | 37.8735 | -1.4735 | 0.98505 | 2026-09-03 10:40 | 218.984 | 222.713 | 107.3 | 37.1188 | 38.4229 | -1.3041 | 230.5375 | 36.4 | 37.8735 | -1.4735 | 0.98326 | 2026-09-03 10:40 | 218.212 | 222.297 | 107 | 37.0495 | 38.4229 | -1.3734 | 230.5375 | 36.2 | 37.8735 | -1.6735 | 0.98162 | 2026-09-03 10:40 | 220.499 | 227.142 | 108.1 | 37.857 | 38.4229 | -0.56592 | 230.5375 | 36.6 | 37.8735 | -1.2735 | 0.97075 | 2026-09-03 10:40 | 209.163 | 212.327 | 102.2 | 35.3878 | 36.5547 | -1.1668 | 219.3279 | 34.2 | 36.0319 | -1.8319 | 0.9851 | 2026-09-03 10:40 | 385.1743 | 397.7301 | -12.5558 | 2386.3809 | 372.3 | 392.0426 | -19.7426
2026-09-03 10:30 | 846 | 49.36 | 286.134 | 290.816 | 93.7 | 48.4693 | 50.2667 | -1.7974 | 301.6002 | 47.2 | 49.5479 | -2.3479 | 0.9839 | 2026-09-03 10:30 | 290.348 | 295.129 | 95.2 | 49.1882 | 50.2667 | -1.0785 | 301.6002 | 47.9 | 49.5479 | -1.6479 | 0.9838 | 2026-09-03 10:30 | 284.532 | 292.073 | 93.8 | 48.6788 | 50.2667 | -1.5879 | 301.6002 | 46.9 | 49.5479 | -2.6479 | 0.97418 | 2026-09-03 10:30 | 287.536 | 292.241 | 94.7 | 48.7068 | 50.2667 | -1.5599 | 301.6002 | 47.5 | 49.5479 | -2.0479 | 0.9839 | 2026-09-03 10:30 | 213.578 | 216.786 | 70.8 | 36.131 | 37.2346 | -1.1036 | 223.4075 | 34.7 | 36.7021 | -2.0021 | 0.9852 | 2026-09-03 10:30 | 213.607 | 216.884 | 70.9 | 36.1473 | 37.2346 | -1.0873 | 223.4075 | 34.7 | 36.7021 | -2.0021 | 0.98489 | 2026-09-03 10:30 | 212.718 | 216.27 | 70.8 | 36.045 | 37.2346 | -1.1896 | 223.4075 | 34.6 | 36.7021 | -2.1021 | 0.98358 | 2026-09-03 10:30 | 214.892 | 221.365 | 71.5 | 36.8942 | 37.2346 | -0.34042 | 223.4075 | 35 | 36.7021 | -1.7021 | 0.97076 | 2026-09-03 10:30 | 204.147 | 207.193 | 68 | 34.5322 | 35.4241 | -0.89193 | 212.5446 | 33.2 | 34.9175 | -1.7175 | 0.9853 | 2026-09-03 10:30 | 374.7928 | 385.4292 | -10.6364 | 2312.5753 | 361.7 | 379.9176 | -18.2176
2026-09-03 10:20 | 812 | 49.65 | 274.981 | 279.424 | 46.5 | 46.5707 | 48.193 | -1.6223 | 289.1579 | 44.3 | 47.5038 | -3.2038 | 0.9841 | 2026-09-03 10:20 | 277.173 | 281.737 | 47.3 | 46.9562 | 48.193 | -1.2368 | 289.1579 | 44.6 | 47.5038 | -2.9038 | 0.9838 | 2026-09-03 10:20 | 272.768 | 279.39 | 46.9 | 46.565 | 48.193 | -1.628 | 289.1579 | 44.2 | 47.5038 | -3.3038 | 0.9763 | 2026-09-03 10:20 | 275.399 | 279.934 | 47.2 | 46.6557 | 48.193 | -1.5373 | 289.1579 | 44.4 | 47.5038 | -3.1038 | 0.9838 | 2026-09-03 10:20 | 204.235 | 207.282 | 36.1 | 34.547 | 35.6985 | -1.1515 | 214.191 | 33.2 | 35.188 | -1.988 | 0.9853 | 2026-09-03 10:20 | 204.662 | 207.715 | 36.2 | 34.6192 | 35.6985 | -1.0793 | 214.191 | 33.2 | 35.188 | -1.988 | 0.9853 | 2026-09-03 10:20 | 203.956 | 207.257 | 36.2 | 34.5428 | 35.6985 | -1.1557 | 214.191 | 33.2 | 35.188 | -1.988 | 0.98407 | 2026-09-03 10:20 | 206.25 | 212.457 | 36.5 | 35.4095 | 35.6985 | -0.28901 | 214.191 | 33.9 | 35.188 | -1.288 | 0.97078 | 2026-09-03 10:20 | 195.954 | 198.857 | 34.8 | 33.1428 | 33.9627 | -0.81987 | 203.7762 | 32.2 | 33.477 | -1.277 | 0.9854 | 2026-09-03 10:20 | 359.0088 | 369.5287 | -10.5198 | 2217.172 | 343.2 | 364.2444 | -21.0444
2026-09-03 10:10 | 776 | 49.65 | 176.597 | 178.579 | 2.2 | 29.7632 | 46.0563 | -16.2932 | 276.3381 | 2.2 | 45.3977 | -43.1977 | 0.9889 | 2026-09-03 10:10 | 179.416 | 182.629 | 2.7 | 30.4382 | 46.0563 | -15.6182 | 276.3381 | 2.7 | 45.3977 | -42.6977 | 0.98241 | 2026-09-03 10:10 | 196.275 | 201.667 | 2.7 | 33.6112 | 46.0563 | -12.4452 | 276.3381 | 2.7 | 45.3977 | -42.6977 | 0.97326 | 2026-09-03 10:10 | 199.653 | 202.057 | 2.8 | 33.6762 | 46.0563 | -12.3802 | 276.3381 | 2.8 | 45.3977 | -42.5977 | 0.9881 | 2026-09-03 10:10 | 193.637 | 196.706 | 2.9 | 32.7843 | 34.1158 | -1.3315 | 204.6949 | 2.9 | 33.628 | -30.728 | 0.9844 | 2026-09-03 10:10 | 194.205 | 197.223 | 3 | 32.8705 | 34.1158 | -1.2453 | 204.6949 | 3 | 33.628 | -30.628 | 0.9847 | 2026-09-03 10:10 | 193.821 | 196.833 | 3 | 32.8055 | 34.1158 | -1.3103 | 204.6949 | 3 | 33.628 | -30.628 | 0.9847 | 2026-09-03 10:10 | 190.798 | 197.399 | 2.6 | 32.8998 | 34.1158 | -1.216 | 204.6949 | 2.6 | 33.628 | -31.028 | 0.96656 | 2026-09-03 10:10 | 184.875 | 187.728 | 2.6 | 31.288 | 32.457 | -1.169 | 194.7418 | 2.6 | 31.9928 | -29.3928 | 0.9848 | 2026-09-03 10:10 | 290.1368 | 353.1456 | -63.0088 | 2118.8737 | 24.5 | 348.0956 | -323.5956
2026-09-03 10:00 | 740 | 49.65 | 0 | 0 | 0 | 0 | 43.9197 | -43.9197 | 263.5183 | 0 | 43.2917 | -43.2917 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 43.9197 | -43.9197 | 263.5183 | 0 | 43.2917 | -43.2917 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 43.9197 | -43.9197 | 263.5183 | 0 | 43.2917 | -43.2917 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 43.9197 | -43.9197 | 263.5183 | 0 | 43.2917 | -43.2917 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 32.5331 | -32.5331 | 195.1987 | 0 | 32.0679 | -32.0679 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 32.5331 | -32.5331 | 195.1987 | 0 | 32.0679 | -32.0679 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 32.5331 | -32.5331 | 195.1987 | 0 | 32.0679 | -32.0679 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 32.5331 | -32.5331 | 195.1987 | 0 | 32.0679 | -32.0679 |  | 2026-09-03 10:00 | 0 | 0 | 0 | 0 | 30.9512 | -30.9512 | 185.7074 | 0 | 30.5086 | -30.5086 |  | 2026-09-03 10:00 | 0 | 336.7626 | -336.7626 | 2020.5755 | 0 | 331.9469 | -331.9469
2026-09-03 09:50 | 703 | 49.65 | 0 | 0 | 0 | 0 | 41.7237 | -41.7237 | 250.3424 | 0 | 41.1271 | -41.1271 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 41.7237 | -41.7237 | 250.3424 | 0 | 41.1271 | -41.1271 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 41.7237 | -41.7237 | 250.3424 | 0 | 41.1271 | -41.1271 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 41.7237 | -41.7237 | 250.3424 | 0 | 41.1271 | -41.1271 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 30.9065 | -30.9065 | 185.4388 | 0 | 30.4645 | -30.4645 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 30.9065 | -30.9065 | 185.4388 | 0 | 30.4645 | -30.4645 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 30.9065 | -30.9065 | 185.4388 | 0 | 30.4645 | -30.4645 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 30.9065 | -30.9065 | 185.4388 | 0 | 30.4645 | -30.4645 |  | 2026-09-03 09:50 | 0 | 0 | 0 | 0 | 29.4037 | -29.4037 | 176.422 | 0 | 28.9832 | -28.9832 |  | 2026-09-03 09:50 | 0 | 319.9244 | -319.9244 | 1919.5467 | 0 | 315.3495 | -315.3495
2026-09-03 09:40 | 662 | 48.5 | 0 | 0 | 0 | 0 | 39.4634 | -39.4634 | 236.7805 | 0 | 38.8991 | -38.8991 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 39.4634 | -39.4634 | 236.7805 | 0 | 38.8991 | -38.8991 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 39.4634 | -39.4634 | 236.7805 | 0 | 38.8991 | -38.8991 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 39.4634 | -39.4634 | 236.7805 | 0 | 38.8991 | -38.8991 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 29.2322 | -29.2322 | 175.393 | 0 | 28.8141 | -28.8141 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 29.2322 | -29.2322 | 175.393 | 0 | 28.8141 | -28.8141 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 29.2322 | -29.2322 | 175.393 | 0 | 28.8141 | -28.8141 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 29.2322 | -29.2322 | 175.393 | 0 | 28.8141 | -28.8141 |  | 2026-09-03 09:40 | 0 | 0 | 0 | 0 | 27.8108 | -27.8108 | 166.8647 | 0 | 27.4131 | -27.4131 |  | 2026-09-03 09:40 | 0 | 302.5931 | -302.5931 | 1815.5584 | 0 | 298.266 | -298.266
2026-09-03 09:30 | 623 | 48.5 | 0 | 0 | 0 | 0 | 37.1385 | -37.1385 | 222.8312 | 0 | 36.6074 | -36.6074 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 37.1385 | -37.1385 | 222.8312 | 0 | 36.6074 | -36.6074 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 37.1385 | -37.1385 | 222.8312 | 0 | 36.6074 | -36.6074 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 37.1385 | -37.1385 | 222.8312 | 0 | 36.6074 | -36.6074 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 27.51 | -27.51 | 165.0601 | 0 | 27.1166 | -27.1166 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 27.51 | -27.51 | 165.0601 | 0 | 27.1166 | -27.1166 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 27.51 | -27.51 | 165.0601 | 0 | 27.1166 | -27.1166 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 27.51 | -27.51 | 165.0601 | 0 | 27.1166 | -27.1166 |  | 2026-09-03 09:30 | 0 | 0 | 0 | 0 | 26.1724 | -26.1724 | 157.0343 | 0 | 25.7981 | -25.7981 |  | 2026-09-03 09:30 | 0 | 284.7666 | -284.7666 | 1708.5995 | 0 | 280.6944 | -280.6944
2026-09-03 09:20 | 585 | 48.79 | 0 | 0 | 0 | 0 | 34.8347 | -34.8347 | 209.0081 | 0 | 34.3366 | -34.3366 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 34.8347 | -34.8347 | 209.0081 | 0 | 34.3366 | -34.3366 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 34.8347 | -34.8347 | 209.0081 | 0 | 34.3366 | -34.3366 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 34.8347 | -34.8347 | 209.0081 | 0 | 34.3366 | -34.3366 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 25.8035 | -25.8035 | 154.8208 | 0 | 25.4345 | -25.4345 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 25.8035 | -25.8035 | 154.8208 | 0 | 25.4345 | -25.4345 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 25.8035 | -25.8035 | 154.8208 | 0 | 25.4345 | -25.4345 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 25.8035 | -25.8035 | 154.8208 | 0 | 25.4345 | -25.4345 |  | 2026-09-03 09:20 | 0 | 0 | 0 | 0 | 24.5488 | -24.5488 | 147.2929 | 0 | 24.1978 | -24.1978 |  | 2026-09-03 09:20 | 0 | 267.1015 | -267.1015 | 1602.6088 | 0 | 263.2819 | -263.2819
2026-09-03 09:10 | 542 | 49.08 | 0 | 0 | 0 | 0 | 32.2385 | -32.2385 | 193.4307 | 0 | 31.7774 | -31.7774 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 32.2385 | -32.2385 | 193.4307 | 0 | 31.7774 | -31.7774 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 32.2385 | -32.2385 | 193.4307 | 0 | 31.7774 | -31.7774 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 32.2385 | -32.2385 | 193.4307 | 0 | 31.7774 | -31.7774 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 23.8803 | -23.8803 | 143.282 | 0 | 23.5389 | -23.5389 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 23.8803 | -23.8803 | 143.282 | 0 | 23.5389 | -23.5389 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 23.8803 | -23.8803 | 143.282 | 0 | 23.5389 | -23.5389 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 23.8803 | -23.8803 | 143.282 | 0 | 23.5389 | -23.5389 |  | 2026-09-03 09:10 | 0 | 0 | 0 | 0 | 22.7192 | -22.7192 | 136.3151 | 0 | 22.3943 | -22.3943 |  | 2026-09-03 09:10 | 0 | 247.1944 | -247.1944 | 1483.1662 | 0 | 243.6595 | -243.6595
2026-09-03 09:00 | 501 | 48.5 | 0 | 0 | 0 | 0 | 29.8658 | -29.8658 | 179.1949 | 0 | 29.4387 | -29.4387 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 29.8658 | -29.8658 | 179.1949 | 0 | 29.4387 | -29.4387 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 29.8658 | -29.8658 | 179.1949 | 0 | 29.4387 | -29.4387 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 29.8658 | -29.8658 | 179.1949 | 0 | 29.4387 | -29.4387 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 22.1228 | -22.1228 | 132.737 | 0 | 21.8065 | -21.8065 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 22.1228 | -22.1228 | 132.737 | 0 | 21.8065 | -21.8065 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 22.1228 | -22.1228 | 132.737 | 0 | 21.8065 | -21.8065 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 22.1228 | -22.1228 | 132.737 | 0 | 21.8065 | -21.8065 |  | 2026-09-03 09:00 | 0 | 0 | 0 | 0 | 21.0471 | -21.0471 | 126.2828 | 0 | 20.7462 | -20.7462 |  | 2026-09-03 09:00 | 0 | 229.0017 | -229.0017 | 1374.0102 | 0 | 225.727 | -225.727
2026-09-03 08:50 | 456 | 47.64 | 0 | 0 | 0 | 0 | 27.2724 | -27.2724 | 163.6345 | 0 | 26.8824 | -26.8824 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 27.2724 | -27.2724 | 163.6345 | 0 | 26.8824 | -26.8824 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 27.2724 | -27.2724 | 163.6345 | 0 | 26.8824 | -26.8824 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 27.2724 | -27.2724 | 163.6345 | 0 | 26.8824 | -26.8824 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 20.2018 | -20.2018 | 121.2107 | 0 | 19.9129 | -19.9129 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 20.2018 | -20.2018 | 121.2107 | 0 | 19.9129 | -19.9129 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 20.2018 | -20.2018 | 121.2107 | 0 | 19.9129 | -19.9129 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 20.2018 | -20.2018 | 121.2107 | 0 | 19.9129 | -19.9129 |  | 2026-09-03 08:50 | 0 | 0 | 0 | 0 | 19.2195 | -19.2195 | 115.317 | 0 | 18.9447 | -18.9447 |  | 2026-09-03 08:50 | 0 | 209.1163 | -209.1163 | 1254.6978 | 0 | 206.1259 | -206.1259
2026-09-03 08:40 | 410 | 47.35 | 0 | 0 | 0 | 0 | 24.5483 | -24.5483 | 147.2897 | 0 | 24.1972 | -24.1972 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 24.5483 | -24.5483 | 147.2897 | 0 | 24.1972 | -24.1972 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 24.5483 | -24.5483 | 147.2897 | 0 | 24.1972 | -24.1972 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 24.5483 | -24.5483 | 147.2897 | 0 | 24.1972 | -24.1972 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 18.1839 | -18.1839 | 109.1035 | 0 | 17.9239 | -17.9239 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 18.1839 | -18.1839 | 109.1035 | 0 | 17.9239 | -17.9239 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 18.1839 | -18.1839 | 109.1035 | 0 | 17.9239 | -17.9239 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 18.1839 | -18.1839 | 109.1035 | 0 | 17.9239 | -17.9239 |  | 2026-09-03 08:40 | 0 | 0 | 0 | 0 | 17.2997 | -17.2997 | 103.7984 | 0 | 17.0524 | -17.0524 |  | 2026-09-03 08:40 | 0 | 188.2285 | -188.2285 | 1129.371 | 0 | 185.5368 | -185.5368
2026-09-03 08:30 | 365 | 46.78 | 0 | 0 | 0 | 0 | 21.9013 | -21.9013 | 131.4075 | 0 | 21.5881 | -21.5881 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 21.9013 | -21.9013 | 131.4075 | 0 | 21.5881 | -21.5881 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 21.9013 | -21.9013 | 131.4075 | 0 | 21.5881 | -21.5881 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 21.9013 | -21.9013 | 131.4075 | 0 | 21.5881 | -21.5881 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 16.2232 | -16.2232 | 97.3389 | 0 | 15.9912 | -15.9912 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 16.2232 | -16.2232 | 97.3389 | 0 | 15.9912 | -15.9912 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 16.2232 | -16.2232 | 97.3389 | 0 | 15.9912 | -15.9912 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 16.2232 | -16.2232 | 97.3389 | 0 | 15.9912 | -15.9912 |  | 2026-09-03 08:30 | 0 | 0 | 0 | 0 | 15.4343 | -15.4343 | 92.6059 | 0 | 15.2136 | -15.2136 |  | 2026-09-03 08:30 | 0 | 167.9319 | -167.9319 | 1007.5917 | 0 | 165.5305 | -165.5305
2026-09-03 08:20 | 319 | 43.05 | 0 | 0 | 0 | 0 | 19.4116 | -19.4116 | 116.4696 | 0 | 19.134 | -19.134 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 19.4116 | -19.4116 | 116.4696 | 0 | 19.134 | -19.134 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 19.4116 | -19.4116 | 116.4696 | 0 | 19.134 | -19.134 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 19.4116 | -19.4116 | 116.4696 | 0 | 19.134 | -19.134 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 14.379 | -14.379 | 86.2738 | 0 | 14.1733 | -14.1733 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 14.379 | -14.379 | 86.2738 | 0 | 14.1733 | -14.1733 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 14.379 | -14.379 | 86.2738 | 0 | 14.1733 | -14.1733 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 14.379 | -14.379 | 86.2738 | 0 | 14.1733 | -14.1733 |  | 2026-09-03 08:20 | 0 | 0 | 0 | 0 | 13.6798 | -13.6798 | 82.0788 | 0 | 13.4842 | -13.4842 |  | 2026-09-03 08:20 | 0 | 148.8421 | -148.8421 | 893.0525 | 0 | 146.7136 | -146.7136
2026-09-03 08:10 | 275 | 36.74 | 0 | 0 | 0 | 0 | 17.1286 | -17.1286 | 102.7718 | 0 | 16.8837 | -16.8837 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 17.1286 | -17.1286 | 102.7718 | 0 | 16.8837 | -16.8837 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 17.1286 | -17.1286 | 102.7718 | 0 | 16.8837 | -16.8837 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 17.1286 | -17.1286 | 102.7718 | 0 | 16.8837 | -16.8837 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 12.6879 | -12.6879 | 76.1273 | 0 | 12.5064 | -12.5064 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 12.6879 | -12.6879 | 76.1273 | 0 | 12.5064 | -12.5064 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 12.6879 | -12.6879 | 76.1273 | 0 | 12.5064 | -12.5064 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 12.6879 | -12.6879 | 76.1273 | 0 | 12.5064 | -12.5064 |  | 2026-09-03 08:10 | 0 | 0 | 0 | 0 | 12.0709 | -12.0709 | 72.4257 | 0 | 11.8983 | -11.8983 |  | 2026-09-03 08:10 | 0 | 131.337 | -131.337 | 788.0221 | 0 | 129.4589 | -129.4589
2026-09-03 08:00 | 228 | 31.28 | 0 | 0 | 0 | 0 | 14.4842 | -14.4842 | 86.9053 | 0 | 14.2771 | -14.2771 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 14.4842 | -14.4842 | 86.9053 | 0 | 14.2771 | -14.2771 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 14.4842 | -14.4842 | 86.9053 | 0 | 14.2771 | -14.2771 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 14.4842 | -14.4842 | 86.9053 | 0 | 14.2771 | -14.2771 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 10.729 | -10.729 | 64.3743 | 0 | 10.5756 | -10.5756 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 10.729 | -10.729 | 64.3743 | 0 | 10.5756 | -10.5756 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 10.729 | -10.729 | 64.3743 | 0 | 10.5756 | -10.5756 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 10.729 | -10.729 | 64.3743 | 0 | 10.5756 | -10.5756 |  | 2026-09-03 08:00 | 0 | 0 | 0 | 0 | 10.2074 | -10.2074 | 61.2441 | 0 | 10.0614 | -10.0614 |  | 2026-09-03 08:00 | 0 | 111.0604 | -111.0604 | 666.3623 | 0 | 109.4722 | -109.4722
2026-09-03 07:50 | 182 | 20.38 | 0 | 0 | 0 | 0 | 12.013 | -12.013 | 72.0778 | 0 | 11.8412 | -11.8412 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 12.013 | -12.013 | 72.0778 | 0 | 11.8412 | -11.8412 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 12.013 | -12.013 | 72.0778 | 0 | 11.8412 | -11.8412 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 12.013 | -12.013 | 72.0778 | 0 | 11.8412 | -11.8412 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 8.8985 | -8.8985 | 53.3909 | 0 | 8.7712 | -8.7712 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 8.8985 | -8.8985 | 53.3909 | 0 | 8.7712 | -8.7712 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 8.8985 | -8.8985 | 53.3909 | 0 | 8.7712 | -8.7712 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 8.8985 | -8.8985 | 53.3909 | 0 | 8.7712 | -8.7712 |  | 2026-09-03 07:50 | 0 | 0 | 0 | 0 | 8.4658 | -8.4658 | 50.7949 | 0 | 8.3447 | -8.3447 |  | 2026-09-03 07:50 | 0 | 92.1116 | -92.1116 | 552.6696 | 0 | 90.7944 | -90.7944
2026-09-03 07:40 | 136 | 18.94 | 0 | 0 | 0 | 0 | 9.0212 | -9.0212 | 54.1274 | 0 | 8.8922 | -8.8922 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 9.0212 | -9.0212 | 54.1274 | 0 | 8.8922 | -8.8922 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 9.0212 | -9.0212 | 54.1274 | 0 | 8.8922 | -8.8922 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 9.0212 | -9.0212 | 54.1274 | 0 | 8.8922 | -8.8922 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 6.6824 | -6.6824 | 40.0944 | 0 | 6.5868 | -6.5868 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 6.6824 | -6.6824 | 40.0944 | 0 | 6.5868 | -6.5868 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 6.6824 | -6.6824 | 40.0944 | 0 | 6.5868 | -6.5868 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 6.6824 | -6.6824 | 40.0944 | 0 | 6.5868 | -6.5868 |  | 2026-09-03 07:40 | 0 | 0 | 0 | 0 | 6.3575 | -6.3575 | 38.1449 | 0 | 6.2666 | -6.2666 |  | 2026-09-03 07:40 | 0 | 69.172 | -69.172 | 415.0322 | 0 | 68.1829 | -68.1829
2026-09-03 07:30 | 94 | 16.36 | 0 | 0 | 0 | 0 | 6.2904 | -6.2904 | 37.7424 | 0 | 6.2005 | -6.2005 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 6.2904 | -6.2904 | 37.7424 | 0 | 6.2005 | -6.2005 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 6.2904 | -6.2904 | 37.7424 | 0 | 6.2005 | -6.2005 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 6.2904 | -6.2904 | 37.7424 | 0 | 6.2005 | -6.2005 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 4.6596 | -4.6596 | 27.9574 | 0 | 4.5929 | -4.5929 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 4.6596 | -4.6596 | 27.9574 | 0 | 4.5929 | -4.5929 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 4.6596 | -4.6596 | 27.9574 | 0 | 4.5929 | -4.5929 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 4.6596 | -4.6596 | 27.9574 | 0 | 4.5929 | -4.5929 |  | 2026-09-03 07:30 | 0 | 0 | 0 | 0 | 4.433 | -4.433 | 26.598 | 0 | 4.3696 | -4.3696 |  | 2026-09-03 07:30 | 0 | 48.2328 | -48.2328 | 289.3971 | 0 | 47.5431 | -47.5431
2026-09-03 07:20 | 26 | 14.92 | 0 | 0 | 0 | 0 | 1.7484 | -1.7484 | 10.4905 | 0 | 1.7234 | -1.7234 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.7484 | -1.7484 | 10.4905 | 0 | 1.7234 | -1.7234 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.7484 | -1.7484 | 10.4905 | 0 | 1.7234 | -1.7234 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.7484 | -1.7484 | 10.4905 | 0 | 1.7234 | -1.7234 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.2951 | -1.2951 | 7.7707 | 0 | 1.2766 | -1.2766 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.2951 | -1.2951 | 7.7707 | 0 | 1.2766 | -1.2766 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.2951 | -1.2951 | 7.7707 | 0 | 1.2766 | -1.2766 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.2951 | -1.2951 | 7.7707 | 0 | 1.2766 | -1.2766 |  | 2026-09-03 07:20 | 0 | 0 | 0 | 0 | 1.2321 | -1.2321 | 7.3929 | 0 | 1.2145 | -1.2145 |  | 2026-09-03 07:20 | 0 | 13.4063 | -13.4063 | 80.4376 | 0 | 13.2146 | -13.2146
2026-09-03 07:10 | 15 | 14.35 | 0 | 0 | 0 | 0 | 1.0106 | -1.0106 | 6.0639 | 0 | 0.99619 | -0.99619 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 1.0106 | -1.0106 | 6.0639 | 0 | 0.99619 | -0.99619 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 1.0106 | -1.0106 | 6.0639 | 0 | 0.99619 | -0.99619 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 1.0106 | -1.0106 | 6.0639 | 0 | 0.99619 | -0.99619 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 0.74862 | -0.74862 | 4.4917 | 0 | 0.73792 | -0.73792 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 0.74862 | -0.74862 | 4.4917 | 0 | 0.73792 | -0.73792 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 0.74862 | -0.74862 | 4.4917 | 0 | 0.73792 | -0.73792 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 0.74862 | -0.74862 | 4.4917 | 0 | 0.73792 | -0.73792 |  | 2026-09-03 07:10 | 0 | 0 | 0 | 0 | 0.71222 | -0.71222 | 4.2733 | 0 | 0.70204 | -0.70204 |  | 2026-09-03 07:10 | 0 | 7.7493 | -7.7493 | 46.4957 | 0 | 7.6385 | -7.6385
2026-09-03 07:00 | 4 | 13.49 | 0 | 0 | 0 | 0 | 0.27029 | -0.27029 | 1.6217 | 0 | 0.26642 | -0.26642 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.27029 | -0.27029 | 1.6217 | 0 | 0.26642 | -0.26642 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.27029 | -0.27029 | 1.6217 | 0 | 0.26642 | -0.26642 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.27029 | -0.27029 | 1.6217 | 0 | 0.26642 | -0.26642 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.20021 | -0.20021 | 1.2013 | 0 | 0.19735 | -0.19735 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.20021 | -0.20021 | 1.2013 | 0 | 0.19735 | -0.19735 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.20021 | -0.20021 | 1.2013 | 0 | 0.19735 | -0.19735 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.20021 | -0.20021 | 1.2013 | 0 | 0.19735 | -0.19735 |  | 2026-09-03 07:00 | 0 | 0 | 0 | 0 | 0.19048 | -0.19048 | 1.1429 | 0 | 0.18775 | -0.18775 |  | 2026-09-03 07:00 | 0 | 2.0725 | -2.0725 | 12.4348 | 0 | 2.0428 | -2.0428
[110 empty] | Total: - | 16352.1303 | 20703.3875 | -4351.2572 |  | 16158.2 | 20407.3291 | -4249.1291
Sum:- | 45299 |  | 12629.205 |  | 70044.7 |  |  |  |  | 2097.1 | 2661.4717 | -564.3717 | 0.98364 |  | 11438.605 |  | 69343.6 |  |  |  |  | 2117.3 | 2661.4717 | -544.1717 | 0.98203 |  | 12598.208 |  | 69734.1 |  |  |  |  | 2090.3 | 2661.4717 | -571.1717 | 0.97158 |  | 12637.365 |  | 70004.6 |  |  |  |  | 2096.4 | 2661.4717 | -565.0717 | 0.98327 |  | 9559.623 |  | 52808.2 |  |  |  |  | 1580.8 | 1971.4605 | -390.6605 | 0.98415 |  | 9429.672 |  | 52212.7 |  |  |  |  | 1558.8 | 1971.4605 | -412.6605 | 0.9814 |  | 9439.922 |  | 52228.9 |  |  |  |  | 1560.9 | 1971.4605 | -410.5605 | 0.98021 |  | 9498.795 |  | 52650.4 |  |  |  |  | 1571 | 1971.4605 | -400.4605 | 0.97112 |  | 8990.807 |  | 49803.3 |  |  |  |  | 1485.6 | 1875.6005 | -390.0005 | 0.98434
Formulas:
Time = [Time]

## 10 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [12 empty] | Inverter 09 | [17 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Column1 | Time | Output Active Power | Total DC I/P power TrackSo(Inv.)2 | Daily Energy(Inv.)3 | Actual Inv. I/P DC Energy at MPPT4 | Expected Inv. I/P DC energy5 | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss6 | Expected O/P Power Generated7 | Actual Inv. O/P AC Energy8 | Expected Inv. O/P AC energy9 | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss10 | Efficiency11 | Column12 | Column13 | Time 14 | Actual Inv. I/P DC Energy at MPPT15 | Expected Inv. I/P DC energy16 | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss17 | Expected O/P Power Generated18 | Actual Inv. O/P AC Energy19 | Expected Inv. O/P AC energy20 | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss21 | Column22 | Inverter No. | Efficiency23
2026-10-03 19:00 | 0 | 34.73 | 0.088 | 0.064 | 2426.3 | 0.010667 | 0 | 0.010667 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.068 | 0.171 | 2451.7 | 0.0285 | 0 | 0.0285 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.083 | 0.087 | 2406.9 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.072 | 0.23 | 2430.7 | 0.038333 | 0 | 0.038333 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.056 | 0.064 | 1811.6 | 0.010667 | 0 | 0.010667 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.062 | 0.085 | 1794.9 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.099 | 0.104 | 1792.7 | 0.017333 | 0 | 0.017333 | 0 | 0 | 0 | 0 |  | 2026-10-03 19:00 | 0.078 | 0.089 | 1802.8 | 0.014833 | 0 | 0.014833 | 0 | 0 | 0 | 0 |  |  | 2026-10-03 19:00 | 0.061 | 0.07 | 1706.4 | 0.011667 | 0 | 0.011667 | 0 | 0 | 0 | 0 |  |  |  | 2026-10-03 19:00 | 0.16067 | 0 | 0.16067 | 0 | 0 | 0 | 0 |  | 1 | 98.33%
2026-10-03 18:50 | 0 | 36.16 | 0.35 | 0.368 | 2426.3 | 0.061333 | 0 | 0.061333 | 0 | 0.2 | 0 | 0.2 |  | 2026-10-03 18:50 | 0.52 | 0.892 | 2451.7 | 0.14867 | 0 | 0.14867 | 0 | 0.2 | 0 | 0.2 |  | 2026-10-03 18:50 | 0.398 | 0.418 | 2406.9 | 0.069667 | 0 | 0.069667 | 0 | 0.3 | 0 | 0.3 |  | 2026-10-03 18:50 | 0.397 | 0.67 | 2430.7 | 0.11167 | 0 | 0.11167 | 0 | 0.2 | 0 | 0.2 |  | 2026-10-03 18:50 | 0.116 | 0.122 | 1811.6 | 0.020333 | 0 | 0.020333 | 0 | 0.2 | 0 | 0.2 |  | 2026-10-03 18:50 | 0.111 | 0.139 | 1794.9 | 0.023167 | 0 | 0.023167 | 0 | 0.1 | 0 | 0.1 |  | 2026-10-03 18:50 | 0.054 | 0.101 | 1792.7 | 0.016833 | 0 | 0.016833 | 0 | 0.1 | 0 | 0.1 |  | 2026-10-03 18:50 | 0.228 | 0.609 | 1802.8 | 0.1015 | 0 | 0.1015 | 0 | 0.2 | 0 | 0.2 |  |  | 2026-10-03 18:50 | 0.035 | 0.09 | 1706.3 | 0.015 | 0 | 0.015 | 0 | 0.1 | 0 | 0.1 |  |  |  | 2026-10-03 18:50 | 0.56817 | 0 | 0.56817 | 0 | 1.6 | 0 | 1.6 |  | 2 | 98.39%
2026-10-03 18:40 | 0 | 38.46 | 2.368 | 2.49 | 2426.1 | 0.415 | 0 | 0.415 | 0 | 0.7 | 0 | 0.7 |  | 2026-10-03 18:40 | 2.517 | 3.124 | 2451.5 | 0.52067 | 0 | 0.52067 | 0 | 0.8 | 0 | 0.8 |  | 2026-10-03 18:40 | 2.383 | 2.506 | 2406.6 | 0.41767 | 0 | 0.41767 | 0 | 0.7 | 0 | 0.7 |  | 2026-10-03 18:40 | 2.255 | 2.818 | 2430.5 | 0.46967 | 0 | 0.46967 | 0 | 0.7 | 0 | 0.7 |  | 2026-10-03 18:40 | 1.613 | 1.696 | 1811.4 | 0.28267 | 0 | 0.28267 | 0 | 0.4 | 0 | 0.4 |  | 2026-10-03 18:40 | 1.57 | 1.651 | 1794.8 | 0.27517 | 0 | 0.27517 | 0 | 0.5 | 0 | 0.5 |  | 2026-10-03 18:40 | 1.55 | 1.63 | 1792.6 | 0.27167 | 0 | 0.27167 | 0 | 0.5 | 0 | 0.5 |  | 2026-10-03 18:40 | 1.658 | 1.973 | 1802.6 | 0.32883 | 0 | 0.32883 | 0 | 0.4 | 0 | 0.4 |  |  | 2026-10-03 18:40 | 1.473 | 1.549 | 1706.2 | 0.25817 | 0 | 0.25817 | 0 | 0.4 | 0 | 0.4 |  |  |  | 2026-10-03 18:40 | 3.2395 | 0 | 3.2395 | 0 | 5.1 | 0 | 5.1 |  | 3 | 97.26%
2026-10-03 18:30 | 10 | 41.33 | 6.092 | 6.374 | 2425.4 | 1.0623 | 0.61242 | 0.44991 | 3.6745 | 1.5 | 0.60367 | 0.89633 |  | 2026-10-03 18:30 | 6.606 | 6.954 | 2450.7 | 1.159 | 0.61242 | 0.54658 | 3.6745 | 1.6 | 0.60367 | 0.99633 |  | 2026-10-03 18:30 | 6.356 | 6.643 | 2405.9 | 1.1072 | 0.61242 | 0.49474 | 3.6745 | 1.5 | 0.60367 | 0.89633 |  | 2026-10-03 18:30 | 6.494 | 6.79 | 2429.8 | 1.1317 | 0.61242 | 0.51924 | 3.6745 | 1.6 | 0.60367 | 0.99633 |  | 2026-10-03 18:30 | 4.611 | 4.835 | 1811 | 0.80583 | 0.45365 | 0.35219 | 2.7219 | 1.2 | 0.44716 | 0.75284 |  | 2026-10-03 18:30 | 4.492 | 4.721 | 1794.3 | 0.78683 | 0.45365 | 0.33319 | 2.7219 | 1.1 | 0.44716 | 0.65284 |  | 2026-10-03 18:30 | 4.434 | 4.652 | 1792.1 | 0.77533 | 0.45365 | 0.32169 | 2.7219 | 1 | 0.44716 | 0.55284 |  | 2026-10-03 18:30 | 4.208 | 4.675 | 1802.2 | 0.77917 | 0.45365 | 0.32552 | 2.7219 | 1 | 0.44716 | 0.55284 |  |  | 2026-10-03 18:30 | 4.012 | 4.211 | 1705.8 | 0.70183 | 0.43159 | 0.27024 | 2.5895 | 1 | 0.42542 | 0.57458 |  |  |  | 2026-10-03 18:30 | 8.3092 | 4.6959 | 3.6133 | 28.1753 | 11.5 | 4.6287 | 6.8713 |  | 4 | 98.3%
2026-10-03 18:20 | 24 | 44.2 | 12.074 | 12.478 | 2423.9 | 2.0797 | 1.4542 | 0.62551 | 8.725 | 2.7 | 1.4334 | 1.2666 |  | 2026-10-03 18:20 | 13.093 | 13.554 | 2449.1 | 2.259 | 1.4542 | 0.80484 | 8.725 | 2.8 | 1.4334 | 1.3666 |  | 2026-10-03 18:20 | 12.484 | 12.899 | 2404.4 | 2.1498 | 1.4542 | 0.69567 | 8.725 | 2.8 | 1.4334 | 1.3666 |  | 2026-10-03 18:20 | 12.588 | 13.008 | 2428.2 | 2.168 | 1.4542 | 0.71384 | 8.725 | 2.8 | 1.4334 | 1.3666 |  | 2026-10-03 18:20 | 9.223 | 9.582 | 1809.8 | 1.597 | 1.0772 | 0.51984 | 6.4629 | 2 | 1.0618 | 0.93825 |  | 2026-10-03 18:20 | 8.914 | 9.26 | 1793.2 | 1.5433 | 1.0772 | 0.46618 | 6.4629 | 2 | 1.0618 | 0.93825 |  | 2026-10-03 18:20 | 8.889 | 9.239 | 1791.1 | 1.5398 | 1.0772 | 0.46268 | 6.4629 | 2 | 1.0618 | 0.93825 |  | 2026-10-03 18:20 | 7.327 | 7.812 | 1801.2 | 1.302 | 1.0772 | 0.22484 | 6.4629 | 1.6 | 1.0618 | 0.53825 |  |  | 2026-10-03 18:20 | 7.741 | 8.059 | 1704.8 | 1.3432 | 1.0248 | 0.31839 | 6.1487 | 1.7 | 1.0101 | 0.68987 |  |  |  | 2026-10-03 18:20 | 15.9818 | 11.15 | 4.8318 | 66.9002 | 20.4 | 10.9906 | 9.4094 |  | 5 | 98.44%
2026-10-03 18:10 | 37 | 46.78 | 20.87 | 21.377 | 2421.2 | 3.5628 | 2.2201 | 1.3427 | 13.3208 | 4.3 | 2.1884 | 2.1116 |  | 2026-10-03 18:10 | 22.593 | 23.127 | 2446.3 | 3.8545 | 2.2201 | 1.6344 | 13.3208 | 2446.3 | 2.1884 | 2444.1116 |  | 2026-10-03 18:10 | 21.674 | 22.191 | 2401.6 | 3.6985 | 2.2201 | 1.4784 | 13.3208 | 4.6 | 2.1884 | 2.4116 |  | 2026-10-03 18:10 | 21.509 | 22.02 | 2425.4 | 3.67 | 2.2201 | 1.4499 | 13.3208 | 4.5 | 2.1884 | 2.3116 |  | 2026-10-03 18:10 | 15.987 | 16.412 | 1807.8 | 2.7353 | 1.6445 | 1.0908 | 9.8672 | 3.4 | 1.621 | 1.779 |  | 2026-10-03 18:10 | 15.348 | 15.764 | 1791.2 | 2.6273 | 1.6445 | 0.98279 | 9.8672 | 3.2 | 1.621 | 1.579 |  | 2026-10-03 18:10 | 15.453 | 15.872 | 1789.1 | 2.6453 | 1.6445 | 1.0008 | 9.8672 | 3.3 | 1.621 | 1.679 |  | 2026-10-03 18:10 | 12.275 | 13.02 | 1799.6 | 2.17 | 1.6445 | 0.52546 | 9.8672 | 2.8 | 1.621 | 1.179 |  |  | 2026-10-03 18:10 | 14.038 | 14.457 | 1703.1 | 2.4095 | 1.5646 | 0.84493 | 9.3874 | 3.1 | 1.5422 | 1.5578 |  |  |  | 2026-10-03 18:10 | 27.3733 | 17.0232 | 10.3501 | 102.1394 | 2475.5 | 16.7798 | 2458.7202 |  | 6 | 98.16%
2026-10-03 18:00 | 52 | 47.64 | 32.887 | 33.49 | 2416.9 | 5.5817 | 3.11 | 2.4717 | 18.6601 | 2416.9 | 3.0655 | 2413.8345 | [5 empty] | 0 | 3.11 | -3.11 | 18.6601 | -2434.7 | 3.0655 | -2437.7655 |  | 2026-10-03 18:00 | 34.036 | 34.653 | 2397 | 5.7755 | 3.11 | 2.6655 | 18.6601 | 6.8 | 3.0655 | 3.7345 |  | 2026-10-03 18:00 | 33.57 | 34.185 | 2420.9 | 5.6975 | 3.11 | 2.5875 | 18.6601 | 6.8 | 3.0655 | 3.7345 |  | 2026-10-03 18:00 | 25.345 | 25.891 | 1804.4 | 4.3152 | 2.3037 | 2.0115 | 13.8223 | 5.1 | 2.2708 | 2.8292 |  | 2026-10-03 18:00 | 24.177 | 24.716 | 1788 | 4.1193 | 2.3037 | 1.8156 | 13.8223 | 4.9 | 2.2708 | 2.6292 |  | 2026-10-03 18:00 | 24.414 | 24.95 | 1785.8 | 4.1583 | 2.3037 | 1.8546 | 13.8223 | 4.9 | 2.2708 | 2.6292 |  | 2026-10-03 18:00 | 22.215 | 23.094 | 1796.8 | 3.849 | 2.3037 | 1.5453 | 13.8223 | 4.7 | 2.2708 | 2.4292 |  |  | 2026-10-03 18:00 | 22.604 | 23.12 | 1700 | 3.8533 | 2.1917 | 1.6616 | 13.1502 | 4.5 | 2.1604 | 2.3396 |  |  |  | 2026-10-03 18:00 | 37.3498 | 23.8466 | 13.5032 | 143.0796 | 19.9 | 23.5056 | -3.6056 |  | 7 | 98.11%
2026-10-03 17:50 | 140 | 47.93 |  |  |  | 0 | 8.3639 | -8.3639 | 50.1833 | -2401.1 | 8.2443 | -2409.3443 |  | 2026-10-03 17:50 | 48.083 | 48.865 | 2434.7 | 8.1442 | 8.3639 | -0.21971 | 50.1833 | 9.3 | 8.2443 | 1.0557 |  | 2026-10-03 17:50 | 47.674 | 48.444 | 2390.2 | 8.074 | 8.3639 | -0.28988 | 50.1833 | 9.2 | 8.2443 | 0.95572 |  | 2026-10-03 17:50 | 46.969 | 47.733 | 2414.1 | 7.9555 | 8.3639 | -0.40838 | 50.1833 | 9.1 | 8.2443 | 0.85572 |  | 2026-10-03 17:50 | 35.434 | 36.065 | 1799.3 | 6.0108 | 6.1955 | -0.18463 | 37.1728 | 6.9 | 6.1069 | 0.79313 |  | 2026-10-03 17:50 | 34.007 | 34.627 | 1783.1 | 5.7712 | 6.1955 | -0.4243 | 37.1728 | 6.6 | 6.1069 | 0.49313 |  | 2026-10-03 17:50 | 34.16 | 34.772 | 1780.9 | 5.7953 | 6.1955 | -0.40013 | 37.1728 | 6.7 | 6.1069 | 0.59313 |  | 2026-10-03 17:50 | 33.896 | 35.105 | 1792.1 | 5.8508 | 6.1955 | -0.34463 | 37.1728 | 6.6 | 6.1069 | 0.49313 |  |  | 2026-10-03 17:50 | 31.935 | 32.52 | 1695.5 | 5.42 | 5.8942 | -0.47422 | 35.3653 | 6.2 | 5.8099 | 0.39007 |  |  |  | 2026-10-03 17:50 | 53.0218 | 64.1316 | -11.1098 | 384.7896 | -2340.5 | 63.2145 | -2403.7145 |  | 8 | 97.15%
2026-10-03 17:40 | 195 | 47.93 | 62.793 | 63.646 | 2401.1 | 10.6077 | 11.6497 | -1.042 | 69.8981 | 11.7 | 11.4831 | 0.2169 |  | 2026-10-03 17:40 | 64.555 | 64.997 | 2425.4 | 10.8328 | 11.6497 | -0.81686 | 69.8981 | 11.7 | 11.4831 | 0.2169 |  | 2026-10-03 17:40 | 63.539 | 64.545 | 2381 | 10.7575 | 11.6497 | -0.89219 | 69.8981 | 11.8 | 11.4831 | 0.3169 |  | 2026-10-03 17:40 | 62.78 | 63.658 | 2405 | 10.6097 | 11.6497 | -1.04 | 69.8981 | 11.6 | 11.4831 | 0.1169 |  | 2026-10-03 17:40 | 47.212 | 47.97 | 1792.4 | 7.995 | 8.6294 | -0.6344 | 51.7764 | 8.7 | 8.506 | 0.194 |  | 2026-10-03 17:40 | 45.512 | 46.277 | 1776.5 | 7.7128 | 8.6294 | -0.91657 | 51.7764 | 8.6 | 8.506 | 0.094001 |  | 2026-10-03 17:40 | 45.884 | 46.625 | 1774.2 | 7.7708 | 8.6294 | -0.85857 | 51.7764 | 8.5 | 8.506 | -0.0059986 |  | 2026-10-03 17:40 | 45.402 | 46.861 | 1785.5 | 7.8102 | 8.6294 | -0.81923 | 51.7764 | 8.5 | 8.506 | -0.0059986 |  |  | 2026-10-03 17:40 | 42.894 | 43.605 | 1689.3 | 7.2675 | 8.2098 | -0.9423 | 49.2588 | 8 | 8.0924 | -0.092404 |  |  |  | 2026-10-03 17:40 | 81.364 | 89.3262 | -7.9622 | 535.9569 | 89.1 | 88.0488 | 1.0512 |  | 9 | 98.47%
2026-10-03 17:30 | 235 | 47.64 | 77.467 | 78.471 | 2389.4 | 13.0785 | 14.0549 | -0.97636 | 84.3292 | 14.3 | 13.8539 | 0.44612 |  | 2026-10-03 17:30 | 78.59 | 79.467 | 2413.7 | 13.2445 | 14.0549 | -0.81036 | 84.3292 | 14.6 | 13.8539 | 0.74612 |  | 2026-10-03 17:30 | 77.887 | 79.287 | 2369.2 | 13.2145 | 14.0549 | -0.84036 | 84.3292 | 14.4 | 13.8539 | 0.54612 |  | 2026-10-03 17:30 | 76.927 | 77.964 | 2393.4 | 12.994 | 14.0549 | -1.0609 | 84.3292 | 14.3 | 13.8539 | 0.44612 |  | 2026-10-03 17:30 | 58.001 | 58.69 | 1783.7 | 9.7817 | 10.411 | -0.62934 | 62.4661 | 10.8 | 10.2621 | 0.53787 |  | 2026-10-03 17:30 | 56.019 | 56.843 | 1767.9 | 9.4738 | 10.411 | -0.93718 | 62.4661 | 10.4 | 10.2621 | 0.13787 |  | 2026-10-03 17:30 | 56.329 | 57.158 | 1765.7 | 9.5263 | 10.411 | -0.88468 | 62.4661 | 10.5 | 10.2621 | 0.23787 |  | 2026-10-03 17:30 | 55.995 | 57.825 | 1777 | 9.6375 | 10.411 | -0.77351 | 62.4661 | 10.4 | 10.2621 | 0.13787 |  |  | 2026-10-03 17:30 | 52.724 | 53.545 | 1681.3 | 8.9242 | 9.9048 | -0.98062 | 59.4287 | 9.8 | 9.7631 | 0.036853 |  |  |  | 2026-10-03 17:30 | 99.875 | 107.7683 | -7.8933 | 646.6096 | 109.5 | 106.2272 | 3.2728
2026-10-03 17:20 | 288 | 48.22 | 95.265 | 96.442 | 2375.1 | 16.0737 | 17.1867 | -1.113 | 103.1202 | 17.4 | 16.9409 | 0.45906 |  | 2026-10-03 17:20 | 98.137 | 99.399 | 2399.1 | 16.5665 | 17.1867 | -0.62021 | 103.1202 | 18 | 16.9409 | 1.0591 |  | 2026-10-03 17:20 | 96.031 | 98.071 | 2354.8 | 16.3452 | 17.1867 | -0.84154 | 103.1202 | 18.1 | 16.9409 | 1.1591 |  | 2026-10-03 17:20 | 95.662 | 96.873 | 2379.1 | 16.1455 | 17.1867 | -1.0412 | 103.1202 | 18 | 16.9409 | 1.0591 |  | 2026-10-03 17:20 | 71.482 | 72.453 | 1772.9 | 12.0755 | 12.7309 | -0.65539 | 76.3854 | 13.4 | 12.5488 | 0.85116 |  | 2026-10-03 17:20 | 69.896 | 70.831 | 1757.5 | 11.8052 | 12.7309 | -0.92573 | 76.3854 | 13 | 12.5488 | 0.45116 |  | 2026-10-03 17:20 | 69.814 | 70.762 | 1755.2 | 11.7937 | 12.7309 | -0.93723 | 76.3854 | 13 | 12.5488 | 0.45116 |  | 2026-10-03 17:20 | 69.518 | 71.369 | 1766.6 | 11.8948 | 12.7309 | -0.83606 | 76.3854 | 13 | 12.5488 | 0.45116 |  |  | 2026-10-03 17:20 | 65.634 | 66.546 | 1671.5 | 11.091 | 12.1119 | -1.0209 | 72.6712 | 12.2 | 11.9387 | 0.26133 |  |  |  | 2026-10-03 17:20 | 123.791 | 131.7823 | -7.9913 | 790.6936 | 136.1 | 129.8978 | 6.2022
2026-10-03 17:10 | 342 | 48.22 | 114.696 | 116.124 | 2357.7 | 19.354 | 20.4092 | -1.0552 | 122.4553 | 21.1 | 20.1174 | 0.98264 |  | 2026-10-03 17:10 | 116.942 | 118.458 | 2381.1 | 19.743 | 20.4092 | -0.66621 | 122.4553 | 20.9 | 20.1174 | 0.78264 |  | 2026-10-03 17:10 | 116.045 | 118.369 | 2336.7 | 19.7282 | 20.4092 | -0.68105 | 122.4553 | 20.5 | 20.1174 | 0.38264 |  | 2026-10-03 17:10 | 114.806 | 116.283 | 2361.1 | 19.3805 | 20.4092 | -1.0287 | 122.4553 | 20.2 | 20.1174 | 0.082638 |  | 2026-10-03 17:10 | 86.489 | 87.628 | 1759.5 | 14.6047 | 15.1179 | -0.51327 | 90.7076 | 15.2 | 14.9017 | 0.29825 |  | 2026-10-03 17:10 | 84.242 | 85.326 | 1744.5 | 14.221 | 15.1179 | -0.89694 | 90.7076 | 14.8 | 14.9017 | -0.10175 |  | 2026-10-03 17:10 | 84.343 | 85.437 | 1742.2 | 14.2395 | 15.1179 | -0.87844 | 90.7076 | 15.1 | 14.9017 | 0.19825 |  | 2026-10-03 17:10 | 84.094 | 86.492 | 1753.6 | 14.4153 | 15.1179 | -0.7026 | 90.7076 | 15 | 14.9017 | 0.09825 |  |  | 2026-10-03 17:10 | 79.262 | 80.379 | 1659.3 | 13.3965 | 14.3828 | -0.98634 | 86.2971 | 14.2 | 14.1772 | 0.022831 |  |  |  | 2026-10-03 17:10 | 149.0827 | 156.4914 | -7.4088 | 938.9487 | 157 | 154.2536 | 2.7464
2026-10-03 17:00 | 382 | 48.22 | 130.373 | 132.05 | 2336.6 | 22.0083 | 22.7963 | -0.78792 | 136.7775 | 22.2 | 22.4703 | -0.27027 |  | 2026-10-03 17:00 | 133.174 | 134.942 | 2360.2 | 22.4903 | 22.7963 | -0.30592 | 136.7775 | 24.1 | 22.4703 | 1.6297 |  | 2026-10-03 17:00 | 131.094 | 133.95 | 2316.2 | 22.325 | 22.7963 | -0.47126 | 136.7775 | 23.2 | 22.4703 | 0.72973 |  | 2026-10-03 17:00 | 129.394 | 131.085 | 2340.9 | 21.8475 | 22.7963 | -0.94876 | 136.7775 | 23 | 22.4703 | 0.52973 |  | 2026-10-03 17:00 | 98.109 | 99.391 | 1744.3 | 16.5652 | 16.8861 | -0.32095 | 101.3167 | 17.3 | 16.6446 | 0.65536 |  | 2026-10-03 17:00 | 95.36 | 96.567 | 1729.7 | 16.0945 | 16.8861 | -0.79162 | 101.3167 | 16.9 | 16.6446 | 0.25536 |  | 2026-10-03 17:00 | 95.888 | 97.102 | 1727.1 | 16.1837 | 16.8861 | -0.70245 | 101.3167 | 16.7 | 16.6446 | 0.055356 |  | 2026-10-03 17:00 | 95.476 | 98.322 | 1738.6 | 16.387 | 16.8861 | -0.49912 | 101.3167 | 16.7 | 16.6446 | 0.055356 |  |  | 2026-10-03 17:00 | 90.042 | 91.2 | 1645.1 | 15.2 | 16.065 | -0.86505 | 96.3903 | 15.7 | 15.8353 | -0.13532 |  |  |  | 2026-10-03 17:00 | 169.1015 | 174.7945 | -5.693 | 1048.7672 | 175.8 | 172.295 | 3.505
2026-10-03 16:50 | 424 | 48.22 | 145.252 | 147.15 | 2314.4 | 24.525 | 25.3027 | -0.77765 | 151.8159 | 53.4 | 24.9408 | 28.4592 |  | 2026-10-03 16:50 | 148.988 | 149.783 | 2336.1 | 24.9638 | 25.3027 | -0.33882 | 151.8159 | 25.2 | 24.9408 | 0.25918 |  | 2026-10-03 16:50 | 144.72 | 147.643 | 2293 | 24.6072 | 25.3027 | -0.69548 | 151.8159 | 25.1 | 24.9408 | 0.15918 |  | 2026-10-03 16:50 | 145.048 | 146.988 | 2317.9 | 24.498 | 25.3027 | -0.80465 | 151.8159 | 25.1 | 24.9408 | 0.15918 |  | 2026-10-03 16:50 | 108.696 | 110.117 | 1727 | 18.3528 | 18.7427 | -0.38987 | 112.4562 | 18.9 | 18.4747 | 0.42532 |  | 2026-10-03 16:50 | 105.926 | 107.394 | 1712.8 | 17.899 | 18.7427 | -0.8437 | 112.4562 | 18.4 | 18.4747 | -0.074684 |  | 2026-10-03 16:50 | 106.31 | 107.688 | 1710.4 | 17.948 | 18.7427 | -0.7947 | 112.4562 | 18.4 | 18.4747 | -0.074684 |  | 2026-10-03 16:50 | 106.119 | 109.279 | 1721.9 | 18.2132 | 18.7427 | -0.52954 | 112.4562 | 18.6 | 18.4747 | 0.12532 |  |  | 2026-10-03 16:50 | 100.028 | 101.335 | 1629.4 | 16.8892 | 17.8314 | -0.9422 | 106.9882 | 17.4 | 17.5764 | -0.17637 |  |  |  | 2026-10-03 16:50 | 187.8962 | 194.0128 | -6.1166 | 1164.0767 | 220.5 | 191.2384 | 29.2616
2026-10-03 16:40 | 462 | 48.5 | 158.781 | 160.905 | 2288.5 | 26.8175 | 27.5409 | -0.72343 | 165.2456 | 0 | 27.1471 | -27.1471 |  | 2026-10-03 16:40 | 162.399 | 163.044 | 2310.9 | 27.174 | 27.5409 | -0.36693 | 165.2456 | 28.2 | 27.1471 | 1.0529 |  | 2026-10-03 16:40 | 158.848 | 162.079 | 2267.9 | 27.0132 | 27.5409 | -0.52777 | 165.2456 | 27.8 | 27.1471 | 0.6529 |  | 2026-10-03 16:40 | 158.428 | 160.58 | 2292.8 | 26.7633 | 27.5409 | -0.7776 | 165.2456 | 27.8 | 27.1471 | 0.6529 |  | 2026-10-03 16:40 | 118.934 | 120.513 | 1708.1 | 20.0855 | 20.4007 | -0.31519 | 122.4041 | 20.9 | 20.109 | 0.79104 |  | 2026-10-03 16:40 | 116.155 | 117.673 | 1694.4 | 19.6122 | 20.4007 | -0.78852 | 122.4041 | 20.4 | 20.109 | 0.29104 |  | 2026-10-03 16:40 | 116.366 | 117.899 | 1692 | 19.6498 | 20.4007 | -0.75086 | 122.4041 | 20.5 | 20.109 | 0.39104 |  | 2026-10-03 16:40 | 116.894 | 119.867 | 1703.3 | 19.9778 | 20.4007 | -0.42286 | 122.4041 | 20.3 | 20.109 | 0.19104 |  |  | 2026-10-03 16:40 | 109.722 | 111.178 | 1612 | 18.5297 | 19.4087 | -0.87906 | 116.4524 | 19.3 | 19.1312 | 0.16881 |  |  |  | 2026-10-03 16:40 | 205.623 | 211.1752 | -5.5522 | 1267.0513 | 185.2 | 208.1554 | -22.9554
2026-10-03 16:30 | 505 | 48.5 | 174.186 | 176.552 | 2261 | 29.4253 | 30.1043 | -0.67893 | 180.6256 | 30.7 | 29.6738 | 1.0262 |  | 2026-10-03 16:30 | 175.939 | 178.45 | 2282.7 | 29.7417 | 30.1043 | -0.3626 | 180.6256 | 31.1 | 29.6738 | 1.4262 |  | 2026-10-03 16:30 | 173.715 | 177.51 | 2240.1 | 29.585 | 30.1043 | -0.51927 | 180.6256 | 30.1 | 29.6738 | 0.42622 |  | 2026-10-03 16:30 | 173.658 | 176.088 | 2265 | 29.348 | 30.1043 | -0.75627 | 180.6256 | 30.3 | 29.6738 | 0.62622 |  | 2026-10-03 16:30 | 130.224 | 131.966 | 1687.2 | 21.9943 | 22.2995 | -0.30512 | 133.7967 | 22.6 | 21.9806 | 0.61943 |  | 2026-10-03 16:30 | 127.431 | 129.123 | 1674 | 21.5205 | 22.2995 | -0.77896 | 133.7967 | 22.2 | 21.9806 | 0.21943 |  | 2026-10-03 16:30 | 127.618 | 129.41 | 1671.5 | 21.5683 | 22.2995 | -0.73112 | 133.7967 | 22.2 | 21.9806 | 0.21943 |  | 2026-10-03 16:30 | 127.751 | 131.506 | 1683 | 21.9177 | 22.2995 | -0.38179 | 133.7967 | 22.2 | 21.9806 | 0.21943 |  |  | 2026-10-03 16:30 | 120.395 | 122.018 | 1592.7 | 20.3363 | 21.2152 | -0.87884 | 127.291 | 20.9 | 20.9118 | -0.011794 |  |  |  | 2026-10-03 16:30 | 225.4372 | 230.8301 | -5.3929 | 1384.9804 | 232.3 | 227.5292 | 4.7708
2026-10-03 16:20 | 545 | 48.5 | 188.7 | 191.321 | 2230.3 | 31.8868 | 32.4888 | -0.60193 | 194.9326 | 31.8 | 32.0242 | -0.22417 |  | 2026-10-03 16:20 | 190.154 | 192.874 | 2251.6 | 32.1457 | 32.4888 | -0.3431 | 194.9326 | 32 | 32.0242 | -0.024173 |  | 2026-10-03 16:20 | 188.064 | 192.587 | 2210 | 32.0978 | 32.4888 | -0.39093 | 194.9326 | 32.1 | 32.0242 | 0.075827 |  | 2026-10-03 16:20 | 188.541 | 191.218 | 2234.7 | 31.8697 | 32.4888 | -0.6191 | 194.9326 | 32.6 | 32.0242 | 0.57583 |  | 2026-10-03 16:20 | 141.37 | 143.305 | 1664.6 | 23.8842 | 24.0657 | -0.18158 | 144.3945 | 24.5 | 23.7216 | 0.77839 |  | 2026-10-03 16:20 | 138.496 | 140.494 | 1651.8 | 23.4157 | 24.0657 | -0.65008 | 144.3945 | 24 | 23.7216 | 0.27839 |  | 2026-10-03 16:20 | 138.618 | 140.472 | 1649.3 | 23.412 | 24.0657 | -0.65375 | 144.3945 | 24 | 23.7216 | 0.27839 |  | 2026-10-03 16:20 | 138.777 | 142.587 | 1660.8 | 23.7645 | 24.0657 | -0.30125 | 144.3945 | 24 | 23.7216 | 0.27839 |  |  | 2026-10-03 16:20 | 131.079 | 132.658 | 1571.8 | 22.1097 | 22.8956 | -0.78591 | 137.3735 | 22.7 | 22.5682 | 0.13183 |  |  |  | 2026-10-03 16:20 | 244.586 | 249.1136 | -4.5276 | 1494.6818 | 247.7 | 245.5513 | 2.1487
2026-10-03 16:10 | 586 | 48.5 | 203.134 | 205.481 | 2198.5 | 34.2468 | 34.9329 | -0.68604 | 209.5972 | 35.6 | 34.4333 | 1.1667 |  | 2026-10-03 16:10 | 205.072 | 208.026 | 2219.6 | 34.671 | 34.9329 | -0.26187 | 209.5972 | 36.5 | 34.4333 | 2.0667 |  | 2026-10-03 16:10 | 202.093 | 206.806 | 2177.9 | 34.4677 | 34.9329 | -0.4652 | 209.5972 | 35 | 34.4333 | 0.56667 |  | 2026-10-03 16:10 | 202.696 | 205.595 | 2202.1 | 34.2658 | 34.9329 | -0.66704 | 209.5972 | 34.7 | 34.4333 | 0.26667 |  | 2026-10-03 16:10 | 152.087 | 154.153 | 1640.1 | 25.6922 | 25.8762 | -0.18403 | 155.2572 | 26 | 25.5062 | 0.49383 |  | 2026-10-03 16:10 | 149.007 | 151.229 | 1627.8 | 25.2048 | 25.8762 | -0.67137 | 155.2572 | 25.4 | 25.5062 | -0.10617 |  | 2026-10-03 16:10 | 149.177 | 151.218 | 1625.3 | 25.203 | 25.8762 | -0.6732 | 155.2572 | 25.5 | 25.5062 | -0.0061712 |  | 2026-10-03 16:10 | 149.289 | 153.694 | 1636.8 | 25.6157 | 25.8762 | -0.26053 | 155.2572 | 25.5 | 25.5062 | -0.0061712 |  |  | 2026-10-03 16:10 | 140.835 | 142.748 | 1549.1 | 23.7913 | 24.618 | -0.82667 | 147.708 | 24 | 24.266 | -0.26596 |  |  |  | 2026-10-03 16:10 | 263.1583 | 267.8543 | -4.696 | 1607.1257 | 268.2 | 264.024 | 4.176
2026-10-03 16:00 | 623 | 48.79 | 214.726 | 217.819 | 2162.9 | 36.3032 | 37.0975 | -0.79429 | 222.5847 | 35.9 | 36.567 | -0.66696 |  | 2026-10-03 16:00 | 217.053 | 220.224 | 2183.1 | 36.704 | 37.0975 | -0.39346 | 222.5847 | 36.9 | 36.567 | 0.33304 |  | 2026-10-03 16:00 | 213.532 | 218.719 | 2142.9 | 36.4532 | 37.0975 | -0.64429 | 222.5847 | 36.2 | 36.567 | -0.36696 |  | 2026-10-03 16:00 | 213.895 | 217.02 | 2167.4 | 36.17 | 37.0975 | -0.92746 | 222.5847 | 36.8 | 36.567 | 0.23304 |  | 2026-10-03 16:00 | 160.38 | 162.624 | 1614.1 | 27.104 | 27.4796 | -0.3756 | 164.8776 | 27.6 | 27.0866 | 0.51336 |  | 2026-10-03 16:00 | 157.113 | 159.329 | 1602.4 | 26.5548 | 27.4796 | -0.92476 | 164.8776 | 27.1 | 27.0866 | 0.013361 |  | 2026-10-03 16:00 | 157.239 | 159.668 | 1599.8 | 26.6113 | 27.4796 | -0.86826 | 164.8776 | 27 | 27.0866 | -0.086639 |  | 2026-10-03 16:00 | 157.202 | 161.789 | 1611.3 | 26.9648 | 27.4796 | -0.51476 | 164.8776 | 27.1 | 27.0866 | 0.013361 |  |  | 2026-10-03 16:00 | 148.602 | 150.651 | 1525.1 | 25.1085 | 26.1434 | -1.0349 | 156.8606 | 25.6 | 25.7696 | -0.16958 |  |  |  | 2026-10-03 16:00 | 277.9738 | 284.4516 | -6.4778 | 1706.7099 | 280.2 | 280.384 | -0.18399
2026-10-03 15:50 | 663 | 49.08 | 226.612 | 229.993 | 2127 | 38.3322 | 39.4356 | -1.1034 | 236.6136 | 39.7 | 38.8717 | 0.82832 |  | 2026-10-03 15:50 | 229.995 | 233.545 | 2146.2 | 38.9242 | 39.4356 | -0.51144 | 236.6136 | 38.5 | 38.8717 | -0.37168 |  | 2026-10-03 15:50 | 226.11 | 231.57 | 2106.7 | 38.595 | 39.4356 | -0.8406 | 236.6136 | 39.5 | 38.8717 | 0.62832 |  | 2026-10-03 15:50 | 227.043 | 230.524 | 2130.6 | 38.4207 | 39.4356 | -1.0149 | 236.6136 | 39.1 | 38.8717 | 0.22832 |  | 2026-10-03 15:50 | 170.423 | 172.825 | 1586.5 | 28.8042 | 29.2116 | -0.40739 | 175.2694 | 29.3 | 28.7938 | 0.50617 |  | 2026-10-03 15:50 | 167.069 | 169.961 | 1575.3 | 28.3268 | 29.2116 | -0.88473 | 175.2694 | 28.8 | 28.7938 | 0.0061665 |  | 2026-10-03 15:50 | 167.105 | 169.732 | 1572.8 | 28.2887 | 29.2116 | -0.92289 | 175.2694 | 28.8 | 28.7938 | 0.0061665 |  | 2026-10-03 15:50 | 167.281 | 171.95 | 1584.2 | 28.6583 | 29.2116 | -0.55323 | 175.2694 | 29.2 | 28.7938 | 0.40617 |  |  | 2026-10-03 15:50 | 157.879 | 160.104 | 1499.5 | 26.684 | 27.7912 | -1.1072 | 166.7471 | 27.7 | 27.3938 | 0.30623 |  |  |  | 2026-10-03 15:50 | 295.034 | 302.3798 | -7.3458 | 1814.279 | 300.6 | 298.0558 | 2.5442
2026-10-03 15:40 | 708 | 49.36 | 240.093 | 243.799 | 2087.3 | 40.6332 | 42.0672 | -1.434 | 252.403 | 40.3 | 41.4656 | -1.1656 |  | 2026-10-03 15:40 | 242.991 | 246.857 | 2107.7 | 41.1428 | 42.0672 | -0.92433 | 252.403 | 41.5 | 41.4656 | 0.0344 |  | 2026-10-03 15:40 | 239.399 | 245.738 | 2067.2 | 40.9563 | 42.0672 | -1.1108 | 252.403 | 40.3 | 41.4656 | -1.1656 |  | 2026-10-03 15:40 | 240.594 | 244.407 | 2091.5 | 40.7345 | 42.0672 | -1.3327 | 252.403 | 40.5 | 41.4656 | -0.9656 |  | 2026-10-03 15:40 | 180.318 | 182.953 | 1557.2 | 30.4922 | 31.1609 | -0.66869 | 186.9652 | 30.3 | 30.7153 | -0.41526 |  | 2026-10-03 15:40 | 177.005 | 179.954 | 1546.5 | 29.9923 | 31.1609 | -1.1685 | 186.9652 | 30.2 | 30.7153 | -0.51526 |  | 2026-10-03 15:40 | 176.947 | 180.133 | 1544 | 30.0222 | 31.1609 | -1.1387 | 186.9652 | 30.2 | 30.7153 | -0.51526 |  | 2026-10-03 15:40 | 177.576 | 182.698 | 1555 | 30.4497 | 31.1609 | -0.71119 | 186.9652 | 29.8 | 30.7153 | -0.91526 |  |  | 2026-10-03 15:40 | 167.857 | 170.292 | 1471.8 | 28.382 | 29.6457 | -1.2637 | 177.8742 | 28.1 | 29.2218 | -1.1218 |  |  |  | 2026-10-03 15:40 | 312.8052 | 322.5578 | -9.7526 | 1935.3467 | 311.2 | 317.9452 | -6.7452
2026-10-03 15:30 | 737 | 49.36 | 248.604 | 252.569 | 2047 | 42.0948 | 43.7903 | -1.6954 | 262.7415 | 42.9 | 43.1641 | -0.26405 |  | 2026-10-03 15:30 | 251.471 | 255.56 | 2066.2 | 42.5933 | 43.7903 | -1.1969 | 262.7415 | 42.9 | 43.1641 | -0.26405 |  | 2026-10-03 15:30 | 247.825 | 253.888 | 2026.9 | 42.3147 | 43.7903 | -1.4756 | 262.7415 | 42 | 43.1641 | -1.1641 |  | 2026-10-03 15:30 | 248.286 | 252.298 | 2051 | 42.0497 | 43.7903 | -1.7406 | 262.7415 | 42.4 | 43.1641 | -0.76405 |  | 2026-10-03 15:30 | 186.385 | 189.185 | 1526.9 | 31.5308 | 32.4372 | -0.90639 | 194.6233 | 31.8 | 31.9734 | -0.17337 |  | 2026-10-03 15:30 | 183.115 | 186.261 | 1516.3 | 31.0435 | 32.4372 | -1.3937 | 194.6233 | 30.8 | 31.9734 | -1.1734 |  | 2026-10-03 15:30 | 183.04 | 186.413 | 1513.8 | 31.0688 | 32.4372 | -1.3684 | 194.6233 | 30.7 | 31.9734 | -1.2734 |  | 2026-10-03 15:30 | 183.337 | 188.764 | 1525.2 | 31.4607 | 32.4372 | -0.97656 | 194.6233 | 30.9 | 31.9734 | -1.0734 |  |  | 2026-10-03 15:30 | 173.123 | 175.688 | 1443.7 | 29.2813 | 30.86 | -1.5787 | 185.16 | 29.2 | 30.4187 | -1.2187 |  |  |  | 2026-10-03 15:30 | 323.4377 | 335.7699 | -12.3322 | 2014.6194 | 323.6 | 330.9684 | -7.3684
2026-10-03 15:20 | 763 | 49.36 | 256.649 | 260.769 | 2004.1 | 43.4615 | 45.3351 | -1.8736 | 272.0105 | 42.6 | 44.6868 | -2.0868 |  | 2026-10-03 15:20 | 263.078 | 265.114 | 2023.3 | 44.1857 | 45.3351 | -1.1494 | 272.0105 | 42.7 | 44.6868 | -1.9868 |  | 2026-10-03 15:20 | 254.934 | 261.561 | 1984.9 | 43.5935 | 45.3351 | -1.7416 | 272.0105 | 42.4 | 44.6868 | -2.2868 |  | 2026-10-03 15:20 | 257.127 | 261.308 | 2008.6 | 43.5513 | 45.3351 | -1.7838 | 272.0105 | 43.3 | 44.6868 | -1.3868 |  | 2026-10-03 15:20 | 192.244 | 195.132 | 1495.1 | 32.522 | 33.5815 | -1.0595 | 201.4893 | 32.4 | 33.1013 | -0.70133 |  | 2026-10-03 15:20 | 189.815 | 193.297 | 1485.5 | 32.2162 | 33.5815 | -1.3654 | 201.4893 | 32 | 33.1013 | -1.1013 |  | 2026-10-03 15:20 | 189.726 | 193.167 | 1483.1 | 32.1945 | 33.5815 | -1.387 | 201.4893 | 32 | 33.1013 | -1.1013 |  | 2026-10-03 15:20 | 191.026 | 196.152 | 1494.3 | 32.692 | 33.5815 | -0.88955 | 201.4893 | 32 | 33.1013 | -1.1013 |  |  | 2026-10-03 15:20 | 180.447 | 183.139 | 1414.5 | 30.5232 | 31.9487 | -1.4255 | 191.6921 | 30.4 | 31.4918 | -1.0918 |  |  |  | 2026-10-03 15:20 | 334.9398 | 347.6152 | -12.6754 | 2085.6914 | 329.8 | 342.6443 | -12.8443
2026-10-03 15:10 | 786 | 49.36 | 263.944 | 268.236 | 1961.5 | 44.706 | 46.7017 | -1.9957 | 280.2101 | 44.6 | 46.0338 | -1.4338 |  | 2026-10-03 15:10 | 267.118 | 271.544 | 1980.6 | 45.2573 | 46.7017 | -1.4443 | 280.2101 | 45.7 | 46.0338 | -0.33384 |  | 2026-10-03 15:10 | 261.56 | 268.501 | 1942.5 | 44.7502 | 46.7017 | -1.9515 | 280.2101 | 44.7 | 46.0338 | -1.3338 |  | 2026-10-03 15:10 | 263.852 | 268.163 | 1965.3 | 44.6938 | 46.7017 | -2.0078 | 280.2101 | 44.5 | 46.0338 | -1.5338 |  | 2026-10-03 15:10 | 197.138 | 200.12 | 1462.7 | 33.3533 | 34.5938 | -1.2405 | 207.563 | 33.3 | 34.0991 | -0.79914 |  | 2026-10-03 15:10 | 194.318 | 197.905 | 1453.5 | 32.9842 | 34.5938 | -1.6097 | 207.563 | 33.4 | 34.0991 | -0.69914 |  | 2026-10-03 15:10 | 193.854 | 197.679 | 1451.1 | 32.9465 | 34.5938 | -1.6473 | 207.563 | 33.3 | 34.0991 | -0.79914 |  | 2026-10-03 15:10 | 194.4 | 199.975 | 1462.3 | 33.3292 | 34.5938 | -1.2647 | 207.563 | 33.5 | 34.0991 | -0.59914 |  |  | 2026-10-03 15:10 | 184.538 | 187.302 | 1384.1 | 31.217 | 32.9118 | -1.6948 | 197.4705 | 31.7 | 32.4411 | -0.74111 |  |  |  | 2026-10-03 15:10 | 343.2375 | 358.0938 | -14.8563 | 2148.5628 | 344.7 | 352.9731 | -8.2731
2026-10-03 15:00 | 823 | 49.08 | 275.051 | 279.58 | 1916.9 | 46.5967 | 48.9525 | -2.3558 | 293.715 | 46.6 | 48.2525 | -1.6525 | 0.9838 | 2026-10-03 15:00 | 281.21 | 283.168 | 1934.9 | 47.1947 | 48.9525 | -1.7578 | 293.715 | 47.2 | 48.2525 | -1.0525 | 0.99309 | 2026-10-03 15:00 | 273.299 | 280.505 | 1897.8 | 46.7508 | 48.9525 | -2.2017 | 293.715 | 46.3 | 48.2525 | -1.9525 | 0.97431 | 2026-10-03 15:00 | 275.173 | 279.79 | 1920.8 | 46.6317 | 48.9525 | -2.3208 | 293.715 | 46.7 | 48.2525 | -1.5525 | 0.9835 | 2026-10-03 15:00 | 206.041 | 209.231 | 1429.4 | 34.8718 | 36.2611 | -1.3893 | 217.5666 | 34.8 | 35.7426 | -0.94257 | 0.98475 | 2026-10-03 15:00 | 202.987 | 206.48 | 1420.1 | 34.4133 | 36.2611 | -1.8478 | 217.5666 | 33.7 | 35.7426 | -2.0426 | 0.98308 | 2026-10-03 15:00 | 202.905 | 206.503 | 1417.8 | 34.4172 | 36.2611 | -1.8439 | 217.5666 | 33.7 | 35.7426 | -2.0426 | 0.98258 | 2026-10-03 15:00 | 203.753 | 209.861 | 1428.8 | 34.9768 | 36.2611 | -1.2843 | 217.5666 | 33.9 | 35.7426 | -1.8426 | 0.9709 |  | 2026-10-03 15:00 | 192.765 | 195.661 | 1352.4 | 32.6102 | 34.498 | -1.8878 | 206.9877 | 32.1 | 34.0046 | -1.9046 | 0.9852 |  |  | 2026-10-03 15:00 | 358.4632 | 375.3523 | -16.8892 | 2252.114 | 355 | 369.9848 | -14.9848
2026-10-03 14:50 | 848 | 49.36 | 282.702 | 287.416 | 1870.3 | 47.9027 | 50.3855 | -2.4829 | 302.3132 | 47.5 | 49.665 | -2.165 | 0.9836 | 2026-10-03 14:50 | 286.418 | 291.312 | 1887.7 | 48.552 | 50.3855 | -1.8335 | 302.3132 | 48.1 | 49.665 | -1.565 | 0.9832 | 2026-10-03 14:50 | 280.441 | 288.106 | 1851.5 | 48.0177 | 50.3855 | -2.3679 | 302.3132 | 47.1 | 49.665 | -2.565 | 0.9734 | 2026-10-03 14:50 | 282.632 | 287.432 | 1874.1 | 47.9053 | 50.3855 | -2.4802 | 302.3132 | 47.5 | 49.665 | -2.165 | 0.9833 | 2026-10-03 14:50 | 211.528 | 214.815 | 1394.6 | 35.8025 | 37.3226 | -1.5201 | 223.9357 | 35.6 | 36.7889 | -1.1889 | 0.9847 | 2026-10-03 14:50 | 208.299 | 212.243 | 1386.4 | 35.3738 | 37.3226 | -1.9488 | 223.9357 | 35.1 | 36.7889 | -1.6889 | 0.98142 | 2026-10-03 14:50 | 208.33 | 212.316 | 1384.1 | 35.386 | 37.3226 | -1.9366 | 223.9357 | 35 | 36.7889 | -1.7889 | 0.98123 | 2026-10-03 14:50 | 209.219 | 215.408 | 1394.9 | 35.9013 | 37.3226 | -1.4213 | 223.9357 | 35.7 | 36.7889 | -1.0889 | 0.97127 |  | 2026-10-03 14:50 | 197.991 | 201.027 | 1320.3 | 33.5045 | 35.5078 | -2.0033 | 213.0471 | 33.8 | 35.0001 | -1.2001 | 0.9849 |  |  | 2026-10-03 14:50 | 368.3458 | 386.3404 | -17.9946 | 2318.0424 | 365.4 | 380.8157 | -15.4157
2026-10-03 14:40 | 879 | 49.08 | 292.609 | 297.488 | 1822.8 | 49.5813 | 52.2834 | -2.7021 | 313.7004 | 49.7 | 51.5358 | -1.8358 | 0.9836 | 2026-10-03 14:40 | 297.015 | 302.029 | 1839.6 | 50.3382 | 52.2834 | -1.9452 | 313.7004 | 50.4 | 51.5358 | -1.1358 | 0.9834 | 2026-10-03 14:40 | 289.493 | 297.59 | 1804.4 | 49.5983 | 52.2834 | -2.6851 | 313.7004 | 48.9 | 51.5358 | -2.6358 | 0.97279 | 2026-10-03 14:40 | 292.698 | 297.669 | 1826.6 | 49.6115 | 52.2834 | -2.6719 | 313.7004 | 49.3 | 51.5358 | -2.2358 | 0.9833 | 2026-10-03 14:40 | 218.293 | 221.685 | 1359 | 36.9475 | 38.7284 | -1.7809 | 232.3707 | 36.8 | 38.1746 | -1.3746 | 0.9847 | 2026-10-03 14:40 | 215.305 | 219.53 | 1351.3 | 36.5883 | 38.7284 | -2.1401 | 232.3707 | 36.2 | 38.1746 | -1.9746 | 0.98075 | 2026-10-03 14:40 | 214.882 | 218.877 | 1349.1 | 36.4795 | 38.7284 | -2.2489 | 232.3707 | 36.8 | 38.1746 | -1.3746 | 0.98175 | 2026-10-03 14:40 | 216.412 | 222.613 | 1359.2 | 37.1022 | 38.7284 | -1.6263 | 232.3707 | 36.4 | 38.1746 | -1.7746 | 0.97214 |  | 2026-10-03 14:40 | 204.652 | 207.79 | 1286.5 | 34.6317 | 36.8453 | -2.2137 | 221.0719 | 34.3 | 36.3184 | -2.0184 | 0.9849 |  |  | 2026-10-03 14:40 | 380.8785 | 400.8927 | -20.0142 | 2405.3563 | 378.8 | 395.16 | -16.36
2026-10-03 14:30 | 900 | 49.36 | 297.481 | 302.533 | 1773.1 | 50.4222 | 53.4752 | -3.053 | 320.8512 | 49.2 | 52.7105 | -3.5105 | 0.9833 | 2026-10-03 14:30 | 302.072 | 307.372 | 1789.2 | 51.2287 | 53.4752 | -2.2465 | 320.8512 | 50.6 | 52.7105 | -2.1105 | 0.98276 | 2026-10-03 14:30 | 296.272 | 304.727 | 1755.5 | 50.7878 | 53.4752 | -2.6874 | 320.8512 | 49.4 | 52.7105 | -3.3105 | 0.97225 | 2026-10-03 14:30 | 298.816 | 303.984 | 1777.3 | 50.664 | 53.4752 | -2.8112 | 320.8512 | 50.6 | 52.7105 | -2.1105 | 0.983 | 2026-10-03 14:30 | 224.065 | 227.57 | 1322.2 | 37.9283 | 39.6113 | -1.6829 | 237.6676 | 37.9 | 39.0448 | -1.1448 | 0.9846 | 2026-10-03 14:30 | 220.469 | 224.616 | 1315.1 | 37.436 | 39.6113 | -2.1753 | 237.6676 | 37.3 | 39.0448 | -1.7448 | 0.98154 | 2026-10-03 14:30 | 220.804 | 225.252 | 1312.3 | 37.542 | 39.6113 | -2.0693 | 237.6676 | 36.9 | 39.0448 | -2.1448 | 0.98025 | 2026-10-03 14:30 | 221.789 | 228.151 | 1322.8 | 38.0252 | 39.6113 | -1.5861 | 237.6676 | 37.1 | 39.0448 | -1.9448 | 0.97211 |  | 2026-10-03 14:30 | 209.374 | 212.606 | 1252.2 | 35.4343 | 37.6852 | -2.2509 | 226.1113 | 35 | 37.1463 | -2.1463 | 0.9848 |  |  | 2026-10-03 14:30 | 389.4685 | 410.0311 | -20.5626 | 2460.1865 | 384 | 404.1676 | -20.1676
2026-10-03 14:20 | 917 | 49.65 | 301.474 | 306.325 | 1723.9 | 51.0542 | 54.4248 | -3.3707 | 326.549 | 51.1 | 53.6466 | -2.5466 | 0.98416 | 2026-10-03 14:20 | 307.45 | 311.894 | 1738.6 | 51.9823 | 54.4248 | -2.4425 | 326.549 | 51.2 | 53.6466 | -2.4466 | 0.98575 | 2026-10-03 14:20 | 299.577 | 308.055 | 1706.1 | 51.3425 | 54.4248 | -3.0823 | 326.549 | 50.8 | 53.6466 | -2.8466 | 0.97248 | 2026-10-03 14:20 | 303.375 | 308.684 | 1726.7 | 51.4473 | 54.4248 | -2.9775 | 326.549 | 50.7 | 53.6466 | -2.9466 | 0.9828 | 2026-10-03 14:20 | 226.428 | 230.063 | 1284.3 | 38.3438 | 40.3147 | -1.9709 | 241.8882 | 37.9 | 39.7382 | -1.8382 | 0.9842 | 2026-10-03 14:20 | 223.402 | 228.005 | 1277.8 | 38.0008 | 40.3147 | -2.3139 | 241.8882 | 37.4 | 39.7382 | -2.3382 | 0.97981 | 2026-10-03 14:20 | 223.114 | 227.48 | 1275.4 | 37.9133 | 40.3147 | -2.4014 | 241.8882 | 37.3 | 39.7382 | -2.4382 | 0.98081 | 2026-10-03 14:20 | 224.419 | 230.895 | 1285.7 | 38.4825 | 40.3147 | -1.8322 | 241.8882 | 37.5 | 39.7382 | -2.2382 | 0.97195 |  | 2026-10-03 14:20 | 212.43 | 215.753 | 1217.2 | 35.9588 | 38.3544 | -2.3956 | 230.1266 | 36.2 | 37.806 | -1.606 | 0.9846 |  |  | 2026-10-03 14:20 | 394.5257 | 417.3125 | -22.7869 | 2503.8753 | 390.1 | 411.345 | -21.245
2026-10-03 14:10 | 935 | 49.08 | 306.461 | 311.856 | 1672.8 | 51.976 | 55.6143 | -3.6383 | 333.6859 | 52.9 | 54.819 | -1.919 | 0.9827 | 2026-10-03 14:10 | 311.663 | 316.918 | 1687.4 | 52.8197 | 55.6143 | -2.7946 | 333.6859 | 52.2 | 54.819 | -2.619 | 0.98342 | 2026-10-03 14:10 | 304.446 | 313.346 | 1655.3 | 52.2243 | 55.6143 | -3.39 | 333.6859 | 51.7 | 54.819 | -3.119 | 0.9716 | 2026-10-03 14:10 | 308.792 | 314.26 | 1676 | 52.3767 | 55.6143 | -3.2376 | 333.6859 | 52.4 | 54.819 | -2.419 | 0.9826 | 2026-10-03 14:10 | 230.339 | 234.132 | 1246.4 | 39.022 | 41.1958 | -2.1738 | 247.1747 | 39 | 40.6067 | -1.6067 | 0.9838 | 2026-10-03 14:10 | 228.074 | 232.486 | 1240.4 | 38.7477 | 41.1958 | -2.4481 | 247.1747 | 38.7 | 40.6067 | -1.9067 | 0.98102 | 2026-10-03 14:10 | 227.309 | 232.021 | 1238.1 | 38.6702 | 41.1958 | -2.5256 | 247.1747 | 38.5 | 40.6067 | -2.1067 | 0.97969 | 2026-10-03 14:10 | 228.933 | 235.621 | 1248.2 | 39.2702 | 41.1958 | -1.9256 | 247.1747 | 38.8 | 40.6067 | -1.8067 | 0.97162 |  | 2026-10-03 14:10 | 217.202 | 220.622 | 1181 | 36.7703 | 39.1927 | -2.4224 | 235.1561 | 36.2 | 38.6322 | -2.4322 | 0.9845 |  |  | 2026-10-03 14:10 | 401.877 | 426.4331 | -24.5561 | 2558.5986 | 400.4 | 420.3351 | -19.9351
2026-10-03 14:00 | 959 | 49.36 | 314.442 | 319.91 | 1619.9 | 53.3183 | 56.9808 | -3.6625 | 341.8848 | 52.4 | 56.166 | -3.766 | 0.98291 | 2026-10-03 14:00 | 318.645 | 324.255 | 1635.2 | 54.0425 | 56.9808 | -2.9383 | 341.8848 | 54.6 | 56.166 | -1.566 | 0.9827 | 2026-10-03 14:00 | 310.392 | 319.328 | 1603.6 | 53.2213 | 56.9808 | -3.7595 | 341.8848 | 51.8 | 56.166 | -4.366 | 0.97202 | 2026-10-03 14:00 | 314.478 | 320.047 | 1623.6 | 53.3412 | 56.9808 | -3.6396 | 341.8848 | 52.4 | 56.166 | -3.766 | 0.9826 | 2026-10-03 14:00 | 233.956 | 237.784 | 1207.4 | 39.6307 | 42.208 | -2.5773 | 253.248 | 39.1 | 41.6044 | -2.5044 | 0.9839 | 2026-10-03 14:00 | 231.293 | 235.82 | 1201.7 | 39.3033 | 42.208 | -2.9047 | 253.248 | 38.6 | 41.6044 | -3.0044 | 0.9808 | 2026-10-03 14:00 | 230.375 | 234.839 | 1199.6 | 39.1398 | 42.208 | -3.0682 | 253.248 | 38.5 | 41.6044 | -3.1044 | 0.98099 | 2026-10-03 14:00 | 231.283 | 238.273 | 1209.4 | 39.7122 | 42.208 | -2.4958 | 253.248 | 39.1 | 41.6044 | -2.5044 | 0.97066 |  | 2026-10-03 14:00 | 219.579 | 223.059 | 1144.8 | 37.1765 | 40.1557 | -2.9792 | 240.9341 | 37.1 | 39.5815 | -2.4815 | 0.9844 |  |  | 2026-10-03 14:00 | 408.8858 | 436.9109 | -28.0251 | 2621.4654 | 403.6 | 430.6631 | -27.0631
2026-10-03 13:50 | 970 | 49.08 | 318.235 | 323.772 | 1567.5 | 53.962 | 57.6961 | -3.7341 | 346.1768 | 53.6 | 56.8711 | -3.2711 | 0.9829 | 2026-10-03 13:50 | 322.753 | 328.502 | 1580.6 | 54.7503 | 57.6961 | -2.9458 | 346.1768 | 54.4 | 56.8711 | -2.4711 | 0.9825 | 2026-10-03 13:50 | 315.029 | 323.93 | 1551.8 | 53.9883 | 57.6961 | -3.7078 | 346.1768 | 53 | 56.8711 | -3.8711 | 0.97252 | 2026-10-03 13:50 | 318.248 | 323.813 | 1571.2 | 53.9688 | 57.6961 | -3.7273 | 346.1768 | 54.3 | 56.8711 | -2.5711 | 0.98281 | 2026-10-03 13:50 | 237.56 | 241.423 | 1168.3 | 40.2372 | 42.7379 | -2.5007 | 256.4273 | 40.5 | 42.1267 | -1.6267 | 0.984 | 2026-10-03 13:50 | 234.002 | 238.571 | 1163.1 | 39.7618 | 42.7379 | -2.976 | 256.4273 | 39.9 | 42.1267 | -2.2267 | 0.98085 | 2026-10-03 13:50 | 233.691 | 238.515 | 1161.1 | 39.7525 | 42.7379 | -2.9854 | 256.4273 | 39.9 | 42.1267 | -2.2267 | 0.97977 | 2026-10-03 13:50 | 233.747 | 240.488 | 1170.3 | 40.0813 | 42.7379 | -2.6565 | 256.4273 | 39.6 | 42.1267 | -2.5267 | 0.97197 |  | 2026-10-03 13:50 | 221.658 | 225.171 | 1107.7 | 37.5285 | 40.6598 | -3.1313 | 243.9588 | 37.5 | 40.0784 | -2.5784 | 0.9844 |  |  | 2026-10-03 13:50 | 414.0308 | 442.3958 | -28.365 | 2654.375 | 412.7 | 436.0696 | -23.3696
2026-10-03 13:40 | 991 | 49.36 | 327.217 | 332.978 | 1513.9 | 55.4963 | 58.8821 | -3.3858 | 353.2928 | 53.5 | 58.0401 | -4.5401 | 0.9827 | 2026-10-03 13:40 | 335.174 | 339.042 | 1526.2 | 56.507 | 58.8821 | -2.3751 | 353.2928 | 55.3 | 58.0401 | -2.7401 | 0.98859 | 2026-10-03 13:40 | 324.131 | 333.669 | 1498.8 | 55.6115 | 58.8821 | -3.2706 | 353.2928 | 54.6 | 58.0401 | -3.4401 | 0.97141 | 2026-10-03 13:40 | 327.745 | 333.583 | 1516.9 | 55.5972 | 58.8821 | -3.285 | 353.2928 | 54.6 | 58.0401 | -3.4401 | 0.9825 | 2026-10-03 13:40 | 244.84 | 248.872 | 1127.8 | 41.4787 | 43.6164 | -2.1377 | 261.6984 | 40.7 | 42.9927 | -2.2927 | 0.9838 | 2026-10-03 13:40 | 241.449 | 246.149 | 1123.2 | 41.0248 | 43.6164 | -2.5916 | 261.6984 | 40.3 | 42.9927 | -2.6927 | 0.98091 | 2026-10-03 13:40 | 241.355 | 246.144 | 1121.2 | 41.024 | 43.6164 | -2.5924 | 261.6984 | 40.1 | 42.9927 | -2.8927 | 0.98054 | 2026-10-03 13:40 | 242.606 | 249.475 | 1130.7 | 41.5792 | 43.6164 | -2.0372 | 261.6984 | 40.2 | 42.9927 | -2.7927 | 0.97247 |  | 2026-10-03 13:40 | 229.048 | 232.772 | 1070.2 | 38.7953 | 41.4956 | -2.7003 | 248.9736 | 38.1 | 40.9022 | -2.8022 | 0.984 |  |  | 2026-10-03 13:40 | 427.114 | 451.4898 | -24.3758 | 2708.9387 | 417.4 | 445.0335 | -27.6335
2026-10-03 13:30 | 1005 | 48.79 | 327.822 | 333.661 | 1460.4 | 55.6102 | 59.8442 | -4.234 | 359.0653 | 55.8 | 58.9884 | -3.1884 | 0.9825 | 2026-10-03 13:30 | 332.577 | 338.535 | 1470.9 | 56.4225 | 59.8442 | -3.4217 | 359.0653 | 58.4 | 58.9884 | -0.58844 | 0.9824 | 2026-10-03 13:30 | 324.004 | 333.677 | 1444.2 | 55.6128 | 59.8442 | -4.2314 | 359.0653 | 54.3 | 58.9884 | -4.6884 | 0.97101 | 2026-10-03 13:30 | 328.104 | 334.05 | 1462.3 | 55.675 | 59.8442 | -4.1692 | 359.0653 | 54.5 | 58.9884 | -4.4884 | 0.9822 | 2026-10-03 13:30 | 244.807 | 248.889 | 1087.1 | 41.4815 | 44.329 | -2.8475 | 265.9743 | 41.7 | 43.6951 | -1.9951 | 0.9836 | 2026-10-03 13:30 | 241.903 | 246.379 | 1082.9 | 41.0632 | 44.329 | -3.2659 | 265.9743 | 40.4 | 43.6951 | -3.2951 | 0.98183 | 2026-10-03 13:30 | 241.295 | 246.054 | 1081.1 | 41.009 | 44.329 | -3.32 | 265.9743 | 40.5 | 43.6951 | -3.1951 | 0.98066 | 2026-10-03 13:30 | 242.719 | 249.686 | 1090.5 | 41.6143 | 44.329 | -2.7147 | 265.9743 | 40.7 | 43.6951 | -2.9951 | 0.9721 |  | 2026-10-03 13:30 | 229.668 | 233.426 | 1032.1 | 38.9043 | 42.1736 | -3.2693 | 253.0416 | 39 | 41.5705 | -2.5705 | 0.9839 |  |  | 2026-10-03 13:30 | 427.3928 | 458.8666 | -31.4738 | 2753.1997 | 425.3 | 452.3048 | -27.0048
2026-10-03 13:20 | 1022 | 49.65 | 334 | 339.949 | 1404.6 | 56.6582 | 60.6567 | -3.9985 | 363.9401 | 55.6 | 59.7893 | -4.1893 | 0.9825 | 2026-10-03 13:20 | 339.253 | 345.366 | 1412.5 | 57.561 | 60.6567 | -3.0957 | 363.9401 | 52.6 | 59.7893 | -7.1893 | 0.9823 | 2026-10-03 13:20 | 331.863 | 341.888 | 1389.9 | 56.9813 | 60.6567 | -3.6754 | 363.9401 | 54.8 | 59.7893 | -4.9893 | 0.97068 | 2026-10-03 13:20 | 334.354 | 340.448 | 1407.8 | 56.7413 | 60.6567 | -3.9154 | 363.9401 | 55.6 | 59.7893 | -4.1893 | 0.9821 | 2026-10-03 13:20 | 250.749 | 254.878 | 1045.4 | 42.4797 | 44.9309 | -2.4512 | 269.5853 | 40.9 | 44.2884 | -3.3884 | 0.9838 | 2026-10-03 13:20 | 247.006 | 252.183 | 1042.5 | 42.0305 | 44.9309 | -2.9004 | 269.5853 | 41.1 | 44.2884 | -3.1884 | 0.97947 | 2026-10-03 13:20 | 247.87 | 252.898 | 1040.6 | 42.1497 | 44.9309 | -2.7812 | 269.5853 | 41 | 44.2884 | -3.2884 | 0.98012 | 2026-10-03 13:20 | 248.018 | 255.283 | 1049.8 | 42.5472 | 44.9309 | -2.3837 | 269.5853 | 41.2 | 44.2884 | -3.0884 | 0.97154 |  | 2026-10-03 13:20 | 233.74 | 237.541 | 993.1 | 39.5902 | 42.7462 | -3.156 | 256.477 | 39.1 | 42.1349 | -3.0349 | 0.984 |  |  | 2026-10-03 13:20 | 436.739 | 465.0964 | -28.3574 | 2790.5785 | 421.9 | 458.4455 | -36.5455
2026-10-03 13:10 | 1018 | 49.36 | 332.127 | 338.043 | 1349 | 56.3405 | 60.4864 | -4.1459 | 362.9184 | 56.1 | 59.6214 | -3.5214 | 0.9825 | 2026-10-03 13:10 | 325.444 | 330.769 | 1359.9 | 55.1282 | 60.4864 | -5.3582 | 362.9184 | 56.2 | 59.6214 | -3.4214 | 0.9839 | 2026-10-03 13:10 | 328.611 | 338.363 | 1335.1 | 56.3938 | 60.4864 | -4.0926 | 362.9184 | 54.9 | 59.6214 | -4.7214 | 0.97118 | 2026-10-03 13:10 | 332.937 | 338.986 | 1352.2 | 56.4977 | 60.4864 | -3.9887 | 362.9184 | 55.6 | 59.6214 | -4.0214 | 0.98216 | 2026-10-03 13:10 | 248.611 | 252.756 | 1004.5 | 42.126 | 44.8047 | -2.6787 | 268.8284 | 41.6 | 44.164 | -2.564 | 0.9836 | 2026-10-03 13:10 | 246.014 | 251.11 | 1001.4 | 41.8517 | 44.8047 | -2.9531 | 268.8284 | 41.1 | 44.164 | -3.064 | 0.97971 | 2026-10-03 13:10 | 246.307 | 251.24 | 999.6 | 41.8733 | 44.8047 | -2.9314 | 268.8284 | 41.6 | 44.164 | -2.564 | 0.98037 | 2026-10-03 13:10 | 247.682 | 254.851 | 1008.6 | 42.4752 | 44.8047 | -2.3296 | 268.8284 | 41.9 | 44.164 | -2.264 | 0.97187 |  | 2026-10-03 13:10 | 234.22 | 238.004 | 954 | 39.6673 | 42.6262 | -2.9588 | 255.757 | 38.9 | 42.0166 | -3.1166 | 0.9841 |  |  | 2026-10-03 13:10 | 432.3537 | 463.7907 | -31.437 | 2782.7442 | 427.9 | 457.1585 | -29.2585
2026-10-03 13:00 | 1023 | 49.08 | 335.454 | 339.445 | 1292.9 | 56.5742 | 60.8486 | -4.2744 | 365.0916 | 55.1 | 59.9785 | -4.8785 | 0.98824 | 2026-10-03 13:00 | 326.193 | 331.497 | 1303.7 | 55.2495 | 60.8486 | -5.5991 | 365.0916 | 56.2 | 59.9785 | -3.7785 | 0.984 | 2026-10-03 13:00 | 331.615 | 341.178 | 1280.2 | 56.863 | 60.8486 | -3.9856 | 365.0916 | 55.5 | 59.9785 | -4.4785 | 0.97197 | 2026-10-03 13:00 | 335.289 | 341.365 | 1296.6 | 56.8942 | 60.8486 | -3.9544 | 365.0916 | 56.2 | 59.9785 | -3.7785 | 0.9822 | 2026-10-03 13:00 | 251.347 | 255.512 | 962.9 | 42.5853 | 45.073 | -2.4877 | 270.4382 | 41.9 | 44.4285 | -2.5285 | 0.9837 | 2026-10-03 13:00 | 248.448 | 253.613 | 960.3 | 42.2688 | 45.073 | -2.8042 | 270.4382 | 41.5 | 44.4285 | -2.9285 | 0.97963 | 2026-10-03 13:00 | 248.866 | 254.077 | 958 | 42.3462 | 45.073 | -2.7269 | 270.4382 | 41 | 44.4285 | -3.4285 | 0.97949 | 2026-10-03 13:00 | 250.497 | 258.156 | 966.7 | 43.026 | 45.073 | -2.047 | 270.4382 | 41.8 | 44.4285 | -2.6285 | 0.97033 |  | 2026-10-03 13:00 | 236.7 | 240.549 | 915.1 | 40.0915 | 42.8814 | -2.7899 | 257.2885 | 39.5 | 42.2682 | -2.7682 | 0.984 |  |  | 2026-10-03 13:00 | 435.8987 | 466.568 | -30.6693 | 2799.4079 | 428.7 | 459.8961 | -31.1961
2026-10-03 12:50 | 1030 | 49.36 | 337.194 | 343.235 | 1237.8 | 57.2058 | 61.1994 | -3.9936 | 367.1964 | 56 | 60.3242 | -4.3242 | 0.9824 | 2026-10-03 12:50 | 331.888 | 337.422 | 1247.5 | 56.237 | 61.1994 | -4.9624 | 367.1964 | 55.1 | 60.3242 | -5.2242 | 0.9836 | 2026-10-03 12:50 | 333.427 | 343.633 | 1224.7 | 57.2722 | 61.1994 | -3.9272 | 367.1964 | 56.2 | 60.3242 | -4.1242 | 0.9703 | 2026-10-03 12:50 | 337.117 | 343.31 | 1240.4 | 57.2183 | 61.1994 | -3.9811 | 367.1964 | 56.9 | 60.3242 | -3.4242 | 0.98196 | 2026-10-03 12:50 | 252.194 | 256.347 | 921 | 42.7245 | 45.3329 | -2.6084 | 271.9973 | 42.7 | 44.6846 | -1.9846 | 0.9838 | 2026-10-03 12:50 | 249.052 | 254.081 | 918.8 | 42.3468 | 45.3329 | -2.9861 | 271.9973 | 42.1 | 44.6846 | -2.5846 | 0.98021 | 2026-10-03 12:50 | 249.145 | 254.349 | 917 | 42.3915 | 45.3329 | -2.9414 | 271.9973 | 42.1 | 44.6846 | -2.5846 | 0.97954 | 2026-10-03 12:50 | 250.788 | 258.225 | 924.9 | 43.0375 | 45.3329 | -2.2954 | 271.9973 | 41.9 | 44.6846 | -2.7846 | 0.9712 |  | 2026-10-03 12:50 | 237.024 | 240.878 | 875.6 | 40.1463 | 43.1286 | -2.9823 | 258.7718 | 39.6 | 42.5119 | -2.9119 | 0.984 |  |  | 2026-10-03 12:50 | 438.58 | 469.2578 | -30.6778 | 2815.5467 | 432.6 | 462.5474 | -29.9474
2026-10-03 12:40 | 1036 | 48.79 | 339.798 | 345.886 | 1181.8 | 57.6477 | 61.6902 | -4.0425 | 370.1409 | 56.4 | 60.808 | -4.408 | 0.9824 | 2026-10-03 12:40 | 337.89 | 343.559 | 1192.4 | 57.2598 | 61.6902 | -4.4303 | 370.1409 | 58.7 | 60.808 | -2.108 | 0.9835 | 2026-10-03 12:40 | 336.908 | 347.135 | 1168.5 | 57.8558 | 61.6902 | -3.8343 | 370.1409 | 55.1 | 60.808 | -5.708 | 0.97054 | 2026-10-03 12:40 | 328.964 | 334.313 | 1183.5 | 55.7188 | 61.6902 | -5.9713 | 370.1409 | 55.6 | 60.808 | -5.208 | 0.984 | 2026-10-03 12:40 | 255.167 | 259.395 | 878.3 | 43.2325 | 45.6964 | -2.4639 | 274.1785 | 41.7 | 45.043 | -3.343 | 0.9837 | 2026-10-03 12:40 | 251.926 | 256.891 | 876.7 | 42.8152 | 45.6964 | -2.8812 | 274.1785 | 41.3 | 45.043 | -3.743 | 0.98067 | 2026-10-03 12:40 | 252.494 | 257.555 | 874.9 | 42.9258 | 45.6964 | -2.7706 | 274.1785 | 42 | 45.043 | -3.043 | 0.98035 | 2026-10-03 12:40 | 254.455 | 262.031 | 883 | 43.6718 | 45.6964 | -2.0246 | 274.1785 | 42.2 | 45.043 | -2.843 | 0.97109 |  | 2026-10-03 12:40 | 239.902 | 243.803 | 836 | 40.6338 | 43.4745 | -2.8406 | 260.8468 | 39.8 | 42.8528 | -3.0528 | 0.984 |  |  | 2026-10-03 12:40 | 441.7613 | 473.0207 | -31.2594 | 2838.1243 | 432.8 | 466.2565 | -33.4565
2026-10-03 12:30 | 1027 | 49.08 | 335.138 | 341.107 | 1125.4 | 56.8512 | 61.0865 | -4.2354 | 366.5191 | 56.4 | 60.213 | -3.813 | 0.9825 | 2026-10-03 12:30 | 339.358 | 345.543 | 1133.7 | 57.5905 | 61.0865 | -3.496 | 366.5191 | 54.7 | 60.213 | -5.513 | 0.9821 | 2026-10-03 12:30 | 332.055 | 341.642 | 1113.4 | 56.9403 | 61.0865 | -4.1462 | 366.5191 | 55.8 | 60.213 | -4.413 | 0.97194 | 2026-10-03 12:30 | 335.391 | 341.504 | 1127.9 | 56.9173 | 61.0865 | -4.1692 | 366.5191 | 56.3 | 60.213 | -3.913 | 0.9821 | 2026-10-03 12:30 | 251.384 | 255.549 | 836.6 | 42.5915 | 45.2493 | -2.6578 | 271.4957 | 42.2 | 44.6022 | -2.4022 | 0.9837 | 2026-10-03 12:30 | 248.627 | 253.485 | 835.4 | 42.2475 | 45.2493 | -3.0018 | 271.4957 | 41.6 | 44.6022 | -3.0022 | 0.98084 | 2026-10-03 12:30 | 249.084 | 254.137 | 832.9 | 42.3562 | 45.2493 | -2.8931 | 271.4957 | 41.1 | 44.6022 | -3.5022 | 0.98012 | 2026-10-03 12:30 | 250.689 | 258.044 | 840.8 | 43.0073 | 45.2493 | -2.2419 | 271.4957 | 42.1 | 44.6022 | -2.5022 | 0.9715 |  | 2026-10-03 12:30 | 236.419 | 240.263 | 796.2 | 40.0438 | 43.0491 | -3.0052 | 258.2945 | 39.7 | 42.4335 | -2.7335 | 0.984 |  |  | 2026-10-03 12:30 | 438.5457 | 468.3923 | -29.8466 | 2810.3537 | 429.9 | 461.6943 | -31.7943
2026-10-03 12:20 | 1025 | 49.08 | 334.973 | 341.367 | 1069 | 56.8945 | 60.9676 | -4.0731 | 365.8054 | 55.2 | 60.0957 | -4.8957 | 0.98127 | 2026-10-03 12:20 | 333.261 | 338.418 | 1079 | 56.403 | 60.9676 | -4.5646 | 365.8054 | 59.1 | 60.0957 | -0.99573 | 0.98476 | 2026-10-03 12:20 | 333.635 | 343.674 | 1057.6 | 57.279 | 60.9676 | -3.6886 | 365.8054 | 55.7 | 60.0957 | -4.3957 | 0.97079 | 2026-10-03 12:20 | 337.547 | 343.594 | 1071.6 | 57.2657 | 60.9676 | -3.7019 | 365.8054 | 56.4 | 60.0957 | -3.6957 | 0.9824 | 2026-10-03 12:20 | 252.439 | 256.544 | 794.4 | 42.7573 | 45.1612 | -2.4038 | 270.9669 | 42 | 44.5154 | -2.5154 | 0.984 | 2026-10-03 12:20 | 249.96 | 254.845 | 793.8 | 42.4742 | 45.1612 | -2.687 | 270.9669 | 41.8 | 44.5154 | -2.7154 | 0.98083 | 2026-10-03 12:20 | 250.09 | 255.124 | 791.8 | 42.5207 | 45.1612 | -2.6405 | 270.9669 | 41.7 | 44.5154 | -2.8154 | 0.98027 | 2026-10-03 12:20 | 252.306 | 259.644 | 798.7 | 43.274 | 45.1612 | -1.8872 | 270.9669 | 41.3 | 44.5154 | -3.2154 | 0.97174 |  | 2026-10-03 12:20 | 237.844 | 241.687 | 756.5 | 40.2812 | 42.9652 | -2.6841 | 257.7915 | 39.1 | 42.3508 | -3.2508 | 0.9841 |  |  | 2026-10-03 12:20 | 439.1495 | 467.4801 | -28.3306 | 2804.8808 | 432.3 | 460.7952 | -28.4952
2026-10-03 12:10 | 1020 | 49.08 | 333.764 | 339.733 | 1013.8 | 56.6222 | 60.6702 | -4.048 | 364.021 | 56.8 | 59.8026 | -3.0026 | 0.98243 | 2026-10-03 12:10 | 339.232 | 345.518 | 1019.9 | 57.5863 | 60.6702 | -3.0838 | 364.021 | 54.6 | 59.8026 | -5.2026 | 0.98181 | 2026-10-03 12:10 | 331.183 | 340.608 | 1001.9 | 56.768 | 60.6702 | -3.9022 | 364.021 | 54.6 | 59.8026 | -5.2026 | 0.97233 | 2026-10-03 12:10 | 335.871 | 341.923 | 1015.2 | 56.9872 | 60.6702 | -3.683 | 364.021 | 56.1 | 59.8026 | -3.7026 | 0.9823 | 2026-10-03 12:10 | 250.474 | 254.573 | 752.4 | 42.4288 | 44.9409 | -2.512 | 269.6452 | 41.4 | 44.2982 | -2.8982 | 0.9839 | 2026-10-03 12:10 | 248.603 | 253.572 | 752 | 42.262 | 44.9409 | -2.6789 | 269.6452 | 41 | 44.2982 | -3.2982 | 0.9804 | 2026-10-03 12:10 | 247.819 | 253.236 | 750.1 | 42.206 | 44.9409 | -2.7349 | 269.6452 | 41.3 | 44.2982 | -2.9982 | 0.97861 | 2026-10-03 12:10 | 249.946 | 257.015 | 757.4 | 42.8358 | 44.9409 | -2.105 | 269.6452 | 41.7 | 44.2982 | -2.5982 | 0.9725 |  | 2026-10-03 12:10 | 236.727 | 240.552 | 717.4 | 40.092 | 42.7557 | -2.6637 | 256.534 | 39.4 | 42.1443 | -2.7443 | 0.9841 |  |  | 2026-10-03 12:10 | 437.7883 | 465.1997 | -27.4114 | 2791.1985 | 426.9 | 458.5474 | -31.6474
2026-10-03 12:00 | 1015 | 49.36 | 332.557 | 338.446 | 957 | 56.4077 | 60.3081 | -3.9005 | 361.8489 | 55.4 | 59.4457 | -4.0457 | 0.9826 | 2026-10-03 12:00 | 337.754 | 343.84 | 965.3 | 57.3067 | 60.3081 | -3.0015 | 361.8489 | 56.2 | 59.4457 | -3.2457 | 0.9823 | 2026-10-03 12:00 | 329.791 | 339.023 | 947.3 | 56.5038 | 60.3081 | -3.8043 | 361.8489 | 54.9 | 59.4457 | -4.5457 | 0.97277 | 2026-10-03 12:00 | 334.347 | 340.372 | 959.1 | 56.7287 | 60.3081 | -3.5795 | 361.8489 | 54.9 | 59.4457 | -4.5457 | 0.9823 | 2026-10-03 12:00 | 249.04 | 253.089 | 711 | 42.1815 | 44.6727 | -2.4912 | 268.0362 | 41.4 | 44.0339 | -2.6339 | 0.984 | 2026-10-03 12:00 | 247.313 | 251.911 | 711 | 41.9852 | 44.6727 | -2.6875 | 268.0362 | 41.1 | 44.0339 | -2.9339 | 0.98175 | 2026-10-03 12:00 | 246.635 | 251.941 | 708.8 | 41.9902 | 44.6727 | -2.6825 | 268.0362 | 41.1 | 44.0339 | -2.9339 | 0.97894 | 2026-10-03 12:00 | 248.618 | 256.29 | 715.7 | 42.715 | 44.6727 | -1.9577 | 268.0362 | 41.5 | 44.0339 | -2.5339 | 0.97007 |  | 2026-10-03 12:00 | 235.347 | 239.125 | 678 | 39.8542 | 42.5005 | -2.6464 | 255.0033 | 39.2 | 41.8928 | -2.6928 | 0.9842 |  |  | 2026-10-03 12:00 | 435.6728 | 462.4239 | -26.7511 | 2774.5436 | 425.7 | 455.8113 | -30.1113
2026-10-03 11:50 | 998 | 49.36 | 330.809 | 336.633 | 901.6 | 56.1055 | 59.2981 | -3.1926 | 355.7884 | 55 | 58.4501 | -3.4501 | 0.9827 | 2026-10-03 11:50 | 335.04 | 340.973 | 909.1 | 56.8288 | 59.2981 | -2.4692 | 355.7884 | 55.7 | 58.4501 | -2.7501 | 0.9826 | 2026-10-03 11:50 | 327.695 | 337.058 | 892.4 | 56.1763 | 59.2981 | -3.1217 | 355.7884 | 54.5 | 58.4501 | -3.9501 | 0.97222 | 2026-10-03 11:50 | 331.147 | 336.976 | 904.2 | 56.1627 | 59.2981 | -3.1354 | 355.7884 | 55.2 | 58.4501 | -3.2501 | 0.9827 | 2026-10-03 11:50 | 246.928 | 250.918 | 669.6 | 41.8197 | 43.9245 | -2.1048 | 263.5469 | 41.1 | 43.2964 | -2.1964 | 0.9841 | 2026-10-03 11:50 | 244.943 | 249.5 | 669.9 | 41.5833 | 43.9245 | -2.3412 | 263.5469 | 40.8 | 43.2964 | -2.4964 | 0.98174 | 2026-10-03 11:50 | 244.779 | 249.927 | 667.7 | 41.6545 | 43.9245 | -2.27 | 263.5469 | 40.3 | 43.2964 | -2.9964 | 0.9794 | 2026-10-03 11:50 | 247.119 | 254.342 | 674.2 | 42.3903 | 43.9245 | -1.5342 | 263.5469 | 40.6 | 43.2964 | -2.6964 | 0.9716 |  | 2026-10-03 11:50 | 233.325 | 237.037 | 638.8 | 39.5062 | 41.7887 | -2.2825 | 250.7323 | 38.9 | 41.1911 | -2.2911 | 0.98434 |  |  | 2026-10-03 11:50 | 432.2273 | 454.6789 | -22.4516 | 2728.0734 | 422.1 | 448.177 | -26.077
2026-10-03 11:40 | 986 | 49.36 | 327.062 | 332.747 | 846.6 | 55.4578 | 58.5851 | -3.1272 | 351.5103 | 53.9 | 57.7473 | -3.8473 | 0.98291 | 2026-10-03 11:40 | 0 | 0 | 853.4 | 0 | 58.5851 | -58.5851 | 351.5103 | 55.4 | 57.7473 | -2.3473 |  | 2026-10-03 11:40 | 323.814 | 333.298 | 837.9 | 55.5497 | 58.5851 | -3.0354 | 351.5103 | 53.4 | 57.7473 | -4.3473 | 0.97154 | 2026-10-03 11:40 | 328.322 | 334.068 | 849 | 55.678 | 58.5851 | -2.9071 | 351.5103 | 54.1 | 57.7473 | -3.6473 | 0.9828 | 2026-10-03 11:40 | 244.177 | 248.097 | 628.5 | 41.3495 | 43.3963 | -2.0468 | 260.378 | 40.2 | 42.7758 | -2.5758 | 0.9842 | 2026-10-03 11:40 | 242.959 | 247.374 | 629.1 | 41.229 | 43.3963 | -2.1673 | 260.378 | 40.5 | 42.7758 | -2.2758 | 0.98215 | 2026-10-03 11:40 | 242.199 | 247.02 | 627.4 | 41.17 | 43.3963 | -2.2263 | 260.378 | 40.3 | 42.7758 | -2.4758 | 0.98048 | 2026-10-03 11:40 | 244.151 | 251.693 | 633.6 | 41.9488 | 43.3963 | -1.4475 | 260.378 | 40.7 | 42.7758 | -2.0758 | 0.97003 |  | 2026-10-03 11:40 | 231.584 | 235.23 | 599.9 | 39.205 | 41.2862 | -2.0812 | 247.7174 | 38.1 | 40.6958 | -2.5958 | 0.9845 |  |  | 2026-10-03 11:40 | 371.5878 | 449.2118 | -77.624 | 2695.2709 | 416.6 | 442.7881 | -26.1881
2026-10-03 11:30 | 968 | 49.36 | 322.316 | 327.823 | 792.7 | 54.6372 | 57.5156 | -2.8784 | 345.0933 | 52.9 | 56.6931 | -3.7931 | 0.9832 | 2026-10-03 11:30 | 325.586 | 331.284 | 798 | 55.214 | 57.5156 | -2.3016 | 345.0933 | 53.6 | 56.6931 | -3.0931 | 0.9828 | 2026-10-03 11:30 | 319.295 | 328.207 | 784.5 | 54.7012 | 57.5156 | -2.8144 | 345.0933 | 52.4 | 56.6931 | -4.2931 | 0.97285 | 2026-10-03 11:30 | 323.182 | 328.805 | 794.9 | 54.8008 | 57.5156 | -2.7147 | 345.0933 | 53 | 56.6931 | -3.6931 | 0.9829 | 2026-10-03 11:30 | 240.493 | 244.354 | 588.3 | 40.7257 | 42.6041 | -1.8784 | 255.6247 | 40.1 | 41.9949 | -1.8949 | 0.9842 | 2026-10-03 11:30 | 239.029 | 243.736 | 588.6 | 40.6227 | 42.6041 | -1.9814 | 255.6247 | 39.3 | 41.9949 | -2.6949 | 0.98069 | 2026-10-03 11:30 | 238.464 | 243.236 | 587.1 | 40.5393 | 42.6041 | -2.0648 | 255.6247 | 39.3 | 41.9949 | -2.6949 | 0.98038 | 2026-10-03 11:30 | 240.58 | 247.629 | 592.9 | 41.2715 | 42.6041 | -1.3326 | 255.6247 | 39.6 | 41.9949 | -2.3949 | 0.97153 |  | 2026-10-03 11:30 | 227.959 | 231.501 | 561.8 | 38.5835 | 40.5325 | -1.949 | 243.1952 | 37.5 | 39.9529 | -2.4529 | 0.9847 |  |  | 2026-10-03 11:30 | 421.0958 | 441.0112 | -19.9154 | 2646.0672 | 407.7 | 434.7047 | -27.0047
2026-10-03 11:20 | 944 | 49.36 | 316.978 | 322.361 | 739.8 | 53.7268 | 56.0895 | -2.3627 | 336.5373 | 52.3 | 55.2875 | -2.9875 | 0.9833 | 2026-10-03 11:20 | 321.361 | 326.852 | 744.4 | 54.4753 | 56.0895 | -1.6142 | 336.5373 | 52.2 | 55.2875 | -3.0875 | 0.9832 | 2026-10-03 11:20 | 313.692 | 322.624 | 732.1 | 53.7707 | 56.0895 | -2.3189 | 336.5373 | 53.2 | 55.2875 | -2.0875 | 0.97231 | 2026-10-03 11:20 | 316.468 | 321.941 | 741.9 | 53.6568 | 56.0895 | -2.4327 | 336.5373 | 53.2 | 55.2875 | -2.0875 | 0.983 | 2026-10-03 11:20 | 236.471 | 240.194 | 548.2 | 40.0323 | 41.5478 | -1.5155 | 249.2869 | 39 | 40.9537 | -1.9537 | 0.9845 | 2026-10-03 11:20 | 234.305 | 238.738 | 549.3 | 39.7897 | 41.5478 | -1.7581 | 249.2869 | 38.8 | 40.9537 | -2.1537 | 0.98143 | 2026-10-03 11:20 | 234.158 | 238.598 | 547.8 | 39.7663 | 41.5478 | -1.7815 | 249.2869 | 38.7 | 40.9537 | -2.2537 | 0.98139 | 2026-10-03 11:20 | 235.895 | 242.782 | 553.3 | 40.4637 | 41.5478 | -1.0841 | 249.2869 | 39 | 40.9537 | -1.9537 | 0.97163 |  | 2026-10-03 11:20 | 223.069 | 226.512 | 524.3 | 37.752 | 39.5276 | -1.7756 | 237.1656 | 38 | 38.9624 | -0.96235 | 0.9848 |  |  | 2026-10-03 11:20 | 413.4337 | 430.077 | -16.6434 | 2580.4622 | 404.4 | 423.9269 | -19.5269
2026-10-03 11:10 | 930 | 49.65 | 313.334 | 318.526 | 687.5 | 53.0877 | 55.1964 | -2.1087 | 331.1784 | 52.3 | 54.4071 | -2.1071 | 0.9837 | 2026-10-03 11:10 | 317.688 | 323.084 | 692.2 | 53.8473 | 55.1964 | -1.3491 | 331.1784 | 55.2 | 54.4071 | 0.79291 | 0.9833 | 2026-10-03 11:10 | 310.337 | 318.978 | 678.9 | 53.163 | 55.1964 | -2.0334 | 331.1784 | 50.4 | 54.4071 | -4.0071 | 0.97291 | 2026-10-03 11:10 | 314.274 | 319.579 | 688.7 | 53.2632 | 55.1964 | -1.9332 | 331.1784 | 51.7 | 54.4071 | -2.7071 | 0.9834 | 2026-10-03 11:10 | 233.906 | 237.516 | 509.2 | 39.586 | 40.8862 | -1.3002 | 245.3173 | 38.5 | 40.3015 | -1.8015 | 0.9848 | 2026-10-03 11:10 | 232.964 | 237.129 | 510.5 | 39.5215 | 40.8862 | -1.3647 | 245.3173 | 38.4 | 40.3015 | -1.9015 | 0.98244 | 2026-10-03 11:10 | 232.215 | 236.856 | 509.1 | 39.476 | 40.8862 | -1.4102 | 245.3173 | 38.2 | 40.3015 | -2.1015 | 0.98041 | 2026-10-03 11:10 | 234.251 | 241.452 | 514.3 | 40.242 | 40.8862 | -0.64422 | 245.3173 | 39.1 | 40.3015 | -1.2015 | 0.97018 |  | 2026-10-03 11:10 | 221.851 | 225.207 | 486.3 | 37.5345 | 38.8982 | -1.3637 | 233.389 | 36 | 38.3419 | -2.3419 | 0.9851 |  |  | 2026-10-03 11:10 | 409.7212 | 423.2286 | -13.5075 | 2539.3719 | 399.8 | 417.1765 | -17.3765
2026-10-03 11:00 | 905 | 49.36 | 307.614 | 312.711 | 635.2 | 52.1185 | 53.7723 | -1.6538 | 322.6337 | 49.7 | 53.0033 | -3.3033 | 0.9837 | 2026-10-03 11:00 | 0 | 0 | 637 | 0 | 53.7723 | -53.7723 | 322.6337 | 48.8 | 53.0033 | -4.2033 |  | 2026-10-03 11:00 | 304.114 | 312.309 | 628.5 | 52.0515 | 53.7723 | -1.7208 | 322.6337 | 49.9 | 53.0033 | -3.1033 | 0.97376 | 2026-10-03 11:00 | 308.226 | 313.365 | 637 | 52.2275 | 53.7723 | -1.5448 | 322.6337 | 51.1 | 53.0033 | -1.9033 | 0.9836 | 2026-10-03 11:00 | 228.788 | 232.296 | 470.7 | 38.716 | 39.8313 | -1.1153 | 238.988 | 38 | 39.2617 | -1.2617 | 0.9849 | 2026-10-03 11:00 | 228.168 | 232.312 | 472.1 | 38.7187 | 39.8313 | -1.1127 | 238.988 | 37.9 | 39.2617 | -1.3617 | 0.98216 | 2026-10-03 11:00 | 226.998 | 231.116 | 470.9 | 38.5193 | 39.8313 | -1.312 | 238.988 | 37.7 | 39.2617 | -1.5617 | 0.98218 | 2026-10-03 11:00 | 229.022 | 235.869 | 475.2 | 39.3115 | 39.8313 | -0.51983 | 238.988 | 37.6 | 39.2617 | -1.6617 | 0.97097 |  | 2026-10-03 11:00 | 217.488 | 220.755 | 450.3 | 36.7925 | 37.8946 | -1.1021 | 227.3674 | 35.6 | 37.3527 | -1.7527 | 0.9852 |  |  | 2026-10-03 11:00 | 348.4555 | 412.309 | -63.8535 | 2473.8542 | 386.3 | 406.413 | -20.113
2026-10-03 10:50 | 879 | 49.65 | 299.852 | 304.697 | 585.5 | 50.7828 | 52.1695 | -1.3867 | 313.017 | 49.2 | 51.4235 | -2.2235 | 0.9841 | 2026-10-03 10:50 | 302.806 | 307.855 | 588.2 | 51.3092 | 52.1695 | -0.86033 | 313.017 | 49.8 | 51.4235 | -1.6235 | 0.9836 | 2026-10-03 10:50 | 297.013 | 304.796 | 578.6 | 50.7993 | 52.1695 | -1.3702 | 313.017 | 48.9 | 51.4235 | -2.5235 | 0.97446 | 2026-10-03 10:50 | 299.714 | 304.68 | 585.9 | 50.78 | 52.1695 | -1.3895 | 313.017 | 48.7 | 51.4235 | -2.7235 | 0.9837 | 2026-10-03 10:50 | 223.086 | 226.358 | 432.7 | 37.7263 | 38.6441 | -0.91774 | 231.8644 | 36.3 | 38.0915 | -1.7915 | 0.98555 | 2026-10-03 10:50 | 222.071 | 226.057 | 434.2 | 37.6762 | 38.6441 | -0.96791 | 231.8644 | 36 | 38.0915 | -2.0915 | 0.98237 | 2026-10-03 10:50 | 221.23 | 225.045 | 433.2 | 37.5075 | 38.6441 | -1.1366 | 231.8644 | 36.5 | 38.0915 | -1.5915 | 0.98305 | 2026-10-03 10:50 | 223.131 | 229.651 | 437.6 | 38.2752 | 38.6441 | -0.36891 | 231.8644 | 36.8 | 38.0915 | -1.2915 | 0.97161 |  | 2026-10-03 10:50 | 211.542 | 214.676 | 414.7 | 35.7793 | 36.765 | -0.98572 | 220.5903 | 34.9 | 36.2393 | -1.3393 | 0.9854 |  |  | 2026-10-03 10:50 | 390.6358 | 400.0193 | -9.3835 | 2400.116 | 377.1 | 394.2991 | -17.1991
2026-10-03 10:40 | 849 | 49.36 | 288.051 | 292.66 | 536.3 | 48.7767 | 50.4449 | -1.6683 | 302.6697 | 49.6 | 49.7236 | -0.12358 | 0.98425 | 2026-10-03 10:40 | 291.568 | 296.369 | 538.4 | 49.3948 | 50.4449 | -1.0501 | 302.6697 | 47.9 | 49.7236 | -1.8236 | 0.9838 | 2026-10-03 10:40 | 285.931 | 293.875 | 529.7 | 48.9792 | 50.4449 | -1.4658 | 302.6697 | 47.1 | 49.7236 | -2.6236 | 0.97297 | 2026-10-03 10:40 | 289.663 | 294.433 | 537.2 | 49.0722 | 50.4449 | -1.3728 | 302.6697 | 47.7 | 49.7236 | -2.0236 | 0.9838 | 2026-10-03 10:40 | 215.271 | 218.505 | 396.4 | 36.4175 | 37.3666 | -0.94912 | 224.1997 | 35.4 | 36.8323 | -1.4323 | 0.9852 | 2026-10-03 10:40 | 214.376 | 218.108 | 398.2 | 36.3513 | 37.3666 | -1.0153 | 224.1997 | 35.4 | 36.8323 | -1.4323 | 0.98289 | 2026-10-03 10:40 | 213.823 | 217.566 | 396.7 | 36.261 | 37.3666 | -1.1056 | 224.1997 | 34.7 | 36.8323 | -2.1323 | 0.9828 | 2026-10-03 10:40 | 215.605 | 222.111 | 400.8 | 37.0185 | 37.3666 | -0.34812 | 224.1997 | 35.4 | 36.8323 | -1.4323 | 0.97071 |  | 2026-10-03 10:40 | 204.563 | 207.573 | 379.8 | 34.5955 | 35.5497 | -0.95422 | 213.2983 | 33.6 | 35.0414 | -1.4414 | 0.9855 |  |  | 2026-10-03 10:40 | 376.8667 | 386.796 | -9.9293 | 2320.7759 | 366.8 | 381.2648 | -14.4648
2026-10-03 10:30 | 818 | 49.65 | 279.707 | 284.111 | 486.7 | 47.3518 | 48.5491 | -1.1973 | 291.2945 | 43.8 | 47.8548 | -4.0548 | 0.9845 | 2026-10-03 10:30 | 282.42 | 286.983 | 490.5 | 47.8305 | 48.5491 | -0.71859 | 291.2945 | 45.6 | 47.8548 | -2.2548 | 0.9841 | 2026-10-03 10:30 | 277.58 | 285.075 | 482.6 | 47.5125 | 48.5491 | -1.0366 | 291.2945 | 45.3 | 47.8548 | -2.5548 | 0.97371 | 2026-10-03 10:30 | 280.254 | 284.753 | 489.5 | 47.4588 | 48.5491 | -1.0903 | 291.2945 | 45.9 | 47.8548 | -1.9548 | 0.9842 | 2026-10-03 10:30 | 208.58 | 211.649 | 361 | 35.2748 | 35.9623 | -0.68745 | 215.7737 | 34.1 | 35.448 | -1.348 | 0.9855 | 2026-10-03 10:30 | 207.775 | 211.316 | 362.8 | 35.2193 | 35.9623 | -0.74295 | 215.7737 | 34 | 35.448 | -1.448 | 0.98324 | 2026-10-03 10:30 | 207.36 | 210.91 | 362 | 35.1517 | 35.9623 | -0.81062 | 215.7737 | 34 | 35.448 | -1.448 | 0.98317 | 2026-10-03 10:30 | 208.943 | 214.973 | 365.4 | 35.8288 | 35.9623 | -0.13345 | 215.7737 | 33.8 | 35.448 | -1.648 | 0.97195 |  | 2026-10-03 10:30 | 197.891 | 200.782 | 346.2 | 33.4637 | 34.2137 | -0.75 | 205.282 | 32.5 | 33.7244 | -1.2244 | 0.9856 |  |  | 2026-10-03 10:30 | 365.092 | 372.2592 | -7.1672 | 2233.555 | 349 | 366.9359 | -17.9359
2026-10-03 10:20 | 783 | 49.65 | 267.939 | 272.743 | 442.9 | 45.4572 | 46.4718 | -1.0146 | 278.8308 | 44.3 | 45.8073 | -1.5073 | 0.98239 | 2026-10-03 10:20 | 271.509 | 275.84 | 444.9 | 45.9733 | 46.4718 | -0.49847 | 278.8308 | 44.3 | 45.8073 | -1.5073 | 0.9843 | 2026-10-03 10:20 | 265.461 | 272.205 | 437.3 | 45.3675 | 46.4718 | -1.1043 | 278.8308 | 43.3 | 45.8073 | -2.5073 | 0.97522 | 2026-10-03 10:20 | 269.305 | 273.601 | 443.6 | 45.6002 | 46.4718 | -0.87164 | 278.8308 | 43.8 | 45.8073 | -2.0073 | 0.9843 | 2026-10-03 10:20 | 199.434 | 202.368 | 326.9 | 33.728 | 34.4236 | -0.69556 | 206.5414 | 32.5 | 33.9313 | -1.4313 | 0.9855 | 2026-10-03 10:20 | 199.473 | 202.646 | 328.8 | 33.7743 | 34.4236 | -0.64923 | 206.5414 | 32.5 | 33.9313 | -1.4313 | 0.98434 | 2026-10-03 10:20 | 198.474 | 201.678 | 328 | 33.613 | 34.4236 | -0.81056 | 206.5414 | 32.3 | 33.9313 | -1.6313 | 0.98411 | 2026-10-03 10:20 | 200.39 | 206.082 | 331.6 | 34.347 | 34.4236 | -0.076559 | 206.5414 | 32.6 | 33.9313 | -1.3313 | 0.97238 |  | 2026-10-03 10:20 | 189.982 | 192.777 | 313.7 | 32.1295 | 32.7498 | -0.62025 | 196.4985 | 30.9 | 32.2814 | -1.3814 | 0.9855 |  |  | 2026-10-03 10:20 | 349.99 | 356.3312 | -6.3412 | 2137.9873 | 336.5 | 351.2357 | -14.7357
2026-10-03 10:10 | 746 | 49.65 | 257.817 | 262.008 | 398.6 | 43.668 | 44.2758 | -0.60782 | 265.6549 | 41.2 | 43.6427 | -2.4427 | 0.984 | 2026-10-03 10:10 | 259.326 | 263.409 | 400.6 | 43.9015 | 44.2758 | -0.37432 | 265.6549 | 43.3 | 43.6427 | -0.34268 | 0.9845 | 2026-10-03 10:10 | 255.22 | 261.476 | 394 | 43.5793 | 44.2758 | -0.69649 | 265.6549 | 41.9 | 43.6427 | -1.7427 | 0.97607 | 2026-10-03 10:10 | 257.982 | 262.017 | 399.8 | 43.6695 | 44.2758 | -0.60632 | 265.6549 | 42.4 | 43.6427 | -1.2427 | 0.9846 | 2026-10-03 10:10 | 191.484 | 194.242 | 294.4 | 32.3737 | 32.7969 | -0.42324 | 196.7814 | 31.5 | 32.3279 | -0.82791 | 0.9858 | 2026-10-03 10:10 | 190.992 | 193.948 | 296.3 | 32.3247 | 32.7969 | -0.47224 | 196.7814 | 31.4 | 32.3279 | -0.92791 | 0.98476 | 2026-10-03 10:10 | 190.415 | 193.457 | 295.7 | 32.2428 | 32.7969 | -0.55407 | 196.7814 | 31.3 | 32.3279 | -1.0279 | 0.98428 | 2026-10-03 10:10 | 191.724 | 197.416 | 299 | 32.9027 | 32.7969 | 0.10576 | 196.7814 | 31.6 | 32.3279 | -0.72791 | 0.97117 |  | 2026-10-03 10:10 | 181.707 | 184.324 | 282.8 | 30.7207 | 31.2022 | -0.48152 | 187.2131 | 29.5 | 30.756 | -1.256 | 0.9858 |  |  | 2026-10-03 10:10 | 335.3828 | 339.4931 | -4.1102 | 2036.9585 | 324.1 | 334.6383 | -10.5383
2026-10-03 10:00 | 712 | 49.65 | 247.259 | 250.999 | 357.4 | 41.8332 | 42.2579 | -0.42472 | 253.5473 | 40.3 | 41.6536 | -1.3536 | 0.9851 | 2026-10-03 10:00 | 249.283 | 253.079 | 357.3 | 42.1798 | 42.2579 | -0.078053 | 253.5473 | 39.5 | 41.6536 | -2.1536 | 0.985 | 2026-10-03 10:00 | 244.024 | 250.088 | 352.1 | 41.6813 | 42.2579 | -0.57655 | 253.5473 | 39.7 | 41.6536 | -1.9536 | 0.97575 | 2026-10-03 10:00 | 247.704 | 251.502 | 357.4 | 41.917 | 42.2579 | -0.34089 | 253.5473 | 40.3 | 41.6536 | -1.3536 | 0.9849 | 2026-10-03 10:00 | 183.154 | 185.773 | 262.9 | 30.9622 | 31.3021 | -0.33997 | 187.8128 | 29.8 | 30.8545 | -1.0545 | 0.9859 | 2026-10-03 10:00 | 183.368 | 185.999 | 264.9 | 30.9998 | 31.3021 | -0.3023 | 187.8128 | 29.9 | 30.8545 | -0.95452 | 0.98585 | 2026-10-03 10:00 | 182.629 | 185.227 | 264.4 | 30.8712 | 31.3021 | -0.43097 | 187.8128 | 29.7 | 30.8545 | -1.1545 | 0.98597 | 2026-10-03 10:00 | 184.519 | 189.674 | 267.4 | 31.6123 | 31.3021 | 0.3102 | 187.8128 | 29.9 | 30.8545 | -0.95452 | 0.97282 |  | 2026-10-03 10:00 | 174.921 | 177.405 | 253.3 | 29.5675 | 29.7801 | -0.21261 | 178.6806 | 28.8 | 29.3543 | -0.55425 | 0.986 |  |  | 2026-10-03 10:00 | 321.6243 | 324.0202 | -2.3959 | 1944.1212 | 307.9 | 319.3867 | -11.4867
2026-10-03 09:50 | 674 | 49.65 | 234.485 | 239.267 | 317.1 | 39.8778 | 40.0026 | -0.12472 | 240.0153 | 39.2 | 39.4305 | -0.23051 |  | 2026-10-03 09:50 | 237.571 | 241.164 | 317.8 | 40.194 | 40.0026 | 0.19145 | 240.0153 | 39.4 | 39.4305 | -0.030514 |  | 2026-10-03 09:50 | 232.752 | 238.308 | 312.4 | 39.718 | 40.0026 | -0.28455 | 240.0153 | 37.7 | 39.4305 | -1.7305 |  | 2026-10-03 09:50 | 236.045 | 239.615 | 317.1 | 39.9358 | 40.0026 | -0.066717 | 240.0153 | 38.2 | 39.4305 | -1.2305 |  | 2026-10-03 09:50 | 174.698 | 177.179 | 233.1 | 29.5298 | 29.6315 | -0.10169 | 177.7891 | 28.2 | 29.2078 | -1.0078 |  | 2026-10-03 09:50 | 174.977 | 177.64 | 235 | 29.6067 | 29.6315 | -0.024852 | 177.7891 | 28.3 | 29.2078 | -0.90779 |  | 2026-10-03 09:50 | 174.249 | 176.719 | 234.7 | 29.4532 | 29.6315 | -0.17835 | 177.7891 | 28.2 | 29.2078 | -1.0078 |  | 2026-10-03 09:50 | 175.406 | 180.803 | 237.5 | 30.1338 | 29.6315 | 0.50231 | 177.7891 | 28.5 | 29.2078 | -0.70779 |  |  | 2026-10-03 09:50 | 166.422 | 168.734 | 224.5 | 28.1223 | 28.1907 | -0.068387 | 169.1443 | 26.9 | 27.7876 | -0.88759 |  |  |  | 2026-10-03 09:50 | 306.5715 | 306.727 | -0.15549 | 1840.362 | 294.6 | 302.3408 | -7.7408
2026-10-03 09:40 | 636 | 49.65 | 224.204 | 227.411 | 277.9 | 37.9018 | 37.7472 | 0.15462 | 226.4833 | 36.3 | 37.2074 | -0.90743 |  | 2026-10-03 09:40 | 226.021 | 229.347 | 278.4 | 38.2245 | 37.7472 | 0.47729 | 226.4833 | 36.2 | 37.2074 | -1.0074 |  | 2026-10-03 09:40 | 221.714 | 226.878 | 274.7 | 37.813 | 37.7472 | 0.065787 | 226.4833 | 35.9 | 37.2074 | -1.3074 |  | 2026-10-03 09:40 | 224.717 | 227.977 | 278.9 | 37.9962 | 37.7472 | 0.24895 | 226.4833 | 36.3 | 37.2074 | -0.90743 |  | 2026-10-03 09:40 | 166.008 | 168.285 | 204.9 | 28.0475 | 27.9609 | 0.086601 | 167.7654 | 26.9 | 27.5611 | -0.66106 |  | 2026-10-03 09:40 | 166.703 | 168.967 | 206.7 | 28.1612 | 27.9609 | 0.20027 | 167.7654 | 27 | 27.5611 | -0.56106 |  | 2026-10-03 09:40 | 165.75 | 168.151 | 206.5 | 28.0252 | 27.9609 | 0.064268 | 167.7654 | 26.9 | 27.5611 | -0.66106 |  | 2026-10-03 09:40 | 167.095 | 171.77 | 209 | 28.6283 | 27.9609 | 0.66743 | 167.7654 | 27.1 | 27.5611 | -0.46106 |  |  | 2026-10-03 09:40 | 158.636 | 160.823 | 197.6 | 26.8038 | 26.6013 | 0.2025 | 159.608 | 25.8 | 26.2209 | -0.42093 |  |  |  | 2026-10-03 09:40 | 291.6015 | 289.4338 | 2.1677 | 1736.6027 | 278.4 | 285.2949 | -6.8949
2026-10-03 09:30 | 597 | 49.36 | 209.883 | 213.884 | 241.6 | 35.6473 | 35.4719 | 0.17545 | 212.8313 | 33.2 | 34.9646 | -1.7646 |  | 2026-10-03 09:30 | 212.33 | 215.323 | 242.2 | 35.8872 | 35.4719 | 0.41528 | 212.8313 | 34.7 | 34.9646 | -0.26464 |  | 2026-10-03 09:30 | 208.545 | 213.024 | 238.8 | 35.504 | 35.4719 | 0.032114 | 212.8313 | 33.7 | 34.9646 | -1.2646 |  | 2026-10-03 09:30 | 211.158 | 214.156 | 242.6 | 35.6927 | 35.4719 | 0.22078 | 212.8313 | 34.2 | 34.9646 | -0.76464 |  | 2026-10-03 09:30 | 156.209 | 158.275 | 178 | 26.3792 | 26.2755 | 0.1037 | 157.6528 | 25.3 | 25.8997 | -0.59973 |  | 2026-10-03 09:30 | 156.809 | 158.923 | 179.7 | 26.4872 | 26.2755 | 0.2117 | 157.6528 | 25.4 | 25.8997 | -0.49973 |  | 2026-10-03 09:30 | 156.162 | 158.235 | 179.6 | 26.3725 | 26.2755 | 0.097029 | 157.6528 | 25.3 | 25.8997 | -0.59973 |  | 2026-10-03 09:30 | 157.467 | 161.654 | 181.9 | 26.9423 | 26.2755 | 0.66686 | 157.6528 | 25.5 | 25.8997 | -0.39973 |  |  | 2026-10-03 09:30 | 149.202 | 151.213 | 171.8 | 25.2022 | 24.9979 | 0.20431 | 149.9871 | 23.8 | 24.6404 | -0.84039 |  |  |  | 2026-10-03 09:30 | 274.1145 | 271.9873 | 2.1272 | 1631.9237 | 261.1 | 268.0979 | -6.9979
2026-10-03 09:20 | 554 | 49.36 | 195.924 | 199.828 | 208.4 | 33.3047 | 32.917 | 0.38771 | 197.5018 | 32.3 | 32.4462 | -0.14625 |  | 2026-10-03 09:20 | 196.932 | 199.667 | 207.5 | 33.2778 | 32.917 | 0.36087 | 197.5018 | 31.3 | 32.4462 | -1.1462 |  | 2026-10-03 09:20 | 194.811 | 198.82 | 205.1 | 33.1367 | 32.917 | 0.21971 | 197.5018 | 30.9 | 32.4462 | -1.5462 |  | 2026-10-03 09:20 | 197.393 | 200.135 | 208.4 | 33.3558 | 32.917 | 0.43887 | 197.5018 | 31.5 | 32.4462 | -0.94625 |  | 2026-10-03 09:20 | 145.838 | 147.75 | 152.7 | 24.625 | 24.3829 | 0.24207 | 146.2976 | 23.4 | 24.0343 | -0.63426 |  | 2026-10-03 09:20 | 146.609 | 148.525 | 154.3 | 24.7542 | 24.3829 | 0.37123 | 146.2976 | 23.6 | 24.0343 | -0.43426 |  | 2026-10-03 09:20 | 145.944 | 147.851 | 154.3 | 24.6418 | 24.3829 | 0.2589 | 146.2976 | 23.4 | 24.0343 | -0.63426 |  | 2026-10-03 09:20 | 147.276 | 151.356 | 156.4 | 25.226 | 24.3829 | 0.84307 | 146.2976 | 23.7 | 24.0343 | -0.33426 |  |  | 2026-10-03 09:20 | 139.709 | 141.549 | 148 | 23.5915 | 23.1973 | 0.39416 | 139.184 | 22.5 | 22.8656 | -0.36562 |  |  |  | 2026-10-03 09:20 | 255.9135 | 252.3969 | 3.5166 | 1514.3814 | 242.6 | 248.7876 | -6.1876
2026-10-03 09:10 | 514 | 48.5 | 182.739 | 185.61 | 176.1 | 30.935 | 30.6408 | 0.29422 | 183.8447 | 28.8 | 30.2026 | -1.4026 |  | 2026-10-03 09:10 | 180.472 | 183.953 | 176.2 | 30.6588 | 30.6408 | 0.018056 | 183.8447 | 29.5 | 30.2026 | -0.70261 |  | 2026-10-03 09:10 | 180.575 | 183.983 | 174.2 | 30.6638 | 30.6408 | 0.023056 | 183.8447 | 29.1 | 30.2026 | -1.1026 |  | 2026-10-03 09:10 | 183.32 | 185.791 | 176.9 | 30.9652 | 30.6408 | 0.32439 | 183.8447 | 29.5 | 30.2026 | -0.70261 |  | 2026-10-03 09:10 | 134.946 | 136.668 | 129.3 | 22.778 | 22.6969 | 0.081128 | 136.1812 | 21.6 | 22.3723 | -0.77231 |  | 2026-10-03 09:10 | 136.068 | 137.804 | 130.7 | 22.9673 | 22.6969 | 0.27046 | 136.1812 | 21.7 | 22.3723 | -0.67231 |  | 2026-10-03 09:10 | 135.192 | 136.917 | 130.9 | 22.8195 | 22.6969 | 0.12263 | 136.1812 | 21.6 | 22.3723 | -0.77231 |  | 2026-10-03 09:10 | 136.414 | 140.061 | 132.7 | 23.3435 | 22.6969 | 0.64663 | 136.1812 | 21.8 | 22.3723 | -0.57231 |  |  | 2026-10-03 09:10 | 129.759 | 131.428 | 125.5 | 21.9047 | 21.5933 | 0.3114 | 129.5596 | 20.7 | 21.2845 | -0.58448 |  |  |  | 2026-10-03 09:10 | 237.0358 | 234.9439 | 2.092 | 1409.6632 | 224.3 | 231.5842 | -7.2842
2026-10-03 09:00 | 469 | 48.22 | 167.95 | 170.093 | 147.3 | 28.3488 | 27.9881 | 0.36076 | 167.9284 | 26.9 | 27.5878 | -0.68784 |  | 2026-10-03 09:00 | 166.437 | 168.612 | 146.7 | 28.102 | 27.9881 | 0.11393 | 167.9284 | 26.4 | 27.5878 | -1.1878 |  | 2026-10-03 09:00 | 164.863 | 167.749 | 145.1 | 27.9582 | 27.9881 | -0.029907 | 167.9284 | 26 | 27.5878 | -1.5878 |  | 2026-10-03 09:00 | 167.082 | 169.248 | 147.4 | 28.208 | 27.9881 | 0.21993 | 167.9284 | 26.4 | 27.5878 | -1.1878 |  | 2026-10-03 09:00 | 123.185 | 124.732 | 107.7 | 20.7887 | 20.7319 | 0.05676 | 124.3914 | 19.4 | 20.4354 | -1.0354 |  | 2026-10-03 09:00 | 124.177 | 125.723 | 109 | 20.9538 | 20.7319 | 0.22193 | 124.3914 | 19.9 | 20.4354 | -0.53544 |  | 2026-10-03 09:00 | 123.664 | 125.204 | 109.3 | 20.8673 | 20.7319 | 0.13543 | 124.3914 | 19.8 | 20.4354 | -0.63544 |  | 2026-10-03 09:00 | 124.916 | 128.416 | 110.9 | 21.4027 | 20.7319 | 0.67076 | 124.3914 | 20.2 | 20.4354 | -0.23544 |  |  | 2026-10-03 09:00 | 118.533 | 120.009 | 104.8 | 20.0015 | 19.7238 | 0.27766 | 118.343 | 19 | 19.4418 | -0.44179 |  |  |  | 2026-10-03 09:00 | 216.631 | 214.6038 | 2.0272 | 1287.6226 | 204 | 211.5349 | -7.5349
2026-10-03 08:50 | 429 | 48.22 | 152.618 | 154.503 | 120.4 | 25.7505 | 25.601 | 0.14947 | 153.6062 | 24 | 25.2349 | -1.2349 |  | 2026-10-03 08:50 | 153.228 | 155.136 | 120.3 | 25.856 | 25.601 | 0.25497 | 153.6062 | 24.1 | 25.2349 | -1.1349 |  | 2026-10-03 08:50 | 150.706 | 153.088 | 119.1 | 25.5147 | 25.601 | -0.086365 | 153.6062 | 23.8 | 25.2349 | -1.4349 |  | 2026-10-03 08:50 | 153.298 | 155.207 | 121 | 25.8678 | 25.601 | 0.2668 | 153.6062 | 24.3 | 25.2349 | -0.93494 |  | 2026-10-03 08:50 | 112.778 | 114.159 | 88.3 | 19.0265 | 18.9637 | 0.062773 | 113.7824 | 17.8 | 18.6925 | -0.89255 |  | 2026-10-03 08:50 | 113.791 | 115.15 | 89.1 | 19.1917 | 18.9637 | 0.22794 | 113.7824 | 18 | 18.6925 | -0.69255 |  | 2026-10-03 08:50 | 113.327 | 114.703 | 89.5 | 19.1172 | 18.9637 | 0.15344 | 113.7824 | 17.9 | 18.6925 | -0.79255 |  | 2026-10-03 08:50 | 114.379 | 117.5 | 90.7 | 19.5833 | 18.9637 | 0.61961 | 113.7824 | 17.9 | 18.6925 | -0.79255 |  |  | 2026-10-03 08:50 | 108.667 | 109.987 | 85.8 | 18.3312 | 18.0416 | 0.28953 | 108.2498 | 17.2 | 17.7836 | -0.58364 |  |  |  | 2026-10-03 08:50 | 198.2388 | 196.3007 | 1.9382 | 1177.804 | 185 | 193.4936 | -8.4936
2026-10-03 08:40 | 386 | 47.35 | 136.249 | 137.848 | 96.4 | 22.9747 | 23.1113 | -0.13664 | 138.6678 | 21.8 | 22.7808 | -0.98082 |  | 2026-10-03 08:40 | 137.179 | 138.845 | 96.2 | 23.1408 | 23.1113 | 0.029527 | 138.6678 | 21.6 | 22.7808 | -1.1808 |  | 2026-10-03 08:40 | 135.118 | 137.334 | 95.3 | 22.889 | 23.1113 | -0.22231 | 138.6678 | 21.3 | 22.7808 | -1.4808 |  | 2026-10-03 08:40 | 137.485 | 139.127 | 96.7 | 23.1878 | 23.1113 | 0.076527 | 138.6678 | 21.7 | 22.7808 | -1.0808 |  | 2026-10-03 08:40 | 100.711 | 101.893 | 70.5 | 16.9822 | 17.1195 | -0.13732 | 102.7169 | 15.9 | 16.8747 | -0.97468 |  | 2026-10-03 08:40 | 102.181 | 103.37 | 71.1 | 17.2283 | 17.1195 | 0.10885 | 102.7169 | 15.9 | 16.8747 | -0.97468 |  | 2026-10-03 08:40 | 101.588 | 102.77 | 71.6 | 17.1283 | 17.1195 | 0.0088468 | 102.7169 | 15.9 | 16.8747 | -0.97468 |  | 2026-10-03 08:40 | 102.777 | 105.735 | 72.8 | 17.6225 | 17.1195 | 0.50301 | 102.7169 | 16 | 16.8747 | -0.87468 |  |  | 2026-10-03 08:40 | 97.508 | 98.662 | 68.6 | 16.4437 | 16.2871 | 0.1566 | 97.7224 | 15.2 | 16.0542 | -0.85417 |  |  |  | 2026-10-03 08:40 | 177.5973 | 177.2102 | 0.38709 | 1063.2615 | 165.3 | 174.6761 | -9.3761
2026-10-03 08:30 | 340 | 41.33 | 118.997 | 120.345 | 74.6 | 20.0575 | 20.8224 | -0.76493 | 124.9346 | 18.7 | 20.5247 | -1.8247 |  | 2026-10-03 08:30 | 119.695 | 121.088 | 74.6 | 20.1813 | 20.8224 | -0.6411 | 124.9346 | 18.5 | 20.5247 | -2.0247 |  | 2026-10-03 08:30 | 118.131 | 119.941 | 74 | 19.9902 | 20.8224 | -0.83227 | 124.9346 | 18.2 | 20.5247 | -2.3247 |  | 2026-10-03 08:30 | 120.272 | 121.645 | 75 | 20.2742 | 20.8224 | -0.54827 | 124.9346 | 18.5 | 20.5247 | -2.0247 |  | 2026-10-03 08:30 | 88.23 | 89.247 | 54.6 | 14.8745 | 15.424 | -0.54953 | 92.5442 | 13.6 | 15.2035 | -1.6035 |  | 2026-10-03 08:30 | 89.715 | 90.74 | 55.2 | 15.1233 | 15.424 | -0.30069 | 92.5442 | 13.9 | 15.2035 | -1.3035 |  | 2026-10-03 08:30 | 89.165 | 90.193 | 55.7 | 15.0322 | 15.424 | -0.39186 | 92.5442 | 13.7 | 15.2035 | -1.5035 |  | 2026-10-03 08:30 | 90.327 | 92.786 | 56.8 | 15.4643 | 15.424 | 0.040308 | 92.5442 | 14.1 | 15.2035 | -1.1035 |  |  | 2026-10-03 08:30 | 85.749 | 86.758 | 53.4 | 14.4597 | 14.674 | -0.21438 | 88.0443 | 13.4 | 14.4642 | -1.0642 |  |  |  | 2026-10-03 08:30 | 155.4572 | 159.6599 | -4.2027 | 957.9593 | 142.6 | 157.3767 | -14.7767
2026-10-03 08:20 | 294 | 35.88 | 99.724 | 101.785 | 55.9 | 16.9642 | 18.3696 | -1.4054 | 110.2173 | 15 | 18.1069 | -3.1069 |  | 2026-10-03 08:20 | 101.147 | 103.621 | 56.1 | 17.2702 | 18.3696 | -1.0994 | 110.2173 | 15.5 | 18.1069 | -2.6069 |  | 2026-10-03 08:20 | 100.963 | 102.118 | 55.8 | 17.0197 | 18.3696 | -1.3499 | 110.2173 | 15.4 | 18.1069 | -2.7069 |  | 2026-10-03 08:20 | 102.795 | 103.938 | 56.5 | 17.323 | 18.3696 | -1.0466 | 110.2173 | 15.7 | 18.1069 | -2.4069 |  | 2026-10-03 08:20 | 75.141 | 76.023 | 41 | 12.6705 | 13.6071 | -0.93658 | 81.6425 | 11.4 | 13.4125 | -2.0125 |  | 2026-10-03 08:20 | 76.707 | 77.592 | 41.3 | 12.932 | 13.6071 | -0.67508 | 81.6425 | 11.8 | 13.4125 | -1.6125 |  | 2026-10-03 08:20 | 76.213 | 77.123 | 42 | 12.8538 | 13.6071 | -0.75324 | 81.6425 | 11.8 | 13.4125 | -1.6125 |  | 2026-10-03 08:20 | 77.114 | 79.227 | 42.7 | 13.2045 | 13.6071 | -0.40258 | 81.6425 | 11.7 | 13.4125 | -1.7125 |  |  | 2026-10-03 08:20 | 73.196 | 74.07 | 40 | 12.345 | 12.9454 | -0.60045 | 77.6727 | 11.2 | 12.7603 | -1.5603 |  |  |  | 2026-10-03 08:20 | 132.5828 | 140.852 | -8.2691 | 845.1117 | 119.5 | 138.8378 | -19.3378
2026-10-03 08:10 | 248 | 31.86 | 84.833 | 85.759 | 40.9 | 14.2932 | 15.7221 | -1.4289 | 94.3323 | 12.6 | 15.4972 | -2.8972 |  | 2026-10-03 08:10 | 82.093 | 86.362 | 40.6 | 14.3937 | 15.7221 | -1.3284 | 94.3323 | 12.8 | 15.4972 | -2.6972 |  | 2026-10-03 08:10 | 83.955 | 84.88 | 40.4 | 14.1467 | 15.7221 | -1.5754 | 94.3323 | 12.6 | 15.4972 | -2.8972 |  | 2026-10-03 08:10 | 85.523 | 86.474 | 40.8 | 14.4123 | 15.7221 | -1.3097 | 94.3323 | 12.8 | 15.4972 | -2.6972 |  | 2026-10-03 08:10 | 62.239 | 63.241 | 29.6 | 10.5402 | 11.646 | -1.1058 | 69.8758 | 9.4 | 11.4794 | -2.0794 |  | 2026-10-03 08:10 | 63.747 | 64.502 | 29.5 | 10.7503 | 11.646 | -0.89563 | 69.8758 | 9.4 | 11.4794 | -2.0794 |  | 2026-10-03 08:10 | 63.365 | 64.135 | 30.2 | 10.6892 | 11.646 | -0.9568 | 69.8758 | 9.4 | 11.4794 | -2.0794 |  | 2026-10-03 08:10 | 64.232 | 66.133 | 31 | 11.0222 | 11.646 | -0.6238 | 69.8758 | 9.7 | 11.4794 | -1.7794 |  |  | 2026-10-03 08:10 | 61.003 | 61.763 | 28.8 | 10.2938 | 11.0797 | -0.78586 | 66.4782 | 9.1 | 10.9213 | -1.8213 |  |  |  | 2026-10-03 08:10 | 110.5415 | 120.5518 | -10.0103 | 723.3107 | 97.8 | 118.8279 | -21.0279
2026-10-03 08:00 | 204 | 21.52 | 68.019 | 68.789 | 28.3 | 11.4648 | 13.4122 | -1.9474 | 80.4732 | 10.1 | 13.2204 | -3.1204 |  | 2026-10-03 08:00 | 67.714 | 68.519 | 27.8 | 11.4198 | 13.4122 | -1.9924 | 80.4732 | 10.3 | 13.2204 | -2.9204 |  | 2026-10-03 08:00 | 67.168 | 67.943 | 27.8 | 11.3238 | 13.4122 | -2.0884 | 80.4732 | 9.8 | 13.2204 | -3.4204 |  | 2026-10-03 08:00 | 68.279 | 69.073 | 28 | 11.5122 | 13.4122 | -1.9 | 80.4732 | 10 | 13.2204 | -3.2204 |  | 2026-10-03 08:00 | 49.781 | 50.467 | 20.2 | 8.4112 | 9.935 | -1.5238 | 59.6098 | 7.3 | 9.7929 | -2.4929 |  | 2026-10-03 08:00 | 51.099 | 51.772 | 20.1 | 8.6287 | 9.935 | -1.3063 | 59.6098 | 7.5 | 9.7929 | -2.2929 |  | 2026-10-03 08:00 | 50.691 | 51.385 | 20.8 | 8.5642 | 9.935 | -1.3708 | 59.6098 | 7.5 | 9.7929 | -2.2929 |  | 2026-10-03 08:00 | 51.367 | 52.882 | 21.3 | 8.8137 | 9.935 | -1.1213 | 59.6098 | 7.6 | 9.7929 | -2.1929 |  |  | 2026-10-03 08:00 | 48.827 | 49.5 | 19.7 | 8.25 | 9.4519 | -1.2019 | 56.7113 | 7.2 | 9.3167 | -2.1167 |  |  |  | 2026-10-03 08:00 | 88.3883 | 102.8406 | -14.4522 | 617.0435 | 77.3 | 101.37 | -24.07
2026-10-03 07:50 | 161 | 18.66 | 50.464 | 52.418 | 18.2 | 8.7363 | 10.6898 | -1.9535 | 64.1388 | 7.3 | 10.5369 | -3.2369 |  | 2026-10-03 07:50 | 50.997 | 51.847 | 17.5 | 8.6412 | 10.6898 | -2.0486 | 64.1388 | 7.1 | 10.5369 | -3.4369 |  | 2026-10-03 07:50 | 51.122 | 51.795 | 18 | 8.6325 | 10.6898 | -2.0573 | 64.1388 | 7.4 | 10.5369 | -3.1369 |  | 2026-10-03 07:50 | 52.232 | 52.92 | 18 | 8.82 | 10.6898 | -1.8698 | 64.1388 | 7.5 | 10.5369 | -3.0369 |  | 2026-10-03 07:50 | 37.829 | 38.409 | 12.9 | 6.4015 | 7.9184 | -1.5169 | 47.5102 | 5.4 | 7.8051 | -2.4051 |  | 2026-10-03 07:50 | 36.914 | 37.457 | 12.6 | 6.2428 | 7.9184 | -1.6755 | 47.5102 | 5.3 | 7.8051 | -2.5051 |  | 2026-10-03 07:50 | 38.737 | 39.319 | 13.3 | 6.5532 | 7.9184 | -1.3652 | 47.5102 | 5.5 | 7.8051 | -2.3051 |  | 2026-10-03 07:50 | 39.357 | 40.328 | 13.7 | 6.7213 | 7.9184 | -1.197 | 47.5102 | 5.6 | 7.8051 | -2.2051 |  |  | 2026-10-03 07:50 | 37.368 | 37.941 | 12.5 | 6.3235 | 7.5334 | -1.2099 | 45.2001 | 5.3 | 7.4256 | -2.1256 |  |  |  | 2026-10-03 07:50 | 67.0723 | 81.9661 | -14.8937 | 491.7964 | 56.4 | 80.794 | -24.394
2026-10-03 07:40 | 119 | 16.07 | 37.18 | 37.727 | 10.9 | 6.2878 | 7.9712 | -1.6834 | 47.8274 | 5.3 | 7.8572 | -2.5572 |  | 2026-10-03 07:40 | 35.264 | 36.007 | 10.4 | 6.0012 | 7.9712 | -1.9701 | 47.8274 | 4.9 | 7.8572 | -2.9572 |  | 2026-10-03 07:40 | 36.452 | 37.007 | 10.6 | 6.1678 | 7.9712 | -1.8034 | 47.8274 | 5 | 7.8572 | -2.8572 |  | 2026-10-03 07:40 | 36.628 | 37.19 | 10.5 | 6.1983 | 7.9712 | -1.7729 | 47.8274 | 5.1 | 7.8572 | -2.7572 |  | 2026-10-03 07:40 | 26.965 | 27.448 | 7.5 | 4.5747 | 5.9046 | -1.3299 | 35.4277 | 3.7 | 5.8202 | -2.1202 |  | 2026-10-03 07:40 | 26.418 | 26.889 | 7.3 | 4.4815 | 5.9046 | -1.4231 | 35.4277 | 3.6 | 5.8202 | -2.2202 |  | 2026-10-03 07:40 | 27.787 | 28.273 | 7.8 | 4.7122 | 5.9046 | -1.1924 | 35.4277 | 3.8 | 5.8202 | -2.0202 |  | 2026-10-03 07:40 | 28.288 | 29.08 | 8.1 | 4.8467 | 5.9046 | -1.0579 | 35.4277 | 3.9 | 5.8202 | -1.9202 |  |  | 2026-10-03 07:40 | 26.592 | 27.066 | 7.2 | 4.511 | 5.6175 | -1.1065 | 33.7051 | 3.6 | 5.5372 | -1.9372 |  |  |  | 2026-10-03 07:40 | 47.7812 | 61.1209 | -13.3397 | 366.7253 | 38.9 | 60.2469 | -21.3469
2026-10-03 07:30 | 81 | 13.78 | 24.278 | 24.728 | 5.6 | 4.1213 | 5.468 | -1.3466 | 32.8078 | 3.1 | 5.3898 | -2.2898 |  | 2026-10-03 07:30 | 23.852 | 24.427 | 5.5 | 4.0712 | 5.468 | -1.3968 | 32.8078 | 3.1 | 5.3898 | -2.2898 |  | 2026-10-03 07:30 | 24.029 | 24.499 | 5.6 | 4.0832 | 5.468 | -1.3848 | 32.8078 | 3.1 | 5.3898 | -2.2898 |  | 2026-10-03 07:30 | 23.759 | 24.252 | 5.4 | 4.042 | 5.468 | -1.426 | 32.8078 | 3 | 5.3898 | -2.3898 |  | 2026-10-03 07:30 | 17.529 | 17.931 | 3.8 | 2.9885 | 4.0503 | -1.0618 | 24.3021 | 2.3 | 3.9924 | -1.6924 |  | 2026-10-03 07:30 | 17.212 | 17.599 | 3.7 | 2.9332 | 4.0503 | -1.1172 | 24.3021 | 2.2 | 3.9924 | -1.7924 |  | 2026-10-03 07:30 | 18.197 | 18.61 | 4 | 3.1017 | 4.0503 | -0.94868 | 24.3021 | 2.4 | 3.9924 | -1.5924 |  | 2026-10-03 07:30 | 18.568 | 19.404 | 4.2 | 3.234 | 4.0503 | -0.81634 | 24.3021 | 2.4 | 3.9924 | -1.5924 |  |  | 2026-10-03 07:30 | 16.926 | 17.317 | 3.6 | 2.8862 | 3.8534 | -0.96723 | 23.1204 | 2.2 | 3.7983 | -1.5983 |  |  |  | 2026-10-03 07:30 | 31.4612 | 41.9266 | -10.4655 | 251.5598 | 23.8 | 41.3271 | -17.5271
2026-10-03 07:20 | 29 | 13.2 | 13.762 | 14.134 | 2.5 | 2.3557 | 1.9615 | 0.39418 | 11.7689 | 1.7 | 1.9334 | -0.23344 |  | 2026-10-03 07:20 | 13.278 | 13.981 | 2.4 | 2.3302 | 1.9615 | 0.36868 | 11.7689 | 1.6 | 1.9334 | -0.33344 |  | 2026-10-03 07:20 | 14.027 | 14.404 | 2.5 | 2.4007 | 1.9615 | 0.43918 | 11.7689 | 1.7 | 1.9334 | -0.23344 |  | 2026-10-03 07:20 | 13.383 | 14.217 | 2.4 | 2.3695 | 1.9615 | 0.40801 | 11.7689 | 1.6 | 1.9334 | -0.33344 |  | 2026-10-03 07:20 | 10.187 | 10.527 | 1.5 | 1.7545 | 1.453 | 0.30154 | 8.7177 | 1.2 | 1.4322 | -0.23218 |  | 2026-10-03 07:20 | 9.924 | 10.252 | 1.5 | 1.7087 | 1.453 | 0.25571 | 8.7177 | 1.2 | 1.4322 | -0.23218 |  | 2026-10-03 07:20 | 10.491 | 10.836 | 1.6 | 1.806 | 1.453 | 0.35304 | 8.7177 | 1.3 | 1.4322 | -0.13218 |  | 2026-10-03 07:20 | 10.727 | 11.377 | 1.8 | 1.8962 | 1.453 | 0.44321 | 8.7177 | 1.2 | 1.4322 | -0.23218 |  |  | 2026-10-03 07:20 | 9.481 | 9.804 | 1.4 | 1.634 | 1.3823 | 0.25169 | 8.2938 | 1.1 | 1.3625 | -0.26254 |  |  |  | 2026-10-03 07:20 | 18.2553 | 15.0401 | 3.2152 | 90.2405 | 12.6 | 14.825 | -2.225
2026-10-03 07:10 | 17 | 12.91 | 6.763 | 7.041 | 0.8 | 1.1735 | 1.151 | 0.02254 | 6.9058 | 0.7 | 1.1345 | -0.4345 |  | 2026-10-03 07:10 | 6.468 | 7.188 | 0.8 | 1.198 | 1.151 | 0.04704 | 6.9058 | 0.7 | 1.1345 | -0.4345 |  | 2026-10-03 07:10 | 6.622 | 6.896 | 0.8 | 1.1493 | 1.151 | -0.0016265 | 6.9058 | 0.7 | 1.1345 | -0.4345 |  | 2026-10-03 07:10 | 6.501 | 7.309 | 0.8 | 1.2182 | 1.151 | 0.067207 | 6.9058 | 0.7 | 1.1345 | -0.4345 |  | 2026-10-03 07:10 | 4.77 | 5.105 | 0.3 | 0.85083 | 0.85256 | -0.0017295 | 5.1154 | 0.3 | 0.84037 | -0.54037 |  | 2026-10-03 07:10 | 4.506 | 4.707 | 0.3 | 0.7845 | 0.85256 | -0.068063 | 5.1154 | 0.3 | 0.84037 | -0.54037 |  | 2026-10-03 07:10 | 4.92 | 5.137 | 0.3 | 0.85617 | 0.85256 | 0.0036038 | 5.1154 | 0.3 | 0.84037 | -0.54037 |  | 2026-10-03 07:10 | 5.007 | 5.582 | 0.6 | 0.93033 | 0.85256 | 0.07777 | 5.1154 | 0.6 | 0.84037 | -0.24037 |  |  | 2026-10-03 07:10 | 4.511 | 4.715 | 0.3 | 0.78583 | 0.81111 | -0.025275 | 4.8666 | 0.3 | 0.79951 | -0.49951 |  |  |  | 2026-10-03 07:10 | 8.9467 | 8.8252 | 0.12147 | 52.9512 | 4.6 | 8.699 | -4.099
2026-10-03 07:00 | 5 | 12.34 | 2.174 | 2.286 | 0.1 | 0.381 | 0.33917 | 0.041834 | 2.035 | 0.1 | 0.33432 | -0.23432 |  | 2026-10-03 07:00 | 2.225 | 2.783 | 0.1 | 0.46383 | 0.33917 | 0.12467 | 2.035 | 0.1 | 0.33432 | -0.23432 |  | 2026-10-03 07:00 | 2.175 | 2.287 | 0.1 | 0.38117 | 0.33917 | 0.042001 | 2.035 | 0.1 | 0.33432 | -0.23432 |  | 2026-10-03 07:00 | 2.232 | 3.09 | 0.1 | 0.515 | 0.33917 | 0.17583 | 2.035 | 0.1 | 0.33432 | -0.23432 |  | 2026-10-03 07:00 | 0 | 0 | 0 | 0 | 0.25123 | -0.25123 | 1.5074 | 0 | 0.24764 | -0.24764 |  | 2026-10-03 07:00 | 0 | 0 | 0 | 0 | 0.25123 | -0.25123 | 1.5074 | 0 | 0.24764 | -0.24764 |  | 2026-10-03 07:00 | 0 | 0 | 0 | 0 | 0.25123 | -0.25123 | 1.5074 | 0 | 0.24764 | -0.24764 |  | 2026-10-03 07:00 | 1.486 | 2.082 | 0 | 0.347 | 0.25123 | 0.095766 | 1.5074 | 0 | 0.24764 | -0.24764 |  |  | 2026-10-03 07:00 | 0 | 0 | 0 | 0 | 0.23902 | -0.23902 | 1.4341 | 0 | 0.2356 | -0.2356 |  |  |  | 2026-10-03 07:00 | 2.088 | 2.6006 | -0.51261 | 15.6037 | 0.4 | 2.5634 | -2.1634
[113 empty] | Total: - | 18847.2098 | 19760.5421 | -913.3322 |  | 18623.9 | 19477.9663 | -854.0663
Sum:- | 43225 |  | 14503.487 |  | 89315.1 |  |  |  |  | 2426.3 | 2540.2665 | -113.9665 | 0.98332 |  | 14013.876 |  | 90102.5 |  |  |  |  | 2451.7 | 2540.2665 | -88.5665 | 0.98391 |  | 14444.56 |  | 90853.9 |  |  |  |  | 2406.9 | 2540.2665 | -133.3665 | 0.97258 |  | 14572.812 |  | 91902.1 |  |  |  |  | 2430.7 | 2540.2665 | -109.5665 | 0.98303 |  | 10869.955 |  | 68346.9 |  |  |  |  | 1811.6 | 1881.6789 | -70.0789 | 0.9844 |  | 10767.272 |  | 67956.5 |  |  |  |  | 1794.9 | 1881.6789 | -86.7789 | 0.9816 |  | 10757.867 |  | 67850.1 |  |  |  |  | 1792.7 | 1881.6789 | -88.9789 | 0.98109 |  | 10817.434 |  | 68363 |  |  |  |  | 1802.8 | 1881.6789 | -78.8789 | 0.97147 |  |  | 10237.221 |  | 64700 |  |  |  |  | 1706.3 | 1790.1844 | -83.8844 | 0.98466
Formulas:
Time 14 = [Time]

## 11 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-11-03 19:00 | 0 | 38.46 | 0.082 | 0.097 | 2420.1 | 0.016167 | 0 | 0.016167 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.09 | 0.163 | 2445 | 0.027167 | 0 | 0.027167 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.093 | 0.098 | 2405.9 | 0.016333 | 0 | 0.016333 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.061 | 0.065 | 2425.5 | 0.010833 | 0 | 0.010833 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.058 | 0.075 | 1814.9 | 0.0125 | 0 | 0.0125 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.087 | 0.091 | 1791 | 0.015167 | 0 | 0.015167 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.083 | 0.077 | 1792 | 0.012833 | 0 | 0.012833 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.072 | 0.076 | 1799.1 | 0.012667 | 0 | 0.012667 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.067 | 0.096 | 1699.3 | 0.016 | 0 | 0.016 | 0 | 0 | 0 | 0 |  | 2026-11-03 19:00 | 0.13967 | 0 | 0.13967 | 0 | 0 | 0 | 0 | 1 | 98.29%
2026-11-03 18:50 | 0 | 39.61 | 0.057 | 0.075 | 2420.1 | 0.0125 | 0 | 0.0125 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.22 | 0.597 | 2445 | 0.0995 | 0 | 0.0995 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.043 | 0.071 | 2405.9 | 0.011833 | 0 | 0.011833 | 0 | 0.2 | 0 | 0.2 |  | 2026-11-03 18:50 | 0.066 | 0.566 | 2425.5 | 0.094333 | 0 | 0.094333 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.001 | 0.108 | 1814.8 | 0.018 | 0 | 0.018 | 0 | 0 | 0 | 0 |  | 2026-11-03 18:50 | 0.09 | 0.09 | 1791 | 0.015 | 0 | 0.015 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.083 | 0.09 | 1792 | 0.015 | 0 | 0.015 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.007 | 0.338 | 1799.1 | 0.056333 | 0 | 0.056333 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.104 | 0.086 | 1699.3 | 0.014333 | 0 | 0.014333 | 0 | 0.1 | 0 | 0.1 |  | 2026-11-03 18:50 | 0.33683 | 0 | 0.33683 | 0 | 0.9 | 0 | 0.9 | 2 | 98.29%
2026-11-03 18:40 | 1 | 40.18 | 2.008 | 2.111 | 2420 | 0.35183 | 0.061504 | 0.29033 | 0.36902 | 0.7 | 0.060624 | 0.63938 |  | 2026-11-03 18:40 | 2.42 | 2.691 | 2444.9 | 0.4485 | 0.061504 | 0.387 | 0.36902 | 0.8 | 0.060624 | 0.73938 |  | 2026-11-03 18:40 | 2.075 | 2.19 | 2405.7 | 0.365 | 0.061504 | 0.3035 | 0.36902 | 0.7 | 0.060624 | 0.63938 |  | 2026-11-03 18:40 | 2.119 | 2.591 | 2425.4 | 0.43183 | 0.061504 | 0.37033 | 0.36902 | 0.7 | 0.060624 | 0.63938 |  | 2026-11-03 18:40 | 1.384 | 1.455 | 1814.8 | 0.2425 | 0.045558 | 0.19694 | 0.27335 | 0.5 | 0.044907 | 0.45509 |  | 2026-11-03 18:40 | 1.262 | 1.327 | 1790.9 | 0.22117 | 0.045558 | 0.17561 | 0.27335 | 0.4 | 0.044907 | 0.35509 |  | 2026-11-03 18:40 | 1.333 | 1.402 | 1791.9 | 0.23367 | 0.045558 | 0.18811 | 0.27335 | 0.5 | 0.044907 | 0.45509 |  | 2026-11-03 18:40 | 1.45 | 1.78 | 1799 | 0.29667 | 0.045558 | 0.25111 | 0.27335 | 0.5 | 0.044907 | 0.45509 |  | 2026-11-03 18:40 | 1.252 | 1.316 | 1699.2 | 0.21933 | 0.043343 | 0.17599 | 0.26006 | 0.4 | 0.042723 | 0.35728 |  | 2026-11-03 18:40 | 2.8105 | 0.47159 | 2.3389 | 2.8296 | 5.2 | 0.46485 | 4.7352 | 3 | 97.25%
2026-11-03 18:30 | 13 | 42.19 | 6.442 | 6.736 | 2419.3 | 1.1227 | 0.79361 | 0.32906 | 4.7617 | 1.7 | 0.78226 | 0.91774 |  | 2026-11-03 18:30 | 6.873 | 7.326 | 2444.1 | 1.221 | 0.79361 | 0.42739 | 4.7617 | 1.6 | 0.78226 | 0.81774 |  | 2026-11-03 18:30 | 6.622 | 6.919 | 2405 | 1.1532 | 0.79361 | 0.35956 | 4.7617 | 1.5 | 0.78226 | 0.71774 |  | 2026-11-03 18:30 | 6.687 | 6.989 | 2424.7 | 1.1648 | 0.79361 | 0.37122 | 4.7617 | 1.6 | 0.78226 | 0.81774 |  | 2026-11-03 18:30 | 4.79 | 5.025 | 1814.3 | 0.8375 | 0.58786 | 0.24964 | 3.5272 | 1.2 | 0.57945 | 0.62055 |  | 2026-11-03 18:30 | 4.39 | 4.606 | 1790.5 | 0.76767 | 0.58786 | 0.17981 | 3.5272 | 1.1 | 0.57945 | 0.52055 |  | 2026-11-03 18:30 | 4.663 | 4.891 | 1791.4 | 0.81517 | 0.58786 | 0.22731 | 3.5272 | 1.1 | 0.57945 | 0.52055 |  | 2026-11-03 18:30 | 4.559 | 5.002 | 1798.5 | 0.83367 | 0.58786 | 0.24581 | 3.5272 | 1.1 | 0.57945 | 0.52055 |  | 2026-11-03 18:30 | 4.285 | 4.498 | 1698.8 | 0.74967 | 0.55928 | 0.19039 | 3.3557 | 1 | 0.55128 | 0.44872 |  | 2026-11-03 18:30 | 8.6653 | 6.0852 | 2.5802 | 36.5109 | 11.9 | 5.9981 | 5.9019 | 4 | 98.3%
2026-11-03 18:20 | 27 | 44.77 | 13.389 | 13.814 | 2417.6 | 2.3023 | 1.6324 | 0.6699 | 9.7946 | 2.5 | 1.6091 | 0.89091 |  | 2026-11-03 18:20 | 13.968 | 14.397 | 2442.5 | 2.3995 | 1.6324 | 0.76707 | 9.7946 | 2.8 | 1.6091 | 1.1909 |  | 2026-11-03 18:20 | 13.103 | 13.529 | 2403.5 | 2.2548 | 1.6324 | 0.6224 | 9.7946 | 2.8 | 1.6091 | 1.1909 |  | 2026-11-03 18:20 | 13.201 | 13.655 | 2423.1 | 2.2758 | 1.6324 | 0.6434 | 9.7946 | 2.8 | 1.6091 | 1.1909 |  | 2026-11-03 18:20 | 9.663 | 10.031 | 1813.1 | 1.6718 | 1.2092 | 0.46263 | 7.2552 | 2 | 1.1919 | 0.80808 |  | 2026-11-03 18:20 | 9.339 | 9.698 | 1789.4 | 1.6163 | 1.2092 | 0.40713 | 7.2552 | 2 | 1.1919 | 0.80808 |  | 2026-11-03 18:20 | 9.435 | 9.799 | 1790.3 | 1.6332 | 1.2092 | 0.42396 | 7.2552 | 2 | 1.1919 | 0.80808 |  | 2026-11-03 18:20 | 8.268 | 8.675 | 1797.4 | 1.4458 | 1.2092 | 0.23663 | 7.2552 | 1.6 | 1.1919 | 0.40808 |  | 2026-11-03 18:20 | 8.369 | 8.711 | 1697.8 | 1.4518 | 1.1504 | 0.30142 | 6.9025 | 1.8 | 1.134 | 0.66604 |  | 2026-11-03 18:20 | 17.0515 | 12.517 | 4.5345 | 75.1018 | 20.3 | 12.338 | 7.962 | 5 | 98.44%
2026-11-03 18:10 | 42 | 46.49 | 20.657 | 21.163 | 2415.1 | 3.5272 | 2.5229 | 1.0043 | 15.1375 | 4.3 | 2.4868 | 1.8132 |  | 2026-11-03 18:10 | 22.035 | 22.563 | 2439.7 | 3.7605 | 2.5229 | 1.2376 | 15.1375 | 4.4 | 2.4868 | 1.9132 |  | 2026-11-03 18:10 | 21.293 | 21.803 | 2400.7 | 3.6338 | 2.5229 | 1.1109 | 15.1375 | 4.4 | 2.4868 | 1.9132 |  | 2026-11-03 18:10 | 21.224 | 21.737 | 2420.3 | 3.6228 | 2.5229 | 1.0999 | 15.1375 | 4.3 | 2.4868 | 1.8132 |  | 2026-11-03 18:10 | 15.916 | 16.343 | 1811.1 | 2.7238 | 1.8688 | 0.85501 | 11.2129 | 3.3 | 1.8421 | 1.4579 |  | 2026-11-03 18:10 | 15.304 | 15.717 | 1787.4 | 2.6195 | 1.8688 | 0.75068 | 11.2129 | 3.1 | 1.8421 | 1.2579 |  | 2026-11-03 18:10 | 15.38 | 15.794 | 1788.3 | 2.6323 | 1.8688 | 0.76351 | 11.2129 | 3.2 | 1.8421 | 1.3579 |  | 2026-11-03 18:10 | 12.924 | 13.694 | 1795.8 | 2.2823 | 1.8688 | 0.41351 | 11.2129 | 2.8 | 1.8421 | 0.9579 |  | 2026-11-03 18:10 | 13.794 | 14.21 | 1696 | 2.3683 | 1.778 | 0.59038 | 10.6677 | 2.9 | 1.7525 | 1.1475 |  | 2026-11-03 18:10 | 27.1707 | 19.3449 | 7.8258 | 116.0694 | 32.7 | 19.0683 | 13.6317 | 6 | 98.13%
2026-11-03 18:00 | 51 | 47.64 | 27.976 | 28.489 | 2410.8 | 4.7482 | 3.0502 | 1.698 | 18.3012 | 6.1 | 3.0066 | 3.0934 |  | 2026-11-03 18:00 | 28.922 | 29.515 | 2435.3 | 4.9192 | 3.0502 | 1.869 | 18.3012 | 6.3 | 3.0066 | 3.2934 |  | 2026-11-03 18:00 | 28.814 | 29.399 | 2396.3 | 4.8998 | 3.0502 | 1.8496 | 18.3012 | 6.2 | 3.0066 | 3.1934 |  | 2026-11-03 18:00 | 28.071 | 29.117 | 2416 | 4.8528 | 3.0502 | 1.8026 | 18.3012 | 6.2 | 3.0066 | 3.1934 |  | 2026-11-03 18:00 | 21.177 | 21.68 | 1807.8 | 3.6133 | 2.2594 | 1.3539 | 13.5565 | 4.7 | 2.2271 | 2.4729 |  | 2026-11-03 18:00 | 20.288 | 20.758 | 1784.3 | 3.4597 | 2.2594 | 1.2003 | 13.5565 | 4.5 | 2.2271 | 2.2729 |  | 2026-11-03 18:00 | 20.471 | 20.972 | 1785.1 | 3.4953 | 2.2594 | 1.2359 | 13.5565 | 4.5 | 2.2271 | 2.2729 |  | 2026-11-03 18:00 | 18.661 | 19.335 | 1793 | 3.2225 | 2.2594 | 0.96309 | 13.5565 | 4.3 | 2.2271 | 2.0729 |  | 2026-11-03 18:00 | 19.023 | 19.458 | 1693.1 | 3.243 | 2.1495 | 1.0935 | 12.8973 | 4.2 | 2.1188 | 2.0812 |  | 2026-11-03 18:00 | 36.4538 | 23.388 | 13.0658 | 140.328 | 47 | 23.0536 | 23.9464 | 7 | 98.06%
2026-11-03 17:50 | 135 | 47.93 | 44.492 | 45.243 | 2404.7 | 7.5405 | 8.0652 | -0.52467 | 48.391 | 8.9 | 7.9498 | 0.95016 |  | 2026-11-03 17:50 | 45.868 | 46.638 | 2429 | 7.773 | 8.0652 | -0.29217 | 48.391 | 9.5 | 7.9498 | 1.5502 |  | 2026-11-03 17:50 | 45.592 | 46.343 | 2390.1 | 7.7238 | 8.0652 | -0.34134 | 48.391 | 9 | 7.9498 | 1.0502 |  | 2026-11-03 17:50 | 45.26 | 46.019 | 2409.8 | 7.6698 | 8.0652 | -0.39534 | 48.391 | 9 | 7.9498 | 1.0502 |  | 2026-11-03 17:50 | 34.123 | 34.745 | 1803.1 | 5.7908 | 5.9742 | -0.18337 | 35.8452 | 6.7 | 5.8888 | 0.81123 |  | 2026-11-03 17:50 | 32.828 | 33.426 | 1779.8 | 5.571 | 5.9742 | -0.4032 | 35.8452 | 6.4 | 5.8888 | 0.51123 |  | 2026-11-03 17:50 | 33.029 | 33.631 | 1780.6 | 5.6052 | 5.9742 | -0.36903 | 35.8452 | 6.4 | 5.8888 | 0.51123 |  | 2026-11-03 17:50 | 32.12 | 33.251 | 1788.7 | 5.5418 | 5.9742 | -0.43237 | 35.8452 | 6.3 | 5.8888 | 0.41123 |  | 2026-11-03 17:50 | 30.714 | 31.283 | 1688.9 | 5.2138 | 5.6837 | -0.46988 | 34.1023 | 6 | 5.6024 | 0.39757 |  | 2026-11-03 17:50 | 58.4298 | 61.8412 | -3.4114 | 371.0471 | 68.2 | 60.9569 | 7.2431 | 8 | 97.16%
2026-11-03 17:40 | 187 | 47.93 | 61.354 | 61.571 | 2395.8 | 10.2618 | 11.1718 | -0.90992 | 67.0305 | 11.1 | 11.012 | 0.088003 |  | 2026-11-03 17:40 | 62.632 | 63.515 | 2419.5 | 10.5858 | 11.1718 | -0.58592 | 67.0305 | 11.3 | 11.012 | 0.288 |  | 2026-11-03 17:40 | 61.426 | 62.286 | 2381.1 | 10.381 | 11.1718 | -0.79075 | 67.0305 | 11.5 | 11.012 | 0.488 |  | 2026-11-03 17:40 | 61.117 | 61.985 | 2400.8 | 10.3308 | 11.1718 | -0.84092 | 67.0305 | 11.4 | 11.012 | 0.388 |  | 2026-11-03 17:40 | 45.945 | 46.703 | 1796.4 | 7.7838 | 8.2754 | -0.49154 | 49.6522 | 8.5 | 8.157 | 0.34297 |  | 2026-11-03 17:40 | 44.473 | 45.196 | 1773.4 | 7.5327 | 8.2754 | -0.74271 | 49.6522 | 8.3 | 8.157 | 0.14297 |  | 2026-11-03 17:40 | 44.713 | 45.449 | 1774.2 | 7.5748 | 8.2754 | -0.70054 | 49.6522 | 8.4 | 8.157 | 0.24297 |  | 2026-11-03 17:40 | 43.227 | 44.63 | 1782.4 | 7.4383 | 8.2754 | -0.83704 | 49.6522 | 8.2 | 8.157 | 0.042965 |  | 2026-11-03 17:40 | 41.837 | 42.548 | 1682.9 | 7.0913 | 7.873 | -0.78166 | 47.238 | 7.7 | 7.7604 | -0.060408 |  | 2026-11-03 17:40 | 78.9805 | 85.6615 | -6.681 | 513.969 | 86.4 | 84.4365 | 1.9635 | 9 | 98.46%
2026-11-03 17:30 | 231 | 47.93 | 75.757 | 76.755 | 2384.7 | 12.7925 | 13.8004 | -1.0079 | 82.8024 | 13.5 | 13.6031 | -0.10305 |  | 2026-11-03 17:30 | 77.558 | 78.595 | 2408.2 | 13.0992 | 13.8004 | -0.70123 | 82.8024 | 13.2 | 13.6031 | -0.40305 |  | 2026-11-03 17:30 | 76.889 | 78.106 | 2369.6 | 13.0177 | 13.8004 | -0.78273 | 82.8024 | 13.5 | 13.6031 | -0.10305 |  | 2026-11-03 17:30 | 76.606 | 77.631 | 2389.4 | 12.9385 | 13.8004 | -0.8619 | 82.8024 | 13.5 | 13.6031 | -0.10305 |  | 2026-11-03 17:30 | 57.49 | 58.348 | 1787.9 | 9.7247 | 10.2225 | -0.49785 | 61.3351 | 10.1 | 10.0763 | 0.023663 |  | 2026-11-03 17:30 | 55.741 | 56.567 | 1765.1 | 9.4278 | 10.2225 | -0.79469 | 61.3351 | 9.8 | 10.0763 | -0.27634 |  | 2026-11-03 17:30 | 55.574 | 56.409 | 1765.8 | 9.4015 | 10.2225 | -0.82102 | 61.3351 | 9.8 | 10.0763 | -0.27634 |  | 2026-11-03 17:30 | 55.37 | 57.098 | 1774.2 | 9.5163 | 10.2225 | -0.70619 | 61.3351 | 9.8 | 10.0763 | -0.27634 |  | 2026-11-03 17:30 | 52.268 | 53.075 | 1675.2 | 8.8458 | 9.7255 | -0.87963 | 58.3528 | 9.1 | 9.5864 | -0.48639 |  | 2026-11-03 17:30 | 98.764 | 105.8171 | -7.0531 | 634.9028 | 102.3 | 104.304 | -2.004
2026-11-03 17:20 | 281 | 47.93 | 94.563 | 95.712 | 2371.2 | 15.952 | 16.7875 | -0.8355 | 100.725 | 16.3 | 16.5474 | -0.24744 |  | 2026-11-03 17:20 | 95.503 | 96.712 | 2395 | 16.1187 | 16.7875 | -0.66883 | 100.725 | 17.4 | 16.5474 | 0.85256 |  | 2026-11-03 17:20 | 95.06 | 96.608 | 2356.1 | 16.1013 | 16.7875 | -0.68617 | 100.725 | 16.5 | 16.5474 | -0.047439 |  | 2026-11-03 17:20 | 94.838 | 96.029 | 2375.9 | 16.0048 | 16.7875 | -0.78267 | 100.725 | 16.4 | 16.5474 | -0.14744 |  | 2026-11-03 17:20 | 71.273 | 72.241 | 1777.8 | 12.0402 | 12.4352 | -0.39502 | 74.6111 | 12.3 | 12.2574 | 0.042638 |  | 2026-11-03 17:20 | 69.083 | 70.014 | 1755.3 | 11.669 | 12.4352 | -0.76619 | 74.6111 | 12 | 12.2574 | -0.25736 |  | 2026-11-03 17:20 | 69.551 | 70.503 | 1756 | 11.7505 | 12.4352 | -0.68469 | 74.6111 | 12 | 12.2574 | -0.25736 |  | 2026-11-03 17:20 | 69.008 | 70.957 | 1764.4 | 11.8262 | 12.4352 | -0.60902 | 74.6111 | 12.1 | 12.2574 | -0.15736 |  | 2026-11-03 17:20 | 64.804 | 65.755 | 1666.1 | 10.9592 | 11.8305 | -0.87137 | 70.9832 | 11.4 | 11.6614 | -0.26136 |  | 2026-11-03 17:20 | 122.4218 | 128.7213 | -6.2994 | 772.3277 | 126.4 | 126.8806 | -0.48057
2026-11-03 17:10 | 269 | 47.93 | 89.166 | 90.16 | 2354.9 | 15.0267 | 16.0706 | -1.0439 | 96.4236 | 18.2 | 15.8408 | 2.3592 |  | 2026-11-03 17:10 | 85.137 | 86.293 | 2377.6 | 14.3822 | 16.0706 | -1.6884 | 96.4236 | 18.5 | 15.8408 | 2.6592 |  | 2026-11-03 17:10 | 90.158 | 92.307 | 2339.6 | 15.3845 | 16.0706 | -0.6861 | 96.4236 | 18 | 15.8408 | 2.1592 |  | 2026-11-03 17:10 | 90.01 | 91.168 | 2359.5 | 15.1947 | 16.0706 | -0.87593 | 96.4236 | 18.1 | 15.8408 | 2.2592 |  | 2026-11-03 17:10 | 68.573 | 69.533 | 1765.5 | 11.5888 | 11.9041 | -0.31531 | 71.4249 | 13.6 | 11.7339 | 1.8661 |  | 2026-11-03 17:10 | 66.884 | 67.799 | 1743.3 | 11.2998 | 11.9041 | -0.60431 | 71.4249 | 13.1 | 11.7339 | 1.3661 |  | 2026-11-03 17:10 | 68.752 | 69.337 | 1744 | 11.5562 | 11.9041 | -0.34798 | 71.4249 | 13.2 | 11.7339 | 1.4661 |  | 2026-11-03 17:10 | 65.25 | 67.109 | 1752.3 | 11.1848 | 11.9041 | -0.71931 | 71.4249 | 13 | 11.7339 | 1.2661 |  | 2026-11-03 17:10 | 61.33 | 61.844 | 1654.7 | 10.3073 | 11.3253 | -1.018 | 67.9519 | 12.4 | 11.1634 | 1.2366 |  | 2026-11-03 17:10 | 115.925 | 123.2243 | -7.2993 | 739.3457 | 138.1 | 121.4622 | 16.6378
2026-11-03 17:00 | 372 | 48.5 | 127.509 | 129.318 | 2336.7 | 21.553 | 22.1758 | -0.62282 | 133.0549 | 21.9 | 21.8587 | 0.041298 |  | 2026-11-03 17:00 | 131.239 | 132.968 | 2359.1 | 22.1613 | 22.1758 | -0.014482 | 133.0549 | 21.7 | 21.8587 | -0.1587 |  | 2026-11-03 17:00 | 127.218 | 129.73 | 2321.6 | 21.6217 | 22.1758 | -0.55415 | 133.0549 | 22.3 | 21.8587 | 0.4413 |  | 2026-11-03 17:00 | 127.602 | 129.27 | 2341.4 | 21.545 | 22.1758 | -0.63082 | 133.0549 | 22.3 | 21.8587 | 0.4413 |  | 2026-11-03 17:00 | 95.519 | 96.748 | 1751.9 | 16.1247 | 16.4265 | -0.30186 | 98.5592 | 17 | 16.1916 | 0.80837 |  | 2026-11-03 17:00 | 92.965 | 94.132 | 1730.2 | 15.6887 | 16.4265 | -0.73786 | 98.5592 | 16.6 | 16.1916 | 0.40837 |  | 2026-11-03 17:00 | 93.131 | 94.319 | 1730.8 | 15.7198 | 16.4265 | -0.7067 | 98.5592 | 16.7 | 16.1916 | 0.50837 |  | 2026-11-03 17:00 | 93.491 | 95.297 | 1739.3 | 15.8828 | 16.4265 | -0.5437 | 98.5592 | 16.6 | 16.1916 | 0.40837 |  | 2026-11-03 17:00 | 88.082 | 89.233 | 1642.3 | 14.8722 | 15.6278 | -0.75564 | 93.7669 | 15.5 | 15.4043 | 0.095669 |  | 2026-11-03 17:00 | 165.1692 | 170.0372 | -4.868 | 1020.2232 | 170.6 | 167.6057 | 2.9943
2026-11-03 16:50 | 424 | 48.5 | 144.352 | 146.224 | 2314.8 | 24.3707 | 25.2757 | -0.90499 | 151.654 | 52.8 | 24.9142 | 27.8858 |  | 2026-11-03 16:50 | 146.664 | 148.656 | 2337.4 | 24.776 | 25.2757 | -0.49966 | 151.654 | 25.6 | 24.9142 | 0.68578 |  | 2026-11-03 16:50 | 145.521 | 148.625 | 2299.3 | 24.7708 | 25.2757 | -0.50483 | 151.654 | 25.3 | 24.9142 | 0.38578 |  | 2026-11-03 16:50 | 145.921 | 147.888 | 2319.1 | 24.648 | 25.2757 | -0.62766 | 151.654 | 25.4 | 24.9142 | 0.48578 |  | 2026-11-03 16:50 | 109.186 | 110.635 | 1734.9 | 18.4392 | 18.7227 | -0.28355 | 112.3363 | 18.8 | 18.455 | 0.34502 |  | 2026-11-03 16:50 | 106.677 | 108.049 | 1713.6 | 18.0082 | 18.7227 | -0.71455 | 112.3363 | 18.3 | 18.455 | -0.15498 |  | 2026-11-03 16:50 | 105.871 | 107.223 | 1714.1 | 17.8705 | 18.7227 | -0.85221 | 112.3363 | 18.2 | 18.455 | -0.25498 |  | 2026-11-03 16:50 | 106.627 | 109.894 | 1722.7 | 18.3157 | 18.7227 | -0.40705 | 112.3363 | 18.5 | 18.455 | 0.045023 |  | 2026-11-03 16:50 | 100.413 | 101.725 | 1626.8 | 16.9542 | 17.8123 | -0.85817 | 106.874 | 17.5 | 17.5576 | -0.057625 |  | 2026-11-03 16:50 | 188.1532 | 193.8058 | -5.6527 | 1162.835 | 220.4 | 191.0344 | 29.3656
2026-11-03 16:40 | 465 | 48.79 | 159.213 | 161.908 | 2289.2 | 26.9847 | 27.6891 | -0.70445 | 166.1347 | 0 | 27.2932 | -27.2932 |  | 2026-11-03 16:40 | 161.708 | 163.904 | 2311.8 | 27.3173 | 27.6891 | -0.37178 | 166.1347 | 27.8 | 27.2932 | 0.50684 |  | 2026-11-03 16:40 | 159.632 | 162.997 | 2274 | 27.1662 | 27.6891 | -0.52295 | 166.1347 | 27.5 | 27.2932 | 0.20684 |  | 2026-11-03 16:40 | 160.11 | 162.285 | 2293.7 | 27.0475 | 27.6891 | -0.64161 | 166.1347 | 27.5 | 27.2932 | 0.20684 |  | 2026-11-03 16:40 | 119.85 | 121.416 | 1716.1 | 20.236 | 20.5105 | -0.27445 | 123.0627 | 21 | 20.2172 | 0.78285 |  | 2026-11-03 16:40 | 117.165 | 118.708 | 1695.3 | 19.7847 | 20.5105 | -0.72579 | 123.0627 | 20.5 | 20.2172 | 0.28285 |  | 2026-11-03 16:40 | 116.994 | 118.511 | 1695.9 | 19.7518 | 20.5105 | -0.75862 | 123.0627 | 20.6 | 20.2172 | 0.38285 |  | 2026-11-03 16:40 | 116.935 | 120.14 | 1704.2 | 20.0233 | 20.5105 | -0.48712 | 123.0627 | 20.2 | 20.2172 | -0.017154 |  | 2026-11-03 16:40 | 110.382 | 111.836 | 1609.3 | 18.6393 | 19.5132 | -0.87382 | 117.0789 | 19 | 19.2341 | -0.23412 |  | 2026-11-03 16:40 | 206.9508 | 212.3114 | -5.3606 | 1273.8685 | 184.1 | 209.2754 | -25.1754
2026-11-03 16:30 | 506 | 48.5 | 174.027 | 176.373 | 2262 | 29.3955 | 30.1639 | -0.76838 | 180.9833 | 31 | 29.7325 | 1.2675 |  | 2026-11-03 16:30 | 176.322 | 178.771 | 2284 | 29.7952 | 30.1639 | -0.36871 | 180.9833 | 30.6 | 29.7325 | 0.86746 |  | 2026-11-03 16:30 | 174.348 | 178.107 | 2246.5 | 29.6845 | 30.1639 | -0.47938 | 180.9833 | 30.2 | 29.7325 | 0.46746 |  | 2026-11-03 16:30 | 174.787 | 177.215 | 2266.2 | 29.5358 | 30.1639 | -0.62805 | 180.9833 | 30.4 | 29.7325 | 0.66746 |  | 2026-11-03 16:30 | 131.316 | 133.046 | 1695.1 | 22.1743 | 22.3436 | -0.16928 | 134.0617 | 22.4 | 22.0241 | 0.3759 |  | 2026-11-03 16:30 | 128.207 | 129.896 | 1674.8 | 21.6493 | 22.3436 | -0.69428 | 134.0617 | 22.3 | 22.0241 | 0.2759 |  | 2026-11-03 16:30 | 128.499 | 130.191 | 1675.3 | 21.6985 | 22.3436 | -0.64511 | 134.0617 | 22.3 | 22.0241 | 0.2759 |  | 2026-11-03 16:30 | 128.244 | 131.434 | 1684 | 21.9057 | 22.3436 | -0.43795 | 134.0617 | 22.2 | 22.0241 | 0.1759 |  | 2026-11-03 16:30 | 120.87 | 122.487 | 1590.3 | 20.4145 | 21.2572 | -0.84268 | 127.5431 | 21 | 20.9532 | 0.046797 |  | 2026-11-03 16:30 | 226.2533 | 231.2871 | -5.0338 | 1387.7229 | 232.4 | 227.9797 | 4.4203
2026-11-03 16:20 | 555 | 48.79 | 189.033 | 191.678 | 2231 | 31.9463 | 33.0483 | -1.102 | 198.2898 | 32.3 | 32.5757 | -0.27571 |  | 2026-11-03 16:20 | 191.877 | 194.495 | 2253.4 | 32.4158 | 33.0483 | -0.63246 | 198.2898 | 33.1 | 32.5757 | 0.52429 |  | 2026-11-03 16:20 | 190.259 | 194.875 | 2216.3 | 32.4792 | 33.0483 | -0.56913 | 198.2898 | 32.7 | 32.5757 | 0.12429 |  | 2026-11-03 16:20 | 191.888 | 194.613 | 2235.8 | 32.4355 | 33.0483 | -0.6128 | 198.2898 | 32.8 | 32.5757 | 0.22429 |  | 2026-11-03 16:20 | 143.396 | 145.344 | 1672.7 | 24.224 | 24.4802 | -0.25622 | 146.8813 | 24.6 | 24.1302 | 0.46985 |  | 2026-11-03 16:20 | 140.803 | 142.837 | 1652.5 | 23.8062 | 24.4802 | -0.67405 | 146.8813 | 23.7 | 24.1302 | -0.43015 |  | 2026-11-03 16:20 | 140.735 | 142.808 | 1653 | 23.8013 | 24.4802 | -0.67889 | 146.8813 | 23.7 | 24.1302 | -0.43015 |  | 2026-11-03 16:20 | 140.797 | 144.612 | 1661.8 | 24.102 | 24.4802 | -0.37822 | 146.8813 | 23.8 | 24.1302 | -0.33015 |  | 2026-11-03 16:20 | 132.932 | 134.724 | 1569.3 | 22.454 | 23.2899 | -0.8359 | 139.7394 | 22.4 | 22.9569 | -0.55685 |  | 2026-11-03 16:20 | 247.6643 | 253.404 | -5.7396 | 1520.4237 | 249.1 | 249.7803 | -0.68028
2026-11-03 16:10 | 597 | 48.79 | 205.646 | 208.545 | 2198.7 | 34.7575 | 35.5492 | -0.79175 | 213.2955 | 33.8 | 35.0409 | -1.2409 |  | 2026-11-03 16:10 | 208.106 | 211.125 | 2220.3 | 35.1875 | 35.5492 | -0.36175 | 213.2955 | 36.3 | 35.0409 | 1.2591 |  | 2026-11-03 16:10 | 205.439 | 210.401 | 2183.6 | 35.0668 | 35.5492 | -0.48241 | 213.2955 | 34.4 | 35.0409 | -0.64089 |  | 2026-11-03 16:10 | 206.459 | 209.454 | 2203 | 34.909 | 35.5492 | -0.64025 | 213.2955 | 34.5 | 35.0409 | -0.54089 |  | 2026-11-03 16:10 | 154.796 | 156.867 | 1648.1 | 26.1445 | 26.3328 | -0.18828 | 157.9967 | 25.9 | 25.9562 | -0.056217 |  | 2026-11-03 16:10 | 151.347 | 153.461 | 1628.8 | 25.5768 | 26.3328 | -0.75594 | 157.9967 | 25.3 | 25.9562 | -0.65622 |  | 2026-11-03 16:10 | 151.466 | 153.549 | 1629.3 | 25.5915 | 26.3328 | -0.74128 | 157.9967 | 25.8 | 25.9562 | -0.15622 |  | 2026-11-03 16:10 | 151.431 | 155.985 | 1638 | 25.9975 | 26.3328 | -0.33528 | 157.9967 | 25.3 | 25.9562 | -0.65622 |  | 2026-11-03 16:10 | 142.725 | 144.664 | 1546.9 | 24.1107 | 25.0524 | -0.94171 | 150.3143 | 23.9 | 24.6941 | -0.79413 |  | 2026-11-03 16:10 | 267.3418 | 272.5805 | -5.2386 | 1635.4828 | 265.2 | 268.6826 | -3.4826
2026-11-03 16:00 | 597 | 49.08 | 219.899 | 214.685 | 2164.9 | 35.7808 | 35.5099 | 0.27095 | 213.0593 | 37.1 | 35.0021 | 2.0979 |  | 2026-11-03 16:00 | 200.459 | 203.404 | 2184 | 33.9007 | 35.5099 | -1.6092 | 213.0593 | 36.1 | 35.0021 | 1.0979 |  | 2026-11-03 16:00 | 211.351 | 216.13 | 2149.2 | 36.0217 | 35.5099 | 0.51178 | 213.0593 | 37.1 | 35.0021 | 2.0979 |  | 2026-11-03 16:00 | 211.859 | 214.954 | 2168.5 | 35.8257 | 35.5099 | 0.31578 | 213.0593 | 37.2 | 35.0021 | 2.1979 |  | 2026-11-03 16:00 | 155.944 | 158.062 | 1622.2 | 26.3437 | 26.3036 | 0.040046 | 157.8217 | 28.5 | 25.9275 | 2.5725 |  | 2026-11-03 16:00 | 152.485 | 154.572 | 1603.5 | 25.762 | 26.3036 | -0.54162 | 157.8217 | 27.9 | 25.9275 | 1.9725 |  | 2026-11-03 16:00 | 154.907 | 157.521 | 1603.5 | 26.2535 | 26.3036 | -0.050121 | 157.8217 | 27.4 | 25.9275 | 1.4725 |  | 2026-11-03 16:00 | 146.468 | 150.34 | 1612.7 | 25.0567 | 26.3036 | -1.247 | 157.8217 | 27.9 | 25.9275 | 1.9725 |  | 2026-11-03 16:00 | 138.035 | 139.938 | 1523 | 23.323 | 25.0246 | -1.7016 | 150.1478 | 26.2 | 24.6668 | 1.5332 |  | 2026-11-03 16:00 | 268.2677 | 272.2787 | -4.011 | 1633.672 | 285.4 | 268.3851 | 17.0149
2026-11-03 15:50 | 673 | 49.36 | 234.712 | 232.844 | 2127.8 | 38.8073 | 39.9876 | -1.1802 | 239.9254 | 38.8 | 39.4157 | -0.61575 |  | 2026-11-03 15:50 | 237.474 | 242.07 | 2147.9 | 40.345 | 39.9876 | 0.35743 | 239.9254 | 41.1 | 39.4157 | 1.6843 |  | 2026-11-03 15:50 | 228.132 | 232.528 | 2112.1 | 38.7547 | 39.9876 | -1.2329 | 239.9254 | 38.8 | 39.4157 | -0.61575 |  | 2026-11-03 15:50 | 230.584 | 234.095 | 2131.3 | 39.0158 | 39.9876 | -0.97174 | 239.9254 | 39.5 | 39.4157 | 0.084253 |  | 2026-11-03 15:50 | 174.409 | 176.885 | 1593.7 | 29.4808 | 29.6204 | -0.13959 | 177.7225 | 29.4 | 29.1968 | 0.20315 |  | 2026-11-03 15:50 | 171.052 | 173.544 | 1575.6 | 28.924 | 29.6204 | -0.69642 | 177.7225 | 28.6 | 29.1968 | -0.59685 |  | 2026-11-03 15:50 | 170.205 | 173.221 | 1576.1 | 28.8702 | 29.6204 | -0.75026 | 177.7225 | 28.6 | 29.1968 | -0.59685 |  | 2026-11-03 15:50 | 170.747 | 175.551 | 1584.8 | 29.2585 | 29.6204 | -0.36192 | 177.7225 | 28.7 | 29.1968 | -0.49685 |  | 2026-11-03 15:50 | 160.707 | 162.972 | 1496.8 | 27.162 | 28.1802 | -1.0182 | 169.081 | 27.1 | 27.7772 | -0.67719 |  | 2026-11-03 15:50 | 300.6183 | 306.6121 | -5.9938 | 1839.6728 | 300.6 | 302.2276 | -1.6276
2026-11-03 15:40 | 633 | 49.08 | 215.945 | 219.619 | 2089 | 36.6032 | 37.6512 | -1.048 | 225.9071 | 84 | 37.1128 | 46.8872 |  | 2026-11-03 15:40 | 232.245 | 235.83 | 2106.8 | 39.305 | 37.6512 | 1.6538 | 225.9071 | 39.5 | 37.1128 | 2.3872 |  | 2026-11-03 15:40 | 220.621 | 226.868 | 2073.3 | 37.8113 | 37.6512 | 0.16015 | 225.9071 | 40.1 | 37.1128 | 2.9872 |  | 2026-11-03 15:40 | 204.256 | 207.303 | 2091.8 | 34.5505 | 37.6512 | -3.1007 | 225.9071 | 39.9 | 37.1128 | 2.7872 |  | 2026-11-03 15:40 | 150.789 | 152.899 | 1564.3 | 25.4832 | 27.8898 | -2.4066 | 167.3386 | 29.5 | 27.4909 | 2.0091 |  | 2026-11-03 15:40 | 152.441 | 155.95 | 1547 | 25.9917 | 27.8898 | -1.8981 | 167.3386 | 29.5 | 27.4909 | 2.0091 |  | 2026-11-03 15:40 | 156.519 | 159.925 | 1547.5 | 26.6542 | 27.8898 | -1.2356 | 167.3386 | 29.6 | 27.4909 | 2.1091 |  | 2026-11-03 15:40 | 157.679 | 163.485 | 1556.1 | 27.2475 | 27.8898 | -0.64227 | 167.3386 | 29.6 | 27.4909 | 2.1091 |  | 2026-11-03 15:40 | 148.4 | 151.003 | 1469.7 | 25.1672 | 26.5337 | -1.3665 | 159.202 | 27.9 | 26.1542 | 1.7458 |  | 2026-11-03 15:40 | 278.8137 | 288.6975 | -9.8838 | 1732.1849 | 349.6 | 284.5691 | 65.0309
2026-11-03 15:30 | 747 | 48.79 |  |  |  | 0 | 44.4812 | -44.4812 | 266.8873 | 0 | 43.8451 | -43.8451 |  | 2026-11-03 15:30 | 265.552 | 269.76 | 2067.3 | 44.96 | 44.4812 | 0.47878 | 266.8873 | 44.4 | 43.8451 | 0.55486 |  | 2026-11-03 15:30 | 253.364 | 258.934 | 2033.2 | 43.1557 | 44.4812 | -1.3256 | 266.8873 | 43.7 | 43.8451 | -0.14514 |  | 2026-11-03 15:30 | 256.125 | 260.184 | 2051.9 | 43.364 | 44.4812 | -1.1172 | 266.8873 | 44 | 43.8451 | 0.15486 |  | 2026-11-03 15:30 | 189.55 | 192.28 | 1534.8 | 32.0467 | 32.9491 | -0.90238 | 197.6943 | 33.1 | 32.4779 | 0.62212 |  | 2026-11-03 15:30 | 185.441 | 189.806 | 1517.5 | 31.6343 | 32.9491 | -1.3147 | 197.6943 | 32 | 32.4779 | -0.47788 |  | 2026-11-03 15:30 | 188.702 | 192.301 | 1517.9 | 32.0502 | 32.9491 | -0.89888 | 197.6943 | 32.2 | 32.4779 | -0.27788 |  | 2026-11-03 15:30 | 188.344 | 193.883 | 1526.5 | 32.3138 | 32.9491 | -0.63522 | 197.6943 | 32.2 | 32.4779 | -0.27788 |  | 2026-11-03 15:30 | 177.427 | 179.983 | 1441.8 | 29.9972 | 31.3469 | -1.3498 | 188.0817 | 30.7 | 30.8987 | -0.19868 |  | 2026-11-03 15:30 | 289.5218 | 341.068 | -51.5462 | 2046.4082 | 292.3 | 336.1908 | -43.8908
2026-11-03 15:20 | 685 | 48.79 | 234.528 | 238.124 | 2005 | 39.6873 | 40.7893 | -1.102 | 244.736 | 44.9 | 40.2061 | 4.6939 |  | 2026-11-03 15:20 | 235.642 | 239.279 | 2022.9 | 39.8798 | 40.7893 | -0.9095 | 244.736 | 45.7 | 40.2061 | 5.4939 |  | 2026-11-03 15:20 | 234.697 | 241.061 | 1989.5 | 40.1768 | 40.7893 | -0.6125 | 244.736 | 44.8 | 40.2061 | 4.5939 |  | 2026-11-03 15:20 | 244.144 | 247.963 | 2007.9 | 41.3272 | 40.7893 | 0.53783 | 244.736 | 45 | 40.2061 | 4.7939 |  | 2026-11-03 15:20 | 176.681 | 179.244 | 1501.7 | 29.874 | 30.2143 | -0.34032 | 181.2859 | 33.8 | 29.7823 | 4.0177 |  | 2026-11-03 15:20 | 174.992 | 177.884 | 1485.5 | 29.6473 | 30.2143 | -0.56699 | 181.2859 | 33.2 | 29.7823 | 3.4177 |  | 2026-11-03 15:20 | 180.85 | 184.988 | 1485.7 | 30.8313 | 30.2143 | 0.61701 | 181.2859 | 33.2 | 29.7823 | 3.4177 |  | 2026-11-03 15:20 | 184.498 | 190.474 | 1494.3 | 31.7457 | 30.2143 | 1.5313 | 181.2859 | 33.2 | 29.7823 | 3.4177 |  | 2026-11-03 15:20 | 175.327 | 178.371 | 1411.1 | 29.7285 | 28.7452 | 0.98331 | 172.4711 | 31.4 | 28.3341 | 3.0659 |  | 2026-11-03 15:20 | 312.898 | 312.7598 | 0.13816 | 1876.559 | 345.2 | 308.2874 | 36.9126
2026-11-03 15:10 | 819 | 49.08 | 279.847 | 284.311 | 1960.1 | 47.3852 | 48.7146 | -1.3294 | 292.2874 | 46.5 | 48.018 | -1.518 |  | 2026-11-03 15:10 | 282.622 | 287.247 | 1977.2 | 47.8745 | 48.7146 | -0.84007 | 292.2874 | 47.8 | 48.018 | -0.21795 |  | 2026-11-03 15:10 | 276.395 | 284.149 | 1944.7 | 47.3582 | 48.7146 | -1.3564 | 292.2874 | 46.3 | 48.018 | -1.718 |  | 2026-11-03 15:10 | 279.081 | 283.648 | 1962.9 | 47.2747 | 48.7146 | -1.4399 | 292.2874 | 46.7 | 48.018 | -1.318 |  | 2026-11-03 15:10 | 208.954 | 212.055 | 1467.9 | 35.3425 | 36.0849 | -0.74237 | 216.5092 | 35.1 | 35.5689 | -0.46885 |  | 2026-11-03 15:10 | 204.978 | 208.627 | 1452.3 | 34.7712 | 36.0849 | -1.3137 | 216.5092 | 34.3 | 35.5689 | -1.2689 |  | 2026-11-03 15:10 | 205.161 | 208.784 | 1452.5 | 34.7973 | 36.0849 | -1.2875 | 216.5092 | 34.9 | 35.5689 | -0.66885 |  | 2026-11-03 15:10 | 205.159 | 210.901 | 1461.1 | 35.1502 | 36.0849 | -0.9347 | 216.5092 | 34.9 | 35.5689 | -0.66885 |  | 2026-11-03 15:10 | 193.849 | 196.701 | 1379.7 | 32.7835 | 34.3303 | -1.5468 | 205.9817 | 32.4 | 33.8394 | -1.4394 |  | 2026-11-03 15:10 | 362.7372 | 373.528 | -10.7909 | 2241.1682 | 358.9 | 368.1866 | -9.2866
2026-11-03 15:00 | 842 | 48.79 | 283.829 | 289.092 | 1913.6 | 48.182 | 50.1381 | -1.9561 | 300.8288 | 49.8 | 49.4212 | 0.37884 | 0.98179 | 2026-11-03 15:00 | 287.568 | 292.261 | 1929.4 | 48.7102 | 50.1381 | -1.428 | 300.8288 | 47.8 | 49.4212 | -1.6212 | 0.98394 | 2026-11-03 15:00 | 283.878 | 291.366 | 1898.4 | 48.561 | 50.1381 | -1.5771 | 300.8288 | 47.7 | 49.4212 | -1.7212 | 0.9743 | 2026-11-03 15:00 | 285.017 | 289.71 | 1916.2 | 48.285 | 50.1381 | -1.8531 | 300.8288 | 48 | 49.4212 | -1.4212 | 0.9838 | 2026-11-03 15:00 | 214.955 | 218.43 | 1432.8 | 36.405 | 37.1394 | -0.73436 | 222.8362 | 36.1 | 36.6083 | -0.50827 | 0.98409 | 2026-11-03 15:00 | 210.116 | 214.011 | 1418 | 35.6685 | 37.1394 | -1.4709 | 222.8362 | 35.9 | 36.6083 | -0.70827 | 0.9818 | 2026-11-03 15:00 | 210.9 | 214.768 | 1417.6 | 35.7947 | 37.1394 | -1.3447 | 222.8362 | 35 | 36.6083 | -1.6083 | 0.98199 | 2026-11-03 15:00 | 211.25 | 217.227 | 1426.2 | 36.2045 | 37.1394 | -0.93486 | 222.8362 | 35 | 36.6083 | -1.6083 | 0.97249 | 2026-11-03 15:00 | 198.882 | 201.849 | 1347.3 | 33.6415 | 35.3335 | -1.692 | 212.001 | 33 | 34.8282 | -1.8282 | 0.9853 | 2026-11-03 15:00 | 371.4523 | 384.4435 | -12.9911 | 2306.6609 | 368.3 | 378.9459 | -10.6459
2026-11-03 14:50 | 863 | 48.79 | 288.207 | 293.307 | 1863.8 | 48.8845 | 51.3886 | -2.5041 | 308.3317 | 47.1 | 50.6538 | -3.5538 | 0.98261 | 2026-11-03 14:50 | 293.644 | 298.54 | 1881.6 | 49.7567 | 51.3886 | -1.6319 | 308.3317 | 49.2 | 50.6538 | -1.4538 | 0.9836 | 2026-11-03 14:50 | 289.472 | 297.803 | 1850.7 | 49.6338 | 51.3886 | -1.7548 | 308.3317 | 48.9 | 50.6538 | -1.7538 | 0.97203 | 2026-11-03 14:50 | 291.343 | 296.065 | 1868.2 | 49.3442 | 51.3886 | -2.0444 | 308.3317 | 49.3 | 50.6538 | -1.3538 | 0.98405 | 2026-11-03 14:50 | 219.373 | 222.669 | 1396.7 | 37.1115 | 38.0656 | -0.95414 | 228.3938 | 37.2 | 37.5213 | -0.3213 | 0.9852 | 2026-11-03 14:50 | 214.145 | 217.986 | 1382.1 | 36.331 | 38.0656 | -1.7346 | 228.3938 | 36.5 | 37.5213 | -1.0213 | 0.98238 | 2026-11-03 14:50 | 215.045 | 218.902 | 1382.6 | 36.4837 | 38.0656 | -1.582 | 228.3938 | 37.1 | 37.5213 | -0.4213 | 0.98238 | 2026-11-03 14:50 | 214.793 | 220.842 | 1391.2 | 36.807 | 38.0656 | -1.2586 | 228.3938 | 37.1 | 37.5213 | -0.4213 | 0.97261 | 2026-11-03 14:50 | 202.432 | 205.473 | 1314.3 | 34.2455 | 36.2147 | -1.9692 | 217.2884 | 35 | 35.6969 | -0.69687 | 0.9852 | 2026-11-03 14:50 | 378.5978 | 394.0317 | -15.4339 | 2364.1904 | 377.4 | 388.3971 | -10.9971
2026-11-03 14:40 | 895 | 49.08 | 298.964 | 303.98 | 1816.7 | 50.6633 | 53.2351 | -2.5718 | 319.4106 | 51.3 | 52.4738 | -1.1738 | 0.9835 | 2026-11-03 14:40 | 303.216 | 308.428 | 1832.4 | 51.4047 | 53.2351 | -1.8304 | 319.4106 | 52 | 52.4738 | -0.47383 | 0.9831 | 2026-11-03 14:40 | 298.341 | 306.471 | 1801.8 | 51.0785 | 53.2351 | -2.1566 | 319.4106 | 52 | 52.4738 | -0.47383 | 0.97347 | 2026-11-03 14:40 | 300.186 | 305.346 | 1818.9 | 50.891 | 53.2351 | -2.3441 | 319.4106 | 52.3 | 52.4738 | -0.17383 | 0.9831 | 2026-11-03 14:40 | 226.136 | 229.667 | 1359.5 | 38.2778 | 39.4334 | -1.1556 | 236.6004 | 39.3 | 38.8695 | 0.4305 | 0.98463 | 2026-11-03 14:40 | 221.662 | 225.77 | 1345.6 | 37.6283 | 39.4334 | -1.8051 | 236.6004 | 38 | 38.8695 | -0.8695 | 0.9818 | 2026-11-03 14:40 | 222.702 | 226.818 | 1345.5 | 37.803 | 39.4334 | -1.6304 | 236.6004 | 38.1 | 38.8695 | -0.7695 | 0.98185 | 2026-11-03 14:40 | 223.309 | 229.707 | 1354.1 | 38.2845 | 39.4334 | -1.1489 | 236.6004 | 38.3 | 38.8695 | -0.5695 | 0.97215 | 2026-11-03 14:40 | 210.44 | 213.645 | 1279.3 | 35.6075 | 37.516 | -1.9085 | 225.096 | 36 | 36.9795 | -0.97952 | 0.985 | 2026-11-03 14:40 | 391.6387 | 408.19 | -16.5513 | 2449.1398 | 397.3 | 402.3529 | -5.0529
2026-11-03 14:30 | 945 | 49.08 | 315.706 | 321.068 | 1765.4 | 53.5113 | 56.2091 | -2.6978 | 337.2547 | 52.6 | 55.4053 | -2.8053 | 0.9833 | 2026-11-03 14:30 | 319.389 | 324.913 | 1780.4 | 54.1522 | 56.2091 | -2.057 | 337.2547 | 53.4 | 55.4053 | -2.0053 | 0.983 | 2026-11-03 14:30 | 313.496 | 322.77 | 1749.8 | 53.795 | 56.2091 | -2.4141 | 337.2547 | 51.4 | 55.4053 | -4.0053 | 0.97127 | 2026-11-03 14:30 | 315.008 | 320.488 | 1766.6 | 53.4147 | 56.2091 | -2.7945 | 337.2547 | 52 | 55.4053 | -3.4053 | 0.9829 | 2026-11-03 14:30 | 237.784 | 241.479 | 1320.2 | 40.2465 | 41.6364 | -1.3899 | 249.8183 | 39.1 | 41.041 | -1.941 | 0.9847 | 2026-11-03 14:30 | 232.482 | 236.943 | 1307.6 | 39.4905 | 41.6364 | -2.1459 | 249.8183 | 38.2 | 41.041 | -2.841 | 0.98117 | 2026-11-03 14:30 | 234.132 | 238.78 | 1307.4 | 39.7967 | 41.6364 | -1.8397 | 249.8183 | 38.4 | 41.041 | -2.641 | 0.98053 | 2026-11-03 14:30 | 234.594 | 241.689 | 1315.8 | 40.2815 | 41.6364 | -1.3549 | 249.8183 | 38.5 | 41.041 | -2.541 | 0.97064 | 2026-11-03 14:30 | 220.54 | 223.898 | 1243.3 | 37.3163 | 39.6119 | -2.2955 | 237.6712 | 36.3 | 39.0454 | -2.7454 | 0.985 | 2026-11-03 14:30 | 412.0047 | 430.9939 | -18.9892 | 2585.9633 | 399.9 | 424.8307 | -24.9307
2026-11-03 14:20 | 941 | 49.08 | 311.145 | 316.429 | 1712.8 | 52.7382 | 55.9712 | -3.233 | 335.8272 | 52.8 | 55.1708 | -2.3708 | 0.9833 | 2026-11-03 14:20 | 316.023 | 321.554 | 1727 | 53.5923 | 55.9712 | -2.3789 | 335.8272 | 54.4 | 55.1708 | -0.77081 | 0.9828 | 2026-11-03 14:20 | 309.51 | 317.954 | 1698.4 | 52.9923 | 55.9712 | -2.9789 | 335.8272 | 52.6 | 55.1708 | -2.5708 | 0.97344 | 2026-11-03 14:20 | 312.447 | 317.883 | 1714.6 | 52.9805 | 55.9712 | -2.9907 | 335.8272 | 53 | 55.1708 | -2.1708 | 0.9829 | 2026-11-03 14:20 | 234.863 | 238.561 | 1281.1 | 39.7602 | 41.4601 | -1.7 | 248.7609 | 39.9 | 40.8673 | -0.96727 | 0.9845 | 2026-11-03 14:20 | 230.023 | 234.272 | 1269.4 | 39.0453 | 41.4601 | -2.4148 | 248.7609 | 39.2 | 40.8673 | -1.6673 | 0.98186 | 2026-11-03 14:20 | 231.398 | 236.15 | 1269 | 39.3583 | 41.4601 | -2.1018 | 248.7609 | 39.3 | 40.8673 | -1.5673 | 0.97988 | 2026-11-03 14:20 | 232.382 | 238.961 | 1277.3 | 39.8268 | 41.4601 | -1.6333 | 248.7609 | 39.4 | 40.8673 | -1.4673 | 0.97247 | 2026-11-03 14:20 | 218.372 | 221.765 | 1207 | 36.9608 | 39.4442 | -2.4834 | 236.6652 | 37.2 | 38.8801 | -1.6801 | 0.9847 | 2026-11-03 14:20 | 407.2548 | 429.1696 | -21.9147 | 2575.0174 | 407.8 | 423.0324 | -15.2324
2026-11-03 14:10 | 982 | 49.08 | 323.061 | 328.721 | 1660 | 54.7868 | 58.4099 | -3.6231 | 350.4594 | 53.1 | 57.5746 | -4.4746 | 0.98278 | 2026-11-03 14:10 | 328.141 | 333.986 | 1672.6 | 55.6643 | 58.4099 | -2.7456 | 350.4594 | 53.7 | 57.5746 | -3.8746 | 0.9825 | 2026-11-03 14:10 | 323.724 | 333.092 | 1645.8 | 55.5153 | 58.4099 | -2.8946 | 350.4594 | 52.9 | 57.5746 | -4.6746 | 0.97188 | 2026-11-03 14:10 | 326.295 | 332.005 | 1661.6 | 55.3342 | 58.4099 | -3.0757 | 350.4594 | 53.3 | 57.5746 | -4.2746 | 0.9828 | 2026-11-03 14:10 | 246.256 | 250.235 | 1241.2 | 41.7058 | 43.2666 | -1.5608 | 259.5996 | 40.1 | 42.6479 | -2.5479 | 0.9841 | 2026-11-03 14:10 | 241.012 | 245.986 | 1230.2 | 40.9977 | 43.2666 | -2.2689 | 259.5996 | 39.3 | 42.6479 | -3.3479 | 0.97978 | 2026-11-03 14:10 | 242.27 | 246.996 | 1229.7 | 41.166 | 43.2666 | -2.1006 | 259.5996 | 40.1 | 42.6479 | -2.5479 | 0.98087 | 2026-11-03 14:10 | 243.172 | 250.093 | 1237.9 | 41.6822 | 43.2666 | -1.5844 | 259.5996 | 40.2 | 42.6479 | -2.4479 | 0.97233 | 2026-11-03 14:10 | 228.41 | 232.03 | 1169.8 | 38.6717 | 41.1628 | -2.4911 | 246.9768 | 37.8 | 40.5742 | -2.7742 | 0.9844 | 2026-11-03 14:10 | 425.524 | 447.8688 | -22.3448 | 2687.2126 | 410.5 | 441.4642 | -30.9642
2026-11-03 14:00 | 966 | 48.79 | 318.766 | 324.18 | 1606.9 | 54.03 | 57.5219 | -3.4919 | 345.1314 | 53.6 | 56.6993 | -3.0993 | 0.9833 | 2026-11-03 14:00 | 326.769 | 330.454 | 1618.9 | 55.0757 | 57.5219 | -2.4462 | 345.1314 | 53.8 | 56.6993 | -2.8993 | 0.98885 | 2026-11-03 14:00 | 316.998 | 325.754 | 1592.9 | 54.2923 | 57.5219 | -3.2296 | 345.1314 | 53.4 | 56.6993 | -3.2993 | 0.97312 | 2026-11-03 14:00 | 320.664 | 326.276 | 1608.3 | 54.3793 | 57.5219 | -3.1426 | 345.1314 | 54.7 | 56.6993 | -1.9993 | 0.9828 | 2026-11-03 14:00 | 239.844 | 243.645 | 1201.1 | 40.6075 | 42.6088 | -2.0013 | 255.6529 | 41.1 | 41.9995 | -0.89951 | 0.9844 | 2026-11-03 14:00 | 235.745 | 240.06 | 1190.9 | 40.01 | 42.6088 | -2.5988 | 255.6529 | 40.3 | 41.9995 | -1.6995 | 0.98203 | 2026-11-03 14:00 | 236.297 | 240.907 | 1189.6 | 40.1512 | 42.6088 | -2.4576 | 255.6529 | 39.9 | 41.9995 | -2.0995 | 0.98086 | 2026-11-03 14:00 | 237.166 | 244.102 | 1197.7 | 40.6837 | 42.6088 | -1.9251 | 255.6529 | 39.9 | 41.9995 | -2.0995 | 0.97159 | 2026-11-03 14:00 | 223.148 | 226.657 | 1132 | 37.7762 | 40.537 | -2.7608 | 243.2221 | 37.6 | 39.9573 | -2.3573 | 0.98452 | 2026-11-03 14:00 | 417.0058 | 441.0599 | -24.054 | 2646.3591 | 414.3 | 434.7527 | -20.4527
2026-11-03 13:50 | 989 | 49.08 | 326.258 | 331.998 | 1553.3 | 55.333 | 58.8263 | -3.4933 | 352.9576 | 54.8 | 57.985 | -3.185 | 0.98271 | 2026-11-03 13:50 | 331.818 | 337.667 | 1565.1 | 56.2778 | 58.8263 | -2.5484 | 352.9576 | 57.2 | 57.985 | -0.78505 | 0.98268 | 2026-11-03 13:50 | 325.3 | 334.742 | 1539.5 | 55.7903 | 58.8263 | -3.0359 | 352.9576 | 55.6 | 57.985 | -2.385 | 0.97179 | 2026-11-03 13:50 | 327.721 | 333.49 | 1553.6 | 55.5817 | 58.8263 | -3.2446 | 352.9576 | 55.3 | 57.985 | -2.685 | 0.9827 | 2026-11-03 13:50 | 245.927 | 249.85 | 1160 | 41.6417 | 43.575 | -1.9333 | 261.4501 | 41.5 | 42.9519 | -1.4519 | 0.9843 | 2026-11-03 13:50 | 240.857 | 245.461 | 1150.6 | 40.9102 | 43.575 | -2.6648 | 261.4501 | 40.6 | 42.9519 | -2.3519 | 0.98124 | 2026-11-03 13:50 | 241.265 | 246.156 | 1149.7 | 41.026 | 43.575 | -2.549 | 261.4501 | 40.7 | 42.9519 | -2.2519 | 0.98013 | 2026-11-03 13:50 | 241.756 | 248.824 | 1157.8 | 41.4707 | 43.575 | -2.1043 | 261.4501 | 40.8 | 42.9519 | -2.1519 | 0.97159 | 2026-11-03 13:50 | 228.271 | 231.865 | 1094.4 | 38.6442 | 41.4562 | -2.8121 | 248.7374 | 38.5 | 40.8634 | -2.3634 | 0.9845 | 2026-11-03 13:50 | 426.6755 | 451.0613 | -24.3858 | 2706.3679 | 425 | 444.6111 | -19.6111
2026-11-03 13:40 | 1011 | 48.79 | 332.052 | 337.863 | 1498.5 | 56.3105 | 60.2015 | -3.891 | 361.2089 | 57 | 59.3406 | -2.3406 | 0.9828 | 2026-11-03 13:40 | 337.623 | 343.602 | 1507.9 | 57.267 | 60.2015 | -2.9345 | 361.2089 | 56.4 | 59.3406 | -2.9406 | 0.9826 | 2026-11-03 13:40 | 330.824 | 340.569 | 1483.9 | 56.7615 | 60.2015 | -3.44 | 361.2089 | 55.1 | 59.3406 | -4.2406 | 0.97139 | 2026-11-03 13:40 | 333.779 | 339.69 | 1498.3 | 56.615 | 60.2015 | -3.5865 | 361.2089 | 55.4 | 59.3406 | -3.9406 | 0.9826 | 2026-11-03 13:40 | 250.369 | 254.388 | 1118.5 | 42.398 | 44.5937 | -2.1957 | 267.5622 | 41.6 | 43.956 | -2.356 | 0.9842 | 2026-11-03 13:40 | 245.428 | 250.275 | 1110 | 41.7125 | 44.5937 | -2.8812 | 267.5622 | 40.8 | 43.956 | -3.156 | 0.98063 | 2026-11-03 13:40 | 246.297 | 251.291 | 1109 | 41.8818 | 44.5937 | -2.7119 | 267.5622 | 41 | 43.956 | -2.956 | 0.98013 | 2026-11-03 13:40 | 247.406 | 254.893 | 1117 | 42.4822 | 44.5937 | -2.1115 | 267.5622 | 41.8 | 43.956 | -2.156 | 0.97063 | 2026-11-03 13:40 | 233.078 | 236.796 | 1055.9 | 39.466 | 42.4254 | -2.9594 | 254.5523 | 39.4 | 41.8187 | -2.4187 | 0.9843 | 2026-11-03 13:40 | 434.8945 | 461.6061 | -26.7116 | 2769.6367 | 428.5 | 455.0052 | -26.5052
2026-11-03 13:30 | 1016 | 49.08 | 332.446 | 338.264 | 1441.5 | 56.3773 | 60.4322 | -4.0549 | 362.5934 | 54.8 | 59.5681 | -4.7681 | 0.9828 | 2026-11-03 13:30 | 0 | 0 | 1451.5 | 0 | 60.4322 | -60.4322 | 362.5934 | 59 | 59.5681 | -0.56806 |  | 2026-11-03 13:30 | 332.02 | 342.295 | 1428.8 | 57.0492 | 60.4322 | -3.3831 | 362.5934 | 56.2 | 59.5681 | -3.3681 | 0.96998 | 2026-11-03 13:30 | 333.82 | 339.835 | 1442.9 | 56.6392 | 60.4322 | -3.7931 | 362.5934 | 56.2 | 59.5681 | -3.3681 | 0.9823 | 2026-11-03 13:30 | 251.879 | 255.975 | 1076.9 | 42.6625 | 44.7646 | -2.1021 | 268.5877 | 42.7 | 44.1245 | -1.4245 | 0.984 | 2026-11-03 13:30 | 245.942 | 251.018 | 1069.2 | 41.8363 | 44.7646 | -2.9283 | 268.5877 | 41.9 | 44.1245 | -2.2245 | 0.97978 | 2026-11-03 13:30 | 247.787 | 252.856 | 1068 | 42.1427 | 44.7646 | -2.622 | 268.5877 | 41.9 | 44.1245 | -2.2245 | 0.97995 | 2026-11-03 13:30 | 247.54 | 255.1 | 1075.2 | 42.5167 | 44.7646 | -2.248 | 268.5877 | 41.5 | 44.1245 | -2.6245 | 0.97036 | 2026-11-03 13:30 | 233.158 | 236.925 | 1016.5 | 39.4875 | 42.588 | -3.1005 | 255.528 | 39 | 41.979 | -2.979 | 0.9841 | 2026-11-03 13:30 | 378.7113 | 463.3754 | -84.6641 | 2780.2526 | 433.2 | 456.7492 | -23.5492
2026-11-03 13:20 | 1029 | 48.79 | 337.127 | 343.097 | 1386.7 | 57.1828 | 61.2733 | -4.0905 | 367.64 | 56.3 | 60.3971 | -4.0971 | 0.9826 | 2026-11-03 13:20 | 342.406 | 348.576 | 1392.5 | 58.096 | 61.2733 | -3.1773 | 367.64 | 52.8 | 60.3971 | -7.5971 | 0.9823 | 2026-11-03 13:20 | 335.824 | 345.621 | 1372.6 | 57.6035 | 61.2733 | -3.6698 | 367.64 | 55.3 | 60.3971 | -5.0971 | 0.97165 | 2026-11-03 13:20 | 339.064 | 345.174 | 1386.7 | 57.529 | 61.2733 | -3.7443 | 367.64 | 55.4 | 60.3971 | -4.9971 | 0.9823 | 2026-11-03 13:20 | 254.804 | 258.921 | 1034.2 | 43.1535 | 45.3876 | -2.2341 | 272.3259 | 42.8 | 44.7386 | -1.9386 | 0.9841 | 2026-11-03 13:20 | 249.379 | 254.437 | 1027.3 | 42.4062 | 45.3876 | -2.9815 | 272.3259 | 42.1 | 44.7386 | -2.6386 | 0.98012 | 2026-11-03 13:20 | 249.896 | 255.378 | 1026.1 | 42.563 | 45.3876 | -2.8246 | 272.3259 | 42.2 | 44.7386 | -2.5386 | 0.97853 | 2026-11-03 13:20 | 250.09 | 257.459 | 1033.7 | 42.9098 | 45.3876 | -2.4778 | 272.3259 | 42.2 | 44.7386 | -2.5386 | 0.97138 | 2026-11-03 13:20 | 235.892 | 239.703 | 977.5 | 39.9505 | 43.1807 | -3.2302 | 259.0844 | 39.9 | 42.5632 | -2.6632 | 0.9841 | 2026-11-03 13:20 | 441.3943 | 469.8246 | -28.4303 | 2818.9478 | 429 | 463.1061 | -34.1061
2026-11-03 13:10 | 1027 | 49.65 | 335.244 | 341.25 | 1330.4 | 56.875 | 60.9534 | -4.0784 | 365.7206 | 57.1 | 60.0818 | -2.9818 | 0.9824 | 2026-11-03 13:10 | 336.659 | 342.446 | 1339.7 | 57.0743 | 60.9534 | -3.8791 | 365.7206 | 113.4 | 60.0818 | 53.3182 | 0.9831 | 2026-11-03 13:10 | 332.272 | 342.014 | 1317.3 | 57.0023 | 60.9534 | -3.9511 | 365.7206 | 55.7 | 60.0818 | -4.3818 | 0.97152 | 2026-11-03 13:10 | 331.275 | 336.936 | 1331.3 | 56.156 | 60.9534 | -4.7974 | 365.7206 | 55.6 | 60.0818 | -4.4818 | 0.9832 | 2026-11-03 13:10 | 251.628 | 255.798 | 991.4 | 42.633 | 45.1507 | -2.5177 | 270.9042 | 41.7 | 44.505 | -2.805 | 0.9837 | 2026-11-03 13:10 | 248.014 | 253.098 | 985.2 | 42.183 | 45.1507 | -2.9677 | 270.9042 | 41.5 | 44.505 | -3.005 | 0.97991 | 2026-11-03 13:10 | 248.259 | 253.382 | 983.9 | 42.2303 | 45.1507 | -2.9204 | 270.9042 | 41.6 | 44.505 | -2.905 | 0.97978 | 2026-11-03 13:10 | 249.674 | 256.82 | 991.5 | 42.8033 | 45.1507 | -2.3474 | 270.9042 | 41.9 | 44.505 | -2.605 | 0.97218 | 2026-11-03 13:10 | 235.538 | 239.417 | 937.6 | 39.9028 | 42.9553 | -3.0525 | 257.7318 | 39.4 | 42.341 | -2.941 | 0.9838 | 2026-11-03 13:10 | 436.8602 | 467.3718 | -30.5117 | 2804.2311 | 487.9 | 460.6884 | 27.2116
2026-11-03 13:00 | 1042 | 49.08 | 339.267 | 345.31 | 1273.3 | 57.5517 | 61.9787 | -4.4271 | 371.8724 | 55.1 | 61.0924 | -5.9924 | 0.9825 |  |  |  |  | 0 | 61.9787 | -61.9787 | 371.8724 | 0 | 61.0924 | -61.0924 |  | 2026-11-03 13:00 | 335.103 | 344.992 | 1261.6 | 57.4987 | 61.9787 | -4.4801 | 371.8724 | 56 | 61.0924 | -5.0924 | 0.97134 | 2026-11-03 13:00 | 332.752 | 338.335 | 1275.7 | 56.3892 | 61.9787 | -5.5896 | 371.8724 | 55.6 | 61.0924 | -5.4924 | 0.9835 | 2026-11-03 13:00 | 254.082 | 258.292 | 949.7 | 43.0487 | 45.9102 | -2.8615 | 275.461 | 42.8 | 45.2537 | -2.4537 | 0.9837 | 2026-11-03 13:00 | 250.521 | 255.761 | 943.7 | 42.6268 | 45.9102 | -3.2833 | 275.461 | 41.7 | 45.2537 | -3.5537 | 0.97951 | 2026-11-03 13:00 | 251.066 | 256.525 | 942.3 | 42.7542 | 45.9102 | -3.156 | 275.461 | 41.7 | 45.2537 | -3.5537 | 0.97872 | 2026-11-03 13:00 | 252.373 | 259.755 | 949.6 | 43.2925 | 45.9102 | -2.6177 | 275.461 | 42 | 45.2537 | -3.2537 | 0.97158 | 2026-11-03 13:00 | 237.604 | 241.492 | 898.2 | 40.2487 | 43.6778 | -3.4292 | 262.0671 | 39.7 | 43.0532 | -3.3532 | 0.9839 | 2026-11-03 13:00 | 383.4103 | 475.2335 | -91.8231 | 2851.4008 | 374.6 | 468.4376 | -93.8376
2026-11-03 12:50 | 1039 | 49.08 | 337.999 | 344.054 | 1218.2 | 57.3423 | 61.8003 | -4.458 | 370.8017 | 57.7 | 60.9165 | -3.2165 | 0.9824 | 2026-11-03 12:50 | 331.39 | 340.682 | 1226.3 | 56.7803 | 61.8003 | -5.02 | 370.8017 | 55.5 | 60.9165 | -5.4165 | 0.97273 | 2026-11-03 12:50 | 335.004 | 344.875 | 1205.6 | 57.4792 | 61.8003 | -4.3211 | 370.8017 | 55.2 | 60.9165 | -5.7165 | 0.97138 | 2026-11-03 12:50 | 324.18 | 329.418 | 1220.1 | 54.903 | 61.8003 | -6.8973 | 370.8017 | 55.2 | 60.9165 | -5.7165 | 0.9841 | 2026-11-03 12:50 | 254.212 | 258.451 | 906.9 | 43.0752 | 45.778 | -2.7028 | 274.668 | 42.2 | 45.1234 | -2.9234 | 0.9836 | 2026-11-03 12:50 | 250.614 | 255.861 | 902 | 42.6435 | 45.778 | -3.1345 | 274.668 | 41.6 | 45.1234 | -3.5234 | 0.97949 | 2026-11-03 12:50 | 250.795 | 256.211 | 900.6 | 42.7018 | 45.778 | -3.0762 | 274.668 | 41.6 | 45.1234 | -3.5234 | 0.97886 | 2026-11-03 12:50 | 252.013 | 259.481 | 907.6 | 43.2468 | 45.778 | -2.5312 | 274.668 | 42.3 | 45.1234 | -2.8234 | 0.97122 | 2026-11-03 12:50 | 237.846 | 241.787 | 858.5 | 40.2978 | 43.5521 | -3.2543 | 261.3125 | 40 | 42.9293 | -2.9293 | 0.9837 | 2026-11-03 12:50 | 438.47 | 473.8652 | -35.3952 | 2843.1914 | 431.3 | 467.089 | -35.789
2026-11-03 12:40 | 1035 | 49.08 | 338.015 | 344.071 | 1160.5 | 57.3452 | 61.5624 | -4.2172 | 369.3742 | 54.6 | 60.682 | -6.082 | 0.9824 | 2026-11-03 12:40 | 337.683 | 343.523 | 1170.8 | 57.2538 | 61.5624 | -4.3085 | 369.3742 | 56.2 | 60.682 | -4.482 | 0.983 | 2026-11-03 12:40 | 335.014 | 344.937 | 1150.4 | 57.4895 | 61.5624 | -4.0729 | 369.3742 | 55.6 | 60.682 | -5.082 | 0.97123 | 2026-11-03 12:40 | 337.729 | 343.92 | 1164.9 | 57.32 | 61.5624 | -4.2424 | 369.3742 | 56.2 | 60.682 | -4.482 | 0.982 | 2026-11-03 12:40 | 253.741 | 257.972 | 864.7 | 42.9953 | 45.6018 | -2.6064 | 273.6105 | 42.2 | 44.9496 | -2.7496 | 0.9836 | 2026-11-03 12:40 | 249.58 | 254.422 | 860.4 | 42.4037 | 45.6018 | -3.1981 | 273.6105 | 41.7 | 44.9496 | -3.2496 | 0.98097 | 2026-11-03 12:40 | 250.297 | 255.344 | 859 | 42.5573 | 45.6018 | -3.0444 | 273.6105 | 41.7 | 44.9496 | -3.2496 | 0.98023 | 2026-11-03 12:40 | 251.418 | 258.618 | 865.3 | 43.103 | 45.6018 | -2.4988 | 273.6105 | 41.4 | 44.9496 | -3.5496 | 0.97216 | 2026-11-03 12:40 | 236.917 | 240.818 | 818.5 | 40.1363 | 43.3844 | -3.2481 | 260.3065 | 39.1 | 42.764 | -3.664 | 0.9838 | 2026-11-03 12:40 | 440.6042 | 472.0409 | -31.4367 | 2832.2455 | 428.7 | 465.2907 | -36.5907
2026-11-03 12:30 | 1030 | 49.08 | 333.466 | 339.44 | 1105.9 | 56.5733 | 61.265 | -4.6916 | 367.5898 | 57.1 | 60.3889 | -3.2889 | 0.9824 | 2026-11-03 12:30 | 340.929 | 347.178 | 1114.6 | 57.863 | 61.265 | -3.402 | 367.5898 | 55 | 60.3889 | -5.3889 | 0.982 | 2026-11-03 12:30 | 331.008 | 340.642 | 1094.8 | 56.7737 | 61.265 | -4.4913 | 367.5898 | 55 | 60.3889 | -5.3889 | 0.97172 | 2026-11-03 12:30 | 336.956 | 343.132 | 1108.7 | 57.1887 | 61.265 | -4.0763 | 367.5898 | 55.6 | 60.3889 | -4.7889 | 0.982 | 2026-11-03 12:30 | 251.139 | 255.352 | 822.5 | 42.5587 | 45.3815 | -2.8228 | 272.2887 | 41.6 | 44.7325 | -3.1325 | 0.9835 | 2026-11-03 12:30 | 249.21 | 253.95 | 818.7 | 42.325 | 45.3815 | -3.0565 | 272.2887 | 41.1 | 44.7325 | -3.6325 | 0.98133 | 2026-11-03 12:30 | 248.507 | 253.999 | 817.3 | 42.3332 | 45.3815 | -3.0483 | 272.2887 | 41.1 | 44.7325 | -3.6325 | 0.97838 | 2026-11-03 12:30 | 250.796 | 257.927 | 823.9 | 42.9878 | 45.3815 | -2.3936 | 272.2887 | 41.4 | 44.7325 | -3.3325 | 0.97235 | 2026-11-03 12:30 | 237.188 | 241.069 | 779.4 | 40.1782 | 43.1748 | -2.9967 | 259.049 | 39.1 | 42.5574 | -3.4574 | 0.9839 | 2026-11-03 12:30 | 438.7815 | 469.7605 | -30.979 | 2818.5631 | 427 | 463.0429 | -36.0429
2026-11-03 12:20 | 1026 | 49.08 | 333.931 | 339.914 | 1048.8 | 56.6523 | 61.027 | -4.3747 | 366.1623 | 56.7 | 60.1544 | -3.4544 | 0.9824 | 2026-11-03 12:20 | 337.466 | 343.582 | 1059.6 | 57.2637 | 61.027 | -3.7634 | 366.1623 | 56.9 | 60.1544 | -3.2544 | 0.9822 | 2026-11-03 12:20 | 330.664 | 340.37 | 1039.8 | 56.7283 | 61.027 | -4.2987 | 366.1623 | 54.9 | 60.1544 | -5.2544 | 0.97148 | 2026-11-03 12:20 | 335.16 | 341.269 | 1053.1 | 56.8782 | 61.027 | -4.1489 | 366.1623 | 55.5 | 60.1544 | -4.6544 | 0.9821 | 2026-11-03 12:20 | 249.528 | 253.714 | 780.9 | 42.2857 | 45.2052 | -2.9196 | 271.2313 | 41.4 | 44.5588 | -3.1588 | 0.9835 | 2026-11-03 12:20 | 247.366 | 252.562 | 777.6 | 42.0937 | 45.2052 | -3.1116 | 271.2313 | 41.1 | 44.5588 | -3.4588 | 0.97943 | 2026-11-03 12:20 | 247.151 | 252.7 | 776.2 | 42.1167 | 45.2052 | -3.0886 | 271.2313 | 41 | 44.5588 | -3.5588 | 0.97804 | 2026-11-03 12:20 | 249.058 | 256.453 | 782.5 | 42.7422 | 45.2052 | -2.4631 | 271.2313 | 41.9 | 44.5588 | -2.6588 | 0.97116 | 2026-11-03 12:20 | 235.028 | 238.874 | 740.3 | 39.8123 | 43.0072 | -3.1948 | 258.043 | 39.5 | 42.3922 | -2.8922 | 0.9839 | 2026-11-03 12:20 | 436.573 | 467.9362 | -31.3632 | 2807.6173 | 428.9 | 461.2447 | -32.3447
2026-11-03 12:10 | 1015 | 49.08 | 330.581 | 336.435 | 992.1 | 56.0725 | 60.3728 | -4.3003 | 362.2365 | 53.2 | 59.5094 | -6.3094 | 0.9826 | 2026-11-03 12:10 | 334.609 | 340.673 | 1002.7 | 56.7788 | 60.3728 | -3.5939 | 362.2365 | 54.2 | 59.5094 | -5.3094 | 0.9822 | 2026-11-03 12:10 | 329.805 | 339.753 | 984.9 | 56.6255 | 60.3728 | -3.7473 | 362.2365 | 54.6 | 59.5094 | -4.9094 | 0.97072 | 2026-11-03 12:10 | 332.307 | 338.329 | 997.6 | 56.3882 | 60.3728 | -3.9846 | 362.2365 | 55.3 | 59.5094 | -4.2094 | 0.9822 | 2026-11-03 12:10 | 248.951 | 253.076 | 739.5 | 42.1793 | 44.7206 | -2.5412 | 268.3234 | 41.3 | 44.0811 | -2.7811 | 0.9837 | 2026-11-03 12:10 | 245.452 | 250.406 | 736.5 | 41.7343 | 44.7206 | -2.9862 | 268.3234 | 40.8 | 44.0811 | -3.2811 | 0.98022 | 2026-11-03 12:10 | 245.58 | 250.887 | 735.2 | 41.8145 | 44.7206 | -2.9061 | 268.3234 | 40.8 | 44.0811 | -3.2811 | 0.97885 | 2026-11-03 12:10 | 247.414 | 255.065 | 740.6 | 42.5108 | 44.7206 | -2.2097 | 268.3234 | 40.4 | 44.0811 | -3.6811 | 0.97 | 2026-11-03 12:10 | 232.948 | 236.712 | 700.8 | 39.452 | 42.5461 | -3.0941 | 255.2765 | 38.9 | 41.9377 | -3.0377 | 0.9841 | 2026-11-03 12:10 | 433.556 | 462.9194 | -29.3634 | 2777.5161 | 419.5 | 456.2996 | -36.7996
2026-11-03 12:00 | 1010 | 49.08 | 329.765 | 335.605 | 938.9 | 55.9342 | 60.0754 | -4.1412 | 360.4521 | 54 | 59.2163 | -5.2163 | 0.9826 | 2026-11-03 12:00 | 334.967 | 341.044 | 948.5 | 56.8407 | 60.0754 | -3.2347 | 360.4521 | 56.3 | 59.2163 | -2.9163 | 0.98218 | 2026-11-03 12:00 | 326.66 | 336.146 | 930.3 | 56.0243 | 60.0754 | -4.051 | 360.4521 | 53.7 | 59.2163 | -5.5163 | 0.97178 | 2026-11-03 12:00 | 331.66 | 337.636 | 942.3 | 56.2727 | 60.0754 | -3.8027 | 360.4521 | 55.2 | 59.2163 | -4.0163 | 0.9823 | 2026-11-03 12:00 | 246.51 | 250.595 | 698.2 | 41.7658 | 44.5003 | -2.7344 | 267.0016 | 41.1 | 43.8639 | -2.7639 | 0.9837 | 2026-11-03 12:00 | 244.273 | 249.141 | 695.7 | 41.5235 | 44.5003 | -2.9768 | 267.0016 | 40.7 | 43.8639 | -3.1639 | 0.98046 | 2026-11-03 12:00 | 243.571 | 248.958 | 694.4 | 41.493 | 44.5003 | -3.0073 | 267.0016 | 40.7 | 43.8639 | -3.1639 | 0.97836 | 2026-11-03 12:00 | 245.559 | 252.323 | 700.2 | 42.0538 | 44.5003 | -2.4464 | 267.0016 | 41.1 | 43.8639 | -2.7639 | 0.97319 | 2026-11-03 12:00 | 231.949 | 235.697 | 661.9 | 39.2828 | 42.3365 | -3.0537 | 254.0189 | 38 | 41.7311 | -3.7311 | 0.9841 | 2026-11-03 12:00 | 431.1908 | 460.639 | -29.4481 | 2763.8338 | 420.8 | 454.0518 | -33.2518
2026-11-03 11:50 | 991 | 49.08 | 324.635 | 330.316 | 884.9 | 55.0527 | 58.9452 | -3.8926 | 353.6713 | 53.9 | 58.1023 | -4.2023 | 0.9828 | 2026-11-03 11:50 | 329.559 | 335.374 | 892.2 | 55.8957 | 58.9452 | -3.0496 | 353.6713 | 54 | 58.1023 | -4.1023 | 0.98266 | 2026-11-03 11:50 | 321.681 | 331.047 | 876.6 | 55.1745 | 58.9452 | -3.7707 | 353.6713 | 53.5 | 58.1023 | -4.6023 | 0.97171 | 2026-11-03 11:50 | 326.299 | 332.179 | 887.1 | 55.3632 | 58.9452 | -3.5821 | 353.6713 | 54.1 | 58.1023 | -4.0023 | 0.9823 | 2026-11-03 11:50 | 242.682 | 246.628 | 657.1 | 41.1047 | 43.6631 | -2.5585 | 261.9788 | 40.3 | 43.0387 | -2.7387 | 0.984 | 2026-11-03 11:50 | 240.882 | 245.621 | 655 | 40.9368 | 43.6631 | -2.7263 | 261.9788 | 39.9 | 43.0387 | -3.1387 | 0.98071 | 2026-11-03 11:50 | 240.478 | 245.318 | 653.7 | 40.8863 | 43.6631 | -2.7768 | 261.9788 | 39.8 | 43.0387 | -3.2387 | 0.98027 | 2026-11-03 11:50 | 242.322 | 249.493 | 659.1 | 41.5822 | 43.6631 | -2.081 | 261.9788 | 40.6 | 43.0387 | -2.4387 | 0.97126 | 2026-11-03 11:50 | 229.055 | 232.779 | 623.9 | 38.7965 | 41.5401 | -2.7436 | 249.2404 | 38 | 40.946 | -2.946 | 0.984 | 2026-11-03 11:50 | 424.7925 | 451.9735 | -27.181 | 2711.8409 | 414.1 | 445.5103 | -31.4103
2026-11-03 11:40 | 975 | 48.79 | 321.994 | 327.563 | 831 | 54.5938 | 58.0578 | -3.464 | 348.3469 | 53.6 | 57.2276 | -3.6276 | 0.983 | 2026-11-03 11:40 | 325.426 | 331.189 | 838.2 | 55.1982 | 58.0578 | -2.8597 | 348.3469 | 55.9 | 57.2276 | -1.3276 | 0.9826 | 2026-11-03 11:40 | 318.993 | 328.109 | 823.1 | 54.6848 | 58.0578 | -3.373 | 348.3469 | 53.1 | 57.2276 | -4.1276 | 0.97222 | 2026-11-03 11:40 | 322.533 | 328.278 | 833 | 54.713 | 58.0578 | -3.3448 | 348.3469 | 53 | 57.2276 | -4.2276 | 0.9825 | 2026-11-03 11:40 | 241.086 | 244.955 | 616.8 | 40.8258 | 43.0058 | -2.18 | 258.0347 | 40.2 | 42.3908 | -2.1908 | 0.98421 | 2026-11-03 11:40 | 238.359 | 243.013 | 615.1 | 40.5022 | 43.0058 | -2.5036 | 258.0347 | 39.3 | 42.3908 | -3.0908 | 0.98085 | 2026-11-03 11:40 | 238.156 | 242.779 | 613.9 | 40.4632 | 43.0058 | -2.5426 | 258.0347 | 39.2 | 42.3908 | -3.1908 | 0.98096 | 2026-11-03 11:40 | 239.474 | 246.452 | 618.5 | 41.0753 | 43.0058 | -1.9305 | 258.0347 | 38.9 | 42.3908 | -3.4908 | 0.97169 | 2026-11-03 11:40 | 226.501 | 230.115 | 585.9 | 38.3525 | 40.9147 | -2.5622 | 245.4881 | 37.3 | 40.3296 | -3.0296 | 0.98429 | 2026-11-03 11:40 | 420.4088 | 445.1691 | -24.7603 | 2671.0147 | 410.5 | 438.8032 | -28.3032
2026-11-03 11:30 | 958 | 49.08 | 316.355 | 321.859 | 777.4 | 53.6432 | 56.9824 | -3.3392 | 341.8942 | 51.6 | 56.1675 | -4.5675 | 0.9829 | 2026-11-03 11:30 | 319.508 | 325.131 | 782.3 | 54.1885 | 56.9824 | -2.7939 | 341.8942 | 50.8 | 56.1675 | -5.3675 | 0.98271 | 2026-11-03 11:30 | 313.713 | 322.949 | 770 | 53.8248 | 56.9824 | -3.1575 | 341.8942 | 51.9 | 56.1675 | -4.2675 | 0.9714 | 2026-11-03 11:30 | 317.098 | 322.713 | 780 | 53.7855 | 56.9824 | -3.1969 | 341.8942 | 52.6 | 56.1675 | -3.5675 | 0.9826 | 2026-11-03 11:30 | 236.523 | 240.344 | 576.6 | 40.0573 | 42.2092 | -2.1518 | 253.255 | 38.7 | 41.6056 | -2.9056 | 0.9841 | 2026-11-03 11:30 | 234.468 | 239.068 | 575.8 | 39.8447 | 42.2092 | -2.3645 | 253.255 | 38.8 | 41.6056 | -2.8056 | 0.98076 | 2026-11-03 11:30 | 234.073 | 238.484 | 574.7 | 39.7473 | 42.2092 | -2.4618 | 253.255 | 38.8 | 41.6056 | -2.8056 | 0.9815 | 2026-11-03 11:30 | 235.542 | 242.42 | 579.6 | 40.4033 | 42.2092 | -1.8058 | 253.255 | 39 | 41.6056 | -2.6056 | 0.97163 | 2026-11-03 11:30 | 222.657 | 226.185 | 548.6 | 37.6975 | 40.1568 | -2.4593 | 240.9407 | 36.8 | 39.5825 | -2.7825 | 0.9844 | 2026-11-03 11:30 | 413.1922 | 436.9229 | -23.7307 | 2621.5374 | 399 | 430.6749 | -31.6749
2026-11-03 11:20 | 938 | 49.36 | 309.348 | 315.077 | 725.8 | 52.5128 | 55.733 | -3.2202 | 334.3983 | 52.3 | 54.9361 | -2.6361 | 0.98182 | 2026-11-03 11:20 | 313.789 | 319.313 | 731.5 | 53.2188 | 55.733 | -2.5142 | 334.3983 | 51.5 | 54.9361 | -3.4361 | 0.9827 | 2026-11-03 11:20 | 307.2 | 316.113 | 718.1 | 52.6855 | 55.733 | -3.0475 | 334.3983 | 50.4 | 54.9361 | -4.5361 | 0.9718 | 2026-11-03 11:20 | 310.957 | 316.399 | 727.4 | 52.7332 | 55.733 | -2.9999 | 334.3983 | 51.1 | 54.9361 | -3.8361 | 0.9828 | 2026-11-03 11:20 | 232.125 | 235.862 | 537.9 | 39.3103 | 41.2837 | -1.9734 | 247.7024 | 38 | 40.6934 | -2.6934 | 0.98416 | 2026-11-03 11:20 | 229.938 | 234.275 | 537 | 39.0458 | 41.2837 | -2.2379 | 247.7024 | 37.7 | 40.6934 | -2.9934 | 0.98149 | 2026-11-03 11:20 | 229.83 | 234.116 | 535.9 | 39.0193 | 41.2837 | -2.2644 | 247.7024 | 37.6 | 40.6934 | -3.0934 | 0.98169 | 2026-11-03 11:20 | 231.227 | 237.878 | 540.6 | 39.6463 | 41.2837 | -1.6374 | 247.7024 | 37.9 | 40.6934 | -2.7934 | 0.97204 | 2026-11-03 11:20 | 218.758 | 222.171 | 511.8 | 37.0285 | 39.2764 | -2.2479 | 235.6582 | 36.4 | 38.7147 | -2.3147 | 0.98464 | 2026-11-03 11:20 | 405.2007 | 427.3435 | -22.1428 | 2564.061 | 392.9 | 421.2325 | -28.3325
2026-11-03 11:10 | 912 | 49.08 | 303.81 | 309.001 | 673.5 | 51.5002 | 54.2463 | -2.7461 | 325.4776 | 49.1 | 53.4705 | -4.3705 | 0.9832 | 2026-11-03 11:10 | 307.986 | 313.344 | 680 | 52.224 | 54.2463 | -2.0223 | 325.4776 | 50.4 | 53.4705 | -3.0705 | 0.9829 | 2026-11-03 11:10 | 301.323 | 309.679 | 667.7 | 51.6132 | 54.2463 | -2.6331 | 325.4776 | 49.4 | 53.4705 | -4.0705 | 0.97302 | 2026-11-03 11:10 | 305.472 | 310.755 | 676.3 | 51.7925 | 54.2463 | -2.4538 | 325.4776 | 50 | 53.4705 | -3.4705 | 0.983 | 2026-11-03 11:10 | 227.44 | 231.044 | 499.9 | 38.5073 | 40.1824 | -1.6751 | 241.0945 | 37.3 | 39.6078 | -2.3078 | 0.9844 | 2026-11-03 11:10 | 225.517 | 229.983 | 499.3 | 38.3305 | 40.1824 | -1.8519 | 241.0945 | 37.5 | 39.6078 | -2.1078 | 0.98058 | 2026-11-03 11:10 | 225.245 | 229.877 | 498.3 | 38.3128 | 40.1824 | -1.8696 | 241.0945 | 37.5 | 39.6078 | -2.1078 | 0.97985 | 2026-11-03 11:10 | 226.529 | 233.388 | 502.7 | 38.898 | 40.1824 | -1.2844 | 241.0945 | 37.7 | 39.6078 | -1.9078 | 0.97061 | 2026-11-03 11:10 | 214.249 | 217.578 | 475.4 | 36.263 | 38.2286 | -1.9656 | 229.3716 | 35.1 | 37.6819 | -2.5819 | 0.9847 | 2026-11-03 11:10 | 397.4415 | 415.9433 | -18.5018 | 2495.6598 | 384 | 409.9953 | -25.9953
2026-11-03 11:00 | 883 | 49.08 | 295.657 | 301.839 | 624.4 | 50.3065 | 52.5213 | -2.2148 | 315.128 | 48.5 | 51.7703 | -3.2703 | 0.97952 | 2026-11-03 11:00 | 299.884 | 305.008 | 629.6 | 50.8347 | 52.5213 | -1.6867 | 315.128 | 49.1 | 51.7703 | -2.6703 | 0.9832 | 2026-11-03 11:00 | 294.065 | 302.201 | 618.3 | 50.3668 | 52.5213 | -2.1545 | 315.128 | 48.7 | 51.7703 | -3.0703 | 0.97308 | 2026-11-03 11:00 | 297.235 | 302.345 | 626.3 | 50.3908 | 52.5213 | -2.1305 | 315.128 | 49.4 | 51.7703 | -2.3703 | 0.9831 | 2026-11-03 11:00 | 221.308 | 224.724 | 462.6 | 37.454 | 38.9047 | -1.4507 | 233.4281 | 37.1 | 38.3483 | -1.2483 | 0.9848 | 2026-11-03 11:00 | 219.166 | 223.419 | 461.8 | 37.2365 | 38.9047 | -1.6682 | 233.4281 | 35.9 | 38.3483 | -2.4483 | 0.98096 | 2026-11-03 11:00 | 219.023 | 223.159 | 460.8 | 37.1932 | 38.9047 | -1.7115 | 233.4281 | 35.8 | 38.3483 | -2.5483 | 0.98147 | 2026-11-03 11:00 | 220.404 | 226.981 | 465 | 37.8302 | 38.9047 | -1.0745 | 233.4281 | 36.1 | 38.3483 | -2.2483 | 0.97102 | 2026-11-03 11:00 | 208.201 | 211.147 | 440.3 | 35.1912 | 37.013 | -1.8218 | 222.0779 | 34.2 | 36.4837 | -2.2837 | 0.98605 | 2026-11-03 11:00 | 386.8038 | 402.717 | -15.9132 | 2416.3022 | 374.8 | 396.9582 | -22.1582
2026-11-03 10:50 | 860 | 48.79 | 290.158 | 294.966 | 575.9 | 49.161 | 51.21 | -2.049 | 307.2598 | 49.8 | 50.4777 | -0.67767 | 0.9837 | 2026-11-03 10:50 | 293.661 | 298.588 | 580.5 | 49.7647 | 51.21 | -1.4453 | 307.2598 | 48.4 | 50.4777 | -2.0777 | 0.9835 | 2026-11-03 10:50 | 287.831 | 295.515 | 569.6 | 49.2525 | 51.21 | -1.9575 | 307.2598 | 47.5 | 50.4777 | -2.9777 | 0.974 | 2026-11-03 10:50 | 291.001 | 295.883 | 576.9 | 49.3138 | 51.21 | -1.8961 | 307.2598 | 47.4 | 50.4777 | -3.0777 | 0.9835 | 2026-11-03 10:50 | 216.483 | 219.782 | 425.5 | 36.6303 | 37.9333 | -1.303 | 227.5999 | 34.8 | 37.3909 | -2.5909 | 0.98499 | 2026-11-03 10:50 | 214.634 | 218.397 | 425.9 | 36.3995 | 37.9333 | -1.5338 | 227.5999 | 35 | 37.3909 | -2.3909 | 0.98277 | 2026-11-03 10:50 | 214.496 | 218.495 | 425 | 36.4158 | 37.9333 | -1.5175 | 227.5999 | 35.4 | 37.3909 | -1.9909 | 0.9817 | 2026-11-03 10:50 | 215.66 | 221.942 | 428.9 | 36.9903 | 37.9333 | -0.94298 | 227.5999 | 35.6 | 37.3909 | -1.7909 | 0.9717 | 2026-11-03 10:50 | 203.717 | 206.798 | 406.1 | 34.4663 | 36.0888 | -1.6225 | 216.5331 | 33.7 | 35.5728 | -1.8728 | 0.9851 | 2026-11-03 10:50 | 378.3943 | 392.662 | -14.2677 | 2355.9719 | 367.6 | 387.0469 | -19.4469
2026-11-03 10:40 | 828 | 48.79 | 280.72 | 285.256 | 526.1 | 47.5427 | 49.3045 | -1.7618 | 295.8269 | 44.5 | 48.5994 | -4.0994 | 0.9841 | 2026-11-03 10:40 | 284.483 | 289.197 | 532.1 | 48.1995 | 49.3045 | -1.105 | 295.8269 | 46.9 | 48.5994 | -1.6994 | 0.9837 | 2026-11-03 10:40 | 278.897 | 286.139 | 522.1 | 47.6898 | 49.3045 | -1.6147 | 295.8269 | 45.3 | 48.5994 | -3.2994 | 0.97469 | 2026-11-03 10:40 | 282.559 | 287.212 | 529.5 | 47.8687 | 49.3045 | -1.4358 | 295.8269 | 46.5 | 48.5994 | -2.0994 | 0.9838 | 2026-11-03 10:40 | 210.346 | 213.491 | 390.7 | 35.5818 | 36.5218 | -0.94001 | 219.131 | 34.6 | 35.9996 | -1.3996 | 0.98527 | 2026-11-03 10:40 | 208.717 | 212.346 | 390.9 | 35.391 | 36.5218 | -1.1308 | 219.131 | 34.4 | 35.9996 | -1.5996 | 0.98291 | 2026-11-03 10:40 | 208.266 | 212.225 | 389.6 | 35.3708 | 36.5218 | -1.151 | 219.131 | 34.4 | 35.9996 | -1.5996 | 0.98135 | 2026-11-03 10:40 | 209.439 | 215.763 | 393.3 | 35.9605 | 36.5218 | -0.56134 | 219.131 | 34.6 | 35.9996 | -1.3996 | 0.97069 | 2026-11-03 10:40 | 198.281 | 201.239 | 372.4 | 33.5398 | 34.746 | -1.2062 | 208.476 | 32.7 | 34.2491 | -1.5491 | 0.9853 | 2026-11-03 10:40 | 367.1447 | 378.0513 | -10.9066 | 2268.3078 | 353.9 | 372.6452 | -18.7452
2026-11-03 10:30 | 804 | 48.79 | 273.162 | 277.519 | 481.6 | 46.2532 | 47.8754 | -1.6222 | 287.2522 | 44.4 | 47.1908 | -2.7908 | 0.9843 | 2026-11-03 10:30 | 275.452 | 279.931 | 485.2 | 46.6552 | 47.8754 | -1.2202 | 287.2522 | 45.6 | 47.1908 | -1.5908 | 0.984 | 2026-11-03 10:30 | 270.765 | 278.267 | 476.8 | 46.3778 | 47.8754 | -1.4975 | 287.2522 | 44.1 | 47.1908 | -3.0908 | 0.97304 | 2026-11-03 10:30 | 274.323 | 278.812 | 483 | 46.4687 | 47.8754 | -1.4067 | 287.2522 | 45.3 | 47.1908 | -1.8908 | 0.9839 | 2026-11-03 10:30 | 204.021 | 207.044 | 356.1 | 34.5073 | 35.4632 | -0.9559 | 212.7794 | 34.5 | 34.9561 | -0.45611 | 0.9854 | 2026-11-03 10:30 | 203.094 | 206.471 | 356.5 | 34.4118 | 35.4632 | -1.0514 | 212.7794 | 33.5 | 34.9561 | -1.4561 | 0.98364 | 2026-11-03 10:30 | 202.726 | 206.39 | 355.2 | 34.3983 | 35.4632 | -1.0649 | 212.7794 | 32.9 | 34.9561 | -2.0561 | 0.98225 | 2026-11-03 10:30 | 204.175 | 210.064 | 358.7 | 35.0107 | 35.4632 | -0.45257 | 212.7794 | 33.2 | 34.9561 | -1.7561 | 0.97197 | 2026-11-03 10:30 | 192.956 | 195.835 | 339.7 | 32.6392 | 33.7389 | -1.0997 | 202.4333 | 31.3 | 33.2564 | -1.9564 | 0.9853 | 2026-11-03 10:30 | 356.7222 | 367.0933 | -10.3711 | 2202.5598 | 344.8 | 361.8439 | -17.0439
2026-11-03 10:20 | 772 | 48.79 | 263.429 | 267.787 | 437.2 | 44.6312 | 45.9699 | -1.3387 | 275.8193 | 43.1 | 45.3125 | -2.2125 | 0.98373 | 2026-11-03 10:20 | 266.644 | 270.897 | 439.6 | 45.1495 | 45.9699 | -0.82038 | 275.8193 | 44 | 45.3125 | -1.3125 | 0.9843 | 2026-11-03 10:20 | 261.822 | 268.49 | 432.7 | 44.7483 | 45.9699 | -1.2215 | 275.8193 | 42.7 | 45.3125 | -2.6125 | 0.97516 | 2026-11-03 10:20 | 264.615 | 268.863 | 437.7 | 44.8105 | 45.9699 | -1.1594 | 275.8193 | 42.6 | 45.3125 | -2.7125 | 0.9842 | 2026-11-03 10:20 | 196.249 | 199.136 | 321.6 | 33.1893 | 34.0518 | -0.86243 | 204.3106 | 31.2 | 33.5648 | -2.3648 | 0.9855 | 2026-11-03 10:20 | 195.586 | 198.862 | 323 | 33.1437 | 34.0518 | -0.9081 | 204.3106 | 31.9 | 33.5648 | -1.6648 | 0.98353 | 2026-11-03 10:20 | 194.831 | 198.237 | 322.3 | 33.0395 | 34.0518 | -1.0123 | 204.3106 | 31.8 | 33.5648 | -1.7648 | 0.98282 | 2026-11-03 10:20 | 195.86 | 201.516 | 325.5 | 33.586 | 34.0518 | -0.46576 | 204.3106 | 31.9 | 33.5648 | -1.6648 | 0.97193 | 2026-11-03 10:20 | 185.374 | 188.121 | 308.4 | 31.3535 | 32.396 | -1.0425 | 194.3762 | 30.3 | 31.9328 | -1.6328 | 0.9854 | 2026-11-03 10:20 | 343.6515 | 352.4826 | -8.8311 | 2114.8957 | 329.5 | 347.4421 | -17.9421
2026-11-03 10:10 | 734 | 48.79 | 251.763 | 255.675 | 394.1 | 42.6125 | 43.7071 | -1.0946 | 262.2427 | 41.2 | 43.0821 | -1.8821 | 0.9847 | 2026-11-03 10:10 | 254.782 | 258.793 | 395.6 | 43.1322 | 43.7071 | -0.57495 | 262.2427 | 42.8 | 43.0821 | -0.2821 | 0.9845 | 2026-11-03 10:10 | 250.892 | 256.86 | 390 | 42.81 | 43.7071 | -0.89712 | 262.2427 | 41.4 | 43.0821 | -1.6821 | 0.97677 | 2026-11-03 10:10 | 253.681 | 257.675 | 395.1 | 42.9458 | 43.7071 | -0.76128 | 262.2427 | 42 | 43.0821 | -1.0821 | 0.9845 | 2026-11-03 10:10 | 188.092 | 190.859 | 290.4 | 31.8098 | 32.3756 | -0.56581 | 194.2538 | 30.6 | 31.9127 | -1.3127 | 0.9855 | 2026-11-03 10:10 | 187.398 | 190.578 | 291.1 | 31.763 | 32.3756 | -0.61264 | 194.2538 | 30.7 | 31.9127 | -1.2127 | 0.98331 | 2026-11-03 10:10 | 186.663 | 189.931 | 290.5 | 31.6552 | 32.3756 | -0.72047 | 194.2538 | 30.9 | 31.9127 | -1.0127 | 0.98279 | 2026-11-03 10:10 | 187.831 | 193.518 | 293.6 | 32.253 | 32.3756 | -0.12264 | 194.2538 | 30.8 | 31.9127 | -1.1127 | 0.97061 | 2026-11-03 10:10 | 178.045 | 180.628 | 278.1 | 30.1047 | 30.8014 | -0.69675 | 184.8085 | 29.1 | 30.361 | -1.261 | 0.9857 | 2026-11-03 10:10 | 329.0862 | 335.1324 | -6.0463 | 2010.7946 | 319.5 | 330.34 | -10.84
2026-11-03 10:00 | 705 | 49.36 | 243.342 | 247.048 | 352.9 | 41.1747 | 41.8889 | -0.71424 | 251.3335 | 40.8 | 41.2899 | -0.4899 | 0.985 | 2026-11-03 10:00 | 245.148 | 248.923 | 352.8 | 41.4872 | 41.8889 | -0.40174 | 251.3335 | 38.8 | 41.2899 | -2.4899 | 0.98483 | 2026-11-03 10:00 | 241.043 | 247.132 | 348.6 | 41.1887 | 41.8889 | -0.70024 | 251.3335 | 39.3 | 41.2899 | -1.9899 | 0.97536 | 2026-11-03 10:00 | 244.432 | 248.23 | 353.1 | 41.3717 | 41.8889 | -0.51724 | 251.3335 | 39.8 | 41.2899 | -1.4899 | 0.9847 | 2026-11-03 10:00 | 180.924 | 183.512 | 259.8 | 30.5853 | 31.0288 | -0.44349 | 186.1729 | 29.6 | 30.5851 | -0.98511 | 0.9859 | 2026-11-03 10:00 | 180.677 | 183.426 | 260.4 | 30.571 | 31.0288 | -0.45782 | 186.1729 | 29.5 | 30.5851 | -1.0851 | 0.98501 | 2026-11-03 10:00 | 179.493 | 182.481 | 259.6 | 30.4135 | 31.0288 | -0.61532 | 186.1729 | 28.9 | 30.5851 | -1.6851 | 0.98363 | 2026-11-03 10:00 | 180.71 | 185.848 | 262.8 | 30.9747 | 31.0288 | -0.054156 | 186.1729 | 29.5 | 30.5851 | -1.0851 | 0.97235 | 2026-11-03 10:00 | 171.434 | 173.886 | 249 | 28.981 | 29.5201 | -0.53908 | 177.1205 | 28 | 29.0979 | -1.0979 | 0.9859 | 2026-11-03 10:00 | 316.7477 | 321.191 | -4.4433 | 1927.1461 | 304.2 | 316.598 | -12.398
2026-11-03 09:50 | 670 | 49.08 | 232.215 | 235.679 | 312.1 | 39.2798 | 39.852 | -0.57213 | 239.1118 | 37.1 | 39.2821 | -2.1821 |  | 2026-11-03 09:50 | 234.621 | 238.17 | 314 | 39.695 | 39.852 | -0.15697 | 239.1118 | 38.5 | 39.2821 | -0.78209 |  | 2026-11-03 09:50 | 230.185 | 235.758 | 309.3 | 39.293 | 39.852 | -0.55897 | 239.1118 | 36.9 | 39.2821 | -2.3821 |  | 2026-11-03 09:50 | 233.77 | 237.282 | 313.3 | 39.547 | 39.852 | -0.30497 | 239.1118 | 37.5 | 39.2821 | -1.7821 |  | 2026-11-03 09:50 | 173.027 | 175.466 | 230.2 | 29.2443 | 29.52 | -0.27564 | 177.1199 | 28 | 29.0978 | -1.0978 |  | 2026-11-03 09:50 | 173.017 | 175.438 | 230.9 | 29.2397 | 29.52 | -0.28031 | 177.1199 | 28 | 29.0978 | -1.0978 |  | 2026-11-03 09:50 | 172.013 | 174.824 | 230.7 | 29.1373 | 29.52 | -0.38264 | 177.1199 | 27.9 | 29.0978 | -1.1978 |  | 2026-11-03 09:50 | 173.188 | 178.315 | 233.3 | 29.7192 | 29.52 | 0.19919 | 177.1199 | 28.1 | 29.0978 | -0.99784 |  | 2026-11-03 09:50 | 164.659 | 166.963 | 221 | 27.8272 | 28.0846 | -0.25743 | 168.5076 | 26.7 | 27.683 | -0.98299 |  | 2026-11-03 09:50 | 302.9825 | 305.5724 | -2.5899 | 1833.4343 | 288.7 | 301.2027 | -12.5027
2026-11-03 09:40 | 630 | 49.36 | 220.856 | 223.969 | 275 | 37.3282 | 37.4326 | -0.10448 | 224.5959 | 35.2 | 36.8974 | -1.6974 |  | 2026-11-03 09:40 | 222.655 | 225.885 | 275.5 | 37.6475 | 37.4326 | 0.21486 | 224.5959 | 35.1 | 36.8974 | -1.7974 |  | 2026-11-03 09:40 | 218.953 | 223.761 | 272.4 | 37.2935 | 37.4326 | -0.13914 | 224.5959 | 35.8 | 36.8974 | -1.0974 |  | 2026-11-03 09:40 | 221.741 | 224.958 | 275.8 | 37.493 | 37.4326 | 0.060357 | 224.5959 | 36.3 | 36.8974 | -0.59736 |  | 2026-11-03 09:40 | 164.043 | 166.305 | 202.2 | 27.7175 | 27.7279 | -0.010384 | 166.3673 | 26.5 | 27.3314 | -0.83137 |  | 2026-11-03 09:40 | 164.354 | 166.62 | 202.9 | 27.77 | 27.7279 | 0.042116 | 166.3673 | 26.5 | 27.3314 | -0.83137 |  | 2026-11-03 09:40 | 163.322 | 165.574 | 202.8 | 27.5957 | 27.7279 | -0.13222 | 166.3673 | 26.4 | 27.3314 | -0.93137 |  | 2026-11-03 09:40 | 164.376 | 168.818 | 205.2 | 28.1363 | 27.7279 | 0.40845 | 166.3673 | 26.6 | 27.3314 | -0.73137 |  | 2026-11-03 09:40 | 156 | 158.135 | 194.3 | 26.3558 | 26.3796 | -0.023814 | 158.2779 | 25.2 | 26.0024 | -0.80242 |  | 2026-11-03 09:40 | 287.3375 | 287.0218 | 0.31575 | 1722.1305 | 273.6 | 282.9173 | -9.3173
2026-11-03 09:30 | 594 | 49.08 | 209.083 | 212.009 | 239.8 | 35.3348 | 35.3314 | 0.0033869 | 211.9887 | 34.3 | 34.8262 | -0.52621 |  | 2026-11-03 09:30 | 210.748 | 213.74 | 240.4 | 35.6233 | 35.3314 | 0.29189 | 211.9887 | 33.7 | 34.8262 | -1.1262 |  | 2026-11-03 09:30 | 206.914 | 211.295 | 236.6 | 35.2158 | 35.3314 | -0.11561 | 211.9887 | 33.1 | 34.8262 | -1.7262 |  | 2026-11-03 09:30 | 209.629 | 212.605 | 239.5 | 35.4342 | 35.3314 | 0.10272 | 211.9887 | 33.6 | 34.8262 | -1.2262 |  | 2026-11-03 09:30 | 154.791 | 156.862 | 175.7 | 26.1437 | 26.1714 | -0.027775 | 157.0287 | 24.8 | 25.7972 | -0.99719 |  | 2026-11-03 09:30 | 154.452 | 156.518 | 176.4 | 26.0863 | 26.1714 | -0.085108 | 157.0287 | 25.1 | 25.7972 | -0.69719 |  | 2026-11-03 09:30 | 154.405 | 156.47 | 176.4 | 26.0783 | 26.1714 | -0.093108 | 157.0287 | 25 | 25.7972 | -0.79719 |  | 2026-11-03 09:30 | 155.787 | 160.075 | 178.6 | 26.6792 | 26.1714 | 0.50772 | 157.0287 | 25.2 | 25.7972 | -0.59719 |  | 2026-11-03 09:30 | 147.49 | 149.463 | 169.1 | 24.9105 | 24.8989 | 0.011615 | 149.3933 | 23.9 | 24.5428 | -0.64283 |  | 2026-11-03 09:30 | 271.5062 | 270.9104 | 0.59573 | 1625.4626 | 258.7 | 267.0364 | -8.3364
2026-11-03 09:20 | 553 | 48.5 | 195.225 | 197.877 | 205.5 | 32.9795 | 32.9657 | 0.013838 | 197.794 | 31.2 | 32.4943 | -1.2943 |  | 2026-11-03 09:20 | 197.183 | 200.277 | 206.7 | 33.3795 | 32.9657 | 0.41384 | 197.794 | 32.3 | 32.4943 | -0.19425 |  | 2026-11-03 09:20 | 193.972 | 197.901 | 203.5 | 32.9835 | 32.9657 | 0.017838 | 197.794 | 31.3 | 32.4943 | -1.1943 |  | 2026-11-03 09:20 | 196.529 | 199.229 | 205.9 | 33.2048 | 32.9657 | 0.23917 | 197.794 | 31.7 | 32.4943 | -0.79425 |  | 2026-11-03 09:20 | 145.199 | 147.082 | 150.9 | 24.5137 | 24.419 | 0.094658 | 146.5141 | 23.4 | 24.0698 | -0.66982 |  | 2026-11-03 09:20 | 143.023 | 145.901 | 151.3 | 24.3168 | 24.419 | -0.10218 | 146.5141 | 23 | 24.0698 | -1.0698 |  | 2026-11-03 09:20 | 144.618 | 146.483 | 151.4 | 24.4138 | 24.419 | -0.0051753 | 146.5141 | 23 | 24.0698 | -1.0698 |  | 2026-11-03 09:20 | 145.967 | 150.025 | 153.4 | 25.0042 | 24.419 | 0.58516 | 146.5141 | 23.6 | 24.0698 | -0.46982 |  | 2026-11-03 09:20 | 138.01 | 139.8 | 145.2 | 23.3 | 23.2317 | 0.068338 | 139.39 | 22.3 | 22.8994 | -0.59945 |  | 2026-11-03 09:20 | 254.0958 | 252.7703 | 1.3255 | 1516.6221 | 241.8 | 249.1557 | -7.3557
2026-11-03 09:10 | 512 | 47.64 | 180.535 | 183.854 | 174.3 | 30.6423 | 30.6217 | 0.020677 | 183.7299 | 29.2 | 30.1838 | -0.98377 |  | 2026-11-03 09:10 | 182.675 | 185.137 | 174.4 | 30.8562 | 30.6217 | 0.23451 | 183.7299 | 28.9 | 30.1838 | -1.2838 |  | 2026-11-03 09:10 | 179.738 | 183.247 | 172.2 | 30.5412 | 30.6217 | -0.08049 | 183.7299 | 28.5 | 30.1838 | -1.6838 |  | 2026-11-03 09:10 | 182.548 | 184.99 | 174.2 | 30.8317 | 30.6217 | 0.21001 | 183.7299 | 29.3 | 30.1838 | -0.88377 |  | 2026-11-03 09:10 | 134.473 | 136.189 | 127.5 | 22.6982 | 22.6827 | 0.015458 | 136.0963 | 21.6 | 22.3583 | -0.75835 |  | 2026-11-03 09:10 | 134.134 | 135.832 | 128.3 | 22.6387 | 22.6827 | -0.044042 | 136.0963 | 21.5 | 22.3583 | -0.85835 |  | 2026-11-03 09:10 | 134.35 | 136.051 | 128.4 | 22.6752 | 22.6827 | -0.0075417 | 136.0963 | 21.5 | 22.3583 | -0.85835 |  | 2026-11-03 09:10 | 135.297 | 138.72 | 129.8 | 23.12 | 22.6827 | 0.43729 | 136.0963 | 21.4 | 22.3583 | -0.95835 |  | 2026-11-03 09:10 | 128.222 | 129.845 | 122.9 | 21.6408 | 21.5798 | 0.061046 | 129.4787 | 20.3 | 21.2712 | -0.9712 |  | 2026-11-03 09:10 | 235.6442 | 234.7972 | 0.84692 | 1408.7835 | 222.2 | 231.4396 | -9.2396
2026-11-03 09:00 | 469 | 47.35 | 166.531 | 168.615 | 145.1 | 28.1025 | 28.0808 | 0.021664 | 168.485 | 26.2 | 27.6793 | -1.4793 |  | 2026-11-03 09:00 | 167.763 | 169.955 | 145.5 | 28.3258 | 28.0808 | 0.245 | 168.485 | 27.2 | 27.6793 | -0.47928 |  | 2026-11-03 09:00 | 165.379 | 168.53 | 143.7 | 28.0883 | 28.0808 | 0.0074968 | 168.485 | 26.3 | 27.6793 | -1.3793 |  | 2026-11-03 09:00 | 167.589 | 169.728 | 144.9 | 28.288 | 28.0808 | 0.20716 | 168.485 | 26.9 | 27.6793 | -0.77928 |  | 2026-11-03 09:00 | 123.534 | 125.085 | 105.9 | 20.8475 | 20.8006 | 0.04688 | 124.8037 | 19.7 | 20.5032 | -0.80317 |  | 2026-11-03 09:00 | 123.345 | 124.868 | 106.8 | 20.8113 | 20.8006 | 0.010714 | 124.8037 | 19.8 | 20.5032 | -0.70317 |  | 2026-11-03 09:00 | 123.464 | 125.002 | 106.9 | 20.8337 | 20.8006 | 0.033047 | 124.8037 | 19.7 | 20.5032 | -0.80317 |  | 2026-11-03 09:00 | 124.423 | 127.725 | 108.4 | 21.2875 | 20.8006 | 0.48688 | 124.8037 | 19.9 | 20.5032 | -0.60317 |  | 2026-11-03 09:00 | 118.114 | 119.585 | 102.6 | 19.9308 | 19.7892 | 0.14162 | 118.7353 | 18.9 | 19.5062 | -0.60623 |  | 2026-11-03 09:00 | 216.5155 | 215.315 | 1.2005 | 1291.8902 | 204.6 | 212.236 | -7.636
2026-11-03 08:50 | 427 | 47.35 | 152.318 | 154.184 | 118.9 | 25.6973 | 25.5661 | 0.1312 | 153.3968 | 24.6 | 25.2005 | -0.60054 |  | 2026-11-03 08:50 | 152.281 | 154.633 | 118.3 | 25.7722 | 25.5661 | 0.20603 | 153.3968 | 23.6 | 25.2005 | -1.6005 |  | 2026-11-03 08:50 | 150.514 | 153.025 | 117.4 | 25.5042 | 25.5661 | -0.061968 | 153.3968 | 24 | 25.2005 | -1.2005 |  | 2026-11-03 08:50 | 152.765 | 154.667 | 118 | 25.7778 | 25.5661 | 0.2117 | 153.3968 | 23.8 | 25.2005 | -1.4005 |  | 2026-11-03 08:50 | 112.23 | 113.593 | 86.2 | 18.9322 | 18.9379 | -0.0057109 | 113.6273 | 17.6 | 18.6671 | -1.0671 |  | 2026-11-03 08:50 | 112.262 | 113.591 | 87 | 18.9318 | 18.9379 | -0.0060442 | 113.6273 | 17.6 | 18.6671 | -1.0671 |  | 2026-11-03 08:50 | 112.08 | 113.441 | 87.2 | 18.9068 | 18.9379 | -0.031044 | 113.6273 | 17.8 | 18.6671 | -0.86707 |  | 2026-11-03 08:50 | 113.431 | 116.519 | 88.5 | 19.4198 | 18.9379 | 0.48196 | 113.6273 | 18.1 | 18.6671 | -0.56707 |  | 2026-11-03 08:50 | 107.248 | 108.562 | 83.7 | 18.0937 | 18.017 | 0.076622 | 108.1023 | 17.1 | 17.7594 | -0.6594 |  | 2026-11-03 08:50 | 197.0358 | 196.0331 | 1.0027 | 1176.1986 | 184.2 | 193.2298 | -9.0298
2026-11-03 08:40 | 383 | 46.78 | 136.038 | 137.648 | 94.3 | 22.9413 | 22.9813 | -0.039983 | 137.8879 | 20.8 | 22.6527 | -1.8527 |  | 2026-11-03 08:40 | 137.132 | 138.798 | 94.7 | 23.133 | 22.9813 | 0.15168 | 137.8879 | 21.8 | 22.6527 | -0.85268 |  | 2026-11-03 08:40 | 134.952 | 137.049 | 93.4 | 22.8415 | 22.9813 | -0.13982 | 137.8879 | 21.2 | 22.6527 | -1.4527 |  | 2026-11-03 08:40 | 137.125 | 138.776 | 94.2 | 23.1293 | 22.9813 | 0.14802 | 137.8879 | 21.6 | 22.6527 | -1.0527 |  | 2026-11-03 08:40 | 100.64 | 101.831 | 68.6 | 16.9718 | 17.0232 | -0.051364 | 102.1392 | 15.7 | 16.7798 | -1.0798 |  | 2026-11-03 08:40 | 100.45 | 101.619 | 69.4 | 16.9365 | 17.0232 | -0.086697 | 102.1392 | 15.9 | 16.7798 | -0.87977 |  | 2026-11-03 08:40 | 100.585 | 101.745 | 69.4 | 16.9575 | 17.0232 | -0.065697 | 102.1392 | 15.6 | 16.7798 | -1.1798 |  | 2026-11-03 08:40 | 101.851 | 104.778 | 70.4 | 17.463 | 17.0232 | 0.4398 | 102.1392 | 15.8 | 16.7798 | -0.97977 |  | 2026-11-03 08:40 | 96.492 | 97.634 | 66.6 | 16.2723 | 16.1955 | 0.076869 | 97.1728 | 15 | 15.9639 | -0.96387 |  | 2026-11-03 08:40 | 176.6463 | 176.2135 | 0.43281 | 1057.2811 | 163.4 | 173.6937 | -10.2937
2026-11-03 08:30 | 334 | 43.34 | 118.35 | 119.715 | 73.5 | 19.9525 | 20.3024 | -0.34986 | 121.8141 | 18.3 | 20.012 | -1.712 |  | 2026-11-03 08:30 | 118.432 | 119.822 | 72.9 | 19.9703 | 20.3024 | -0.33202 | 121.8141 | 17.9 | 20.012 | -2.112 |  | 2026-11-03 08:30 | 116.512 | 118.195 | 72.2 | 19.6992 | 20.3024 | -0.60319 | 121.8141 | 17.7 | 20.012 | -2.312 |  | 2026-11-03 08:30 | 118.279 | 119.667 | 72.6 | 19.9445 | 20.3024 | -0.35786 | 121.8141 | 18.2 | 20.012 | -1.812 |  | 2026-11-03 08:30 | 86.726 | 87.762 | 52.9 | 14.627 | 15.0388 | -0.41178 | 90.2327 | 13.4 | 14.8237 | -1.4237 |  | 2026-11-03 08:30 | 86.211 | 87.214 | 53.5 | 14.5357 | 15.0388 | -0.50311 | 90.2327 | 13.5 | 14.8237 | -1.3237 |  | 2026-11-03 08:30 | 87.087 | 88.109 | 53.8 | 14.6848 | 15.0388 | -0.35395 | 90.2327 | 13.5 | 14.8237 | -1.3237 |  | 2026-11-03 08:30 | 88.077 | 90.531 | 54.6 | 15.0885 | 15.0388 | 0.049718 | 90.2327 | 13.6 | 14.8237 | -1.2237 |  | 2026-11-03 08:30 | 83.585 | 84.592 | 51.6 | 14.0987 | 14.3075 | -0.20887 | 85.8452 | 13 | 14.1029 | -1.1029 |  | 2026-11-03 08:30 | 152.6012 | 155.6721 | -3.0709 | 934.0325 | 139.1 | 153.446 | -14.346
2026-11-03 08:20 | 288 | 37.31 | 100.501 | 101.609 | 55.2 | 16.9348 | 17.901 | -0.9662 | 107.4062 | 15.2 | 17.645 | -2.445 |  | 2026-11-03 08:20 | 101.112 | 102.268 | 55 | 17.0447 | 17.901 | -0.85637 | 107.4062 | 15.3 | 17.645 | -2.345 |  | 2026-11-03 08:20 | 99.264 | 100.667 | 54.5 | 16.7778 | 17.901 | -1.1232 | 107.4062 | 15.1 | 17.645 | -2.545 |  | 2026-11-03 08:20 | 100.792 | 101.934 | 54.4 | 16.989 | 17.901 | -0.91203 | 107.4062 | 15.2 | 17.645 | -2.445 |  | 2026-11-03 08:20 | 72.983 | 73.869 | 39.5 | 12.3115 | 13.26 | -0.94853 | 79.5602 | 10.9 | 13.0704 | -2.1704 |  | 2026-11-03 08:20 | 74.505 | 75.372 | 40 | 12.562 | 13.26 | -0.69803 | 79.5602 | 11.2 | 13.0704 | -1.8704 |  | 2026-11-03 08:20 | 74.019 | 74.926 | 40.3 | 12.4877 | 13.26 | -0.77236 | 79.5602 | 11.2 | 13.0704 | -1.8704 |  | 2026-11-03 08:20 | 75.186 | 77.309 | 41 | 12.8848 | 13.26 | -0.37519 | 79.5602 | 11.4 | 13.0704 | -1.6704 |  | 2026-11-03 08:20 | 71.294 | 72.16 | 38.6 | 12.0267 | 12.6153 | -0.58861 | 75.6916 | 10.8 | 12.4349 | -1.6349 |  | 2026-11-03 08:20 | 130.019 | 137.2595 | -7.2405 | 823.5571 | 116.3 | 135.2967 | -18.9967
2026-11-03 08:10 | 240 | 29.27 | 82.198 | 83.061 | 40 | 13.8435 | 15.3562 | -1.5127 | 92.1372 | 12.4 | 15.1366 | -2.7366 |  | 2026-11-03 08:10 | 81.562 | 82.511 | 39.7 | 13.7518 | 15.3562 | -1.6044 | 92.1372 | 12.4 | 15.1366 | -2.7366 |  | 2026-11-03 08:10 | 81.113 | 82.028 | 39.4 | 13.6713 | 15.3562 | -1.6849 | 92.1372 | 12.2 | 15.1366 | -2.9366 |  | 2026-11-03 08:10 | 81.217 | 82.162 | 39.2 | 13.6937 | 15.3562 | -1.6625 | 92.1372 | 12.3 | 15.1366 | -2.8366 |  | 2026-11-03 08:10 | 59.938 | 60.715 | 28.6 | 10.1192 | 11.375 | -1.2558 | 68.2498 | 9 | 11.2123 | -2.2123 |  | 2026-11-03 08:10 | 60.914 | 61.842 | 28.8 | 10.307 | 11.375 | -1.068 | 68.2498 | 9.3 | 11.2123 | -1.9123 |  | 2026-11-03 08:10 | 60.529 | 61.289 | 29.1 | 10.2148 | 11.375 | -1.1601 | 68.2498 | 9.1 | 11.2123 | -2.1123 |  | 2026-11-03 08:10 | 61.412 | 63.283 | 29.6 | 10.5472 | 11.375 | -0.8278 | 68.2498 | 9.2 | 11.2123 | -2.0123 |  | 2026-11-03 08:10 | 58.256 | 59.017 | 27.8 | 9.8362 | 10.8219 | -0.98571 | 64.9312 | 8.7 | 10.6671 | -1.9671 |  | 2026-11-03 08:10 | 105.9847 | 117.7466 | -11.7619 | 706.4795 | 94.6 | 116.0628 | -21.4628
2026-11-03 08:00 | 196 | 26.4 | 65.886 | 66.659 | 27.6 | 11.1098 | 12.6688 | -1.559 | 76.0127 | 9.7 | 12.4876 | -2.7876 |  | 2026-11-03 08:00 | 66.01 | 66.901 | 27.3 | 11.1502 | 12.6688 | -1.5186 | 76.0127 | 9.8 | 12.4876 | -2.6876 |  | 2026-11-03 08:00 | 64.914 | 65.696 | 27.2 | 10.9493 | 12.6688 | -1.7195 | 76.0127 | 9.6 | 12.4876 | -2.8876 |  | 2026-11-03 08:00 | 65.098 | 65.902 | 26.9 | 10.9837 | 12.6688 | -1.6851 | 76.0127 | 9.4 | 12.4876 | -3.0876 |  | 2026-11-03 08:00 | 47.519 | 48.284 | 19.6 | 8.0473 | 9.3843 | -1.337 | 56.3057 | 7 | 9.2501 | -2.2501 |  | 2026-11-03 08:00 | 48.789 | 49.457 | 19.5 | 8.2428 | 9.3843 | -1.1415 | 56.3057 | 7.1 | 9.2501 | -2.1501 |  | 2026-11-03 08:00 | 48.465 | 49.158 | 20 | 8.193 | 9.3843 | -1.1913 | 56.3057 | 7.1 | 9.2501 | -2.1501 |  | 2026-11-03 08:00 | 49.199 | 50.644 | 20.4 | 8.4407 | 9.3843 | -0.94362 | 56.3057 | 7.3 | 9.2501 | -1.9501 |  | 2026-11-03 08:00 | 46.801 | 47.48 | 19.1 | 7.9133 | 8.928 | -1.0147 | 53.5679 | 6.9 | 8.8003 | -1.9003 |  | 2026-11-03 08:00 | 85.0302 | 97.1403 | -12.1101 | 582.8417 | 73.9 | 95.7512 | -21.8512
2026-11-03 07:50 | 154 | 23.82 | 50.58 | 51.246 | 17.9 | 8.541 | 10.0444 | -1.5034 | 60.2663 | 7.3 | 9.9007 | -2.6007 |  | 2026-11-03 07:50 | 49.803 | 50.814 | 17.5 | 8.469 | 10.0444 | -1.5754 | 60.2663 | 7.2 | 9.9007 | -2.7007 |  | 2026-11-03 07:50 | 49.728 | 50.403 | 17.6 | 8.4005 | 10.0444 | -1.6439 | 60.2663 | 7.1 | 9.9007 | -2.8007 |  | 2026-11-03 07:50 | 49.86 | 50.553 | 17.5 | 8.4255 | 10.0444 | -1.6189 | 60.2663 | 7.1 | 9.9007 | -2.8007 |  | 2026-11-03 07:50 | 36.535 | 37.106 | 12.6 | 6.1843 | 7.4403 | -1.2559 | 44.6417 | 5.2 | 7.3339 | -2.1339 |  | 2026-11-03 07:50 | 37.526 | 38.078 | 12.4 | 6.3463 | 7.4403 | -1.0939 | 44.6417 | 5.2 | 7.3339 | -2.1339 |  | 2026-11-03 07:50 | 37.182 | 37.72 | 12.9 | 6.2867 | 7.4403 | -1.1536 | 44.6417 | 5.3 | 7.3339 | -2.0339 |  | 2026-11-03 07:50 | 37.738 | 38.869 | 13.1 | 6.4782 | 7.4403 | -0.96211 | 44.6417 | 5.4 | 7.3339 | -1.9339 |  | 2026-11-03 07:50 | 35.824 | 36.395 | 12.2 | 6.0658 | 7.0785 | -1.0127 | 42.471 | 5.1 | 6.9773 | -1.8773 |  | 2026-11-03 07:50 | 65.1973 | 77.0171 | -11.8198 | 462.1027 | 54.9 | 75.9158 | -21.0158
2026-11-03 07:40 | 114 | 20.38 | 35.986 | 36.53 | 10.6 | 6.0883 | 7.5246 | -1.4363 | 45.1476 | 4.9 | 7.417 | -2.517 |  | 2026-11-03 07:40 | 35.193 | 36.106 | 10.3 | 6.0177 | 7.5246 | -1.5069 | 45.1476 | 4.8 | 7.417 | -2.617 |  | 2026-11-03 07:40 | 35.753 | 36.309 | 10.5 | 6.0515 | 7.5246 | -1.4731 | 45.1476 | 4.9 | 7.417 | -2.517 |  | 2026-11-03 07:40 | 35.68 | 36.253 | 10.4 | 6.0422 | 7.5246 | -1.4824 | 45.1476 | 4.9 | 7.417 | -2.517 |  | 2026-11-03 07:40 | 26.083 | 26.722 | 7.4 | 4.4537 | 5.5738 | -1.1201 | 33.4427 | 3.6 | 5.4941 | -1.8941 |  | 2026-11-03 07:40 | 25.457 | 25.926 | 7.2 | 4.321 | 5.5738 | -1.2528 | 33.4427 | 3.5 | 5.4941 | -1.9941 |  | 2026-11-03 07:40 | 26.798 | 27.298 | 7.6 | 4.5497 | 5.5738 | -1.0241 | 33.4427 | 3.7 | 5.4941 | -1.7941 |  | 2026-11-03 07:40 | 27.192 | 28.192 | 7.7 | 4.6987 | 5.5738 | -0.87511 | 33.4427 | 3.7 | 5.4941 | -1.7941 |  | 2026-11-03 07:40 | 25.615 | 26.098 | 7.1 | 4.3497 | 5.3028 | -0.95309 | 31.8166 | 3.5 | 5.2269 | -1.7269 |  | 2026-11-03 07:40 | 46.5723 | 57.6963 | -11.1239 | 346.1777 | 37.5 | 56.8712 | -19.3712
2026-11-03 07:30 | 76 | 18.37 | 24.007 | 24.472 | 5.7 | 4.0787 | 5.0511 | -0.97246 | 30.3068 | 3.2 | 4.9789 | -1.7789 |  | 2026-11-03 07:30 | 22.985 | 23.56 | 5.5 | 3.9267 | 5.0511 | -1.1245 | 30.3068 | 3.1 | 4.9789 | -1.8789 |  | 2026-11-03 07:30 | 23.575 | 24.044 | 5.6 | 4.0073 | 5.0511 | -1.0438 | 30.3068 | 3.1 | 4.9789 | -1.8789 |  | 2026-11-03 07:30 | 23.212 | 23.795 | 5.5 | 3.9658 | 5.0511 | -1.0853 | 30.3068 | 3.1 | 4.9789 | -1.8789 |  | 2026-11-03 07:30 | 17.027 | 17.776 | 3.8 | 2.9627 | 3.7416 | -0.77891 | 22.4495 | 2.2 | 3.6881 | -1.4881 |  | 2026-11-03 07:30 | 16.635 | 17.023 | 3.7 | 2.8372 | 3.7416 | -0.90441 | 22.4495 | 2.1 | 3.6881 | -1.5881 |  | 2026-11-03 07:30 | 17.56 | 17.973 | 3.9 | 2.9955 | 3.7416 | -0.74608 | 22.4495 | 2.3 | 3.6881 | -1.3881 |  | 2026-11-03 07:30 | 17.861 | 18.719 | 4 | 3.1198 | 3.7416 | -0.62174 | 22.4495 | 2.4 | 3.6881 | -1.2881 |  | 2026-11-03 07:30 | 16.46 | 16.849 | 3.6 | 2.8082 | 3.5596 | -0.75148 | 21.3579 | 2.2 | 3.5087 | -1.3087 |  | 2026-11-03 07:30 | 30.7018 | 38.7305 | -8.0286 | 232.3829 | 23.7 | 38.1766 | -14.4766
2026-11-03 07:20 | 32 | 16.93 | 13.694 | 14.306 | 2.5 | 2.3843 | 2.1373 | 0.24707 | 12.8236 | 1.7 | 2.1067 | -0.4067 |  | 2026-11-03 07:20 | 13.347 | 14.095 | 2.4 | 2.3492 | 2.1373 | 0.2119 | 12.8236 | 1.5 | 2.1067 | -0.6067 |  | 2026-11-03 07:20 | 13.899 | 14.279 | 2.5 | 2.3798 | 2.1373 | 0.24257 | 12.8236 | 1.7 | 2.1067 | -0.4067 |  | 2026-11-03 07:20 | 13.435 | 14.039 | 2.4 | 2.3398 | 2.1373 | 0.20257 | 12.8236 | 1.6 | 2.1067 | -0.5067 |  | 2026-11-03 07:20 | 10.085 | 10.704 | 1.6 | 1.784 | 1.5832 | 0.20084 | 9.499 | 1.3 | 1.5605 | -0.26052 |  | 2026-11-03 07:20 | 10.267 | 10.615 | 1.6 | 1.7692 | 1.5832 | 0.18601 | 9.499 | 1.3 | 1.5605 | -0.26052 |  | 2026-11-03 07:20 | 10.364 | 10.719 | 1.6 | 1.7865 | 1.5832 | 0.20334 | 9.499 | 1.3 | 1.5605 | -0.26052 |  | 2026-11-03 07:20 | 10.456 | 11.027 | 1.6 | 1.8378 | 1.5832 | 0.25467 | 9.499 | 1.2 | 1.5605 | -0.36052 |  | 2026-11-03 07:20 | 9.419 | 9.746 | 1.4 | 1.6243 | 1.5062 | 0.11815 | 9.0371 | 1.1 | 1.4846 | -0.38464 |  | 2026-11-03 07:20 | 18.255 | 16.3879 | 1.8671 | 98.3274 | 12.7 | 16.1535 | -3.4535
2026-11-03 07:10 | 17 | 16.65 | 6.63 | 6.908 | 0.8 | 1.1513 | 1.1365 | 0.014828 | 6.819 | 0.7 | 1.1203 | -0.42025 |  | 2026-11-03 07:10 | 6.556 | 7.365 | 0.9 | 1.2275 | 1.1365 | 0.090995 | 6.819 | 0.8 | 1.1203 | -0.32025 |  | 2026-11-03 07:10 | 6.602 | 6.973 | 0.8 | 1.1622 | 1.1365 | 0.025661 | 6.819 | 0.7 | 1.1203 | -0.42025 |  | 2026-11-03 07:10 | 6.476 | 7.22 | 0.8 | 1.2033 | 1.1365 | 0.066828 | 6.819 | 0.7 | 1.1203 | -0.42025 |  | 2026-11-03 07:10 | 4.744 | 5.452 | 0.3 | 0.90867 | 0.84186 | 0.066811 | 5.0511 | 0.3 | 0.82982 | -0.52982 |  | 2026-11-03 07:10 | 4.741 | 4.956 | 0.3 | 0.826 | 0.84186 | -0.015856 | 5.0511 | 0.3 | 0.82982 | -0.52982 |  | 2026-11-03 07:10 | 4.826 | 5.045 | 0.3 | 0.84083 | 0.84186 | -0.0010226 | 5.0511 | 0.3 | 0.82982 | -0.52982 |  | 2026-11-03 07:10 | 4.864 | 5.368 | 0.4 | 0.89467 | 0.84186 | 0.052811 | 5.0511 | 0.4 | 0.82982 | -0.42982 |  | 2026-11-03 07:10 | 4.488 | 4.694 | 0.3 | 0.78233 | 0.80092 | -0.018588 | 4.8055 | 0.3 | 0.78947 | -0.48947 |  | 2026-11-03 07:10 | 8.9968 | 8.7144 | 0.28247 | 52.2862 | 4.5 | 8.5898 | -4.0898
2026-11-03 07:00 | 5 | 17.22 | 2.075 | 2.227 | 0.1 | 0.37117 | 0.33362 | 0.037548 | 2.0017 | 0.1 | 0.32885 | -0.22885 |  | 2026-11-03 07:00 | 1.879 | 2.765 | 0.1 | 0.46083 | 0.33362 | 0.12721 | 2.0017 | 0.1 | 0.32885 | -0.22885 |  | 2026-11-03 07:00 | 2.221 | 2.335 | 0.1 | 0.38917 | 0.33362 | 0.055548 | 2.0017 | 0.1 | 0.32885 | -0.22885 |  | 2026-11-03 07:00 | 2.243 | 3.16 | 0.1 | 0.52667 | 0.33362 | 0.19305 | 2.0017 | 0.1 | 0.32885 | -0.22885 |  | 2026-11-03 07:00 | 0 | 0 | 0 | 0 | 0.24712 | -0.24712 | 1.4827 | 0 | 0.24359 | -0.24359 |  | 2026-11-03 07:00 | 0 | 0 | 0 | 0 | 0.24712 | -0.24712 | 1.4827 | 0 | 0.24359 | -0.24359 |  | 2026-11-03 07:00 | 0 | 0 | 0 | 0 | 0.24712 | -0.24712 | 1.4827 | 0 | 0.24359 | -0.24359 |  | 2026-11-03 07:00 | 0 | 0 | 0 | 0 | 0.24712 | -0.24712 | 1.4827 | 0 | 0.24359 | -0.24359 |  | 2026-11-03 07:00 | 0 | 0 | 0 | 0 | 0.23511 | -0.23511 | 1.4107 | 0 | 0.23175 | -0.23175 |  | 2026-11-03 07:00 | 1.7478 | 2.5581 | -0.81025 | 15.3485 | 0.4 | 2.5215 | -2.1215
[110 empty] | Total: - | 18732.5947 | 19701.072 | -968.4773 |  | 18592.7 | 19419.3466 | -826.6466
Sum:- | 43067 |  | 14233.564 |  | 89184.5 |  |  |  |  | 2420.1 | 2532.6215 | -112.5215 | 0.9829 |  | 13969.695 |  | 90760.1 |  |  |  |  | 2445 | 2532.6215 | -87.6215 | 0.98291 |  | 14405.475 |  | 90542.6 |  |  |  |  | 2405.9 | 2532.6215 | -126.7215 | 0.97251 |  | 14507.632 |  | 91400 |  |  |  |  | 2425.5 | 2532.6215 | -107.1215 | 0.98305 |  | 10839.62 |  | 68209.4 |  |  |  |  | 1814.8 | 1876.0159 | -61.2159 | 0.98437 |  | 10698.661 |  | 67550.5 |  |  |  |  | 1791 | 1876.0159 | -85.0159 | 0.9813 |  | 10724.269 |  | 67538.5 |  |  |  |  | 1792 | 1876.0159 | -84.0159 | 0.9806 |  | 10758.577 |  | 67942.8 |  |  |  |  | 1799.1 | 1876.0159 | -76.9159 | 0.9716 |  | 10161.842 |  | 64197.5 |  |  |  |  | 1699.3 | 1784.7968 | -85.4968 | 0.98462
Formulas:
Time = [Time]

## 12 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
2026-12-03 19:00 | 0 | 32.72 | 0.099 | 0.104 | 2458 | 0.017333 | 0 | 0.017333 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.091 | 0.249 | 2476.5 | 0.0415 | 0 | 0.0415 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.103 | 0.108 | 2440.9 | 0.018 | 0 | 0.018 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.073 | 0.14 | 2452.4 | 0.023333 | 0 | 0.023333 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.078 | 0.082 | 1849.1 | 0.013667 | 0 | 0.013667 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.064 | 0.067 | 1828.7 | 0.011167 | 0 | 0.011167 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.096 | 0.101 | 1830.7 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.085 | 0.089 | 1839.9 | 0.014833 | 0 | 0.014833 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.075 | 0.079 | 1739.3 | 0.013167 | 0 | 0.013167 | 0 | 0 | 0 | 0 |  | 2026-12-03 19:00 | 0.16983 | 0 | 0.16983 | 0 | 0 | 0 | 0 | 1 | 98.35%
2026-12-03 18:50 | 0 | 34.44 | 0.409 | 0.43 | 2458 | 0.071667 | 0 | 0.071667 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.489 | 0.896 | 2476.5 | 0.14933 | 0 | 0.14933 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.429 | 0.451 | 2440.9 | 0.075167 | 0 | 0.075167 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.455 | 0.786 | 2452.4 | 0.131 | 0 | 0.131 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.146 | 0.354 | 1849.1 | 0.059 | 0 | 0.059 | 0 | 0.1 | 0 | 0.1 |  | 2026-12-03 18:50 | 0.128 | 0.135 | 1828.7 | 0.0225 | 0 | 0.0225 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.075 | 0.082 | 1830.7 | 0.013667 | 0 | 0.013667 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.214 | 0.54 | 1839.9 | 0.09 | 0 | 0.09 | 0 | 0.1 | 0 | 0.1 |  | 2026-12-03 18:50 | 0.066 | 0.102 | 1739.3 | 0.017 | 0 | 0.017 | 0 | 0.2 | 0 | 0.2 |  | 2026-12-03 18:50 | 0.62933 | 0 | 0.62933 | 0 | 1.6 | 0 | 1.6 | 2 | 98.28%
2026-12-03 18:40 | 0 | 37.02 | 2.329 | 2.477 | 2457.8 | 0.41283 | 0 | 0.41283 | 0 | 0.8 | 0 | 0.8 |  | 2026-12-03 18:40 | 3.185 | 2.959 | 2476.3 | 0.49317 | 0 | 0.49317 | 0 | 0.9 | 0 | 0.9 |  | 2026-12-03 18:40 | 2.291 | 2.409 | 2440.7 | 0.4015 | 0 | 0.4015 | 0 | 0.8 | 0 | 0.8 |  | 2026-12-03 18:40 | 2.485 | 2.861 | 2452.2 | 0.47683 | 0 | 0.47683 | 0 | 0.8 | 0 | 0.8 |  | 2026-12-03 18:40 | 1.672 | 1.794 | 1849 | 0.299 | 0 | 0.299 | 0 | 0.6 | 0 | 0.6 |  | 2026-12-03 18:40 | 1.616 | 1.699 | 1828.5 | 0.28317 | 0 | 0.28317 | 0 | 0.5 | 0 | 0.5 |  | 2026-12-03 18:40 | 1.596 | 1.678 | 1830.5 | 0.27967 | 0 | 0.27967 | 0 | 0.5 | 0 | 0.5 |  | 2026-12-03 18:40 | 1.676 | 1.999 | 1839.8 | 0.33317 | 0 | 0.33317 | 0 | 0.5 | 0 | 0.5 |  | 2026-12-03 18:40 | 1.51 | 1.588 | 1739.1 | 0.26467 | 0 | 0.26467 | 0 | 0.4 | 0 | 0.4 |  | 2026-12-03 18:40 | 3.244 | 0 | 3.244 | 0 | 5.8 | 0 | 5.8 | 3 | 97.31%
2026-12-03 18:30 | 13 | 39.61 | 7.224 | 7.534 | 2457 | 1.2557 | 0.80124 | 0.45443 | 4.8074 | 1.7 | 0.78978 | 0.91022 |  | 2026-12-03 18:30 | 7.678 | 8.081 | 2475.4 | 1.3468 | 0.80124 | 0.5456 | 4.8074 | 1.8 | 0.78978 | 1.0102 |  | 2026-12-03 18:30 | 7.252 | 7.568 | 2439.9 | 1.2613 | 0.80124 | 0.4601 | 4.8074 | 1.8 | 0.78978 | 1.0102 |  | 2026-12-03 18:30 | 7.397 | 7.827 | 2451.4 | 1.3045 | 0.80124 | 0.50326 | 4.8074 | 1.8 | 0.78978 | 1.0102 |  | 2026-12-03 18:30 | 5.307 | 5.551 | 1848.4 | 0.92517 | 0.59351 | 0.33166 | 3.561 | 1.2 | 0.58502 | 0.61498 |  | 2026-12-03 18:30 | 5.143 | 5.382 | 1828 | 0.897 | 0.59351 | 0.30349 | 3.561 | 1.2 | 0.58502 | 0.61498 |  | 2026-12-03 18:30 | 5.038 | 5.275 | 1830 | 0.87917 | 0.59351 | 0.28566 | 3.561 | 1.2 | 0.58502 | 0.61498 |  | 2026-12-03 18:30 | 4.766 | 5.213 | 1839.3 | 0.86883 | 0.59351 | 0.27533 | 3.561 | 1.1 | 0.58502 | 0.51498 |  | 2026-12-03 18:30 | 4.556 | 4.776 | 1738.7 | 0.796 | 0.56465 | 0.23135 | 3.3879 | 1.1 | 0.55657 | 0.54343 |  | 2026-12-03 18:30 | 9.5345 | 6.1436 | 3.3909 | 36.8617 | 12.9 | 6.0558 | 6.8442 | 4 | 98.47%
2026-12-03 18:20 | 26 | 42.48 | 13.385 | 13.8 | 2455.3 | 2.3 | 1.5855 | 0.71449 | 9.513 | 2.9 | 1.5628 | 1.3372 |  | 2026-12-03 18:20 | 14.439 | 15.004 | 2473.6 | 2.5007 | 1.5855 | 0.91516 | 9.513 | 3.1 | 1.5628 | 1.5372 |  | 2026-12-03 18:20 | 13.995 | 14.464 | 2438.1 | 2.4107 | 1.5855 | 0.82516 | 9.513 | 3.1 | 1.5628 | 1.5372 |  | 2026-12-03 18:20 | 14.065 | 14.487 | 2449.6 | 2.4145 | 1.5855 | 0.82899 | 9.513 | 3.1 | 1.5628 | 1.5372 |  | 2026-12-03 18:20 | 10.332 | 10.703 | 1847.2 | 1.7838 | 1.1744 | 0.60938 | 7.0467 | 2.3 | 1.1577 | 1.1423 |  | 2026-12-03 18:20 | 9.906 | 10.272 | 1826.8 | 1.712 | 1.1744 | 0.53755 | 7.0467 | 2.2 | 1.1577 | 1.0423 |  | 2026-12-03 18:20 | 9.869 | 10.233 | 1828.8 | 1.7055 | 1.1744 | 0.53105 | 7.0467 | 2.2 | 1.1577 | 1.0423 |  | 2026-12-03 18:20 | 7.763 | 8.315 | 1838.2 | 1.3858 | 1.1744 | 0.21138 | 7.0467 | 1.6 | 1.1577 | 0.44235 |  | 2026-12-03 18:20 | 8.378 | 8.709 | 1737.6 | 1.4515 | 1.1173 | 0.33416 | 6.7041 | 1.9 | 1.1014 | 0.79864 |  | 2026-12-03 18:20 | 17.6645 | 12.1572 | 5.5073 | 72.943 | 22.4 | 11.9833 | 10.4167 | 5 | 98.49%
2026-12-03 18:10 | 39 | 45.35 | 23.081 | 23.6 | 2452.4 | 3.9333 | 2.3528 | 1.5805 | 14.1169 | 4.8 | 2.3192 | 2.4808 |  | 2026-12-03 18:10 | 24.357 | 24.716 | 2470.5 | 4.1193 | 2.3528 | 1.7665 | 14.1169 | 5.3 | 2.3192 | 2.9808 |  | 2026-12-03 18:10 | 23.977 | 24.407 | 2435 | 4.0678 | 2.3528 | 1.715 | 14.1169 | 5 | 2.3192 | 2.6808 |  | 2026-12-03 18:10 | 23.622 | 24.146 | 2446.5 | 4.0243 | 2.3528 | 1.6715 | 14.1169 | 4.9 | 2.3192 | 2.5808 |  | 2026-12-03 18:10 | 17.553 | 17.99 | 1844.9 | 2.9983 | 1.7428 | 1.2555 | 10.4569 | 3.7 | 1.7179 | 1.9821 |  | 2026-12-03 18:10 | 16.773 | 17.201 | 1824.6 | 2.8668 | 1.7428 | 1.124 | 10.4569 | 3.6 | 1.7179 | 1.8821 |  | 2026-12-03 18:10 | 16.946 | 17.381 | 1826.6 | 2.8968 | 1.7428 | 1.154 | 10.4569 | 3.6 | 1.7179 | 1.8821 |  | 2026-12-03 18:10 | 12.656 | 13.162 | 1836.6 | 2.1937 | 1.7428 | 0.45084 | 10.4569 | 2.9 | 1.7179 | 1.1821 |  | 2026-12-03 18:10 | 14.894 | 15.303 | 1735.7 | 2.5505 | 1.6581 | 0.89242 | 9.9485 | 3.2 | 1.6344 | 1.5656 |  | 2026-12-03 18:10 | 29.651 | 18.0406 | 11.6104 | 108.2438 | 37 | 17.7826 | 19.2174 | 6 | 98.1%
2026-12-03 18:00 | 53 | 47.35 | 35.339 | 35.946 | 2447.6 | 5.991 | 3.1733 | 2.8177 | 19.0399 | 7 | 3.1279 | 3.8721 |  | 2026-12-03 18:00 | 40.215 | 38.06 | 2465.2 | 6.3433 | 3.1733 | 3.17 | 19.0399 | 7.3 | 3.1279 | 4.1721 |  | 2026-12-03 18:00 | 36.717 | 37.348 | 2430 | 6.2247 | 3.1733 | 3.0514 | 19.0399 | 7.3 | 3.1279 | 4.1721 |  | 2026-12-03 18:00 | 35.61 | 36.237 | 2441.6 | 6.0395 | 3.1733 | 2.8662 | 19.0399 | 7.1 | 3.1279 | 3.9721 |  | 2026-12-03 18:00 | 27.24 | 27.814 | 1841.2 | 4.6357 | 2.3506 | 2.2851 | 14.1036 | 5.4 | 2.317 | 3.083 |  | 2026-12-03 18:00 | 25.887 | 26.429 | 1821 | 4.4048 | 2.3506 | 2.0542 | 14.1036 | 5.2 | 2.317 | 2.883 |  | 2026-12-03 18:00 | 26.09 | 26.636 | 1823 | 4.4393 | 2.3506 | 2.0887 | 14.1036 | 5.3 | 2.317 | 2.983 |  | 2026-12-03 18:00 | 22.989 | 23.795 | 1833.7 | 3.9658 | 2.3506 | 1.6152 | 14.1036 | 5 | 2.317 | 2.683 |  | 2026-12-03 18:00 | 24.33 | 24.86 | 1732.5 | 4.1433 | 2.2363 | 1.907 | 13.4178 | 5 | 2.2043 | 2.7957 |  | 2026-12-03 18:00 | 46.1875 | 24.332 | 21.8555 | 145.9919 | 54.6 | 23.984 | 30.616 | 7 | 98.06%
2026-12-03 17:50 | 157 | 47.93 | 49.851 | 50.636 | 2440.6 | 8.4393 | 9.3795 | -0.94016 | 56.277 | 10.2 | 9.2454 | 0.95463 |  | 2026-12-03 17:50 | 55.183 | 54.848 | 2457.9 | 9.1413 | 9.3795 | -0.23816 | 56.277 | 10.3 | 9.2454 | 1.0546 |  | 2026-12-03 17:50 | 51.412 | 52.254 | 2422.7 | 8.709 | 9.3795 | -0.67049 | 56.277 | 10.1 | 9.2454 | 0.85463 |  | 2026-12-03 17:50 | 50.611 | 51.397 | 2434.5 | 8.5662 | 9.3795 | -0.81333 | 56.277 | 10 | 9.2454 | 0.75463 |  | 2026-12-03 17:50 | 38.045 | 38.699 | 1835.8 | 6.4498 | 6.9478 | -0.49794 | 41.6866 | 7.5 | 6.8484 | 0.65158 |  | 2026-12-03 17:50 | 36.745 | 37.392 | 1815.8 | 6.232 | 6.9478 | -0.71577 | 41.6866 | 7.1 | 6.8484 | 0.25158 |  | 2026-12-03 17:50 | 36.988 | 37.635 | 1817.7 | 6.2725 | 6.9478 | -0.67527 | 41.6866 | 7.3 | 6.8484 | 0.45158 |  | 2026-12-03 17:50 | 36.522 | 37.511 | 1828.7 | 6.2518 | 6.9478 | -0.69594 | 41.6866 | 7.3 | 6.8484 | 0.45158 |  | 2026-12-03 17:50 | 34.373 | 34.971 | 1727.5 | 5.8285 | 6.6099 | -0.78145 | 39.6597 | 6.8 | 6.5154 | 0.28458 |  | 2026-12-03 17:50 | 65.8905 | 71.919 | -6.0285 | 431.514 | 76.6 | 70.8906 | 5.7094 | 8 | 97.16%
2026-12-03 17:40 | 212 | 47.93 | 67.704 | 68.589 | 2430.4 | 11.4315 | 12.6653 | -1.2338 | 75.9918 | 12.6 | 12.4842 | 0.11581 |  | 2026-12-03 17:40 | 68.968 | 69.912 | 2447.6 | 11.652 | 12.6653 | -1.0133 | 75.9918 | 12.7 | 12.4842 | 0.21581 |  | 2026-12-03 17:40 | 68.614 | 69.674 | 2412.6 | 11.6123 | 12.6653 | -1.053 | 75.9918 | 12.9 | 12.4842 | 0.41581 |  | 2026-12-03 17:40 | 66.87 | 67.825 | 2424.5 | 11.3042 | 12.6653 | -1.3611 | 75.9918 | 12.7 | 12.4842 | 0.21581 |  | 2026-12-03 17:40 | 50.69 | 51.478 | 1828.3 | 8.5797 | 9.3817 | -0.80204 | 56.2902 | 9.7 | 9.2475 | 0.45245 |  | 2026-12-03 17:40 | 48.801 | 49.549 | 1808.7 | 8.2582 | 9.3817 | -1.1235 | 56.2902 | 9.4 | 9.2475 | 0.15245 |  | 2026-12-03 17:40 | 49.421 | 50.184 | 1810.4 | 8.364 | 9.3817 | -1.0177 | 56.2902 | 9.3 | 9.2475 | 0.052453 |  | 2026-12-03 17:40 | 49.07 | 50.621 | 1821.4 | 8.4368 | 9.3817 | -0.94487 | 56.2902 | 9.3 | 9.2475 | 0.052453 |  | 2026-12-03 17:40 | 46.17 | 46.902 | 1720.7 | 7.817 | 8.9255 | -1.1085 | 53.5532 | 8.7 | 8.7979 | -0.097896 |  | 2026-12-03 17:40 | 87.4557 | 97.1136 | -9.6579 | 582.6814 | 97.3 | 95.7248 | 1.5752 | 9 | 98.41%
2026-12-03 17:30 | 263 | 47.93 | 85.489 | 86.545 | 2417.8 | 14.4242 | 15.7121 | -1.288 | 94.2729 | 15.8 | 15.4875 | 0.31254 |  | 2026-12-03 17:30 | 87.729 | 88.848 | 2434.9 | 14.808 | 15.7121 | -0.90414 | 94.2729 | 16.1 | 15.4875 | 0.61254 |  | 2026-12-03 17:30 | 86.61 | 88.208 | 2399.7 | 14.7013 | 15.7121 | -1.0108 | 94.2729 | 16 | 15.4875 | 0.51254 |  | 2026-12-03 17:30 | 85.097 | 86.183 | 2411.8 | 14.3638 | 15.7121 | -1.3483 | 94.2729 | 15.8 | 15.4875 | 0.31254 |  | 2026-12-03 17:30 | 64.355 | 65.24 | 1818.6 | 10.8733 | 11.6386 | -0.76529 | 69.8318 | 11.8 | 11.4722 | 0.32781 |  | 2026-12-03 17:30 | 62.341 | 63.175 | 1799.3 | 10.5292 | 11.6386 | -1.1095 | 69.8318 | 11.4 | 11.4722 | -0.072193 |  | 2026-12-03 17:30 | 62.763 | 63.609 | 1801.1 | 10.6015 | 11.6386 | -1.0371 | 69.8318 | 11.5 | 11.4722 | 0.027807 |  | 2026-12-03 17:30 | 62.535 | 64.109 | 1812.1 | 10.6848 | 11.6386 | -0.95379 | 69.8318 | 11.4 | 11.4722 | -0.072193 |  | 2026-12-03 17:30 | 58.857 | 59.693 | 1712 | 9.9488 | 11.0727 | -1.1239 | 66.4363 | 10.9 | 10.9144 | -0.014371 |  | 2026-12-03 17:30 | 110.935 | 120.4758 | -9.5408 | 722.8547 | 120.7 | 118.753 | 1.947
2026-12-03 17:20 | 313 | 47.93 | 105.787 | 106.363 | 2402 | 17.7272 | 18.6992 | -0.97208 | 112.1955 | 18.8 | 18.4318 | 0.36816 |  | 2026-12-03 17:20 | 104.9 | 106.206 | 2418.8 | 17.701 | 18.6992 | -0.99824 | 112.1955 | 19.4 | 18.4318 | 0.96816 |  | 2026-12-03 17:20 | 104.496 | 106.395 | 2383.7 | 17.7325 | 18.6992 | -0.96674 | 112.1955 | 19 | 18.4318 | 0.56816 |  | 2026-12-03 17:20 | 103.373 | 104.66 | 2396 | 17.4433 | 18.6992 | -1.2559 | 112.1955 | 18.9 | 18.4318 | 0.46816 |  | 2026-12-03 17:20 | 77.47 | 78.474 | 1806.8 | 13.079 | 13.8513 | -0.77229 | 83.1078 | 14.1 | 13.6532 | 0.44678 |  | 2026-12-03 17:20 | 75.382 | 76.345 | 1787.9 | 12.7242 | 13.8513 | -1.1271 | 83.1078 | 13.8 | 13.6532 | 0.14678 |  | 2026-12-03 17:20 | 75.772 | 76.762 | 1789.6 | 12.7937 | 13.8513 | -1.0576 | 83.1078 | 13.9 | 13.6532 | 0.24678 |  | 2026-12-03 17:20 | 75.883 | 77.956 | 1800.7 | 12.9927 | 13.8513 | -0.85863 | 83.1078 | 13.9 | 13.6532 | 0.24678 |  | 2026-12-03 17:20 | 71.386 | 72.334 | 1701.1 | 12.0557 | 13.1778 | -1.1221 | 79.0667 | 13 | 12.9893 | 0.010654 |  | 2026-12-03 17:20 | 134.2492 | 143.3799 | -9.1308 | 860.2796 | 144.8 | 141.3296 | 3.4704
2026-12-03 17:10 | 369 | 48.22 | 123.714 | 125.302 | 2383.2 | 20.8837 | 22.0205 | -1.1368 | 132.1228 | 21.8 | 21.7056 | 0.094425 |  | 2026-12-03 17:10 | 126.792 | 128.474 | 2399.4 | 21.4123 | 22.0205 | -0.60813 | 132.1228 | 23 | 21.7056 | 1.2944 |  | 2026-12-03 17:10 | 124.524 | 126.957 | 2364.7 | 21.1595 | 22.0205 | -0.86097 | 132.1228 | 22 | 21.7056 | 0.29443 |  | 2026-12-03 17:10 | 123.611 | 125.201 | 2377.1 | 20.8668 | 22.0205 | -1.1536 | 132.1228 | 21.9 | 21.7056 | 0.19443 |  | 2026-12-03 17:10 | 92.55 | 93.722 | 1792.7 | 15.6203 | 16.3115 | -0.69112 | 97.8687 | 16.5 | 16.0782 | 0.4218 |  | 2026-12-03 17:10 | 90.448 | 91.556 | 1774.1 | 15.2593 | 16.3115 | -1.0521 | 97.8687 | 16.3 | 16.0782 | 0.2218 |  | 2026-12-03 17:10 | 90.717 | 91.88 | 1775.7 | 15.3133 | 16.3115 | -0.99812 | 97.8687 | 16.3 | 16.0782 | 0.2218 |  | 2026-12-03 17:10 | 90.678 | 93.366 | 1786.8 | 15.561 | 16.3115 | -0.75046 | 97.8687 | 16.2 | 16.0782 | 0.1218 |  | 2026-12-03 17:10 | 85.448 | 86.556 | 1688.1 | 14.426 | 15.5183 | -1.0923 | 93.11 | 15.3 | 15.2964 | 0.0035806 |  | 2026-12-03 17:10 | 160.5023 | 168.846 | -8.3437 | 1013.0762 | 169.3 | 166.4315 | 2.8685
2026-12-03 17:00 | 416 | 48.5 | 140.794 | 142.576 | 2361.4 | 23.7627 | 24.7988 | -1.0361 | 148.7926 | 25.2 | 24.4441 | 0.75586 |  | 2026-12-03 17:00 | 142.458 | 144.334 | 2376.4 | 24.0557 | 24.7988 | -0.7431 | 148.7926 | 24.4 | 24.4441 | -0.044139 |  | 2026-12-03 17:00 | 141.417 | 144.303 | 2342.7 | 24.0505 | 24.7988 | -0.74826 | 148.7926 | 24.9 | 24.4441 | 0.45586 |  | 2026-12-03 17:00 | 140.697 | 142.521 | 2355.2 | 23.7535 | 24.7988 | -1.0453 | 148.7926 | 24.9 | 24.4441 | 0.45586 |  | 2026-12-03 17:00 | 105.672 | 107.01 | 1776.2 | 17.835 | 18.3695 | -0.53445 | 110.2167 | 19.2 | 18.1068 | 1.0932 |  | 2026-12-03 17:00 | 103.153 | 104.448 | 1757.8 | 17.408 | 18.3695 | -0.96145 | 110.2167 | 18.2 | 18.1068 | 0.09323 |  | 2026-12-03 17:00 | 103.531 | 104.831 | 1759.4 | 17.4718 | 18.3695 | -0.89762 | 110.2167 | 18.2 | 18.1068 | 0.09323 |  | 2026-12-03 17:00 | 103.449 | 106.176 | 1770.6 | 17.696 | 18.3695 | -0.67345 | 110.2167 | 18.3 | 18.1068 | 0.19323 |  | 2026-12-03 17:00 | 97.509 | 98.794 | 1672.8 | 16.4657 | 17.4763 | -1.0106 | 104.8576 | 17.2 | 17.2263 | -0.026349 |  | 2026-12-03 17:00 | 182.4988 | 190.1491 | -7.6503 | 1140.8947 | 190.5 | 187.43 | 3.07
2026-12-03 16:50 | 464 | 48.22 | 158.766 | 160.808 | 2336.2 | 26.8013 | 27.6897 | -0.88836 | 166.1382 | 59.7 | 27.2937 | 32.4063 |  | 2026-12-03 16:50 | 161.151 | 162.863 | 2352 | 27.1438 | 27.6897 | -0.54586 | 166.1382 | 28.2 | 27.2937 | 0.90627 |  | 2026-12-03 16:50 | 157.554 | 160.671 | 2317.8 | 26.7785 | 27.6897 | -0.91119 | 166.1382 | 28.1 | 27.2937 | 0.80627 |  | 2026-12-03 16:50 | 158.154 | 160.253 | 2330.3 | 26.7088 | 27.6897 | -0.98086 | 166.1382 | 28.1 | 27.2937 | 0.80627 |  | 2026-12-03 16:50 | 119.089 | 120.621 | 1757 | 20.1035 | 20.5109 | -0.40738 | 123.0653 | 20.5 | 20.2176 | 0.28242 |  | 2026-12-03 16:50 | 115.934 | 117.545 | 1739.6 | 19.5908 | 20.5109 | -0.92005 | 123.0653 | 20.7 | 20.2176 | 0.48242 |  | 2026-12-03 16:50 | 116.189 | 117.684 | 1741.2 | 19.614 | 20.5109 | -0.89688 | 123.0653 | 20.4 | 20.2176 | 0.18242 |  | 2026-12-03 16:50 | 116.307 | 119.488 | 1752.3 | 19.9147 | 20.5109 | -0.59622 | 123.0653 | 20.4 | 20.2176 | 0.18242 |  | 2026-12-03 16:50 | 109.698 | 111.12 | 1655.6 | 18.52 | 19.5136 | -0.99357 | 117.0814 | 19.5 | 19.2345 | 0.26548 |  | 2026-12-03 16:50 | 205.1755 | 212.3159 | -7.1404 | 1273.8953 | 245.6 | 209.2798 | 36.3202
2026-12-03 16:40 | 519 | 48.5 | 178.082 | 180.464 | 2308 | 30.0773 | 30.9388 | -0.86151 | 185.633 | 0 | 30.4964 | -30.4964 |  | 2026-12-03 16:40 | 180.715 | 183.307 | 2323.8 | 30.5512 | 30.9388 | -0.38767 | 185.633 | 32.2 | 30.4964 | 1.7036 |  | 2026-12-03 16:40 | 178.073 | 181.965 | 2289.7 | 30.3275 | 30.9388 | -0.61134 | 185.633 | 31.5 | 30.4964 | 1.0036 |  | 2026-12-03 16:40 | 178.02 | 180.438 | 2302.2 | 30.073 | 30.9388 | -0.86584 | 185.633 | 31.4 | 30.4964 | 0.90359 |  | 2026-12-03 16:40 | 133.737 | 135.485 | 1736.5 | 22.5808 | 22.9177 | -0.33683 | 137.506 | 23.6 | 22.5899 | 1.0101 |  | 2026-12-03 16:40 | 130.795 | 132.584 | 1718.9 | 22.0973 | 22.9177 | -0.82033 | 137.506 | 22.7 | 22.5899 | 0.11006 |  | 2026-12-03 16:40 | 130.844 | 132.554 | 1720.8 | 22.0923 | 22.9177 | -0.82533 | 137.506 | 23.2 | 22.5899 | 0.61006 |  | 2026-12-03 16:40 | 130.815 | 134.198 | 1731.9 | 22.3663 | 22.9177 | -0.55133 | 137.506 | 23.2 | 22.5899 | 0.61006 |  | 2026-12-03 16:40 | 123.668 | 125.31 | 1636.1 | 20.885 | 21.8033 | -0.91831 | 130.8199 | 21.9 | 21.4915 | 0.40847 |  | 2026-12-03 16:40 | 231.0508 | 237.2293 | -6.1785 | 1423.3759 | 209.7 | 233.8369 | -24.1369
2026-12-03 16:30 | 578 | 48.5 | 199.35 | 202.058 | 2276.5 | 33.6763 | 34.456 | -0.77964 | 206.7358 | 34.6 | 33.9633 | 0.63675 |  | 2026-12-03 16:30 | 200.683 | 203.532 | 2291.6 | 33.922 | 34.456 | -0.53397 | 206.7358 | 35 | 33.9633 | 1.0367 |  | 2026-12-03 16:30 | 198.963 | 203.288 | 2258.2 | 33.8813 | 34.456 | -0.57464 | 206.7358 | 34.5 | 33.9633 | 0.53675 |  | 2026-12-03 16:30 | 198.182 | 200.955 | 2270.8 | 33.4925 | 34.456 | -0.96347 | 206.7358 | 34.6 | 33.9633 | 0.63675 |  | 2026-12-03 16:30 | 149.051 | 151.014 | 1712.9 | 25.169 | 25.5229 | -0.35394 | 153.1377 | 26 | 25.158 | 0.84204 |  | 2026-12-03 16:30 | 145.654 | 147.587 | 1696.2 | 24.5978 | 25.5229 | -0.92511 | 153.1377 | 25.7 | 25.158 | 0.54204 |  | 2026-12-03 16:30 | 146.473 | 148.537 | 1697.6 | 24.7562 | 25.5229 | -0.76678 | 153.1377 | 25.8 | 25.158 | 0.64204 |  | 2026-12-03 16:30 | 146.755 | 150.663 | 1708.7 | 25.1105 | 25.5229 | -0.41244 | 153.1377 | 25.8 | 25.158 | 0.64204 |  | 2026-12-03 16:30 | 138.091 | 139.938 | 1614.2 | 23.323 | 24.2819 | -0.95892 | 145.6915 | 24 | 23.9347 | 0.065313 |  | 2026-12-03 16:30 | 257.9287 | 264.1976 | -6.2689 | 1585.1854 | 266 | 260.4195 | 5.5805
2026-12-03 16:20 | 636 | 48.79 | 218.696 | 221.756 | 2241.9 | 36.9593 | 37.8716 | -0.91223 | 227.2294 | 33.6 | 37.33 | -3.73 |  | 2026-12-03 16:20 | 221.455 | 224.622 | 2256.6 | 37.437 | 37.8716 | -0.43456 | 227.2294 | 34.6 | 37.33 | -2.73 |  | 2026-12-03 16:20 | 218.021 | 222.851 | 2223.7 | 37.1418 | 37.8716 | -0.72973 | 227.2294 | 34 | 37.33 | -3.33 |  | 2026-12-03 16:20 | 218.365 | 221.386 | 2236.2 | 36.8977 | 37.8716 | -0.97389 | 227.2294 | 34.2 | 37.33 | -3.13 |  | 2026-12-03 16:20 | 163.368 | 165.516 | 1686.9 | 27.586 | 28.053 | -0.46701 | 168.318 | 25.6 | 27.6518 | -2.0518 |  | 2026-12-03 16:20 | 160.547 | 162.808 | 1670.5 | 27.1347 | 28.053 | -0.91834 | 168.318 | 24.9 | 27.6518 | -2.7518 |  | 2026-12-03 16:20 | 160.245 | 162.599 | 1671.8 | 27.0998 | 28.053 | -0.95317 | 168.318 | 24.8 | 27.6518 | -2.8518 |  | 2026-12-03 16:20 | 160.62 | 164.93 | 1682.9 | 27.4883 | 28.053 | -0.56467 | 168.318 | 25.3 | 27.6518 | -2.3518 |  | 2026-12-03 16:20 | 151.753 | 153.865 | 1590.2 | 25.6442 | 26.689 | -1.0448 | 160.1338 | 23.9 | 26.3073 | -2.4073 |  | 2026-12-03 16:20 | 283.3888 | 290.3872 | -6.9984 | 1742.3234 | 260.9 | 286.2347 | -25.3347
2026-12-03 16:10 | 610 | 49.08 | 214.349 | 210.013 | 2208.3 | 35.0022 | 36.2831 | -1.281 | 217.6988 | 37.5 | 35.7643 | 1.7357 |  | 2026-12-03 16:10 | 211.839 | 214.912 | 2222 | 35.8187 | 36.2831 | -0.46447 | 217.6988 | 38 | 35.7643 | 2.2357 |  | 2026-12-03 16:10 | 207.836 | 213.118 | 2189.7 | 35.5197 | 36.2831 | -0.76347 | 217.6988 | 37.4 | 35.7643 | 1.6357 |  | 2026-12-03 16:10 | 208.594 | 211.599 | 2202 | 35.2665 | 36.2831 | -1.0166 | 217.6988 | 37.4 | 35.7643 | 1.6357 |  | 2026-12-03 16:10 | 156.608 | 158.735 | 1661.3 | 26.4558 | 26.8764 | -0.42056 | 161.2584 | 28.1 | 26.4921 | 1.6079 |  | 2026-12-03 16:10 | 153.738 | 156.131 | 1645.6 | 26.0218 | 26.8764 | -0.85456 | 161.2584 | 28 | 26.4921 | 1.5079 |  | 2026-12-03 16:10 | 154.211 | 156.392 | 1647 | 26.0653 | 26.8764 | -0.81106 | 161.2584 | 28 | 26.4921 | 1.5079 |  | 2026-12-03 16:10 | 155.232 | 159.862 | 1657.6 | 26.6437 | 26.8764 | -0.23273 | 161.2584 | 27.7 | 26.4921 | 1.2079 |  | 2026-12-03 16:10 | 146.185 | 148.186 | 1566.3 | 24.6977 | 25.5696 | -0.8719 | 153.4174 | 26.2 | 25.2039 | 0.99608 |  | 2026-12-03 16:10 | 271.4913 | 278.2077 | -6.7164 | 1669.2461 | 288.3 | 274.2293 | 14.0707
2026-12-03 16:00 | 708 | 48.79 | 240.063 | 243.669 | 2170.8 | 40.6115 | 42.1589 | -1.5474 | 252.9534 | 41.5 | 41.556 | -0.056035 |  | 2026-12-03 16:00 | 250.886 | 254.784 | 2184 | 42.464 | 42.1589 | 0.30509 | 252.9534 | 87.2 | 41.556 | 45.644 |  | 2026-12-03 16:00 | 240.031 | 245.735 | 2152.3 | 40.9558 | 42.1589 | -1.2031 | 252.9534 | 42 | 41.556 | 0.44397 |  | 2026-12-03 16:00 | 240.322 | 243.957 | 2164.6 | 40.6595 | 42.1589 | -1.4994 | 252.9534 | 42.1 | 41.556 | 0.54397 |  | 2026-12-03 16:00 | 180.601 | 183.109 | 1633.2 | 30.5182 | 31.2288 | -0.71065 | 187.3729 | 31.6 | 30.7822 | 0.81775 |  | 2026-12-03 16:00 | 176.783 | 179.435 | 1617.6 | 29.9058 | 31.2288 | -1.323 | 187.3729 | 30.5 | 30.7822 | -0.28225 |  | 2026-12-03 16:00 | 177.539 | 180.185 | 1619 | 30.0308 | 31.2288 | -1.198 | 187.3729 | 30.7 | 30.7822 | -0.082248 |  | 2026-12-03 16:00 | 177.352 | 182.075 | 1629.9 | 30.3458 | 31.2288 | -0.88299 | 187.3729 | 30.7 | 30.7822 | -0.082248 |  | 2026-12-03 16:00 | 167.611 | 169.991 | 1540.1 | 28.3318 | 29.7104 | -1.3785 | 178.2621 | 29 | 29.2855 | -0.2855 |  | 2026-12-03 16:00 | 313.8233 | 323.2613 | -9.4379 | 1939.5676 | 365.3 | 318.6386 | 46.6614
2026-12-03 15:50 | 747 | 49.08 | 238.692 | 254.954 | 2129.3 | 42.4923 | 44.432 | -1.9396 | 266.5918 | 45.9 | 43.7966 | 2.1034 | [5 empty] | 0 | 44.432 | -44.432 | 266.5918 | 0 | 43.7966 | -43.7966 |  | 2026-12-03 15:50 | 252.364 | 259.047 | 2110.3 | 43.1745 | 44.432 | -1.2575 | 266.5918 | 43.9 | 43.7966 | 0.10341 |  | 2026-12-03 15:50 | 252.298 | 256.244 | 2122.5 | 42.7073 | 44.432 | -1.7246 | 266.5918 | 44 | 43.7966 | 0.20341 |  | 2026-12-03 15:50 | 190.563 | 193.308 | 1601.6 | 32.218 | 32.9126 | -0.69457 | 197.4754 | 33.2 | 32.4419 | 0.75808 |  | 2026-12-03 15:50 | 186.19 | 189.088 | 1587.1 | 31.5147 | 32.9126 | -1.3979 | 197.4754 | 32.5 | 32.4419 | 0.058079 |  | 2026-12-03 15:50 | 187.115 | 190.591 | 1588.3 | 31.7652 | 32.9126 | -1.1474 | 197.4754 | 32.6 | 32.4419 | 0.15808 |  | 2026-12-03 15:50 | 187 | 192.561 | 1599.2 | 32.0935 | 32.9126 | -0.81907 | 197.4754 | 32.6 | 32.4419 | 0.15808 |  | 2026-12-03 15:50 | 176.409 | 178.95 | 1511.1 | 29.825 | 31.3122 | -1.4872 | 187.8734 | 30.7 | 30.8645 | -0.16447 |  | 2026-12-03 15:50 | 285.7905 | 340.6904 | -54.8999 | 2044.1424 | 295.4 | 335.8185 | -40.4185
2026-12-03 15:40 | 833 | 48.79 | 287.12 | 291.67 | 2083.4 | 48.6117 | 49.6022 | -0.99055 | 297.6133 | 43 | 48.8929 | -5.8929 |  | 2026-12-03 15:40 | 288.736 | 293.401 | 2096.8 | 48.9002 | 49.6022 | -0.70205 | 297.6133 | 44.9 | 48.8929 | -3.9929 |  | 2026-12-03 15:40 | 283.002 | 289.975 | 2066.4 | 48.3292 | 49.6022 | -1.2731 | 297.6133 | 44.1 | 48.8929 | -4.7929 |  | 2026-12-03 15:40 | 283.963 | 288.58 | 2078.5 | 48.0967 | 49.6022 | -1.5056 | 297.6133 | 44.3 | 48.8929 | -4.5929 |  | 2026-12-03 15:40 | 212.934 | 216.067 | 1568.4 | 36.0112 | 36.7424 | -0.73122 | 220.4543 | 33.2 | 36.217 | -3.017 |  | 2026-12-03 15:40 | 209.068 | 212.278 | 1554.6 | 35.3797 | 36.7424 | -1.3627 | 220.4543 | 32.6 | 36.217 | -3.617 |  | 2026-12-03 15:40 | 208.545 | 212.011 | 1555.7 | 35.3352 | 36.7424 | -1.4072 | 220.4543 | 32.6 | 36.217 | -3.617 |  | 2026-12-03 15:40 | 208.51 | 214.405 | 1566.6 | 35.7342 | 36.7424 | -1.0082 | 220.4543 | 32.6 | 36.217 | -3.617 |  | 2026-12-03 15:40 | 198.437 | 201.336 | 1480.4 | 33.556 | 34.9558 | -1.3998 | 209.735 | 31.3 | 34.456 | -3.156 |  | 2026-12-03 15:40 | 369.9538 | 380.3342 | -10.3804 | 2282.0054 | 338.6 | 374.8954 | -36.2954
2026-12-03 15:30 | 750 | 48.79 | 259.104 | 263.076 | 2040.4 | 43.846 | 44.6599 | -0.81386 | 267.9592 | 43.7 | 44.0212 | -0.32122 |  | 2026-12-03 15:30 | 252.606 | 259.81 | 2051.9 | 43.3017 | 44.6599 | -1.3582 | 267.9592 | 42.2 | 44.0212 | -1.8212 |  | 2026-12-03 15:30 | 253.762 | 257.679 | 2022.3 | 42.9465 | 44.6599 | -1.7134 | 267.9592 | 41.7 | 44.0212 | -2.3212 |  | 2026-12-03 15:30 | 257.435 | 261.462 | 2034.2 | 43.577 | 44.6599 | -1.0829 | 267.9592 | 41.9 | 44.0212 | -2.1212 |  | 2026-12-03 15:30 | 183.662 | 186.308 | 1535.2 | 31.0513 | 33.0814 | -2.03 | 198.4883 | 31.5 | 32.6083 | -1.1083 |  | 2026-12-03 15:30 | 183.103 | 185.722 | 1522 | 30.9537 | 33.0814 | -2.1277 | 198.4883 | 30.9 | 32.6083 | -1.7083 |  | 2026-12-03 15:30 | 176.02 | 178.787 | 1523.1 | 29.7978 | 33.0814 | -3.2835 | 198.4883 | 30.9 | 32.6083 | -1.7083 |  | 2026-12-03 15:30 | 176.52 | 181.311 | 1534 | 30.2185 | 33.0814 | -2.8629 | 198.4883 | 31 | 32.6083 | -1.6083 |  | 2026-12-03 15:30 | 184.277 | 186.95 | 1449.1 | 31.1583 | 31.4728 | -0.3145 | 188.837 | 28.8 | 31.0228 | -2.2228 |  | 2026-12-03 15:30 | 326.8508 | 342.4378 | -15.5869 | 2054.6267 | 322.6 | 337.5409 | -14.9409
2026-12-03 15:20 | 693 | 49.08 | 279.345 | 283.801 | 1996.7 | 47.3002 | 41.22 | 6.0801 | 247.3201 | 40.1 | 40.6306 | -0.53057 |  | 2026-12-03 15:20 | 288.266 | 268.27 | 2009.7 | 44.7117 | 41.22 | 3.4916 | 247.3201 | 43 | 40.6306 | 2.3694 |  | 2026-12-03 15:20 | 231.312 | 235.966 | 1980.6 | 39.3277 | 41.22 | -1.8924 | 247.3201 | 41.4 | 40.6306 | 0.76943 |  | 2026-12-03 15:20 | 236.908 | 240.589 | 1992.3 | 40.0982 | 41.22 | -1.1219 | 247.3201 | 41.6 | 40.6306 | 0.96943 |  | 2026-12-03 15:20 | 176.066 | 178.584 | 1503.7 | 29.764 | 30.5333 | -0.76935 | 183.2001 | 31.2 | 30.0967 | 1.1033 |  | 2026-12-03 15:20 | 172.313 | 175.525 | 1491.1 | 29.2542 | 30.5333 | -1.2792 | 183.2001 | 30.7 | 30.0967 | 0.60328 |  | 2026-12-03 15:20 | 177.32 | 181.945 | 1492.2 | 30.3242 | 30.5333 | -0.20918 | 183.2001 | 31.1 | 30.0967 | 1.0033 |  | 2026-12-03 15:20 | 179.453 | 186.382 | 1503 | 31.0637 | 30.5333 | 0.53032 | 183.2001 | 31.2 | 30.0967 | 1.1033 |  | 2026-12-03 15:20 | 170.14 | 174.071 | 1420.3 | 29.0118 | 29.0487 | -0.036866 | 174.2922 | 29.5 | 28.6333 | 0.8667 |  | 2026-12-03 15:20 | 320.8555 | 316.0622 | 4.7933 | 1896.3731 | 319.8 | 311.5425 | 8.2575
2026-12-03 15:10 | 618 | 49.08 | 269.966 | 274.133 | 1956.6 | 45.6888 | 36.759 | 8.9299 | 220.5539 | 36.9 | 36.2333 | 0.66667 |  | 2026-12-03 15:10 | 272.202 | 276.46 | 1966.7 | 46.0767 | 36.759 | 9.3177 | 220.5539 | 36.1 | 36.2333 | -0.13333 |  | 2026-12-03 15:10 | 212.354 | 217.426 | 1939.2 | 36.2377 | 36.759 | -0.52131 | 220.5539 | 36.7 | 36.2333 | 0.46667 |  | 2026-12-03 15:10 | 211.014 | 214.184 | 1950.7 | 35.6973 | 36.759 | -1.0616 | 220.5539 | 36.8 | 36.2333 | 0.56667 |  | 2026-12-03 15:10 | 153.641 | 155.791 | 1472.5 | 25.9652 | 27.2289 | -1.2637 | 163.3732 | 27.7 | 26.8395 | 0.8605 |  | 2026-12-03 15:10 | 152.193 | 154.323 | 1460.4 | 25.7205 | 27.2289 | -1.5084 | 163.3732 | 27.2 | 26.8395 | 0.3605 |  | 2026-12-03 15:10 | 151.676 | 153.814 | 1461.1 | 25.6357 | 27.2289 | -1.5932 | 163.3732 | 27 | 26.8395 | 0.1605 |  | 2026-12-03 15:10 | 149.753 | 153.53 | 1471.8 | 25.5883 | 27.2289 | -1.6405 | 163.3732 | 27.4 | 26.8395 | 0.5605 |  | 2026-12-03 15:10 | 143.035 | 145.066 | 1390.8 | 24.1777 | 25.9049 | -1.7272 | 155.4294 | 25.9 | 25.5345 | 0.36554 |  | 2026-12-03 15:10 | 290.7878 | 281.8563 | 8.9315 | 1691.1379 | 281.7 | 277.8258 | 3.8742
2026-12-03 15:00 | 578 | 48.79 | 218.653 | 221.893 | 1919.7 | 36.9822 | 34.4179 | 2.5643 | 206.5072 | 43.6 | 33.9257 | 9.6743 | 0.9854 | 2026-12-03 15:00 | 238.379 | 217.169 | 1930.6 | 36.1948 | 34.4179 | 1.777 | 206.5072 | 44.9 | 33.9257 | 10.9743 | 1.0977 | 2026-12-03 15:00 | 202.488 | 205.467 | 1902.5 | 34.2445 | 34.4179 | -0.17336 | 206.5072 | 44.6 | 33.9257 | 10.6743 | 0.9855 | 2026-12-03 15:00 | 204.466 | 207.495 | 1913.9 | 34.5825 | 34.4179 | 0.16464 | 206.5072 | 44.9 | 33.9257 | 10.9743 | 0.9854 | 2026-12-03 15:00 | 145.009 | 147.053 | 1444.8 | 24.5088 | 25.4947 | -0.98588 | 152.9683 | 33.6 | 25.1301 | 8.4699 | 0.9861 | 2026-12-03 15:00 | 145.087 | 147.132 | 1433.2 | 24.522 | 25.4947 | -0.97271 | 152.9683 | 33.1 | 25.1301 | 7.9699 | 0.9861 | 2026-12-03 15:00 | 140.713 | 142.682 | 1434.1 | 23.7803 | 25.4947 | -1.7144 | 152.9683 | 33 | 25.1301 | 7.8699 | 0.9862 | 2026-12-03 15:00 | 152.351 | 155.957 | 1444.4 | 25.9928 | 25.4947 | 0.49812 | 152.9683 | 32.8 | 25.1301 | 7.6699 | 0.97688 | 2026-12-03 15:00 | 144.121 | 146.167 | 1364.9 | 24.3612 | 24.2551 | 0.1061 | 145.5304 | 31 | 23.9082 | 7.0918 | 0.986 | 2026-12-03 15:00 | 265.1692 | 263.9054 | 1.2638 | 1583.4323 | 341.5 | 260.1315 | 81.3685
2026-12-03 14:50 | 855 | 48.79 | 270.714 | 302.348 | 1876.1 | 50.3913 | 50.9122 | -0.52091 | 305.4734 | 44.9 | 50.1842 | -5.2842 | 0.89537 | 2026-12-03 14:50 | 309.237 | 315.777 | 1885.7 | 52.6295 | 50.9122 | 1.7173 | 305.4734 | 44.6 | 50.1842 | -5.5842 | 0.97929 | 2026-12-03 14:50 | 279.702 | 290.675 | 1857.9 | 48.4458 | 50.9122 | -2.4664 | 305.4734 | 43.8 | 50.1842 | -6.3842 | 0.96225 | 2026-12-03 14:50 | 274.187 | 278.617 | 1869 | 46.4362 | 50.9122 | -4.4761 | 305.4734 | 44.1 | 50.1842 | -6.0842 | 0.9841 | 2026-12-03 14:50 | 219.05 | 222.379 | 1411.2 | 37.0632 | 37.7128 | -0.6496 | 226.2766 | 32.9 | 37.1735 | -4.2735 | 0.98503 | 2026-12-03 14:50 | 211.562 | 216.811 | 1400.1 | 36.1352 | 37.7128 | -1.5776 | 226.2766 | 33 | 37.1735 | -4.1735 | 0.97579 | 2026-12-03 14:50 | 216.631 | 221.09 | 1401.1 | 36.8483 | 37.7128 | -0.86444 | 226.2766 | 33 | 37.1735 | -4.1735 | 0.97983 | 2026-12-03 14:50 | 216.63 | 223.438 | 1411.6 | 37.2397 | 37.7128 | -0.4731 | 226.2766 | 33.1 | 37.1735 | -4.0735 | 0.96953 | 2026-12-03 14:50 | 205.205 | 208.288 | 1333.9 | 34.7147 | 35.879 | -1.1644 | 215.2742 | 31.2 | 35.366 | -4.166 | 0.9852 | 2026-12-03 14:50 | 379.9038 | 390.3791 | -10.4752 | 2342.2744 | 340.6 | 384.7966 | -44.1966
2026-12-03 14:40 | 920 | 48.79 | 310.58 | 315.855 | 1831.2 | 52.6425 | 54.7828 | -2.1403 | 328.6966 | 48.7 | 53.9994 | -5.2994 | 0.9833 | 2026-12-03 14:40 | 333.614 | 321.898 | 1841.1 | 53.6497 | 54.7828 | -1.1331 | 328.6966 | 50.4 | 53.9994 | -3.5994 | 1.0364 | 2026-12-03 14:40 | 309.692 | 319.541 | 1814.1 | 53.2568 | 54.7828 | -1.5259 | 328.6966 | 48.5 | 53.9994 | -5.4994 | 0.96918 | 2026-12-03 14:40 | 310.182 | 315.482 | 1824.9 | 52.5803 | 54.7828 | -2.2024 | 328.6966 | 48.8 | 53.9994 | -5.1994 | 0.9832 | 2026-12-03 14:40 | 241.07 | 243.946 | 1378.3 | 40.6577 | 40.5798 | 0.077844 | 243.4789 | 37.2 | 39.9995 | -2.7995 | 0.98821 | 2026-12-03 14:40 | 242.144 | 248.519 | 1367.1 | 41.4198 | 40.5798 | 0.84001 | 243.4789 | 36 | 39.9995 | -3.9995 | 0.97435 | 2026-12-03 14:40 | 243.274 | 247.004 | 1368.1 | 41.1673 | 40.5798 | 0.58751 | 243.4789 | 36 | 39.9995 | -3.9995 | 0.9849 | 2026-12-03 14:40 | 244.88 | 250.228 | 1378.5 | 41.7047 | 40.5798 | 1.1248 | 243.4789 | 36.2 | 39.9995 | -3.7995 | 0.97863 | 2026-12-03 14:40 | 231.799 | 235.401 | 1302.7 | 39.2335 | 38.6067 | 0.62682 | 231.6401 | 34.2 | 38.0546 | -3.8546 | 0.9847 | 2026-12-03 14:40 | 416.3123 | 420.057 | -3.7447 | 2520.342 | 376 | 414.0502 | -38.0502
2026-12-03 14:30 | 676 | 48.79 | 258.918 | 263.493 | 1782.5 | 43.9155 | 40.2534 | 3.6621 | 241.5205 | 44.4 | 39.6778 | 4.7222 | 0.98264 | 2026-12-03 14:30 | 264.633 | 268.881 | 1790.7 | 44.8135 | 40.2534 | 4.5601 | 241.5205 | 44.6 | 39.6778 | 4.9222 | 0.9842 | 2026-12-03 14:30 | 232.592 | 238.757 | 1765.6 | 39.7928 | 40.2534 | -0.46059 | 241.5205 | 44.3 | 39.6778 | 4.6222 | 0.97418 | 2026-12-03 14:30 | 238.569 | 242.251 | 1776.1 | 40.3752 | 40.2534 | 0.12175 | 241.5205 | 44.7 | 39.6778 | 5.0222 | 0.9848 | 2026-12-03 14:30 | 178.75 | 181.38 | 1341.1 | 30.23 | 29.8173 | 0.41265 | 178.9041 | 33 | 29.391 | 3.609 | 0.9855 | 2026-12-03 14:30 | 179.234 | 181.834 | 1331.1 | 30.3057 | 29.8173 | 0.48832 | 178.9041 | 32.6 | 29.391 | 3.209 | 0.9857 | 2026-12-03 14:30 | 180.827 | 184.453 | 1332.1 | 30.7422 | 29.8173 | 0.92482 | 178.9041 | 33 | 29.391 | 3.609 | 0.98034 | 2026-12-03 14:30 | 184.483 | 190.043 | 1342.3 | 31.6738 | 29.8173 | 1.8565 | 178.9041 | 33.2 | 29.391 | 3.809 | 0.97074 | 2026-12-03 14:30 | 172.249 | 174.783 | 1268.5 | 29.1305 | 28.3675 | 0.76299 | 170.2051 | 31.4 | 27.9619 | 3.4381 | 0.9855 | 2026-12-03 14:30 | 320.9792 | 308.6506 | 12.3286 | 1851.9035 | 341.2 | 304.2369 | 36.9631
2026-12-03 14:20 | 757 | 49.08 | 264.657 | 268.851 | 1738.1 | 44.8085 | 45.0268 | -0.21828 | 270.1607 | 42.7 | 44.3829 | -1.6829 | 0.9844 | 2026-12-03 14:20 | 241.751 | 278.472 | 1746.1 | 46.412 | 45.0268 | 1.3852 | 270.1607 | 41.8 | 44.3829 | -2.5829 | 0.86813 | 2026-12-03 14:20 | 252.138 | 256.992 | 1721.3 | 42.832 | 45.0268 | -2.1948 | 270.1607 | 41.6 | 44.3829 | -2.7829 | 0.98111 | 2026-12-03 14:20 | 257.778 | 261.89 | 1731.4 | 43.6483 | 45.0268 | -1.3784 | 270.1607 | 41.7 | 44.3829 | -2.6829 | 0.9843 | 2026-12-03 14:20 | 181.323 | 184.01 | 1308.1 | 30.6683 | 33.3532 | -2.6848 | 200.119 | 31.3 | 32.8762 | -1.5762 | 0.9854 | 2026-12-03 14:20 | 182.21 | 184.872 | 1298.5 | 30.812 | 33.3532 | -2.5412 | 200.119 | 30.8 | 32.8762 | -2.0762 | 0.9856 | 2026-12-03 14:20 | 189.818 | 192.611 | 1299.1 | 32.1018 | 33.3532 | -1.2513 | 200.119 | 30.9 | 32.8762 | -1.9762 | 0.9855 | 2026-12-03 14:20 | 189.328 | 193.472 | 1309.1 | 32.2453 | 33.3532 | -1.1078 | 200.119 | 31 | 32.8762 | -1.8762 | 0.97858 | 2026-12-03 14:20 | 180.554 | 183.211 | 1237.1 | 30.5352 | 31.7314 | -1.1962 | 190.3884 | 29.3 | 31.2776 | -1.9776 | 0.9855 | 2026-12-03 14:20 | 334.0635 | 345.2512 | -11.1877 | 2071.5071 | 321.1 | 340.3141 | -19.2141
2026-12-03 14:10 | 867 | 49.36 | 288.619 | 293.461 | 1695.4 | 48.9102 | 51.5144 | -2.6043 | 309.0867 | 52.2 | 50.7778 | 1.4222 | 0.9835 | 2026-12-03 14:10 | 292.42 | 297.447 | 1704.3 | 49.5745 | 51.5144 | -1.9399 | 309.0867 | 52.8 | 50.7778 | 2.0222 | 0.9831 | 2026-12-03 14:10 | 284.071 | 291.542 | 1679.7 | 48.5903 | 51.5144 | -2.9241 | 309.0867 | 53.3 | 50.7778 | 2.5222 | 0.97437 | 2026-12-03 14:10 | 287.837 | 292.845 | 1689.7 | 48.8075 | 51.5144 | -2.7069 | 309.0867 | 53.1 | 50.7778 | 2.3222 | 0.9829 | 2026-12-03 14:10 | 216.296 | 219.785 | 1276.8 | 36.6308 | 38.1588 | -1.528 | 228.9531 | 42.3 | 37.6132 | 4.6868 | 0.98413 | 2026-12-03 14:10 | 213.739 | 218.386 | 1267.7 | 36.3977 | 38.1588 | -1.7612 | 228.9531 | 41.6 | 37.6132 | 3.9868 | 0.97872 | 2026-12-03 14:10 | 217.284 | 220.729 | 1268.2 | 36.7882 | 38.1588 | -1.3707 | 228.9531 | 41.2 | 37.6132 | 3.5868 | 0.98439 | 2026-12-03 14:10 | 219.889 | 225.398 | 1278.1 | 37.5663 | 38.1588 | -0.59252 | 228.9531 | 41.6 | 37.6132 | 3.9868 | 0.97556 | 2026-12-03 14:10 | 207.807 | 211.036 | 1207.8 | 35.1727 | 36.3034 | -1.1308 | 217.8205 | 39.2 | 35.7843 | 3.4157 | 0.9847 | 2026-12-03 14:10 | 378.4382 | 394.9966 | -16.5584 | 2369.9796 | 417.3 | 389.3482 | 27.9518
2026-12-03 14:00 | 1065 | 49.08 | 331.077 | 336.289 | 1643.2 | 56.0482 | 63.3468 | -7.2986 | 380.0807 | 56.5 | 62.4409 | -5.9409 | 0.9845 | 2026-12-03 14:00 | 339.175 | 344.865 | 1651.5 | 57.4775 | 63.3468 | -5.8693 | 380.0807 | 57.4 | 62.4409 | -5.0409 | 0.9835 | 2026-12-03 14:00 | 341.445 | 350.806 | 1626.4 | 58.4677 | 63.3468 | -4.8791 | 380.0807 | 55.8 | 62.4409 | -6.6409 | 0.97332 | 2026-12-03 14:00 | 334.348 | 339.888 | 1636.6 | 56.648 | 63.3468 | -6.6988 | 380.0807 | 55 | 62.4409 | -7.4409 | 0.9837 | 2026-12-03 14:00 | 255.508 | 259.795 | 1234.5 | 43.2992 | 46.9235 | -3.6244 | 281.5413 | 44.7 | 46.2525 | -1.5525 | 0.9835 | 2026-12-03 14:00 | 249.99 | 255.293 | 1226.1 | 42.5488 | 46.9235 | -4.3747 | 281.5413 | 44.6 | 46.2525 | -1.6525 | 0.97923 | 2026-12-03 14:00 | 252.169 | 258.399 | 1227 | 43.0665 | 46.9235 | -3.857 | 281.5413 | 44.7 | 46.2525 | -1.5525 | 0.97589 | 2026-12-03 14:00 | 254.57 | 262.116 | 1236.5 | 43.686 | 46.9235 | -3.2375 | 281.5413 | 45.1 | 46.2525 | -1.1525 | 0.97121 | 2026-12-03 14:00 | 239.622 | 243.798 | 1168.6 | 40.633 | 44.6419 | -4.0089 | 267.8516 | 42.6 | 44.0036 | -1.4036 | 0.98287 | 2026-12-03 14:00 | 441.8748 | 485.7233 | -43.8484 | 2914.3396 | 446.4 | 478.7774 | -32.3774
2026-12-03 13:50 | 988 | 48.79 | 326.024 | 331.696 | 1586.7 | 55.2827 | 58.8319 | -3.5493 | 352.9915 | 59 | 57.9906 | 1.0094 | 0.9829 | 2026-12-03 13:50 | 333.392 | 339.259 | 1594.1 | 56.5432 | 58.8319 | -2.2888 | 352.9915 | 55.6 | 57.9906 | -2.3906 | 0.98271 | 2026-12-03 13:50 | 318.977 | 326.596 | 1570.6 | 54.4327 | 58.8319 | -4.3993 | 352.9915 | 56.6 | 57.9906 | -1.3906 | 0.97667 | 2026-12-03 13:50 | 322.452 | 328.363 | 1581.6 | 54.7272 | 58.8319 | -4.1048 | 352.9915 | 56.7 | 57.9906 | -1.2906 | 0.982 | 2026-12-03 13:50 | 236.631 | 240.503 | 1189.8 | 40.0838 | 43.5792 | -3.4954 | 261.4752 | 45.5 | 42.956 | 2.544 | 0.9839 | 2026-12-03 13:50 | 244.767 | 249.899 | 1181.5 | 41.6498 | 43.5792 | -1.9294 | 261.4752 | 44.2 | 42.956 | 1.244 | 0.97946 | 2026-12-03 13:50 | 247.958 | 253.054 | 1182.3 | 42.1757 | 43.5792 | -1.4035 | 261.4752 | 44.3 | 42.956 | 1.344 | 0.97986 | 2026-12-03 13:50 | 249.029 | 255.865 | 1191.4 | 42.6442 | 43.5792 | -0.93503 | 261.4752 | 44.4 | 42.956 | 1.444 | 0.97328 | 2026-12-03 13:50 | 234.922 | 238.718 | 1126 | 39.7863 | 41.4602 | -1.6739 | 248.7613 | 42 | 40.8673 | 1.1327 | 0.9841 | 2026-12-03 13:50 | 427.3255 | 451.1047 | -23.7792 | 2706.6282 | 448.3 | 444.6539 | 3.6461
2026-12-03 13:40 | 1043 | 48.79 | 328.62 | 334.371 | 1527.7 | 55.7285 | 62.107 | -6.3785 | 372.6419 | 52.7 | 61.2188 | -8.5188 | 0.9828 | 2026-12-03 13:40 | 351.334 | 357.701 | 1538.5 | 59.6168 | 62.107 | -2.4901 | 372.6419 | 55.2 | 61.2188 | -6.0188 | 0.9822 | 2026-12-03 13:40 | 352.322 | 363.164 | 1514 | 60.5273 | 62.107 | -1.5796 | 372.6419 | 54.5 | 61.2188 | -6.7188 | 0.97015 | 2026-12-03 13:40 | 345.255 | 351.476 | 1524.9 | 58.5793 | 62.107 | -3.5276 | 372.6419 | 53.9 | 61.2188 | -7.3188 | 0.9823 | 2026-12-03 13:40 | 259.607 | 263.855 | 1144.3 | 43.9758 | 46.0052 | -2.0293 | 276.031 | 40.6 | 45.3473 | -4.7473 | 0.9839 | 2026-12-03 13:40 | 253.341 | 259.001 | 1137.3 | 43.1668 | 46.0052 | -2.8383 | 276.031 | 40 | 45.3473 | -5.3473 | 0.97815 | 2026-12-03 13:40 | 257.834 | 264.608 | 1138 | 44.1013 | 46.0052 | -1.9038 | 276.031 | 40.5 | 45.3473 | -4.8473 | 0.9744 | 2026-12-03 13:40 | 261.253 | 269.054 | 1147 | 44.8423 | 46.0052 | -1.1628 | 276.031 | 40.2 | 45.3473 | -5.1473 | 0.97101 | 2026-12-03 13:40 | 242.566 | 248.19 | 1084 | 41.365 | 43.7682 | -2.4032 | 262.6093 | 37.9 | 43.1423 | -5.2423 | 0.97734 | 2026-12-03 13:40 | 451.9033 | 476.2168 | -24.3135 | 2857.3008 | 415.5 | 469.4069 | -53.9069
2026-12-03 13:30 | 880 | 48.79 | 296.063 | 300.938 | 1475 | 50.1563 | 52.4009 | -2.2446 | 314.4054 | 48.7 | 51.6516 | -2.9516 | 0.9838 | 2026-12-03 13:30 | 288.494 | 293.274 | 1483.3 | 48.879 | 52.4009 | -3.5219 | 314.4054 | 50.6 | 51.6516 | -1.0516 | 0.9837 | 2026-12-03 13:30 | 292.535 | 301.569 | 1459.5 | 50.2615 | 52.4009 | -2.1394 | 314.4054 | 48.2 | 51.6516 | -3.4516 | 0.97004 | 2026-12-03 13:30 | 292.332 | 297.236 | 1471 | 49.5393 | 52.4009 | -2.8616 | 314.4054 | 48.6 | 51.6516 | -3.0516 | 0.9835 | 2026-12-03 13:30 | 220.002 | 223.352 | 1103.7 | 37.2253 | 38.8155 | -1.5901 | 232.8929 | 36.9 | 38.2604 | -1.3604 | 0.985 | 2026-12-03 13:30 | 216.885 | 221.064 | 1097.3 | 36.844 | 38.8155 | -1.9715 | 232.8929 | 36.4 | 38.2604 | -1.8604 | 0.9811 | 2026-12-03 13:30 | 214.548 | 217.771 | 1097.5 | 36.2952 | 38.8155 | -2.5203 | 232.8929 | 35.9 | 38.2604 | -2.3604 | 0.9852 | 2026-12-03 13:30 | 216.993 | 223.252 | 1106.8 | 37.2087 | 38.8155 | -1.6068 | 232.8929 | 36.7 | 38.2604 | -1.5604 | 0.97196 | 2026-12-03 13:30 | 205.218 | 208.343 | 1046.1 | 34.7238 | 36.9281 | -2.2043 | 221.5687 | 34.6 | 36.4001 | -1.8001 | 0.985 | 2026-12-03 13:30 | 381.1332 | 401.7937 | -20.6605 | 2410.762 | 376.6 | 396.048 | -19.448
2026-12-03 13:20 | 866 | 49.08 | 293.976 | 299.499 | 1426.3 | 49.9165 | 51.5102 | -1.5937 | 309.0609 | 51.3 | 50.7736 | 0.52644 | 0.98156 | 2026-12-03 13:20 | 291.815 | 296.681 | 1432.7 | 49.4468 | 51.5102 | -2.0633 | 309.0609 | 51.2 | 50.7736 | 0.42644 | 0.9836 | 2026-12-03 13:20 | 284.928 | 290.708 | 1411.3 | 48.4513 | 51.5102 | -3.0588 | 309.0609 | 50.8 | 50.7736 | 0.026439 | 0.98012 | 2026-12-03 13:20 | 295.639 | 296.239 | 1422.4 | 49.3732 | 51.5102 | -2.137 | 309.0609 | 51.1 | 50.7736 | 0.32644 | 0.99797 | 2026-12-03 13:20 | 220.772 | 224.111 | 1066.8 | 37.3518 | 38.1557 | -0.80384 | 228.934 | 37.6 | 37.61 | -0.010045 | 0.9851 | 2026-12-03 13:20 | 218.228 | 221.839 | 1060.9 | 36.9732 | 38.1557 | -1.1825 | 228.934 | 37.7 | 37.61 | 0.089955 | 0.98372 | 2026-12-03 13:20 | 218.215 | 221.98 | 1061.6 | 36.9967 | 38.1557 | -1.159 | 228.934 | 37.3 | 37.61 | -0.31004 | 0.98304 | 2026-12-03 13:20 | 219.648 | 225.672 | 1070.1 | 37.612 | 38.1557 | -0.54367 | 228.934 | 37.5 | 37.61 | -0.11004 | 0.97331 | 2026-12-03 13:20 | 207.287 | 210.38 | 1011.5 | 35.0633 | 36.3004 | -1.2371 | 217.8024 | 35.5 | 35.7813 | -0.2813 | 0.9853 | 2026-12-03 13:20 | 381.1848 | 394.9637 | -13.7789 | 2369.7822 | 390 | 389.3157 | 0.68428
2026-12-03 13:10 | 858 | 48.79 | 294.225 | 299.04 | 1375 | 49.84 | 51.0909 | -1.2509 | 306.5453 | 46.7 | 50.3603 | -3.6603 | 0.9839 | 2026-12-03 13:10 | 276.967 | 295.013 | 1381.5 | 49.1688 | 51.0909 | -1.922 | 306.5453 | 47.7 | 50.3603 | -2.6603 | 0.93883 | 2026-12-03 13:10 | 293.232 | 300.306 | 1360.5 | 50.051 | 51.0909 | -1.0399 | 306.5453 | 47 | 50.3603 | -3.3603 | 0.97644 | 2026-12-03 13:10 | 295.416 | 300.311 | 1371.3 | 50.0518 | 51.0909 | -1.039 | 306.5453 | 47.3 | 50.3603 | -3.0603 | 0.9837 | 2026-12-03 13:10 | 221.522 | 224.85 | 1029.2 | 37.475 | 37.8451 | -0.3701 | 227.0706 | 35.4 | 37.3039 | -1.9039 | 0.9852 | 2026-12-03 13:10 | 215.904 | 221.149 | 1023.2 | 36.8582 | 37.8451 | -0.98693 | 227.0706 | 34.3 | 37.3039 | -3.0039 | 0.97628 | 2026-12-03 13:10 | 218.92 | 222.431 | 1024.3 | 37.0718 | 37.8451 | -0.77326 | 227.0706 | 34.8 | 37.3039 | -2.5039 | 0.98422 | 2026-12-03 13:10 | 219.903 | 226.172 | 1032.6 | 37.6953 | 37.8451 | -0.14976 | 227.0706 | 35 | 37.3039 | -2.3039 | 0.97228 | 2026-12-03 13:10 | 210.653 | 213.796 | 976 | 35.6327 | 36.0049 | -0.37225 | 216.0295 | 33.1 | 35.4901 | -2.3901 | 0.9853 | 2026-12-03 13:10 | 383.8447 | 391.7488 | -7.9042 | 2350.4929 | 361.3 | 386.1468 | -24.8468
2026-12-03 13:00 | 893 | 49.08 | 301.956 | 306.928 | 1328.3 | 51.1547 | 53.1161 | -1.9615 | 318.6968 | 53.6 | 52.3566 | 1.2434 | 0.9838 | 2026-12-03 13:00 | 312.772 | 318.052 | 1333.8 | 53.0087 | 53.1161 | -0.10746 | 318.6968 | 53.6 | 52.3566 | 1.2434 | 0.9834 | 2026-12-03 13:00 | 303.551 | 311.218 | 1313.5 | 51.8697 | 53.1161 | -1.2465 | 318.6968 | 52.5 | 52.3566 | 0.14343 | 0.97536 | 2026-12-03 13:00 | 305.771 | 310.933 | 1324 | 51.8222 | 53.1161 | -1.294 | 318.6968 | 53 | 52.3566 | 0.64343 | 0.9834 | 2026-12-03 13:00 | 226.928 | 230.384 | 993.8 | 38.3973 | 39.3453 | -0.94795 | 236.0717 | 39.7 | 38.7826 | 0.91736 | 0.985 | 2026-12-03 13:00 | 223.955 | 228.015 | 988.9 | 38.0025 | 39.3453 | -1.3428 | 236.0717 | 39.6 | 38.7826 | 0.81736 | 0.98219 | 2026-12-03 13:00 | 223.177 | 227.209 | 989.5 | 37.8682 | 39.3453 | -1.4771 | 236.0717 | 39.7 | 38.7826 | 0.91736 | 0.98225 | 2026-12-03 13:00 | 222.839 | 229.273 | 997.6 | 38.2122 | 39.3453 | -1.1331 | 236.0717 | 39.7 | 38.7826 | 0.91736 | 0.97194 | 2026-12-03 13:00 | 211.778 | 214.981 | 942.9 | 35.8302 | 37.4322 | -1.602 | 224.593 | 37.6 | 36.8969 | 0.70312 | 0.9851 | 2026-12-03 13:00 | 396.1655 | 407.2778 | -11.1123 | 2443.6669 | 409 | 401.4537 | 7.5463
2026-12-03 12:50 | 845 | 49.08 | 294.141 | 298.833 | 1274.7 | 49.8055 | 50.2611 | -0.45556 | 301.5664 | 43.2 | 49.5423 | -6.3423 | 0.9843 | 2026-12-03 12:50 | 284.667 | 289.208 | 1280.2 | 48.2013 | 50.2611 | -2.0597 | 301.5664 | 44.3 | 49.5423 | -5.2423 | 0.9843 | 2026-12-03 12:50 | 293.13 | 300.524 | 1261 | 50.0873 | 50.2611 | -0.17373 | 301.5664 | 43 | 49.5423 | -6.5423 | 0.9754 | 2026-12-03 12:50 | 295.95 | 300.762 | 1271 | 50.127 | 50.2611 | -0.13406 | 301.5664 | 43.3 | 49.5423 | -6.2423 | 0.984 | 2026-12-03 12:50 | 219.732 | 222.942 | 954.1 | 37.157 | 37.2304 | -0.073418 | 223.3825 | 32.4 | 36.698 | -4.298 | 0.9856 | 2026-12-03 12:50 | 212.861 | 216.944 | 949.3 | 36.1573 | 37.2304 | -1.0731 | 223.3825 | 31.5 | 36.698 | -5.198 | 0.98118 | 2026-12-03 12:50 | 216.305 | 220.653 | 949.8 | 36.7755 | 37.2304 | -0.45492 | 223.3825 | 31.4 | 36.698 | -5.298 | 0.98029 | 2026-12-03 12:50 | 215.857 | 222.355 | 957.9 | 37.0592 | 37.2304 | -0.17125 | 223.3825 | 32 | 36.698 | -4.698 | 0.97078 | 2026-12-03 12:50 | 204.245 | 207.25 | 905.3 | 34.5417 | 35.4201 | -0.87847 | 212.5208 | 30.3 | 34.9136 | -4.6136 | 0.9855 | 2026-12-03 12:50 | 379.9118 | 385.3861 | -5.4742 | 2312.3164 | 331.4 | 379.875 | -48.475
2026-12-03 12:40 | 748 | 48.79 | 278.586 | 282.972 | 1231.5 | 47.162 | 44.5408 | 2.6212 | 267.2446 | 43 | 43.9038 | -0.90383 | 0.9845 | 2026-12-03 12:40 | 287.114 | 292.387 | 1235.9 | 48.7312 | 44.5408 | 4.1904 | 267.2446 | 40.3 | 43.9038 | -3.6038 | 0.98197 | 2026-12-03 12:40 | 256.947 | 263.451 | 1218 | 43.9085 | 44.5408 | -0.63227 | 267.2446 | 40.8 | 43.9038 | -3.1038 | 0.97531 | 2026-12-03 12:40 | 264.296 | 268.43 | 1227.7 | 44.7383 | 44.5408 | 0.19757 | 267.2446 | 41.2 | 43.9038 | -2.7038 | 0.9846 | 2026-12-03 12:40 | 190.261 | 192.962 | 921.7 | 32.1603 | 32.9932 | -0.83283 | 197.959 | 31.1 | 32.5214 | -1.4214 | 0.986 | 2026-12-03 12:40 | 190.694 | 193.46 | 917.8 | 32.2433 | 32.9932 | -0.74983 | 197.959 | 30.3 | 32.5214 | -2.2214 | 0.9857 | 2026-12-03 12:40 | 184.826 | 187.45 | 918.4 | 31.2417 | 32.9932 | -1.7515 | 197.959 | 30.3 | 32.5214 | -2.2214 | 0.986 | 2026-12-03 12:40 | 195.623 | 201.025 | 925.9 | 33.5042 | 32.9932 | 0.51101 | 197.959 | 29.8 | 32.5214 | -2.7214 | 0.97313 | 2026-12-03 12:40 | 186.091 | 188.718 | 875 | 31.453 | 31.3889 | 0.064094 | 188.3334 | 28.2 | 30.94 | -2.74 | 0.98608 | 2026-12-03 12:40 | 345.1425 | 341.5246 | 3.6179 | 2049.1477 | 315 | 336.6408 | -21.6408
2026-12-03 12:30 | 807 | 49.08 | 286.414 | 291.042 | 1188.5 | 48.507 | 48.0008 | 0.5062 | 288.0048 | 48.6 | 47.3144 | 1.2856 | 0.9841 | 2026-12-03 12:30 | 267.448 | 271.797 | 1195.6 | 45.2995 | 48.0008 | -2.7013 | 288.0048 | 52.3 | 47.3144 | 4.9856 | 0.984 | 2026-12-03 12:30 | 274.221 | 284.13 | 1177.2 | 47.355 | 48.0008 | -0.6458 | 288.0048 | 50.8 | 47.3144 | 3.4856 | 0.96513 | 2026-12-03 12:30 | 270.066 | 274.569 | 1186.5 | 45.7615 | 48.0008 | -2.2393 | 288.0048 | 51.1 | 47.3144 | 3.7856 | 0.9836 | 2026-12-03 12:30 | 215.479 | 218.672 | 890.6 | 36.4453 | 35.5562 | 0.88918 | 213.3369 | 38.1 | 35.0477 | 3.0523 | 0.9854 | 2026-12-03 12:30 | 203.975 | 209.273 | 887.5 | 34.8788 | 35.5562 | -0.67732 | 213.3369 | 38.1 | 35.0477 | 3.0523 | 0.97468 | 2026-12-03 12:30 | 206.066 | 209.514 | 888.1 | 34.919 | 35.5562 | -0.63715 | 213.3369 | 38 | 35.0477 | 2.9523 | 0.98354 | 2026-12-03 12:30 | 205.75 | 212.443 | 896.1 | 35.4072 | 35.5562 | -0.14898 | 213.3369 | 38.1 | 35.0477 | 3.0523 | 0.9685 | 2026-12-03 12:30 | 194.944 | 197.832 | 846.8 | 32.972 | 33.8273 | -0.85527 | 202.9636 | 36 | 33.3435 | 2.6565 | 0.9854 | 2026-12-03 12:30 | 361.5453 | 368.0551 | -6.5098 | 2208.3305 | 391.1 | 362.7919 | 28.3081
2026-12-03 12:20 | 924 | 48.5 | 307.352 | 313.07 | 1139.9 | 52.1783 | 55.0819 | -2.9035 | 330.4912 | 50.9 | 54.2942 | -3.3942 | 0.98174 | 2026-12-03 12:20 | 308.943 | 314.126 | 1143.3 | 52.3543 | 55.0819 | -2.7275 | 330.4912 | 49.8 | 54.2942 | -4.4942 | 0.9835 | 2026-12-03 12:20 | 308.812 | 317.425 | 1126.4 | 52.9042 | 55.0819 | -2.1777 | 330.4912 | 49.7 | 54.2942 | -4.5942 | 0.97287 | 2026-12-03 12:20 | 306.573 | 311.748 | 1135.4 | 51.958 | 55.0819 | -3.1239 | 330.4912 | 50.1 | 54.2942 | -4.1942 | 0.9834 | 2026-12-03 12:20 | 233.664 | 238.231 | 852.5 | 39.7052 | 40.8014 | -1.0962 | 244.8083 | 38.2 | 40.2179 | -2.0179 | 0.98083 | 2026-12-03 12:20 | 228.804 | 234.057 | 849.4 | 39.0095 | 40.8014 | -1.7919 | 244.8083 | 38.5 | 40.2179 | -1.7179 | 0.97756 | 2026-12-03 12:20 | 236.6 | 242.494 | 850.1 | 40.4157 | 40.8014 | -0.38571 | 244.8083 | 37.8 | 40.2179 | -2.4179 | 0.97569 | 2026-12-03 12:20 | 235.647 | 243.507 | 858 | 40.5845 | 40.8014 | -0.21688 | 244.8083 | 37.9 | 40.2179 | -2.3179 | 0.96772 | 2026-12-03 12:20 | 222.129 | 225.99 | 810.8 | 37.665 | 38.8175 | -1.1525 | 232.9048 | 35.9 | 38.2624 | -2.3624 | 0.98292 | 2026-12-03 12:20 | 406.7747 | 422.3504 | -15.5758 | 2534.1027 | 388.8 | 416.3108 | -27.5108
2026-12-03 12:10 | 843 | 48.79 | 295.487 | 299.872 | 1089 | 49.9787 | 50.1977 | -0.21901 | 301.1861 | 54.1 | 49.4799 | 4.6201 | 0.98538 | 2026-12-03 12:10 | 278.644 | 283.319 | 1093.5 | 47.2198 | 50.1977 | -2.9778 | 301.1861 | 54 | 49.4799 | 4.5201 | 0.9835 | 2026-12-03 12:10 | 297.981 | 308.177 | 1076.7 | 51.3628 | 50.1977 | 1.1652 | 301.1861 | 52.9 | 49.4799 | 3.4201 | 0.96692 | 2026-12-03 12:10 | 277.251 | 281.538 | 1085.3 | 46.923 | 50.1977 | -3.2747 | 301.1861 | 52.8 | 49.4799 | 3.3201 | 0.98477 | 2026-12-03 12:10 | 205.055 | 208.456 | 814.3 | 34.7427 | 37.1835 | -2.4408 | 223.1008 | 39.6 | 36.6517 | 2.9483 | 0.98368 | 2026-12-03 12:10 | 200.415 | 203.488 | 810.9 | 33.9147 | 37.1835 | -3.2688 | 223.1008 | 38.2 | 36.6517 | 1.5483 | 0.9849 | 2026-12-03 12:10 | 200.874 | 205.381 | 812.3 | 34.2302 | 37.1835 | -2.9533 | 223.1008 | 39.1 | 36.6517 | 2.4483 | 0.97806 | 2026-12-03 12:10 | 201.042 | 207.592 | 820.1 | 34.5987 | 37.1835 | -2.5848 | 223.1008 | 39.2 | 36.6517 | 2.5483 | 0.96845 | 2026-12-03 12:10 | 190.427 | 193.268 | 774.9 | 32.2113 | 35.3755 | -3.1641 | 212.2528 | 37.1 | 34.8696 | 2.2304 | 0.9853 | 2026-12-03 12:10 | 365.1818 | 384.9001 | -19.7182 | 2309.4004 | 407 | 379.396 | 27.604
2026-12-03 12:00 | 1046 | 49.08 | 344.654 | 350.294 | 1034.9 | 58.3823 | 62.2167 | -3.8343 | 373.2999 | 55.9 | 61.327 | -5.427 | 0.9839 | 2026-12-03 12:00 | 340.696 | 346.06 | 1039.5 | 57.6767 | 62.2167 | -4.54 | 373.2999 | 57.3 | 61.327 | -4.027 | 0.9845 | 2026-12-03 12:00 | 342.572 | 352.873 | 1023.8 | 58.8122 | 62.2167 | -3.4045 | 373.2999 | 56 | 61.327 | -5.327 | 0.97081 | 2026-12-03 12:00 | 331.831 | 337.158 | 1032.5 | 56.193 | 62.2167 | -6.0237 | 373.2999 | 55.6 | 61.327 | -5.727 | 0.9842 | 2026-12-03 12:00 | 256.604 | 261.976 | 774.7 | 43.6627 | 46.0864 | -2.4237 | 276.5185 | 45.1 | 45.4274 | -0.32738 | 0.97949 | 2026-12-03 12:00 | 254.637 | 259.678 | 772.7 | 43.2797 | 46.0864 | -2.8067 | 276.5185 | 44.5 | 45.4274 | -0.92738 | 0.98059 | 2026-12-03 12:00 | 251.511 | 256.399 | 773.2 | 42.7332 | 46.0864 | -3.3532 | 276.5185 | 45.3 | 45.4274 | -0.12738 | 0.98094 | 2026-12-03 12:00 | 252.624 | 259.592 | 780.9 | 43.2653 | 46.0864 | -2.8211 | 276.5185 | 45.6 | 45.4274 | 0.17262 | 0.97316 | 2026-12-03 12:00 | 239.418 | 243.311 | 737.8 | 40.5518 | 43.8455 | -3.2937 | 263.0731 | 43.1 | 43.2185 | -0.11852 | 0.984 | 2026-12-03 12:00 | 444.5568 | 477.0578 | -32.5009 | 2862.3467 | 448.4 | 470.2358 | -21.8358
2026-12-03 11:50 | 1192 | 48.79 | 343.883 | 348.907 | 979 | 58.1512 | 70.9794 | -12.8282 | 425.8764 | 57.1 | 69.9644 | -12.8644 | 0.9856 | 2026-12-03 11:50 | 345.639 | 354.591 | 982.2 | 59.0985 | 70.9794 | -11.8809 | 425.8764 | 55.7 | 69.9644 | -14.2644 | 0.97475 | 2026-12-03 11:50 | 345.515 | 355.827 | 967.8 | 59.3045 | 70.9794 | -11.6749 | 425.8764 | 57.3 | 69.9644 | -12.6644 | 0.97102 | 2026-12-03 11:50 | 339.148 | 344.103 | 976.9 | 57.3505 | 70.9794 | -13.6289 | 425.8764 | 56.7 | 69.9644 | -13.2644 | 0.9856 | 2026-12-03 11:50 | 294.338 | 299.307 | 729.6 | 49.8845 | 52.5773 | -2.6928 | 315.464 | 46.6 | 51.8255 | -5.2255 | 0.9834 | 2026-12-03 11:50 | 291.231 | 296.907 | 728.2 | 49.4845 | 52.5773 | -3.0928 | 315.464 | 46 | 51.8255 | -5.8255 | 0.98088 | 2026-12-03 11:50 | 293.421 | 300.159 | 727.9 | 50.0265 | 52.5773 | -2.5508 | 315.464 | 46.1 | 51.8255 | -5.7255 | 0.97755 | 2026-12-03 11:50 | 295.22 | 304.174 | 735.3 | 50.6957 | 52.5773 | -1.8817 | 315.464 | 46.4 | 51.8255 | -5.4255 | 0.97056 | 2026-12-03 11:50 | 279.154 | 283.808 | 694.7 | 47.3013 | 50.0208 | -2.7195 | 300.1249 | 43.7 | 49.3055 | -5.6055 | 0.9836 | 2026-12-03 11:50 | 481.2972 | 544.2478 | -62.9506 | 3265.4867 | 455.6 | 536.465 | -80.865
2026-12-03 11:40 | 1023 | 48.79 | 346.833 | 353.058 | 921.9 | 58.843 | 60.916 | -2.073 | 365.4963 | 46.4 | 60.0449 | -13.6449 | 0.98237 | 2026-12-03 11:40 | 221.215 | 220.901 | 926.5 | 36.8168 | 60.916 | -24.0992 | 365.4963 | 47 | 60.0449 | -13.0449 | 1.0014 | 2026-12-03 11:40 | 351.106 | 362.215 | 910.5 | 60.3692 | 60.916 | -0.54688 | 365.4963 | 45.9 | 60.0449 | -14.1449 | 0.96933 | 2026-12-03 11:40 | 350.89 | 356.849 | 920.2 | 59.4748 | 60.916 | -1.4412 | 365.4963 | 46.3 | 60.0449 | -13.7449 | 0.9833 | 2026-12-03 11:40 | 275.017 | 278.215 | 683 | 46.3692 | 45.123 | 1.2462 | 270.738 | 35.2 | 44.4777 | -9.2777 | 0.98851 | 2026-12-03 11:40 | 262.904 | 271.873 | 682.2 | 45.3122 | 45.123 | 0.18917 | 270.738 | 34.8 | 44.4777 | -9.6777 | 0.96701 | 2026-12-03 11:40 | 242.434 | 252.593 | 681.8 | 42.0988 | 45.123 | -3.0242 | 270.738 | 34.1 | 44.4777 | -10.3777 | 0.95978 | 2026-12-03 11:40 | 239.422 | 253.379 | 688.9 | 42.2298 | 45.123 | -2.8932 | 270.738 | 34.2 | 44.4777 | -10.2777 | 0.94492 | 2026-12-03 11:40 | 224.144 | 232.233 | 651 | 38.7055 | 42.9289 | -4.2234 | 257.5737 | 32.5 | 42.3151 | -9.8151 | 0.96517 | 2026-12-03 11:40 | 430.2193 | 467.0851 | -36.8658 | 2802.5108 | 356.4 | 460.4058 | -104.0058
2026-12-03 11:30 | 1005 | 48.79 | 337.891 | 343.63 | 875.5 | 57.2717 | 59.8442 | -2.5725 | 359.0653 | 55.2 | 58.9884 | -3.7884 | 0.9833 | 2026-12-03 11:30 | 342.535 | 348.748 | 879.5 | 58.1247 | 59.8442 | -1.7195 | 359.0653 | 55.7 | 58.9884 | -3.2884 | 0.98218 | 2026-12-03 11:30 | 331.867 | 340.878 | 864.6 | 56.813 | 59.8442 | -3.0312 | 359.0653 | 54.4 | 58.9884 | -4.5884 | 0.97357 | 2026-12-03 11:30 | 336.706 | 342.494 | 873.9 | 57.0823 | 59.8442 | -2.7619 | 359.0653 | 54.9 | 58.9884 | -4.0884 | 0.9831 | 2026-12-03 11:30 | 253.868 | 257.865 | 647.8 | 42.9775 | 44.329 | -1.3515 | 265.9743 | 40.3 | 43.6951 | -3.3951 | 0.9845 | 2026-12-03 11:30 | 251.891 | 256.477 | 647.4 | 42.7462 | 44.329 | -1.5829 | 265.9743 | 39.9 | 43.6951 | -3.7951 | 0.98212 | 2026-12-03 11:30 | 251.832 | 256.798 | 647.7 | 42.7997 | 44.329 | -1.5294 | 265.9743 | 39.9 | 43.6951 | -3.7951 | 0.98066 | 2026-12-03 11:30 | 254.456 | 261.963 | 654.7 | 43.6605 | 44.329 | -0.66855 | 265.9743 | 40.1 | 43.6951 | -3.5951 | 0.97134 | 2026-12-03 11:30 | 240.797 | 244.582 | 618.5 | 40.7637 | 42.1736 | -1.4099 | 253.0416 | 37.9 | 41.5705 | -3.6705 | 0.98452 | 2026-12-03 11:30 | 442.2392 | 458.8666 | -16.6275 | 2753.1997 | 418.3 | 452.3048 | -34.0048
2026-12-03 11:20 | 969 | 48.79 | 328.936 | 334.489 | 820.3 | 55.7482 | 57.7005 | -1.9524 | 346.2032 | 56.8 | 56.8754 | -0.07542 | 0.9834 | 2026-12-03 11:20 | 332.518 | 338.337 | 823.8 | 56.3895 | 57.7005 | -1.311 | 346.2032 | 58.8 | 56.8754 | 1.9246 | 0.9828 | 2026-12-03 11:20 | 326.819 | 336.654 | 810.2 | 56.109 | 57.7005 | -1.5915 | 346.2032 | 56.5 | 56.8754 | -0.37542 | 0.97079 | 2026-12-03 11:20 | 329.876 | 335.649 | 819 | 55.9415 | 57.7005 | -1.759 | 346.2032 | 56.7 | 56.8754 | -0.17542 | 0.9828 | 2026-12-03 11:20 | 243.042 | 246.843 | 607.5 | 41.1405 | 42.7411 | -1.6006 | 256.4468 | 42.7 | 42.1299 | 0.57006 | 0.9846 | 2026-12-03 11:20 | 241.312 | 245.422 | 607.5 | 40.9037 | 42.7411 | -1.8375 | 256.4468 | 42.3 | 42.1299 | 0.17006 | 0.98325 | 2026-12-03 11:20 | 235.289 | 238.848 | 607.8 | 39.808 | 42.7411 | -2.9331 | 256.4468 | 42.3 | 42.1299 | 0.17006 | 0.9851 | 2026-12-03 11:20 | 238.625 | 244.643 | 614.6 | 40.7738 | 42.7411 | -1.9673 | 256.4468 | 42.7 | 42.1299 | 0.57006 | 0.9754 | 2026-12-03 11:20 | 224.665 | 228.086 | 580.6 | 38.0143 | 40.6629 | -2.6486 | 243.9774 | 40.2 | 40.0814 | 0.11858 | 0.985 | 2026-12-03 11:20 | 424.8285 | 442.4296 | -17.6011 | 2654.5777 | 439 | 436.1029 | 2.8971
2026-12-03 11:10 | 1043 | 48.79 | 350.528 | 356.59 | 763.5 | 59.4317 | 62.107 | -2.6753 | 372.6419 | 51.9 | 61.2188 | -9.3188 | 0.983 | 2026-12-03 11:10 | 316.337 | 354.41 | 765 | 59.0683 | 62.107 | -3.0386 | 372.6419 | 50.3 | 61.2188 | -10.9188 | 0.89257 | 2026-12-03 11:10 | 347.011 | 356.98 | 753.7 | 59.4967 | 62.107 | -2.6103 | 372.6419 | 50.8 | 61.2188 | -10.4188 | 0.97207 | 2026-12-03 11:10 | 350.543 | 356.678 | 762.3 | 59.4463 | 62.107 | -2.6606 | 372.6419 | 51.3 | 61.2188 | -9.9188 | 0.9828 | 2026-12-03 11:10 | 261.127 | 265.292 | 564.8 | 44.2153 | 46.0052 | -1.7898 | 276.031 | 38.2 | 45.3473 | -7.1473 | 0.9843 | 2026-12-03 11:10 | 257.983 | 263.126 | 565.2 | 43.8543 | 46.0052 | -2.1508 | 276.031 | 38.4 | 45.3473 | -6.9473 | 0.98045 | 2026-12-03 11:10 | 259.634 | 264.619 | 565.5 | 44.1032 | 46.0052 | -1.902 | 276.031 | 38.5 | 45.3473 | -6.8473 | 0.98116 | 2026-12-03 11:10 | 261.727 | 269.402 | 571.9 | 44.9003 | 46.0052 | -1.1048 | 276.031 | 38.8 | 45.3473 | -6.5473 | 0.97151 | 2026-12-03 11:10 | 246.71 | 250.594 | 540.4 | 41.7657 | 43.7682 | -2.0026 | 262.6093 | 36.6 | 43.1423 | -6.5423 | 0.9845 | 2026-12-03 11:10 | 456.2818 | 476.2168 | -19.935 | 2857.3008 | 394.8 | 469.4069 | -74.6069
2026-12-03 11:00 | 986 | 49.08 | 332.968 | 338.692 | 711.6 | 56.4487 | 58.6478 | -2.1992 | 351.8869 | 54 | 57.8092 | -3.8092 | 0.9831 | 2026-12-03 11:00 | 341.464 | 341.995 | 714.7 | 56.9992 | 58.6478 | -1.6487 | 351.8869 | 56.1 | 57.8092 | -1.7092 | 0.99845 | 2026-12-03 11:00 | 329.567 | 339.804 | 702.9 | 56.634 | 58.6478 | -2.0138 | 351.8869 | 54.2 | 57.8092 | -3.6092 | 0.96987 | 2026-12-03 11:00 | 331.595 | 337.33 | 711 | 56.2217 | 58.6478 | -2.4262 | 351.8869 | 55.5 | 57.8092 | -2.3092 | 0.983 | 2026-12-03 11:00 | 249.879 | 253.813 | 526.6 | 42.3022 | 43.4428 | -1.1407 | 260.657 | 41.4 | 42.8216 | -1.4216 | 0.9845 | 2026-12-03 11:00 | 246.274 | 251.04 | 526.8 | 41.84 | 43.4428 | -1.6028 | 260.657 | 40.5 | 42.8216 | -2.3216 | 0.98101 | 2026-12-03 11:00 | 247.538 | 252.102 | 527 | 42.017 | 43.4428 | -1.4258 | 260.657 | 40.6 | 42.8216 | -2.2216 | 0.9819 | 2026-12-03 11:00 | 249.323 | 256.461 | 533.1 | 42.7435 | 43.4428 | -0.69933 | 260.657 | 40.9 | 42.8216 | -1.9216 | 0.97217 | 2026-12-03 11:00 | 235.444 | 239.102 | 503.8 | 39.8503 | 41.3305 | -1.4801 | 247.9828 | 38.7 | 40.7394 | -2.0394 | 0.9847 | 2026-12-03 11:00 | 435.0565 | 449.6931 | -14.6366 | 2698.1585 | 421.9 | 443.2625 | -21.3625
2026-12-03 10:50 | 994 | 49.08 | 336.49 | 342.205 | 657.6 | 57.0342 | 59.1237 | -2.0895 | 354.742 | 58.1 | 58.2782 | -0.1782 | 0.9833 | 2026-12-03 10:50 | 339.547 | 345.419 | 658.6 | 57.5698 | 59.1237 | -1.5538 | 354.742 | 57 | 58.2782 | -1.2782 | 0.983 | 2026-12-03 10:50 | 332.148 | 341.501 | 648.7 | 56.9168 | 59.1237 | -2.2068 | 354.742 | 56 | 58.2782 | -2.2782 | 0.97261 | 2026-12-03 10:50 | 335.997 | 341.877 | 655.5 | 56.9795 | 59.1237 | -2.1442 | 354.742 | 56.5 | 58.2782 | -1.7782 | 0.9828 | 2026-12-03 10:50 | 251.071 | 255.024 | 485.2 | 42.504 | 43.7953 | -1.2913 | 262.7719 | 41.8 | 43.169 | -1.369 | 0.9845 | 2026-12-03 10:50 | 249.418 | 253.965 | 486.3 | 42.3275 | 43.7953 | -1.4678 | 262.7719 | 41.5 | 43.169 | -1.669 | 0.9821 | 2026-12-03 10:50 | 249.587 | 254.318 | 486.4 | 42.3863 | 43.7953 | -1.409 | 262.7719 | 41.6 | 43.169 | -1.569 | 0.9814 | 2026-12-03 10:50 | 251.586 | 259.104 | 492.2 | 43.184 | 43.7953 | -0.61131 | 262.7719 | 41.8 | 43.169 | -1.369 | 0.97098 | 2026-12-03 10:50 | 237.716 | 241.459 | 465.1 | 40.2432 | 41.6658 | -1.4226 | 249.9949 | 39.5 | 41.07 | -1.57 | 0.9845 | 2026-12-03 10:50 | 439.1453 | 453.3417 | -14.1964 | 2720.0503 | 433.8 | 446.8589 | -13.0589
2026-12-03 10:40 | 954 | 49.08 | 300.402 | 307.343 | 599.5 | 51.2238 | 56.7444 | -5.5206 | 340.4667 | 48.5 | 55.933 | -7.433 | 0.97742 | 2026-12-03 10:40 | 305.09 | 312.362 | 601.6 | 52.0603 | 56.7444 | -4.6841 | 340.4667 | 49.6 | 55.933 | -6.333 | 0.97672 | 2026-12-03 10:40 | 323.347 | 333.127 | 592.7 | 55.5212 | 56.7444 | -1.2233 | 340.4667 | 49.3 | 55.933 | -6.633 | 0.97064 | 2026-12-03 10:40 | 315.357 | 316.652 | 599 | 52.7753 | 56.7444 | -3.9691 | 340.4667 | 49 | 55.933 | -6.933 | 0.99591 | 2026-12-03 10:40 | 246.436 | 250.138 | 443.4 | 41.6897 | 42.0329 | -0.34326 | 252.1975 | 37 | 41.4319 | -4.4319 | 0.9852 | 2026-12-03 10:40 | 245.017 | 249.776 | 444.8 | 41.6293 | 42.0329 | -0.40359 | 252.1975 | 37.5 | 41.4319 | -3.9319 | 0.98095 | 2026-12-03 10:40 | 246.43 | 251.018 | 444.8 | 41.8363 | 42.0329 | -0.19659 | 252.1975 | 37.4 | 41.4319 | -4.0319 | 0.98172 | 2026-12-03 10:40 | 248.184 | 255.662 | 450.4 | 42.6103 | 42.0329 | 0.57741 | 252.1975 | 37.8 | 41.4319 | -3.6319 | 0.97075 | 2026-12-03 10:40 | 234.681 | 238.232 | 425.6 | 39.7053 | 39.9891 | -0.28379 | 239.9347 | 35.7 | 39.4173 | -3.7173 | 0.98509 | 2026-12-03 10:40 | 419.0517 | 435.0986 | -16.0469 | 2610.5915 | 381.8 | 428.8767 | -47.0767
2026-12-03 10:30 | 832 | 49.08 | 287.202 | 292.163 | 551 | 48.6938 | 49.4878 | -0.79398 | 296.9269 | 49.7 | 48.7801 | 0.91986 | 0.98302 | 2026-12-03 10:30 | 302.306 | 293.312 | 552 | 48.8853 | 49.4878 | -0.60248 | 296.9269 | 50.1 | 48.7801 | 1.3199 | 1.0307 | 2026-12-03 10:30 | 287.599 | 294.205 | 543.4 | 49.0342 | 49.4878 | -0.45365 | 296.9269 | 49.2 | 48.7801 | 0.41986 | 0.97755 | 2026-12-03 10:30 | 290.746 | 295.414 | 550 | 49.2357 | 49.4878 | -0.25215 | 296.9269 | 49.7 | 48.7801 | 0.91986 | 0.9842 | 2026-12-03 10:30 | 211.657 | 214.728 | 406.4 | 35.788 | 36.6576 | -0.86964 | 219.9459 | 37.5 | 36.1334 | 1.3666 | 0.9857 | 2026-12-03 10:30 | 213.223 | 216.459 | 407.3 | 36.0765 | 36.6576 | -0.58114 | 219.9459 | 37.1 | 36.1334 | 0.96656 | 0.98505 | 2026-12-03 10:30 | 211.057 | 214.287 | 407.4 | 35.7145 | 36.6576 | -0.94314 | 219.9459 | 36.8 | 36.1334 | 0.66656 | 0.98493 | 2026-12-03 10:30 | 210.805 | 217.023 | 412.6 | 36.1705 | 36.6576 | -0.48714 | 219.9459 | 37 | 36.1334 | 0.86656 | 0.97135 | 2026-12-03 10:30 | 200.01 | 203.086 | 389.9 | 33.8477 | 34.8752 | -1.0275 | 209.2512 | 35 | 34.3765 | 0.62351 | 0.98485 | 2026-12-03 10:30 | 373.4462 | 379.457 | -6.0109 | 2276.7423 | 382.1 | 374.0308 | 8.0692
2026-12-03 10:20 | 772 | 49.36 | 293.905 | 272.777 | 501.3 | 45.4628 | 45.8698 | -0.40701 | 275.2191 | 47 | 45.2139 | 1.7861 | 1.0775 | 2026-12-03 10:20 | 272.236 | 276.466 | 501.9 | 46.0777 | 45.8698 | 0.20782 | 275.2191 | 48 | 45.2139 | 2.7861 | 0.9847 | 2026-12-03 10:20 | 270.2 | 278.061 | 494.2 | 46.3435 | 45.8698 | 0.47366 | 275.2191 | 46.6 | 45.2139 | 1.3861 | 0.97173 | 2026-12-03 10:20 | 272.518 | 276.752 | 500.3 | 46.1253 | 45.8698 | 0.25549 | 275.2191 | 47 | 45.2139 | 1.7861 | 0.9847 | 2026-12-03 10:20 | 211.639 | 214.622 | 368.9 | 35.7703 | 33.9777 | 1.7927 | 203.866 | 34.6 | 33.4918 | 1.1082 | 0.9861 | 2026-12-03 10:20 | 219.368 | 222.812 | 370.2 | 37.1353 | 33.9777 | 3.1577 | 203.866 | 34.4 | 33.4918 | 0.90822 | 0.98454 | 2026-12-03 10:20 | 206.835 | 214.452 | 370.6 | 35.742 | 33.9777 | 1.7643 | 203.866 | 34.8 | 33.4918 | 1.3082 | 0.96448 | 2026-12-03 10:20 | 208.123 | 212.21 | 375.6 | 35.3683 | 33.9777 | 1.3907 | 203.866 | 35.2 | 33.4918 | 1.7082 | 0.98074 | 2026-12-03 10:20 | 197.6 | 200.385 | 354.9 | 33.3975 | 32.3255 | 1.072 | 193.9532 | 33.6 | 31.8633 | 1.7367 | 0.9861 | 2026-12-03 10:20 | 361.4228 | 351.7155 | 9.7073 | 2110.2933 | 361.2 | 346.686 | 14.514
2026-12-03 10:10 | 831 | 48.79 | 288.821 | 295.163 | 454.3 | 49.1938 | 49.4831 | -0.28929 | 296.8987 | 47 | 48.7755 | -1.7755 | 0.97851 | 2026-12-03 10:10 | 291.061 | 295.643 | 453.9 | 49.2738 | 49.4831 | -0.20929 | 296.8987 | 46.7 | 48.7755 | -2.0755 | 0.9845 | 2026-12-03 10:10 | 288.968 | 296.354 | 447.6 | 49.3923 | 49.4831 | -0.090791 | 296.8987 | 47.2 | 48.7755 | -1.5755 | 0.97508 | 2026-12-03 10:10 | 291.5 | 295.923 | 453.3 | 49.3205 | 49.4831 | -0.16262 | 296.8987 | 47.7 | 48.7755 | -1.0755 | 0.98505 | 2026-12-03 10:10 | 217.459 | 220.502 | 334.3 | 36.7503 | 36.6542 | 0.096167 | 219.925 | 35.4 | 36.13 | -0.73001 | 0.9862 | 2026-12-03 10:10 | 216.592 | 219.707 | 335.8 | 36.6178 | 36.6542 | -0.036333 | 219.925 | 35 | 36.13 | -1.13 | 0.98582 | 2026-12-03 10:10 | 216.12 | 219.495 | 335.8 | 36.5825 | 36.6542 | -0.071666 | 219.925 | 34.9 | 36.13 | -1.23 | 0.98462 | 2026-12-03 10:10 | 218.423 | 224.527 | 340.4 | 37.4212 | 36.6542 | 0.767 | 219.925 | 35.1 | 36.13 | -1.03 | 0.97281 | 2026-12-03 10:10 | 206.054 | 208.98 | 321.3 | 34.83 | 34.8719 | -0.041899 | 209.2314 | 32.9 | 34.3732 | -1.4732 | 0.986 | 2026-12-03 10:10 | 379.3823 | 379.4211 | -0.038725 | 2276.5263 | 361.9 | 373.9953 | -12.0953
2026-12-03 10:00 | 763 | 49.36 | 269.843 | 273.813 | 407.3 | 45.6355 | 45.3351 | 0.30041 | 272.0105 | 46 | 44.6868 | 1.3132 | 0.9855 | 2026-12-03 10:00 | 272.219 | 276.364 | 407.2 | 46.0607 | 45.3351 | 0.72558 | 272.0105 | 45.9 | 44.6868 | 1.2132 | 0.985 | 2026-12-03 10:00 | 267.771 | 273.809 | 400.4 | 45.6348 | 45.3351 | 0.29974 | 272.0105 | 44.2 | 44.6868 | -0.4868 | 0.97795 | 2026-12-03 10:00 | 270.26 | 274.348 | 405.6 | 45.7247 | 45.3351 | 0.38958 | 272.0105 | 45.4 | 44.6868 | 0.7132 | 0.9851 | 2026-12-03 10:00 | 200.314 | 203.055 | 298.9 | 33.8425 | 33.5815 | 0.26095 | 201.4893 | 33.8 | 33.1013 | 0.69867 | 0.9865 | 2026-12-03 10:00 | 200 | 202.758 | 300.8 | 33.793 | 33.5815 | 0.21145 | 201.4893 | 33.7 | 33.1013 | 0.59867 | 0.9864 | 2026-12-03 10:00 | 199.344 | 202.704 | 300.9 | 33.784 | 33.5815 | 0.20245 | 201.4893 | 33.7 | 33.1013 | 0.59867 | 0.98342 | 2026-12-03 10:00 | 201.235 | 207.165 | 305.3 | 34.5275 | 33.5815 | 0.94595 | 201.4893 | 34.1 | 33.1013 | 0.99867 | 0.97138 | 2026-12-03 10:00 | 190.612 | 193.26 | 288.4 | 32.21 | 31.9487 | 0.26132 | 191.6921 | 32.3 | 31.4918 | 0.80818 | 0.9863 | 2026-12-03 10:00 | 351.2127 | 347.6152 | 3.5974 | 2085.6914 | 349.1 | 342.6443 | 6.4557
2026-12-03 09:50 | 774 | 48.79 | 278.674 | 283.005 | 361.3 | 47.1675 | 46.089 | 1.0785 | 276.5338 | 29.1 | 45.4299 | -16.3299 |  | 2026-12-03 09:50 | 280.559 | 284.687 | 361.3 | 47.4478 | 46.089 | 1.3589 | 276.5338 | 31.8 | 45.4299 | -13.6299 |  | 2026-12-03 09:50 | 275.83 | 281.749 | 356.2 | 46.9582 | 46.089 | 0.86919 | 276.5338 | 29.2 | 45.4299 | -16.2299 |  | 2026-12-03 09:50 | 278.685 | 282.814 | 360.2 | 47.1357 | 46.089 | 1.0467 | 276.5338 | 28.6 | 45.4299 | -16.8299 |  | 2026-12-03 09:50 | 206.782 | 209.548 | 265.1 | 34.9247 | 34.14 | 0.78469 | 204.8399 | 21.1 | 33.6518 | -12.5518 |  | 2026-12-03 09:50 | 206.924 | 209.692 | 267.1 | 34.9487 | 34.14 | 0.80869 | 204.8399 | 21.6 | 33.6518 | -12.0518 |  | 2026-12-03 09:50 | 206.483 | 209.306 | 267.2 | 34.8843 | 34.14 | 0.74435 | 204.8399 | 21.5 | 33.6518 | -12.1518 |  | 2026-12-03 09:50 | 208.341 | 214.367 | 271.2 | 35.7278 | 34.14 | 1.5879 | 204.8399 | 21.6 | 33.6518 | -12.0518 |  | 2026-12-03 09:50 | 197.427 | 200.085 | 256.1 | 33.3475 | 32.48 | 0.86754 | 194.8798 | 20.4 | 32.0155 | -11.6155 |  | 2026-12-03 09:50 | 362.5422 | 353.3958 | 9.1464 | 2120.3747 | 224.9 | 348.3422 | -123.4422
2026-12-03 09:40 | 599 | 49.65 | 249.064 | 216.045 | 332.2 | 36.0075 | 35.5512 | 0.45627 | 213.3074 | 42 | 35.0428 | 6.9572 |  | 2026-12-03 09:40 | 258.364 | 262.219 | 329.5 | 43.7032 | 35.5512 | 8.1519 | 213.3074 | 78.4 | 35.0428 | 43.3572 |  | 2026-12-03 09:40 | 207.354 | 212.849 | 327 | 35.4748 | 35.5512 | -0.076394 | 213.3074 | 41.5 | 35.0428 | 6.4572 |  | 2026-12-03 09:40 | 207.019 | 209.505 | 331.6 | 34.9175 | 35.5512 | -0.63373 | 213.3074 | 42 | 35.0428 | 6.9572 |  | 2026-12-03 09:40 | 155.899 | 158.159 | 244 | 26.3598 | 26.3342 | 0.025591 | 158.0055 | 31.5 | 25.9577 | 5.5423 |  | 2026-12-03 09:40 | 158.371 | 160.506 | 245.5 | 26.751 | 26.3342 | 0.41676 | 158.0055 | 31.1 | 25.9577 | 5.1423 |  | 2026-12-03 09:40 | 158.314 | 160.399 | 245.7 | 26.7332 | 26.3342 | 0.39892 | 158.0055 | 31.1 | 25.9577 | 5.1423 |  | 2026-12-03 09:40 | 161.7 | 165.561 | 249.6 | 27.5935 | 26.3342 | 1.2593 | 158.0055 | 31.3 | 25.9577 | 5.3423 |  | 2026-12-03 09:40 | 152.494 | 154.534 | 235.7 | 25.7557 | 25.0538 | 0.7019 | 150.3226 | 29.7 | 24.6955 | 5.0045 |  | 2026-12-03 09:40 | 283.2962 | 272.5957 | 10.7005 | 1635.5739 | 358.6 | 268.6975 | 89.9025
2026-12-03 09:30 | 711 | 49.08 | 252.994 | 256.638 | 290.2 | 42.773 | 42.2907 | 0.48233 | 253.744 | 38.8 | 41.6859 | -2.8859 | [5 empty] | 0 | 42.2907 | -42.2907 | 253.744 | 0 | 41.6859 | -41.6859 |  | 2026-12-03 09:30 | 249.919 | 255.795 | 285.5 | 42.6325 | 42.2907 | 0.34183 | 253.744 | 37.5 | 41.6859 | -4.1859 |  | 2026-12-03 09:30 | 252.499 | 256.214 | 289.6 | 42.7023 | 42.2907 | 0.41166 | 253.744 | 38 | 41.6859 | -3.6859 |  | 2026-12-03 09:30 | 186.414 | 188.927 | 212.5 | 31.4878 | 31.3264 | 0.16141 | 187.9585 | 27.7 | 30.8785 | -3.1785 |  | 2026-12-03 09:30 | 186.452 | 189.211 | 214.4 | 31.5352 | 31.3264 | 0.20874 | 187.9585 | 28.1 | 30.8785 | -2.7785 |  | 2026-12-03 09:30 | 186.443 | 189.292 | 214.6 | 31.5487 | 31.3264 | 0.22224 | 187.9585 | 27.9 | 30.8785 | -2.9785 |  | 2026-12-03 09:30 | 188.59 | 193.95 | 218.3 | 32.325 | 31.3264 | 0.99858 | 187.9585 | 28.3 | 30.8785 | -2.5785 |  | 2026-12-03 09:30 | 178.668 | 181.095 | 206 | 30.1825 | 29.8032 | 0.37929 | 178.8193 | 26.8 | 29.377 | -2.577 |  | 2026-12-03 09:30 | 285.187 | 324.2716 | -39.0846 | 1945.6295 | 253.1 | 319.6345 | -66.5345
2026-12-03 09:20 | 625 | 49.36 | 228.857 | 232.012 | 251.4 | 38.6687 | 37.1356 | 1.5331 | 222.8134 | 38.9 | 36.6045 | 2.2955 |  | 2026-12-03 09:20 | 239.797 | 225.138 | 251.1 | 37.523 | 37.1356 | 0.38744 | 222.8134 | 39.4 | 36.6045 | 2.7955 |  | 2026-12-03 09:20 | 218.505 | 222.701 | 248 | 37.1168 | 37.1356 | -0.018725 | 222.8134 | 38.9 | 36.6045 | 2.2955 |  | 2026-12-03 09:20 | 221.054 | 224.147 | 251.6 | 37.3578 | 37.1356 | 0.22227 | 222.8134 | 39.3 | 36.6045 | 2.6955 |  | 2026-12-03 09:20 | 162.966 | 165.096 | 184.8 | 27.516 | 27.5078 | 0.0081788 | 165.0469 | 29 | 27.1145 | 1.8855 |  | 2026-12-03 09:20 | 162.54 | 164.664 | 186.3 | 27.444 | 27.5078 | -0.063821 | 165.0469 | 28.8 | 27.1145 | 1.6855 |  | 2026-12-03 09:20 | 160.522 | 163.101 | 186.7 | 27.1835 | 27.5078 | -0.32432 | 165.0469 | 28.7 | 27.1145 | 1.5855 |  | 2026-12-03 09:20 | 162.109 | 166.658 | 190 | 27.7763 | 27.5078 | 0.26851 | 165.0469 | 29 | 27.1145 | 1.8855 |  | 2026-12-03 09:20 | 153.176 | 155.209 | 179.2 | 25.8682 | 26.1703 | -0.30212 | 157.0217 | 27.5 | 25.796 | 1.704 |  | 2026-12-03 09:20 | 286.4543 | 284.7438 | 1.7105 | 1708.4628 | 299.5 | 280.672 | 18.828
2026-12-03 09:10 | 618 | 48.79 | 220.483 | 223.432 | 212.5 | 37.2387 | 36.7997 | 0.43894 | 220.7983 | 34.9 | 36.2735 | -1.3735 |  | 2026-12-03 09:10 | 220.076 | 223.078 | 211.7 | 37.1797 | 36.7997 | 0.37994 | 220.7983 | 35.3 | 36.2735 | -0.97349 |  | 2026-12-03 09:10 | 217.287 | 221.963 | 209.1 | 36.9938 | 36.7997 | 0.19411 | 220.7983 | 34.1 | 36.2735 | -2.1735 |  | 2026-12-03 09:10 | 220.101 | 223.113 | 212.3 | 37.1855 | 36.7997 | 0.38578 | 220.7983 | 34.5 | 36.2735 | -1.7735 |  | 2026-12-03 09:10 | 162.226 | 164.329 | 155.8 | 27.3882 | 27.2591 | 0.12911 | 163.5543 | 25.5 | 26.8693 | -1.3693 |  | 2026-12-03 09:10 | 163.555 | 165.659 | 157.5 | 27.6098 | 27.2591 | 0.35078 | 163.5543 | 25.6 | 26.8693 | -1.2693 |  | 2026-12-03 09:10 | 162.697 | 164.789 | 158 | 27.4648 | 27.2591 | 0.20578 | 163.5543 | 25.6 | 26.8693 | -1.2693 |  | 2026-12-03 09:10 | 164.724 | 169.253 | 161 | 28.2088 | 27.2591 | 0.94978 | 163.5543 | 25.9 | 26.8693 | -0.96925 |  | 2026-12-03 09:10 | 156.185 | 158.21 | 151.7 | 26.3683 | 25.9336 | 0.43472 | 155.6017 | 24.8 | 25.5628 | -0.76276 |  | 2026-12-03 09:10 | 285.6377 | 282.1687 | 3.4689 | 1693.0124 | 266.2 | 278.1337 | -11.9337
2026-12-03 09:00 | 555 | 47.64 | 196.721 | 199.252 | 177.6 | 33.2087 | 33.1934 | 0.01527 | 199.1604 | 30.8 | 32.7187 | -1.9187 |  | 2026-12-03 09:00 | 197.94 | 200.567 | 176.4 | 33.4278 | 33.1934 | 0.23444 | 199.1604 | 30.7 | 32.7187 | -2.0187 |  | 2026-12-03 09:00 | 193.908 | 197.626 | 175 | 32.9377 | 33.1934 | -0.25573 | 199.1604 | 30.6 | 32.7187 | -2.1187 |  | 2026-12-03 09:00 | 197.603 | 200.185 | 177.8 | 33.3642 | 33.1934 | 0.17077 | 199.1604 | 31.2 | 32.7187 | -1.5187 |  | 2026-12-03 09:00 | 145.429 | 147.24 | 130.3 | 24.54 | 24.5877 | -0.047701 | 147.5262 | 22.9 | 24.2361 | -1.3361 |  | 2026-12-03 09:00 | 146.889 | 148.718 | 131.9 | 24.7863 | 24.5877 | 0.19863 | 147.5262 | 23.5 | 24.2361 | -0.7361 |  | 2026-12-03 09:00 | 146.155 | 147.975 | 132.4 | 24.6625 | 24.5877 | 0.074799 | 147.5262 | 23.4 | 24.2361 | -0.8361 |  | 2026-12-03 09:00 | 148.232 | 152.106 | 135.1 | 25.351 | 24.5877 | 0.7633 | 147.5262 | 23.7 | 24.2361 | -0.5361 |  | 2026-12-03 09:00 | 140.11 | 141.818 | 126.9 | 23.6363 | 23.3922 | 0.24418 | 140.3529 | 22.2 | 23.0576 | -0.85764 |  | 2026-12-03 09:00 | 255.9145 | 254.5165 | 1.398 | 1527.0993 | 239 | 250.877 | -11.877
2026-12-03 08:50 | 503 | 47.35 | 178.071 | 181.191 | 146.8 | 30.1985 | 30.1165 | 0.081953 | 180.6993 | 28.6 | 29.6859 | -1.0859 |  | 2026-12-03 08:50 | 177.605 | 179.871 | 145.7 | 29.9785 | 30.1165 | -0.13805 | 180.6993 | 53.7 | 29.6859 | 24.0141 |  | 2026-12-03 08:50 | 175.965 | 179.003 | 144.4 | 29.8338 | 30.1165 | -0.28271 | 180.6993 | 27.9 | 29.6859 | -1.7859 |  | 2026-12-03 08:50 | 178.562 | 180.804 | 146.6 | 30.134 | 30.1165 | 0.017453 | 180.6993 | 28.5 | 29.6859 | -1.1859 |  | 2026-12-03 08:50 | 131.492 | 133.103 | 107.4 | 22.1838 | 22.3086 | -0.12472 | 133.8513 | 21 | 21.9895 | -0.98954 |  | 2026-12-03 08:50 | 132.832 | 134.432 | 108.4 | 22.4053 | 22.3086 | 0.09678 | 133.8513 | 20.9 | 21.9895 | -1.0895 |  | 2026-12-03 08:50 | 132.167 | 133.745 | 109 | 22.2908 | 22.3086 | -0.01772 | 133.8513 | 20.8 | 21.9895 | -1.1895 |  | 2026-12-03 08:50 | 134.109 | 137.764 | 111.4 | 22.9607 | 22.3086 | 0.65211 | 133.8513 | 21.4 | 21.9895 | -0.58954 |  | 2026-12-03 08:50 | 127.123 | 128.68 | 104.7 | 21.4467 | 21.2238 | 0.22284 | 127.343 | 20.3 | 20.9203 | -0.62033 |  | 2026-12-03 08:50 | 231.4322 | 230.9242 | 0.50794 | 1385.5454 | 243.1 | 227.622 | 15.478
2026-12-03 08:40 | 456 | 47.35 | 161.223 | 163.111 | 118.2 | 27.1852 | 27.3025 | -0.11731 | 163.8149 | 25.2 | 26.9121 | -1.7121 | [5 empty] | 0 | 27.3025 | -27.3025 | 163.8149 | 0 | 26.9121 | -26.9121 |  | 2026-12-03 08:40 | 158.216 | 160.808 | 116.5 | 26.8013 | 27.3025 | -0.50114 | 163.8149 | 24.9 | 26.9121 | -2.0121 |  | 2026-12-03 08:40 | 161.061 | 163.034 | 118.1 | 27.1723 | 27.3025 | -0.13014 | 163.8149 | 25.3 | 26.9121 | -1.6121 |  | 2026-12-03 08:40 | 118.234 | 119.622 | 86.4 | 19.937 | 20.2241 | -0.28706 | 121.3443 | 18.5 | 19.9349 | -1.4349 |  | 2026-12-03 08:40 | 120.102 | 121.512 | 87.5 | 20.252 | 20.2241 | 0.027943 | 121.3443 | 18.9 | 19.9349 | -1.0349 |  | 2026-12-03 08:40 | 119.151 | 120.549 | 88.2 | 20.0915 | 20.2241 | -0.13256 | 121.3443 | 19 | 19.9349 | -0.93485 |  | 2026-12-03 08:40 | 121.012 | 124.131 | 90 | 20.6885 | 20.2241 | 0.46444 | 121.3443 | 19.1 | 19.9349 | -0.83485 |  | 2026-12-03 08:40 | 114.875 | 116.223 | 84.4 | 19.3705 | 19.2407 | 0.12981 | 115.4441 | 18.1 | 18.9655 | -0.86554 |  | 2026-12-03 08:40 | 181.4983 | 209.3468 | -27.8485 | 1256.0809 | 169 | 206.3532 | -37.3532
2026-12-03 08:30 | 407 | 45.92 | 141.494 | 143.14 | 93 | 23.8567 | 24.501 | -0.64431 | 147.0058 | 23 | 24.1506 | -1.1506 |  | 2026-12-03 08:30 | 142.587 | 144.275 | 92 | 24.0458 | 24.501 | -0.45514 | 147.0058 | 22.8 | 24.1506 | -1.3506 |  | 2026-12-03 08:30 | 140.61 | 142.786 | 91.6 | 23.7977 | 24.501 | -0.70331 | 147.0058 | 22.2 | 24.1506 | -1.9506 |  | 2026-12-03 08:30 | 143.003 | 144.623 | 92.8 | 24.1038 | 24.501 | -0.39714 | 147.0058 | 22.4 | 24.1506 | -1.7506 |  | 2026-12-03 08:30 | 105.002 | 106.202 | 67.9 | 17.7003 | 18.1489 | -0.44854 | 108.8932 | 16.4 | 17.8893 | -1.4893 |  | 2026-12-03 08:30 | 106.855 | 108.038 | 68.6 | 18.0063 | 18.1489 | -0.14254 | 108.8932 | 16.7 | 17.8893 | -1.1893 |  | 2026-12-03 08:30 | 105.975 | 107.186 | 69.2 | 17.8643 | 18.1489 | -0.28454 | 108.8932 | 16.5 | 17.8893 | -1.3893 |  | 2026-12-03 08:30 | 107.662 | 110.514 | 70.9 | 18.419 | 18.1489 | 0.27013 | 108.8932 | 16.7 | 17.8893 | -1.1893 |  | 2026-12-03 08:30 | 102.068 | 103.255 | 66.3 | 17.2092 | 17.2664 | -0.057234 | 103.5984 | 15.9 | 17.0195 | -1.1195 |  | 2026-12-03 08:30 | 185.0032 | 187.8658 | -2.8626 | 1127.1946 | 172.6 | 185.1793 | -12.5793
2026-12-03 08:20 | 364 | 40.18 | 123.848 | 125.213 | 70 | 20.8688 | 22.3874 | -1.5186 | 134.3245 | 18 | 22.0673 | -4.0673 |  | 2026-12-03 08:20 | 124.317 | 126.141 | 69.2 | 21.0235 | 22.3874 | -1.3639 | 134.3245 | 17.9 | 22.0673 | -4.1673 |  | 2026-12-03 08:20 | 122.896 | 124.55 | 69.4 | 20.7583 | 22.3874 | -1.6291 | 134.3245 | 18.1 | 22.0673 | -3.9673 |  | 2026-12-03 08:20 | 125.691 | 127.128 | 70.4 | 21.188 | 22.3874 | -1.1994 | 134.3245 | 18.8 | 22.0673 | -3.2673 |  | 2026-12-03 08:20 | 91.604 | 92.613 | 51.5 | 15.4355 | 16.5833 | -1.1478 | 99.4996 | 13.6 | 16.3461 | -2.7461 |  | 2026-12-03 08:20 | 93.706 | 94.729 | 51.9 | 15.7882 | 16.5833 | -0.79511 | 99.4996 | 14 | 16.3461 | -2.3461 |  | 2026-12-03 08:20 | 92.884 | 93.927 | 52.7 | 15.6545 | 16.5833 | -0.92877 | 99.4996 | 13.7 | 16.3461 | -2.6461 |  | 2026-12-03 08:20 | 94.541 | 97.124 | 54.2 | 16.1873 | 16.5833 | -0.39594 | 99.4996 | 14.2 | 16.3461 | -2.1461 |  | 2026-12-03 08:20 | 89.856 | 90.846 | 50.4 | 15.141 | 15.7769 | -0.63593 | 94.6616 | 13.5 | 15.5513 | -2.0513 |  | 2026-12-03 08:20 | 162.0452 | 171.6597 | -9.6145 | 1029.9582 | 141.8 | 169.205 | -27.405
2026-12-03 08:10 | 318 | 35.59 | 106.076 | 107.191 | 52 | 17.8652 | 19.8901 | -2.0249 | 119.3404 | 15.5 | 19.6056 | -4.1056 |  | 2026-12-03 08:10 | 108.333 | 109.516 | 51.3 | 18.2527 | 19.8901 | -1.6374 | 119.3404 | 15.8 | 19.6056 | -3.8056 |  | 2026-12-03 08:10 | 106.19 | 107.51 | 51.3 | 17.9183 | 19.8901 | -1.9717 | 119.3404 | 15.5 | 19.6056 | -4.1056 |  | 2026-12-03 08:10 | 108.615 | 109.801 | 51.6 | 18.3002 | 19.8901 | -1.5899 | 119.3404 | 15.6 | 19.6056 | -4.0056 |  | 2026-12-03 08:10 | 79.05 | 79.953 | 37.9 | 13.3255 | 14.7334 | -1.4079 | 88.4003 | 11.4 | 14.5227 | -3.1227 |  | 2026-12-03 08:10 | 81.181 | 82.084 | 37.9 | 13.6807 | 14.7334 | -1.0527 | 88.4003 | 11.7 | 14.5227 | -2.8227 |  | 2026-12-03 08:10 | 80.66 | 81.582 | 39 | 13.597 | 14.7334 | -1.1364 | 88.4003 | 11.7 | 14.5227 | -2.8227 |  | 2026-12-03 08:10 | 81.927 | 84.098 | 40 | 14.0163 | 14.7334 | -0.71705 | 88.4003 | 11.7 | 14.5227 | -2.8227 |  | 2026-12-03 08:10 | 77.785 | 78.674 | 36.9 | 13.1123 | 14.017 | -0.90466 | 84.102 | 11.2 | 13.8165 | -2.6165 |  | 2026-12-03 08:10 | 140.0682 | 152.5108 | -12.4427 | 915.065 | 120.1 | 150.3299 | -30.2299
2026-12-03 08:00 | 262 | 30.14 | 87.416 | 88.317 | 36.5 | 14.7195 | 16.712 | -1.9925 | 100.2722 | 11.3 | 16.4731 | -5.1731 |  | 2026-12-03 08:00 | 87.739 | 88.67 | 35.5 | 14.7783 | 16.712 | -1.9337 | 100.2722 | 11.6 | 16.4731 | -4.8731 |  | 2026-12-03 08:00 | 86.489 | 87.407 | 35.8 | 14.5678 | 16.712 | -2.1442 | 100.2722 | 11.2 | 16.4731 | -5.2731 |  | 2026-12-03 08:00 | 87.098 | 88.031 | 36 | 14.6718 | 16.712 | -2.0402 | 100.2722 | 11.7 | 16.4731 | -4.7731 |  | 2026-12-03 08:00 | 62.373 | 63.118 | 26.5 | 10.5197 | 12.3793 | -1.8596 | 74.2757 | 8.5 | 12.2023 | -3.7023 |  | 2026-12-03 08:00 | 64.648 | 65.393 | 26.2 | 10.8988 | 12.3793 | -1.4805 | 74.2757 | 8.5 | 12.2023 | -3.7023 |  | 2026-12-03 08:00 | 63.727 | 64.488 | 27.3 | 10.748 | 12.3793 | -1.6313 | 74.2757 | 8.8 | 12.2023 | -3.4023 |  | 2026-12-03 08:00 | 64.857 | 66.622 | 28.3 | 11.1037 | 12.3793 | -1.2756 | 74.2757 | 9 | 12.2023 | -3.2023 |  | 2026-12-03 08:00 | 63.541 | 64.3 | 25.7 | 10.7167 | 11.7774 | -1.0607 | 70.6642 | 8.5 | 11.6089 | -3.1089 |  | 2026-12-03 08:00 | 112.7243 | 128.1427 | -15.4183 | 768.8561 | 89.1 | 126.3102 | -37.2102
2026-12-03 07:50 | 234 | 25.26 | 72.083 | 72.863 | 25.2 | 12.1438 | 15.1856 | -3.0418 | 91.1138 | 10.4 | 14.9685 | -4.5685 |  | 2026-12-03 07:50 | 69.427 | 72.417 | 23.9 | 12.0695 | 15.1856 | -3.1161 | 91.1138 | 10.1 | 14.9685 | -4.8685 |  | 2026-12-03 07:50 | 72.01 | 72.796 | 24.6 | 12.1327 | 15.1856 | -3.053 | 91.1138 | 10.1 | 14.9685 | -4.8685 |  | 2026-12-03 07:50 | 73.786 | 74.455 | 24.3 | 12.4092 | 15.1856 | -2.7765 | 91.1138 | 10.3 | 14.9685 | -4.6685 |  | 2026-12-03 07:50 | 53.409 | 54.091 | 18 | 9.0152 | 11.2486 | -2.2334 | 67.4917 | 7.4 | 11.0878 | -3.6878 |  | 2026-12-03 07:50 | 51.653 | 52.312 | 17.7 | 8.7187 | 11.2486 | -2.5299 | 67.4917 | 7.4 | 11.0878 | -3.6878 |  | 2026-12-03 07:50 | 54.356 | 55.044 | 18.5 | 9.174 | 11.2486 | -2.0746 | 67.4917 | 7.6 | 11.0878 | -3.4878 |  | 2026-12-03 07:50 | 55.627 | 57.421 | 19.3 | 9.5702 | 11.2486 | -1.6784 | 67.4917 | 7.9 | 11.0878 | -3.1878 |  | 2026-12-03 07:50 | 52.938 | 53.624 | 17.2 | 8.9373 | 10.7017 | -1.7643 | 64.21 | 7.4 | 10.5486 | -3.1486 |  | 2026-12-03 07:50 | 94.1705 | 116.4386 | -22.2681 | 698.6317 | 78.6 | 114.7736 | -36.1736
2026-12-03 07:40 | 178 | 20.38 | 52.809 | 53.467 | 14.8 | 8.9112 | 11.7489 | -2.8378 | 70.4936 | 7 | 11.5809 | -4.5809 |  | 2026-12-03 07:40 | 51.501 | 52.153 | 13.8 | 8.6922 | 11.7489 | -3.0568 | 70.4936 | 6.9 | 11.5809 | -4.6809 |  | 2026-12-03 07:40 | 52.045 | 52.728 | 14.5 | 8.788 | 11.7489 | -2.9609 | 70.4936 | 7.1 | 11.5809 | -4.4809 |  | 2026-12-03 07:40 | 52.722 | 53.379 | 14 | 8.8965 | 11.7489 | -2.8524 | 70.4936 | 7.1 | 11.5809 | -4.4809 |  | 2026-12-03 07:40 | 38.439 | 39.005 | 10.6 | 6.5008 | 8.7029 | -2.2021 | 52.2175 | 5.2 | 8.5785 | -3.3785 |  | 2026-12-03 07:40 | 38.125 | 38.674 | 10.3 | 6.4457 | 8.7029 | -2.2573 | 52.2175 | 5.2 | 8.5785 | -3.3785 |  | 2026-12-03 07:40 | 40.008 | 40.58 | 10.9 | 6.7633 | 8.7029 | -1.9396 | 52.2175 | 5.5 | 8.5785 | -3.0785 |  | 2026-12-03 07:40 | 40.79 | 41.858 | 11.4 | 6.9763 | 8.7029 | -1.7266 | 52.2175 | 5.5 | 8.5785 | -3.0785 |  | 2026-12-03 07:40 | 38.574 | 39.142 | 9.8 | 6.5237 | 8.2797 | -1.7561 | 49.6785 | 5.1 | 8.1613 | -3.0613 |  | 2026-12-03 07:40 | 68.4977 | 90.0872 | -21.5895 | 540.523 | 54.6 | 88.7989 | -34.1989
2026-12-03 07:30 | 126 | 18.66 | 34.852 | 35.368 | 7.8 | 5.8947 | 8.3659 | -2.4713 | 50.1956 | 4.6 | 8.2463 | -3.6463 |  | 2026-12-03 07:30 | 32.925 | 33.501 | 6.9 | 5.5835 | 8.3659 | -2.7824 | 50.1956 | 4.2 | 8.2463 | -4.0463 |  | 2026-12-03 07:30 | 33.679 | 34.199 | 7.4 | 5.6998 | 8.3659 | -2.6661 | 50.1956 | 4.3 | 8.2463 | -3.9463 |  | 2026-12-03 07:30 | 33.15 | 33.668 | 6.9 | 5.6113 | 8.3659 | -2.7546 | 50.1956 | 4.1 | 8.2463 | -4.1463 |  | 2026-12-03 07:30 | 24.685 | 25.282 | 5.4 | 4.2137 | 6.197 | -1.9833 | 37.1819 | 3.2 | 6.1084 | -2.9084 |  | 2026-12-03 07:30 | 24.789 | 25.238 | 5.1 | 4.2063 | 6.197 | -1.9907 | 37.1819 | 3.2 | 6.1084 | -2.9084 |  | 2026-12-03 07:30 | 25.91 | 26.372 | 5.4 | 4.3953 | 6.197 | -1.8017 | 37.1819 | 3.3 | 6.1084 | -2.8084 |  | 2026-12-03 07:30 | 26.778 | 27.719 | 5.9 | 4.6198 | 6.197 | -1.5772 | 37.1819 | 3.5 | 6.1084 | -2.6084 |  | 2026-12-03 07:30 | 23.818 | 24.272 | 4.7 | 4.0453 | 5.8957 | -1.8503 | 35.374 | 3 | 5.8114 | -2.8114 |  | 2026-12-03 07:30 | 44.2698 | 64.1474 | -19.8775 | 384.8841 | 33.4 | 63.23 | -29.83
2026-12-03 07:20 | 26 | 17.22 | 19.147 | 19.546 | 3.2 | 3.2577 | 1.7348 | 1.5229 | 10.4089 | 2.3 | 1.71 | 0.58999 |  | 2026-12-03 07:20 | 15.34 | 16.225 | 2.7 | 2.7042 | 1.7348 | 0.96935 | 10.4089 | 1.8 | 1.71 | 0.089992 |  | 2026-12-03 07:20 | 18.781 | 19.186 | 3.1 | 3.1977 | 1.7348 | 1.4629 | 10.4089 | 2.2 | 1.71 | 0.48999 |  | 2026-12-03 07:20 | 17.157 | 17.92 | 2.8 | 2.9867 | 1.7348 | 1.2519 | 10.4089 | 2 | 1.71 | 0.28999 |  | 2026-12-03 07:20 | 13.615 | 14.329 | 2.2 | 2.3882 | 1.285 | 1.1031 | 7.7103 | 1.6 | 1.2667 | 0.33333 |  | 2026-12-03 07:20 | 13.539 | 13.898 | 1.9 | 2.3163 | 1.285 | 1.0313 | 7.7103 | 1.6 | 1.2667 | 0.33333 |  | 2026-12-03 07:20 | 14.497 | 14.858 | 2.1 | 2.4763 | 1.285 | 1.1913 | 7.7103 | 1.7 | 1.2667 | 0.43333 |  | 2026-12-03 07:20 | 15.019 | 15.807 | 2.4 | 2.6345 | 1.285 | 1.3495 | 7.7103 | 1.8 | 1.2667 | 0.53333 |  | 2026-12-03 07:20 | 12.072 | 12.426 | 1.7 | 2.071 | 1.2226 | 0.84844 | 7.3354 | 1.4 | 1.2051 | 0.19492 |  | 2026-12-03 07:20 | 24.0325 | 13.302 | 10.7305 | 79.8121 | 16.4 | 13.1118 | 3.2882
2026-12-03 07:10 | 13 | 16.65 | 6.179 | 6.432 | 0.9 | 1.072 | 0.86909 | 0.20291 | 5.2146 | 0.7 | 0.85666 | -0.15666 |  | 2026-12-03 07:10 | 5.461 | 6.037 | 0.9 | 1.0062 | 0.86909 | 0.13707 | 5.2146 | 0.7 | 0.85666 | -0.15666 |  | 2026-12-03 07:10 | 6.359 | 6.618 | 0.9 | 1.103 | 0.86909 | 0.23391 | 5.2146 | 0.7 | 0.85666 | -0.15666 |  | 2026-12-03 07:10 | 5.994 | 6.774 | 0.8 | 1.129 | 0.86909 | 0.25991 | 5.2146 | 0.6 | 0.85666 | -0.25666 |  | 2026-12-03 07:10 | 4.642 | 5.168 | 0.6 | 0.86133 | 0.64377 | 0.21756 | 3.8626 | 0.5 | 0.63457 | -0.13457 |  | 2026-12-03 07:10 | 4.525 | 4.725 | 0.3 | 0.7875 | 0.64377 | 0.14373 | 3.8626 | 0.3 | 0.63457 | -0.33457 |  | 2026-12-03 07:10 | 4.843 | 5.058 | 0.4 | 0.843 | 0.64377 | 0.19923 | 3.8626 | 0.4 | 0.63457 | -0.23457 |  | 2026-12-03 07:10 | 4.935 | 5.29 | 0.6 | 0.88167 | 0.64377 | 0.23789 | 3.8626 | 0.5 | 0.63457 | -0.13457 |  | 2026-12-03 07:10 | 4.266 | 4.459 | 0.3 | 0.74317 | 0.61247 | 0.1307 | 3.6748 | 0.3 | 0.60371 | -0.30371 |  | 2026-12-03 07:10 | 8.4268 | 6.6639 | 1.7629 | 39.9836 | 4.7 | 6.5686 | -1.8686
2026-12-03 07:00 | 5 | 17.79 | 2.54 | 2.668 | 0.2 | 0.44467 | 0.33297 | 0.1117 | 1.9978 | 0.2 | 0.32821 | -0.12821 |  | 2026-12-03 07:00 | 2.452 | 2.908 | 0.2 | 0.48467 | 0.33297 | 0.1517 | 1.9978 | 0.2 | 0.32821 | -0.12821 |  | 2026-12-03 07:00 | 2.529 | 2.658 | 0.2 | 0.443 | 0.33297 | 0.11003 | 1.9978 | 0.2 | 0.32821 | -0.12821 |  | 2026-12-03 07:00 | 2.548 | 3.334 | 0.2 | 0.55567 | 0.33297 | 0.2227 | 1.9978 | 0.2 | 0.32821 | -0.12821 |  | 2026-12-03 07:00 | 1.737 | 2.124 | 0.1 | 0.354 | 0.24664 | 0.10736 | 1.4799 | 0.1 | 0.24312 | -0.14312 |  | 2026-12-03 07:00 | 0 | 0 | 0 | 0 | 0.24664 | -0.24664 | 1.4799 | 0 | 0.24312 | -0.24312 |  | 2026-12-03 07:00 | 0 | 0 | 0 | 0 | 0.24664 | -0.24664 | 1.4799 | 0 | 0.24312 | -0.24312 |  | 2026-12-03 07:00 | 1.802 | 2.114 | 0.1 | 0.35233 | 0.24664 | 0.10569 | 1.4799 | 0.1 | 0.24312 | -0.14312 |  | 2026-12-03 07:00 | 0 | 0 | 0 | 0 | 0.23465 | -0.23465 | 1.4079 | 0 | 0.2313 | -0.2313 |  | 2026-12-03 07:00 | 2.6343 | 2.5531 | 0.08122 | 15.3187 | 1 | 2.5166 | -1.5166
[110 empty] | Total: - | 19274.5385 | 19961.4019 | -686.8634 |  | 18915.5 | 19675.9538 | -760.4538
Sum:- | 43614 |  | 15019.687 |  | 93969.9 |  |  |  |  | 2458 | 2566.0876 | -108.0876 | 0.98348 |  | 14343.108 |  | 91945 |  |  |  |  | 2476.5 | 2566.0876 | -89.5876 | 0.98275 |  | 14756.935 |  | 93119 |  |  |  |  | 2440.9 | 2566.0876 | -125.1876 | 0.97314 |  | 14788.904 |  | 93719.3 |  |  |  |  | 2452.4 | 2566.0876 | -113.6876 | 0.98465 |  | 11113.538 |  | 70490.2 |  |  |  |  | 1849.1 | 1900.8056 | -51.7056 | 0.98487 |  | 11003.036 |  | 69955 |  |  |  |  | 1828.7 | 1900.8056 | -72.1056 | 0.98099 |  | 10996.942 |  | 70017.7 |  |  |  |  | 1830.7 | 1900.8056 | -70.1056 | 0.98056 |  | 11074.826 |  | 70545.2 |  |  |  |  | 1839.9 | 1900.8056 | -60.9056 | 0.97163 |  | 10490.454 |  | 66651.1 |  |  |  |  | 1739.3 | 1808.3811 | -69.0811 | 0.98407
Formulas:
Time = [Time]

## 13 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
13-03-2026 19:00 | 0 | 37.88 | 0 | 0 | 2385.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 2411.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 2374.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 2387.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 1787.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 1767.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 1770.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 1785.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 1687.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13-03-2026 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 98.38%
13-03-2026 18:50 | 0 | 39.03 | 0.476 | 0.5 | 2385.1 | 0.083333 | 0 | 0.083333 | 0 | 0.3 | 0 | 0.3 |  | 13-03-2026 18:50 | 0.858 | 1.165 | 2411.9 | 0.19417 | 0 | 0.19417 | 0 | 0.3 | 0 | 0.3 |  | 13-03-2026 18:50 | 0.453 | 0.476 | 2374.3 | 0.079333 | 0 | 0.079333 | 0 | 0.3 | 0 | 0.3 |  | 13-03-2026 18:50 | 0.472 | 0.946 | 2387.6 | 0.15767 | 0 | 0.15767 | 0 | 0.3 | 0 | 0.3 |  | 13-03-2026 18:50 | 0.184 | 0.432 | 1787.4 | 0.072 | 0 | 0.072 | 0 | 0.1 | 0 | 0.1 |  | 13-03-2026 18:50 | 0.175 | 0.184 | 1767.9 | 0.030667 | 0 | 0.030667 | 0 | 0.2 | 0 | 0.2 |  | 13-03-2026 18:50 | 0.072 | 0.076 | 1770.7 | 0.012667 | 0 | 0.012667 | 0 | 0.2 | 0 | 0.2 |  | 13-03-2026 18:50 | 0.263 | 0.598 | 1785.3 | 0.099667 | 0 | 0.099667 | 0 | 0.2 | 0 | 0.2 |  | 13-03-2026 18:50 | 0.127 | 0.134 | 1687.5 | 0.022333 | 0 | 0.022333 | 0 | 0.2 | 0 | 0.2 |  | 13-03-2026 18:50 | 0.75183 | 0 | 0.75183 | 0 | 2.1 | 0 | 2.1 | 2 | 97.93%
13-03-2026 18:40 | 4 | 41.04 | 2.808 | 3.022 | 2384.8 | 0.50367 | 0.24523 | 0.25843 | 1.4714 | 0.7 | 0.24173 | 0.45827 |  | 13-03-2026 18:40 | 2.943 | 3.377 | 2411.6 | 0.56283 | 0.24523 | 0.3176 | 1.4714 | 0.8 | 0.24173 | 0.55827 |  | 13-03-2026 18:40 | 2.571 | 2.703 | 2374 | 0.4505 | 0.24523 | 0.20527 | 1.4714 | 0.8 | 0.24173 | 0.55827 |  | 13-03-2026 18:40 | 2.748 | 3.193 | 2387.3 | 0.53217 | 0.24523 | 0.28693 | 1.4714 | 0.8 | 0.24173 | 0.55827 |  | 13-03-2026 18:40 | 1.87 | 2.05 | 1787.3 | 0.34167 | 0.18165 | 0.16001 | 1.0899 | 0.6 | 0.17906 | 0.42094 |  | 13-03-2026 18:40 | 1.853 | 1.948 | 1767.7 | 0.32467 | 0.18165 | 0.14301 | 1.0899 | 0.5 | 0.17906 | 0.32094 |  | 13-03-2026 18:40 | 1.826 | 1.92 | 1770.5 | 0.32 | 0.18165 | 0.13835 | 1.0899 | 0.5 | 0.17906 | 0.32094 |  | 13-03-2026 18:40 | 1.895 | 2.268 | 1785.1 | 0.378 | 0.18165 | 0.19635 | 1.0899 | 0.6 | 0.17906 | 0.42094 |  | 13-03-2026 18:40 | 1.734 | 1.823 | 1687.3 | 0.30383 | 0.17282 | 0.13101 | 1.0369 | 0.5 | 0.17035 | 0.32965 |  | 13-03-2026 18:40 | 3.7173 | 1.8804 | 1.837 | 11.2822 | 5.8 | 1.8535 | 3.9465 | 3 | 97.3%
13-03-2026 18:30 | 17 | 42.19 | 7.034 | 7.187 | 2384.1 | 1.1978 | 1.0378 | 0.16004 | 6.2268 | 1.7 | 1.023 | 0.67704 |  | 13-03-2026 18:30 | 0 | 7.818 | 2410.8 | 1.303 | 1.0378 | 0.2652 | 6.2268 | 4.7 | 1.023 | 3.677 |  | 13-03-2026 18:30 | 7.003 | 7.318 | 2373.2 | 1.2197 | 1.0378 | 0.18187 | 6.2268 | 1.6 | 1.023 | 0.57704 |  | 13-03-2026 18:30 | 7.105 | 7.477 | 2386.5 | 1.2462 | 1.0378 | 0.20837 | 6.2268 | 1.6 | 1.023 | 0.57704 |  | 13-03-2026 18:30 | 5.094 | 5.342 | 1786.7 | 0.89033 | 0.76874 | 0.12159 | 4.6124 | 1.2 | 0.75775 | 0.44225 |  | 13-03-2026 18:30 | 4.99 | 5.212 | 1767.2 | 0.86867 | 0.76874 | 0.099927 | 4.6124 | 1.2 | 0.75775 | 0.44225 |  | 13-03-2026 18:30 | 4.961 | 5.203 | 1770 | 0.86717 | 0.76874 | 0.098427 | 4.6124 | 1.2 | 0.75775 | 0.44225 |  | 13-03-2026 18:30 | 4.939 | 5.366 | 1784.5 | 0.89433 | 0.76874 | 0.12559 | 4.6124 | 1.1 | 0.75775 | 0.34225 |  | 13-03-2026 18:30 | 4.645 | 4.875 | 1686.8 | 0.8125 | 0.73136 | 0.08114 | 4.3882 | 1.1 | 0.7209 | 0.3791 |  | 13-03-2026 18:30 | 9.2997 | 7.9575 | 1.3422 | 47.7451 | 15.4 | 7.8437 | 7.5563 | 4 | 98.34%
13-03-2026 18:20 | 32 | 43.91 | 12.975 | 13.407 | 2382.4 | 2.2345 | 1.941 | 0.29351 | 11.6459 | 2.8 | 1.9132 | 0.88677 | [5 empty] | 0 | 1.941 | -1.941 | 11.6459 | 0 | 1.9132 | -1.9132 |  | 13-03-2026 18:20 | 13.182 | 13.614 | 2371.6 | 2.269 | 1.941 | 0.32801 | 11.6459 | 2.9 | 1.9132 | 0.98677 |  | 13-03-2026 18:20 | 13.272 | 13.705 | 2384.9 | 2.2842 | 1.941 | 0.34318 | 11.6459 | 2.9 | 1.9132 | 0.98677 |  | 13-03-2026 18:20 | 9.624 | 9.999 | 1785.5 | 1.6665 | 1.4378 | 0.22873 | 8.6266 | 2.1 | 1.4172 | 0.68279 |  | 13-03-2026 18:20 | 9.433 | 9.801 | 1766 | 1.6335 | 1.4378 | 0.19573 | 8.6266 | 2 | 1.4172 | 0.58279 |  | 13-03-2026 18:20 | 9.484 | 9.854 | 1768.8 | 1.6423 | 1.4378 | 0.20456 | 8.6266 | 2.1 | 1.4172 | 0.68279 |  | 13-03-2026 18:20 | 9.036 | 9.772 | 1783.4 | 1.6287 | 1.4378 | 0.1909 | 8.6266 | 1.9 | 1.4172 | 0.48279 |  | 13-03-2026 18:20 | 8.73 | 9.081 | 1685.7 | 1.5135 | 1.3679 | 0.14564 | 8.2072 | 1.9 | 1.3483 | 0.5517 |  | 13-03-2026 18:20 | 14.8722 | 14.8829 | -0.010728 | 89.2974 | 18.6 | 14.6701 | 3.9299 | 5 | 98.45%
13-03-2026 18:10 | 50 | 45.92 | 21.498 | 21.878 | 2379.6 | 3.6463 | 3.0099 | 0.63639 | 18.0597 | 4.4 | 2.9669 | 1.4331 |  | 13-03-2026 18:10 | 23.165 | 23.71 | 2406.1 | 3.9517 | 3.0099 | 0.94172 | 18.0597 | 4.4 | 2.9669 | 1.4331 |  | 13-03-2026 18:10 | 21.631 | 22.149 | 2368.7 | 3.6915 | 3.0099 | 0.68155 | 18.0597 | 4.4 | 2.9669 | 1.4331 |  | 13-03-2026 18:10 | 21.575 | 22.096 | 2382 | 3.6827 | 3.0099 | 0.67272 | 18.0597 | 4.4 | 2.9669 | 1.4331 |  | 13-03-2026 18:10 | 16.008 | 16.439 | 1783.4 | 2.7398 | 2.2296 | 0.51024 | 13.3775 | 3.3 | 2.1977 | 1.1023 |  | 13-03-2026 18:10 | 15.613 | 15.914 | 1764 | 2.6523 | 2.2296 | 0.42274 | 13.3775 | 3.3 | 2.1977 | 1.1023 |  | 13-03-2026 18:10 | 15.594 | 16.02 | 1766.7 | 2.67 | 2.2296 | 0.44041 | 13.3775 | 3.2 | 2.1977 | 1.0023 |  | 13-03-2026 18:10 | 14.238 | 15.077 | 1781.5 | 2.5128 | 2.2296 | 0.28324 | 13.3775 | 3 | 2.1977 | 0.80229 |  | 13-03-2026 18:10 | 14.321 | 14.756 | 1683.8 | 2.4593 | 2.1212 | 0.33815 | 12.7271 | 3 | 2.0908 | 0.90915 |  | 13-03-2026 18:10 | 28.0065 | 23.0793 | 4.9272 | 138.476 | 33.4 | 22.7493 | 10.6507 | 6 | 98.15%
13-03-2026 18:00 | 69 | 47.35 | 31.587 | 32.202 | 2375.2 | 5.367 | 4.1313 | 1.2357 | 24.7878 | 6.1 | 4.0722 | 2.0278 |  | 13-03-2026 18:00 | 32.372 | 32.982 | 2401.7 | 5.497 | 4.1313 | 1.3657 | 24.7878 | 6.4 | 4.0722 | 2.3278 |  | 13-03-2026 18:00 | 32.027 | 32.651 | 2364.3 | 5.4418 | 4.1313 | 1.3105 | 24.7878 | 6.3 | 4.0722 | 2.2278 |  | 13-03-2026 18:00 | 31.915 | 32.52 | 2377.6 | 5.42 | 4.1313 | 1.2887 | 24.7878 | 6.3 | 4.0722 | 2.2278 |  | 13-03-2026 18:00 | 23.746 | 24.288 | 1780.1 | 4.048 | 3.0602 | 0.98778 | 18.3613 | 4.7 | 3.0165 | 1.6835 |  | 13-03-2026 18:00 | 23.246 | 23.779 | 1760.7 | 3.9632 | 3.0602 | 0.90295 | 18.3613 | 4.5 | 3.0165 | 1.4835 |  | 13-03-2026 18:00 | 23.249 | 23.782 | 1763.5 | 3.9637 | 3.0602 | 0.90345 | 18.3613 | 4.5 | 3.0165 | 1.4835 |  | 13-03-2026 18:00 | 21.987 | 22.928 | 1778.5 | 3.8213 | 3.0602 | 0.76111 | 18.3613 | 4.4 | 3.0165 | 1.3835 |  | 13-03-2026 18:00 | 21.759 | 22.269 | 1680.8 | 3.7115 | 2.9114 | 0.80008 | 17.4685 | 4.2 | 2.8698 | 1.3302 |  | 13-03-2026 18:00 | 41.2335 | 31.6775 | 9.556 | 190.0649 | 47.4 | 31.2245 | 16.1755 | 7 | 97.97%
13-03-2026 17:50 | 127 | 47.93 | 43.084 | 43.813 | 2369.1 | 7.3022 | 7.5872 | -0.28507 | 45.5234 | 8.5 | 7.4787 | 1.0213 |  | 13-03-2026 17:50 | 44.415 | 45.165 | 2395.3 | 7.5275 | 7.5872 | -0.059733 | 45.5234 | 8.4 | 7.4787 | 0.92126 |  | 13-03-2026 17:50 | 43.915 | 44.652 | 2358 | 7.442 | 7.5872 | -0.14523 | 45.5234 | 8.5 | 7.4787 | 1.0213 |  | 13-03-2026 17:50 | 43.417 | 44.154 | 2371.3 | 7.359 | 7.5872 | -0.22823 | 45.5234 | 8.3 | 7.4787 | 0.82126 |  | 13-03-2026 17:50 | 32.759 | 33.356 | 1775.4 | 5.5593 | 5.6202 | -0.060839 | 33.721 | 6.4 | 5.5398 | 0.8602 |  | 13-03-2026 17:50 | 31.747 | 32.339 | 1756.2 | 5.3898 | 5.6202 | -0.23034 | 33.721 | 6.2 | 5.5398 | 0.6602 |  | 13-03-2026 17:50 | 31.826 | 32.409 | 1759 | 5.4015 | 5.6202 | -0.21867 | 33.721 | 6.3 | 5.5398 | 0.7602 |  | 13-03-2026 17:50 | 31.585 | 32.372 | 1774.1 | 5.3953 | 5.6202 | -0.22484 | 33.721 | 6.2 | 5.5398 | 0.6602 |  | 13-03-2026 17:50 | 29.813 | 30.387 | 1676.6 | 5.0645 | 5.3469 | -0.2824 | 32.0814 | 5.8 | 5.2704 | 0.52956 |  | 13-03-2026 17:50 | 56.4412 | 58.1765 | -1.7354 | 349.0591 | 64.6 | 57.3446 | 7.2554 | 8 | 97.12%
13-03-2026 17:40 | 171 | 47.93 | 57.059 | 57.893 | 2360.6 | 9.6488 | 10.2159 | -0.56705 | 61.2953 | 10.7 | 10.0698 | 0.63021 |  | 13-03-2026 17:40 | 58.025 | 58.897 | 2386.9 | 9.8162 | 10.2159 | -0.39971 | 61.2953 | 24.8 | 10.0698 | 14.7302 |  | 13-03-2026 17:40 | 57.629 | 58.483 | 2349.5 | 9.7472 | 10.2159 | -0.46871 | 61.2953 | 10.9 | 10.0698 | 0.83021 |  | 13-03-2026 17:40 | 57.069 | 57.926 | 2363 | 9.6543 | 10.2159 | -0.56155 | 61.2953 | 10.9 | 10.0698 | 0.83021 |  | 13-03-2026 17:40 | 43.163 | 43.892 | 1769 | 7.3153 | 7.5673 | -0.25199 | 45.4039 | 8 | 7.4591 | 0.54089 |  | 13-03-2026 17:40 | 41.944 | 42.648 | 1750 | 7.108 | 7.5673 | -0.45932 | 45.4039 | 7.8 | 7.4591 | 0.34089 |  | 13-03-2026 17:40 | 42.097 | 42.816 | 1752.7 | 7.136 | 7.5673 | -0.43132 | 45.4039 | 8 | 7.4591 | 0.54089 |  | 13-03-2026 17:40 | 41.704 | 42.698 | 1767.9 | 7.1163 | 7.5673 | -0.45099 | 45.4039 | 7.9 | 7.4591 | 0.44089 |  | 13-03-2026 17:40 | 39.329 | 40.009 | 1670.8 | 6.6682 | 7.1994 | -0.5312 | 43.1962 | 7.5 | 7.0964 | 0.40358 |  | 13-03-2026 17:40 | 74.2103 | 78.3322 | -4.1218 | 469.993 | 96.5 | 77.212 | 19.288 | 9 | 98.44%
13-03-2026 17:30 | 217 | 47.93 | 72.533 | 73.521 | 2349.9 | 12.2535 | 12.964 | -0.71051 | 77.7841 | 13.5 | 12.7786 | 0.72137 | [5 empty] | 0 | 12.964 | -12.964 | 77.7841 | 0 | 12.7786 | -12.7786 |  | 13-03-2026 17:30 | 73.302 | 74.442 | 2338.6 | 12.407 | 12.964 | -0.55701 | 77.7841 | 13.6 | 12.7786 | 0.82137 |  | 13-03-2026 17:30 | 72.905 | 73.88 | 2352.1 | 12.3133 | 12.964 | -0.65068 | 77.7841 | 13.5 | 12.7786 | 0.72137 |  | 13-03-2026 17:30 | 54.508 | 55.332 | 1761 | 9.222 | 9.603 | -0.38097 | 57.6178 | 10.1 | 9.4656 | 0.63435 |  | 13-03-2026 17:30 | 52.839 | 53.638 | 1742.2 | 8.9397 | 9.603 | -0.66331 | 57.6178 | 9.9 | 9.4656 | 0.43435 |  | 13-03-2026 17:30 | 53.692 | 54.515 | 1744.7 | 9.0858 | 9.603 | -0.51714 | 57.6178 | 9.8 | 9.4656 | 0.33435 |  | 13-03-2026 17:30 | 53.262 | 54.874 | 1760 | 9.1457 | 9.603 | -0.45731 | 57.6178 | 9.8 | 9.4656 | 0.33435 |  | 13-03-2026 17:30 | 50.338 | 51.165 | 1663.3 | 8.5275 | 9.136 | -0.60854 | 54.8162 | 9.2 | 9.0054 | 0.19461 |  | 13-03-2026 17:30 | 81.8945 | 99.404 | -17.5095 | 596.4239 | 89.4 | 97.9825 | -8.5825
13-03-2026 17:20 | 265 | 47.93 | 89.053 | 90.171 | 2336.4 | 15.0285 | 15.8316 | -0.80313 | 94.9898 | 16.9 | 15.6052 | 1.2948 |  | 13-03-2026 17:20 | 90.791 | 91.94 | 2362.1 | 15.3233 | 15.8316 | -0.50829 | 94.9898 | 16.7 | 15.6052 | 1.0948 |  | 13-03-2026 17:20 | 89.982 | 91.524 | 2325 | 15.254 | 15.8316 | -0.57763 | 94.9898 | 16.4 | 15.6052 | 0.79476 |  | 13-03-2026 17:20 | 89.714 | 90.859 | 2338.6 | 15.1432 | 15.8316 | -0.68846 | 94.9898 | 16.3 | 15.6052 | 0.69476 |  | 13-03-2026 17:20 | 67.07 | 68.002 | 1750.9 | 11.3337 | 11.7271 | -0.39347 | 70.3628 | 12.2 | 11.5594 | 0.64057 |  | 13-03-2026 17:20 | 65.744 | 66.637 | 1732.3 | 11.1062 | 11.7271 | -0.62097 | 70.3628 | 11.9 | 11.5594 | 0.34057 |  | 13-03-2026 17:20 | 65.29 | 66.19 | 1734.9 | 11.0317 | 11.7271 | -0.69547 | 70.3628 | 11.9 | 11.5594 | 0.34057 |  | 13-03-2026 17:20 | 65.657 | 67.518 | 1750.2 | 11.253 | 11.7271 | -0.47413 | 70.3628 | 12 | 11.5594 | 0.44057 |  | 13-03-2026 17:20 | 61.988 | 62.868 | 1654.1 | 10.478 | 11.1569 | -0.67891 | 66.9415 | 11.4 | 10.9974 | 0.40263 |  | 13-03-2026 17:20 | 115.9515 | 121.392 | -5.4405 | 728.3517 | 125.7 | 119.656 | 6.044
13-03-2026 17:10 | 309 | 47.93 | 105.602 | 106.917 | 2319.5 | 17.8195 | 18.4603 | -0.64078 | 110.7617 | 17.8 | 18.1963 | -0.39629 |  | 13-03-2026 17:10 | 107.015 | 108.392 | 2345.4 | 18.0653 | 18.4603 | -0.39494 | 110.7617 | 18.7 | 18.1963 | 0.50371 |  | 13-03-2026 17:10 | 105.801 | 107.773 | 2308.6 | 17.9622 | 18.4603 | -0.49811 | 110.7617 | 18.7 | 18.1963 | 0.50371 |  | 13-03-2026 17:10 | 105.548 | 106.895 | 2322.3 | 17.8158 | 18.4603 | -0.64444 | 110.7617 | 18.9 | 18.1963 | 0.70371 |  | 13-03-2026 17:10 | 78.893 | 79.948 | 1738.7 | 13.3247 | 13.6743 | -0.34961 | 82.0457 | 14.2 | 13.4787 | 0.72126 |  | 13-03-2026 17:10 | 77.02 | 78.042 | 1720.4 | 13.007 | 13.6743 | -0.66728 | 82.0457 | 13.8 | 13.4787 | 0.32126 |  | 13-03-2026 17:10 | 77.449 | 78.477 | 1723 | 13.0795 | 13.6743 | -0.59478 | 82.0457 | 13.9 | 13.4787 | 0.42126 |  | 13-03-2026 17:10 | 77.384 | 79.429 | 1738.2 | 13.2382 | 13.6743 | -0.43611 | 82.0457 | 13.9 | 13.4787 | 0.42126 |  | 13-03-2026 17:10 | 73.159 | 74.16 | 1642.7 | 12.36 | 13.0094 | -0.64938 | 78.0563 | 13 | 12.8233 | 0.17665 |  | 13-03-2026 17:10 | 136.6722 | 141.5476 | -4.8754 | 849.2856 | 142.9 | 139.5235 | 3.3765
13-03-2026 17:00 | 350 | 48.22 | 119.763 | 121.328 | 2301.7 | 20.2213 | 20.8866 | -0.66529 | 125.3197 | 21.6 | 20.5879 | 1.0121 |  | 13-03-2026 17:00 | 122.009 | 123.151 | 2326.7 | 20.5252 | 20.8866 | -0.36146 | 125.3197 | 22.2 | 20.5879 | 1.6121 |  | 13-03-2026 17:00 | 120.772 | 122.982 | 2289.9 | 20.497 | 20.8866 | -0.38962 | 125.3197 | 21.4 | 20.5879 | 0.81206 |  | 13-03-2026 17:00 | 120.42 | 121.981 | 2303.4 | 20.3302 | 20.8866 | -0.55646 | 125.3197 | 21.1 | 20.5879 | 0.51206 |  | 13-03-2026 17:00 | 90.382 | 91.545 | 1724.5 | 15.2575 | 15.4716 | -0.21407 | 92.8294 | 16 | 15.2503 | 0.74967 |  | 13-03-2026 17:00 | 87.948 | 89.096 | 1706.6 | 14.8493 | 15.4716 | -0.62224 | 92.8294 | 15.6 | 15.2503 | 0.34967 |  | 13-03-2026 17:00 | 88.683 | 89.848 | 1709.1 | 14.9747 | 15.4716 | -0.49691 | 92.8294 | 15.8 | 15.2503 | 0.54967 |  | 13-03-2026 17:00 | 88.68 | 91.166 | 1724.3 | 15.1943 | 15.4716 | -0.27724 | 92.8294 | 15.7 | 15.2503 | 0.44967 |  | 13-03-2026 17:00 | 83.587 | 84.705 | 1629.7 | 14.1175 | 14.7193 | -0.60178 | 88.3157 | 14.9 | 14.5088 | 0.3912 |  | 13-03-2026 17:00 | 155.967 | 160.1521 | -4.1851 | 960.9124 | 164.3 | 157.8619 | 6.4381
13-03-2026 16:50 | 394 | 48.22 | 135.925 | 137.66 | 2280.1 | 22.9433 | 23.5124 | -0.56904 | 141.0742 | 49.7 | 23.1761 | 26.5239 |  | 13-03-2026 16:50 | 137.723 | 139.565 | 2304.5 | 23.2608 | 23.5124 | -0.25154 | 141.0742 | 23.4 | 23.1761 | 0.22386 |  | 13-03-2026 16:50 | 136.029 | 138.514 | 2268.5 | 23.0857 | 23.5124 | -0.4267 | 141.0742 | 23.8 | 23.1761 | 0.62386 |  | 13-03-2026 16:50 | 135.764 | 137.552 | 2282.3 | 22.9253 | 23.5124 | -0.58704 | 141.0742 | 23.8 | 23.1761 | 0.62386 |  | 13-03-2026 16:50 | 101.787 | 103.107 | 1708.5 | 17.1845 | 17.4166 | -0.23207 | 104.4994 | 17.6 | 17.1675 | 0.43249 |  | 13-03-2026 16:50 | 99.248 | 100.54 | 1691 | 16.7567 | 17.4166 | -0.6599 | 104.4994 | 17.2 | 17.1675 | 0.032487 |  | 13-03-2026 16:50 | 100.049 | 101.315 | 1693.3 | 16.8858 | 17.4166 | -0.53074 | 104.4994 | 17.3 | 17.1675 | 0.13249 |  | 13-03-2026 16:50 | 100.078 | 103.035 | 1708.6 | 17.1725 | 17.4166 | -0.24407 | 104.4994 | 17.6 | 17.1675 | 0.43249 |  | 13-03-2026 16:50 | 94.344 | 95.577 | 1614.8 | 15.9295 | 16.5697 | -0.64021 | 99.4183 | 16.5 | 16.3328 | 0.16724 |  | 13-03-2026 16:50 | 176.1442 | 180.2855 | -4.1413 | 1081.7128 | 206.9 | 177.7074 | 29.1926
13-03-2026 16:40 | 433 | 48.5 | 150.044 | 152.02 | 2256.3 | 25.3367 | 25.8122 | -0.47551 | 154.873 | 0 | 25.4431 | -25.4431 |  | 13-03-2026 16:40 | 152.068 | 154.077 | 2281.1 | 25.6795 | 25.8122 | -0.13267 | 154.873 | 27.8 | 25.4431 | 2.3569 |  | 13-03-2026 16:40 | 150.325 | 153.375 | 2244.7 | 25.5625 | 25.8122 | -0.24967 | 154.873 | 26.6 | 25.4431 | 1.1569 |  | 13-03-2026 16:40 | 150.03 | 152.052 | 2258.5 | 25.342 | 25.8122 | -0.47017 | 154.873 | 26.7 | 25.4431 | 1.2569 |  | 13-03-2026 16:40 | 112.393 | 113.873 | 1690.9 | 18.9788 | 19.1201 | -0.14129 | 114.7208 | 20 | 18.8467 | 1.1533 |  | 13-03-2026 16:40 | 109.65 | 111.072 | 1673.8 | 18.512 | 19.1201 | -0.60813 | 114.7208 | 19.5 | 18.8467 | 0.65329 |  | 13-03-2026 16:40 | 110.45 | 111.893 | 1676 | 18.6488 | 19.1201 | -0.47129 | 114.7208 | 19.5 | 18.8467 | 0.65329 |  | 13-03-2026 16:40 | 110.706 | 113.729 | 1691 | 18.9548 | 19.1201 | -0.16529 | 114.7208 | 19.4 | 18.8467 | 0.55329 |  | 13-03-2026 16:40 | 104.401 | 105.765 | 1598.3 | 17.6275 | 18.1904 | -0.56293 | 109.1426 | 18.3 | 17.9303 | 0.36969 |  | 13-03-2026 16:40 | 194.6427 | 197.9196 | -3.277 | 1187.5178 | 177.8 | 195.0894 | -17.2894
13-03-2026 16:30 | 478 | 48.5 | 165.501 | 167.698 | 2230.4 | 27.9497 | 28.4947 | -0.54506 | 170.9684 | 29.8 | 28.0873 | 1.7127 |  | 13-03-2026 16:30 | 169.127 | 171.459 | 2253.3 | 28.5765 | 28.4947 | 0.081769 | 170.9684 | 28.6 | 28.0873 | 0.51274 |  | 13-03-2026 16:30 | 165.44 | 168.919 | 2218.1 | 28.1532 | 28.4947 | -0.34156 | 170.9684 | 28.6 | 28.0873 | 0.51274 |  | 13-03-2026 16:30 | 165.435 | 167.682 | 2231.8 | 27.947 | 28.4947 | -0.54773 | 170.9684 | 28.5 | 28.0873 | 0.41274 |  | 13-03-2026 16:30 | 124.072 | 125.706 | 1670.9 | 20.951 | 21.1072 | -0.15621 | 126.6432 | 21.4 | 20.8054 | 0.59462 |  | 13-03-2026 16:30 | 121.435 | 123.034 | 1654.3 | 20.5057 | 21.1072 | -0.60154 | 126.6432 | 21.2 | 20.8054 | 0.39462 |  | 13-03-2026 16:30 | 121.406 | 123.005 | 1656.5 | 20.5008 | 21.1072 | -0.60637 | 126.6432 | 21.4 | 20.8054 | 0.59462 |  | 13-03-2026 16:30 | 122.263 | 125.42 | 1671.6 | 20.9033 | 21.1072 | -0.20387 | 126.6432 | 21.4 | 20.8054 | 0.59462 |  | 13-03-2026 16:30 | 115.348 | 116.879 | 1580 | 19.4798 | 20.0809 | -0.60106 | 120.4854 | 20.2 | 19.7937 | 0.40626 |  | 13-03-2026 16:30 | 214.967 | 218.4887 | -3.5217 | 1310.9319 | 221.1 | 215.3643 | 5.7357
13-03-2026 16:20 | 519 | 48.5 | 181.224 | 183.704 | 2200.6 | 30.6173 | 30.9388 | -0.32151 | 185.633 | 31.1 | 30.4964 | 0.60359 |  | 13-03-2026 16:20 | 181.98 | 184.571 | 2224.7 | 30.7618 | 30.9388 | -0.17701 | 185.633 | 31.8 | 30.4964 | 1.3036 |  | 13-03-2026 16:20 | 179.677 | 183.721 | 2189.5 | 30.6202 | 30.9388 | -0.31867 | 185.633 | 31.9 | 30.4964 | 1.4036 |  | 13-03-2026 16:20 | 179.61 | 182.123 | 2203.3 | 30.3538 | 30.9388 | -0.58501 | 185.633 | 31.9 | 30.4964 | 1.4036 |  | 13-03-2026 16:20 | 134.702 | 136.529 | 1649.5 | 22.7548 | 22.9177 | -0.16283 | 137.506 | 23.9 | 22.5899 | 1.3101 |  | 13-03-2026 16:20 | 131.906 | 133.67 | 1633.1 | 22.2783 | 22.9177 | -0.63933 | 137.506 | 23.1 | 22.5899 | 0.51006 |  | 13-03-2026 16:20 | 132.423 | 134.181 | 1635.1 | 22.3635 | 22.9177 | -0.55416 | 137.506 | 23.1 | 22.5899 | 0.51006 |  | 13-03-2026 16:20 | 133.104 | 136.681 | 1650.2 | 22.7802 | 22.9177 | -0.13749 | 137.506 | 23.7 | 22.5899 | 1.1101 |  | 13-03-2026 16:20 | 125.411 | 127.101 | 1559.8 | 21.1835 | 21.8033 | -0.61981 | 130.8199 | 22.3 | 21.4915 | 0.80847 |  | 13-03-2026 16:20 | 233.7135 | 237.2293 | -3.5158 | 1423.3759 | 242.8 | 233.8369 | 8.9631
13-03-2026 16:10 | 581 | 48.5 | 200.212 | 203.014 | 2169.5 | 33.8357 | 34.6348 | -0.79914 | 207.8089 | 37.1 | 34.1395 | 2.9605 |  | 13-03-2026 16:10 | 209.972 | 212.997 | 2192.9 | 35.4995 | 34.6348 | 0.86469 | 207.8089 | 36.7 | 34.1395 | 2.5605 |  | 13-03-2026 16:10 | 199.877 | 204.628 | 2157.6 | 34.1047 | 34.6348 | -0.53014 | 207.8089 | 35.7 | 34.1395 | 1.5605 |  | 13-03-2026 16:10 | 200.356 | 203.221 | 2171.4 | 33.8702 | 34.6348 | -0.76464 | 207.8089 | 35.8 | 34.1395 | 1.6605 |  | 13-03-2026 16:10 | 150.228 | 152.268 | 1625.6 | 25.378 | 25.6554 | -0.27741 | 153.9325 | 26.8 | 25.2885 | 1.5115 |  | 13-03-2026 16:10 | 146.785 | 148.936 | 1610 | 24.8227 | 25.6554 | -0.83275 | 153.9325 | 26.3 | 25.2885 | 1.0115 |  | 13-03-2026 16:10 | 147.818 | 150.044 | 1612 | 25.0073 | 25.6554 | -0.64808 | 153.9325 | 26.7 | 25.2885 | 1.4115 |  | 13-03-2026 16:10 | 148.514 | 152.725 | 1626.5 | 25.4542 | 25.6554 | -0.20125 | 153.9325 | 26.4 | 25.2885 | 1.1115 |  | 13-03-2026 16:10 | 139.946 | 141.861 | 1537.5 | 23.6435 | 24.4079 | -0.76445 | 146.4477 | 25 | 24.0589 | 0.94108 |  | 13-03-2026 16:10 | 261.6157 | 265.5688 | -3.9532 | 1593.4131 | 276.5 | 261.7712 | 14.7288
13-03-2026 16:00 | 651 | 49.08 | 222.43 | 226.172 | 2132.4 | 37.6953 | 38.7218 | -1.0265 | 232.331 | 35.7 | 38.1681 | -2.4681 |  | 13-03-2026 16:00 | 226.225 | 229.623 | 2156.2 | 38.2705 | 38.7218 | -0.45134 | 232.331 | 37.7 | 38.1681 | -0.46812 |  | 13-03-2026 16:00 | 221.402 | 226.723 | 2121.9 | 37.7872 | 38.7218 | -0.93467 | 232.331 | 37.6 | 38.1681 | -0.56812 |  | 13-03-2026 16:00 | 222.98 | 226.284 | 2135.6 | 37.714 | 38.7218 | -1.0078 | 232.331 | 37.8 | 38.1681 | -0.36812 |  | 13-03-2026 16:00 | 166.184 | 168.492 | 1598.8 | 28.082 | 28.6828 | -0.60084 | 172.0971 | 28.3 | 28.2727 | 0.027322 |  | 13-03-2026 16:00 | 163.777 | 166.414 | 1583.7 | 27.7357 | 28.6828 | -0.94718 | 172.0971 | 27.7 | 28.2727 | -0.57268 |  | 13-03-2026 16:00 | 163.587 | 166.139 | 1585.3 | 27.6898 | 28.6828 | -0.99301 | 172.0971 | 27.5 | 28.2727 | -0.77268 |  | 13-03-2026 16:00 | 164.603 | 169.107 | 1600.1 | 28.1845 | 28.6828 | -0.49834 | 172.0971 | 27.7 | 28.2727 | -0.57268 |  | 13-03-2026 16:00 | 155.523 | 157.699 | 1512.5 | 26.2832 | 27.2882 | -1.005 | 163.729 | 26.1 | 26.898 | -0.79795 |  | 13-03-2026 16:00 | 289.4422 | 296.9069 | -7.4647 | 1781.4414 | 286.1 | 292.6611 | -6.5611
13-03-2026 15:50 | 677 | 48.79 | 232.219 | 235.247 | 2096.7 | 39.2078 | 40.313 | -1.1051 | 241.8778 | 41 | 39.7365 | 1.2635 |  | 13-03-2026 15:50 | 234.991 | 238.64 | 2118.5 | 39.7733 | 40.313 | -0.53963 | 241.8778 | 41 | 39.7365 | 1.2635 |  | 13-03-2026 15:50 | 232.188 | 237.991 | 2084.3 | 39.6652 | 40.313 | -0.6478 | 241.8778 | 40 | 39.7365 | 0.26351 |  | 13-03-2026 15:50 | 232.832 | 236.402 | 2097.8 | 39.4003 | 40.313 | -0.91263 | 241.8778 | 40 | 39.7365 | 0.26351 |  | 13-03-2026 15:50 | 174.926 | 177.392 | 1570.5 | 29.5653 | 29.8615 | -0.29612 | 179.1687 | 30 | 29.4344 | 0.56556 |  | 13-03-2026 15:50 | 171.292 | 174.131 | 1556 | 29.0218 | 29.8615 | -0.83962 | 179.1687 | 29.5 | 29.4344 | 0.065562 |  | 13-03-2026 15:50 | 172.197 | 174.967 | 1557.8 | 29.1612 | 29.8615 | -0.70029 | 179.1687 | 29.6 | 29.4344 | 0.16556 |  | 13-03-2026 15:50 | 173.39 | 178.198 | 1572.4 | 29.6997 | 29.8615 | -0.16179 | 179.1687 | 29.7 | 29.4344 | 0.26556 |  | 13-03-2026 15:50 | 163.411 | 165.731 | 1486.4 | 27.6218 | 28.4095 | -0.78764 | 170.4569 | 28.4 | 28.0032 | 0.39678 |  | 13-03-2026 15:50 | 303.1165 | 309.1072 | -5.9907 | 1854.643 | 309.2 | 304.6869 | 4.5131
13-03-2026 15:40 | 704 | 48.79 | 240.629 | 244.269 | 2055.7 | 40.7115 | 41.9207 | -1.2092 | 251.5243 | 42 | 41.3213 | 0.67875 |  | 13-03-2026 15:40 | 243.033 | 246.809 | 2077.5 | 41.1348 | 41.9207 | -0.78589 | 251.5243 | 44 | 41.3213 | 2.6787 |  | 13-03-2026 15:40 | 240.538 | 246.484 | 2044.3 | 41.0807 | 41.9207 | -0.84005 | 251.5243 | 41.9 | 41.3213 | 0.57875 |  | 13-03-2026 15:40 | 240.44 | 244.167 | 2057.8 | 40.6945 | 41.9207 | -1.2262 | 251.5243 | 42 | 41.3213 | 0.67875 |  | 13-03-2026 15:40 | 180.82 | 183.369 | 1540.5 | 30.5615 | 31.0524 | -0.49089 | 186.3143 | 31.5 | 30.6083 | 0.89166 |  | 13-03-2026 15:40 | 176.883 | 179.7 | 1526.5 | 29.95 | 31.0524 | -1.1024 | 186.3143 | 30.9 | 30.6083 | 0.29166 |  | 13-03-2026 15:40 | 177.959 | 180.641 | 1528.2 | 30.1068 | 31.0524 | -0.94555 | 186.3143 | 31 | 30.6083 | 0.39166 |  | 13-03-2026 15:40 | 178.734 | 183.897 | 1542.7 | 30.6495 | 31.0524 | -0.40289 | 186.3143 | 31.3 | 30.6083 | 0.69166 |  | 13-03-2026 15:40 | 168.105 | 170.492 | 1458 | 28.4153 | 29.5425 | -1.1272 | 177.255 | 29.1 | 29.12 | -0.020042 |  | 13-03-2026 15:40 | 313.3047 | 321.4349 | -8.1303 | 1928.6096 | 323.7 | 316.8384 | 6.8616
13-03-2026 15:30 | 772 | 48.79 | 266.03 | 270.136 | 2013.7 | 45.0227 | 45.9699 | -0.94721 | 275.8193 | 42.5 | 45.3125 | -2.8125 |  | 13-03-2026 15:30 | 268.297 | 272.549 | 2033.5 | 45.4248 | 45.9699 | -0.54505 | 275.8193 | 41.8 | 45.3125 | -3.5125 |  | 13-03-2026 15:30 | 261.906 | 268.19 | 2002.4 | 44.6983 | 45.9699 | -1.2715 | 275.8193 | 42.7 | 45.3125 | -2.6125 |  | 13-03-2026 15:30 | 264.688 | 268.937 | 2015.8 | 44.8228 | 45.9699 | -1.147 | 275.8193 | 43 | 45.3125 | -2.3125 |  | 13-03-2026 15:30 | 196.747 | 199.622 | 1509 | 33.2703 | 34.0518 | -0.78143 | 204.3106 | 32.4 | 33.5648 | -1.1648 |  | 13-03-2026 15:30 | 192.754 | 195.961 | 1495.6 | 32.6602 | 34.0518 | -1.3916 | 204.3106 | 32 | 33.5648 | -1.5648 |  | 13-03-2026 15:30 | 195.492 | 200.089 | 1497.2 | 33.3482 | 34.0518 | -0.7036 | 204.3106 | 32.3 | 33.5648 | -1.2648 |  | 13-03-2026 15:30 | 197.251 | 203.817 | 1511.4 | 33.9695 | 34.0518 | -0.082264 | 204.3106 | 32.5 | 33.5648 | -1.0648 |  | 13-03-2026 15:30 | 185.7 | 188.375 | 1428.9 | 31.3958 | 32.396 | -1.0002 | 194.3762 | 30.6 | 31.9328 | -1.3328 |  | 13-03-2026 15:30 | 344.6127 | 352.4826 | -7.87 | 2114.8957 | 329.8 | 347.4421 | -17.6421
13-03-2026 15:20 | 614 | 48.79 | 200.582 | 203.513 | 1971.2 | 33.9188 | 36.5615 | -2.6427 | 219.3692 | 42.8 | 36.0387 | 6.7613 |  | 13-03-2026 15:20 | 240.434 | 244.244 | 1991.7 | 40.7073 | 36.5615 | 4.1458 | 219.3692 | 42.9 | 36.0387 | 6.8613 |  | 13-03-2026 15:20 | 212.728 | 218.276 | 1959.7 | 36.3793 | 36.5615 | -0.1822 | 219.3692 | 42.6 | 36.0387 | 6.5613 |  | 13-03-2026 15:20 | 211.563 | 214.741 | 1972.8 | 35.7902 | 36.5615 | -0.77137 | 219.3692 | 42.8 | 36.0387 | 6.7613 |  | 13-03-2026 15:20 | 155.141 | 157.633 | 1476.6 | 26.2722 | 27.0826 | -0.81045 | 162.4957 | 32 | 26.6953 | 5.3047 |  | 13-03-2026 15:20 | 151.521 | 154.424 | 1463.6 | 25.7373 | 27.0826 | -1.3453 | 162.4957 | 31.2 | 26.6953 | 4.5047 |  | 13-03-2026 15:20 | 155.508 | 158.618 | 1464.9 | 26.4363 | 27.0826 | -0.64629 | 162.4957 | 31.6 | 26.6953 | 4.9047 |  | 13-03-2026 15:20 | 155.981 | 159.991 | 1478.9 | 26.6652 | 27.0826 | -0.41745 | 162.4957 | 32.3 | 26.6953 | 5.6047 |  | 13-03-2026 15:20 | 147.231 | 149.415 | 1398.3 | 24.9025 | 25.7658 | -0.86326 | 154.5946 | 30 | 25.3973 | 4.6027 |  | 13-03-2026 15:20 | 276.8092 | 280.3424 | -3.5332 | 1682.0544 | 328.2 | 276.3335 | 51.8665
13-03-2026 15:10 | 741 | 49.08 | 258.222 | 262.314 | 1928.4 | 43.719 | 44.0751 | -0.35609 | 264.4505 | 44.1 | 43.4448 | 0.65519 |  | 13-03-2026 15:10 | 250.615 | 255.987 | 1948.8 | 42.6645 | 44.0751 | -1.4106 | 264.4505 | 46.5 | 43.4448 | 3.0552 |  | 13-03-2026 15:10 | 251.213 | 256.121 | 1917.1 | 42.6868 | 44.0751 | -1.3883 | 264.4505 | 43.8 | 43.4448 | 0.35519 |  | 13-03-2026 15:10 | 253.958 | 257.983 | 1930 | 42.9972 | 44.0751 | -1.0779 | 264.4505 | 44 | 43.4448 | 0.55519 |  | 13-03-2026 15:10 | 182.187 | 184.83 | 1444.6 | 30.805 | 32.6482 | -1.8432 | 195.8893 | 33 | 32.1813 | 0.81866 |  | 13-03-2026 15:10 | 182.043 | 184.684 | 1432.4 | 30.7807 | 32.6482 | -1.8675 | 195.8893 | 32.3 | 32.1813 | 0.11866 |  | 13-03-2026 15:10 | 188.6 | 193.074 | 1433.3 | 32.179 | 32.6482 | -0.46921 | 195.8893 | 32.5 | 32.1813 | 0.31866 |  | 13-03-2026 15:10 | 194.277 | 197.608 | 1446.6 | 32.9347 | 32.6482 | 0.28645 | 195.8893 | 32.1 | 32.1813 | -0.081343 |  | 13-03-2026 15:10 | 174.784 | 180.045 | 1368.3 | 30.0075 | 31.0607 | -1.0532 | 186.3644 | 30.7 | 30.6166 | 0.083438 |  | 13-03-2026 15:10 | 328.7743 | 337.9539 | -9.1796 | 2027.7236 | 339 | 333.1212 | 5.8788
13-03-2026 15:00 | 839 | 48.5 | 283.128 | 287.732 | 1884.3 | 47.9553 | 50.0148 | -2.0595 | 300.0889 | 48.7 | 49.2996 | -0.5996 | 0.984 | 13-03-2026 15:00 | 291.91 | 293.508 | 1902.3 | 48.918 | 50.0148 | -1.0968 | 300.0889 | 48.8 | 49.2996 | -0.4996 | 0.99456 | 13-03-2026 15:00 | 281.351 | 288.794 | 1873.3 | 48.1323 | 50.0148 | -1.8825 | 300.0889 | 48.4 | 49.2996 | -0.8996 | 0.97423 | 13-03-2026 15:00 | 282.655 | 287.368 | 1886 | 47.8947 | 50.0148 | -2.1201 | 300.0889 | 48.7 | 49.2996 | -0.5996 | 0.9836 | 13-03-2026 15:00 | 212.013 | 215.22 | 1411.6 | 35.87 | 37.048 | -1.178 | 222.288 | 36.5 | 36.5182 | -0.018221 | 0.9851 | 13-03-2026 15:00 | 207.921 | 211.712 | 1400.1 | 35.2853 | 37.048 | -1.7627 | 222.288 | 35.9 | 36.5182 | -0.61822 | 0.98209 | 13-03-2026 15:00 | 208.629 | 212.672 | 1400.8 | 35.4453 | 37.048 | -1.6027 | 222.288 | 36.1 | 36.5182 | -0.41822 | 0.98099 | 13-03-2026 15:00 | 210.046 | 215.92 | 1414.5 | 35.9867 | 37.048 | -1.0613 | 222.288 | 36.3 | 36.5182 | -0.21822 | 0.9728 | 13-03-2026 15:00 | 197.928 | 201.016 | 1337.6 | 33.5027 | 35.2466 | -1.7439 | 211.4795 | 34.3 | 34.7426 | -0.44256 | 0.98464 | 13-03-2026 15:00 | 368.9903 | 383.4979 | -14.5075 | 2300.9872 | 373.7 | 378.0138 | -4.3138
13-03-2026 14:50 | 890 | 48.79 | 299.153 | 304.129 | 1835.6 | 50.6882 | 52.9964 | -2.3082 | 317.9782 | 49.1 | 52.2385 | -3.1385 | 0.98364 | 13-03-2026 14:50 | 303.197 | 308.284 | 1853.5 | 51.3807 | 52.9964 | -1.6157 | 317.9782 | 49 | 52.2385 | -3.2385 | 0.9835 | 13-03-2026 14:50 | 297.898 | 305.959 | 1824.9 | 50.9932 | 52.9964 | -2.0032 | 317.9782 | 49.5 | 52.2385 | -2.7385 | 0.97365 | 13-03-2026 14:50 | 298.883 | 303.897 | 1837.3 | 50.6495 | 52.9964 | -2.3469 | 317.9782 | 49.6 | 52.2385 | -2.6385 | 0.9835 | 13-03-2026 14:50 | 225.123 | 228.574 | 1375.1 | 38.0957 | 39.2566 | -1.1609 | 235.5394 | 38 | 38.6952 | -0.6952 | 0.9849 | 13-03-2026 14:50 | 220.053 | 224.147 | 1364.2 | 37.3578 | 39.2566 | -1.8987 | 235.5394 | 37.2 | 38.6952 | -1.4952 | 0.98174 | 13-03-2026 14:50 | 221.622 | 226.099 | 1364.7 | 37.6832 | 39.2566 | -1.5734 | 235.5394 | 37 | 38.6952 | -1.6952 | 0.9802 | 13-03-2026 14:50 | 222.141 | 228.278 | 1378.2 | 38.0463 | 39.2566 | -1.2102 | 235.5394 | 37.1 | 38.6952 | -1.5952 | 0.97312 | 13-03-2026 14:50 | 209.436 | 212.604 | 1303.3 | 35.434 | 37.3478 | -1.9138 | 224.0866 | 35 | 36.8137 | -1.8137 | 0.9851 | 13-03-2026 14:50 | 390.3285 | 406.3595 | -16.031 | 2438.157 | 381.5 | 400.5486 | -19.0486
13-03-2026 14:40 | 919 | 48.79 | 306.836 | 312.015 | 1786.5 | 52.0025 | 54.7232 | -2.7207 | 328.3393 | 49.6 | 53.9407 | -4.3407 | 0.9834 | 13-03-2026 14:40 | 291.711 | 299.609 | 1804.5 | 49.9348 | 54.7232 | -4.7884 | 328.3393 | 50.4 | 53.9407 | -3.5407 | 0.97364 | 13-03-2026 14:40 | 305.541 | 313.749 | 1775.4 | 52.2915 | 54.7232 | -2.4317 | 328.3393 | 50.3 | 53.9407 | -3.6407 | 0.97384 | 13-03-2026 14:40 | 308.276 | 313.48 | 1787.7 | 52.2467 | 54.7232 | -2.4765 | 328.3393 | 50.7 | 53.9407 | -3.2407 | 0.9834 | 13-03-2026 14:40 | 232.639 | 236.23 | 1337.1 | 39.3717 | 40.5357 | -1.164 | 243.2143 | 37.3 | 39.9561 | -2.6561 | 0.9848 | 13-03-2026 14:40 | 228.284 | 232.689 | 1327 | 38.7815 | 40.5357 | -1.7542 | 243.2143 | 36.6 | 39.9561 | -3.3561 | 0.98107 | 13-03-2026 14:40 | 229.848 | 234.714 | 1327.7 | 39.119 | 40.5357 | -1.4167 | 243.2143 | 36.9 | 39.9561 | -3.0561 | 0.97927 | 13-03-2026 14:40 | 231.269 | 237.861 | 1341.1 | 39.6435 | 40.5357 | -0.89221 | 243.2143 | 37.2 | 39.9561 | -2.7561 | 0.97229 | 13-03-2026 14:40 | 218.229 | 221.507 | 1268.3 | 36.9178 | 38.5647 | -1.6469 | 231.3883 | 34.9 | 38.0132 | -3.1132 | 0.9852 | 13-03-2026 14:40 | 400.309 | 419.6004 | -19.2914 | 2517.6025 | 383.9 | 413.6001 | -29.7001
13-03-2026 14:30 | 954 | 49.08 | 315.947 | 321.346 | 1736.9 | 53.5577 | 56.7444 | -3.1868 | 340.4667 | 54 | 55.933 | -1.933 | 0.9832 | 13-03-2026 14:30 | 321.054 | 325.883 | 1754.1 | 54.3138 | 56.7444 | -2.4306 | 340.4667 | 54.9 | 55.933 | -1.033 | 0.98518 | 13-03-2026 14:30 | 313.969 | 323.029 | 1725.1 | 53.8382 | 56.7444 | -2.9063 | 340.4667 | 53.7 | 55.933 | -2.233 | 0.97195 | 13-03-2026 14:30 | 316.356 | 321.893 | 1737 | 53.6488 | 56.7444 | -3.0956 | 340.4667 | 54.1 | 55.933 | -1.833 | 0.9828 | 13-03-2026 14:30 | 237.433 | 241.196 | 1299.8 | 40.1993 | 42.0329 | -1.8336 | 252.1975 | 40.5 | 41.4319 | -0.93185 | 0.9844 | 13-03-2026 14:30 | 232.664 | 237.144 | 1290.4 | 39.524 | 42.0329 | -2.5089 | 252.1975 | 39.8 | 41.4319 | -1.6319 | 0.98111 | 13-03-2026 14:30 | 234.696 | 239.259 | 1290.8 | 39.8765 | 42.0329 | -2.1564 | 252.1975 | 39.8 | 41.4319 | -1.6319 | 0.98093 | 13-03-2026 14:30 | 236.383 | 243.371 | 1303.9 | 40.5618 | 42.0329 | -1.4711 | 252.1975 | 40.1 | 41.4319 | -1.3319 | 0.97129 | 13-03-2026 14:30 | 221.998 | 225.489 | 1233.4 | 37.5815 | 39.9891 | -2.4076 | 239.9347 | 37.9 | 39.4173 | -1.5173 | 0.98452 | 13-03-2026 14:30 | 413.1017 | 435.0986 | -21.9969 | 2610.5915 | 414.8 | 428.8767 | -14.0767
13-03-2026 14:20 | 1008 | 48.79 | 331.699 | 337.47 | 1682.9 | 56.245 | 60.0229 | -3.7779 | 360.1371 | 54.6 | 59.1645 | -4.5645 | 0.9829 | 13-03-2026 14:20 | 338.297 | 344.253 | 1699.2 | 57.3755 | 60.0229 | -2.6474 | 360.1371 | 57.1 | 59.1645 | -2.0645 | 0.9827 | 13-03-2026 14:20 | 330.744 | 340.318 | 1671.4 | 56.7197 | 60.0229 | -3.3032 | 360.1371 | 52.8 | 59.1645 | -6.3645 | 0.97187 | 13-03-2026 14:20 | 333.253 | 339.12 | 1682.9 | 56.52 | 60.0229 | -3.5029 | 360.1371 | 53 | 59.1645 | -6.1645 | 0.9827 | 13-03-2026 14:20 | 248.846 | 252.841 | 1259.3 | 42.1402 | 44.4614 | -2.3212 | 266.7682 | 39.9 | 43.8256 | -3.9256 | 0.9842 | 13-03-2026 14:20 | 244.877 | 249.714 | 1250.6 | 41.619 | 44.4614 | -2.8424 | 266.7682 | 39.6 | 43.8256 | -4.2256 | 0.98063 | 13-03-2026 14:20 | 245.305 | 250.259 | 1251 | 41.7098 | 44.4614 | -2.7515 | 266.7682 | 39.4 | 43.8256 | -4.4256 | 0.9802 | 13-03-2026 14:20 | 246.839 | 254.035 | 1263.8 | 42.3392 | 44.4614 | -2.1222 | 266.7682 | 40 | 43.8256 | -3.8256 | 0.97167 | 13-03-2026 14:20 | 233.405 | 237.104 | 1195.5 | 39.5173 | 42.2995 | -2.7822 | 253.7969 | 37.7 | 41.6946 | -3.9946 | 0.9844 | 13-03-2026 14:20 | 434.1857 | 460.2364 | -26.0507 | 2761.4182 | 414.1 | 453.655 | -39.555
13-03-2026 14:10 | 1005 | 48.79 | 329.465 | 335.299 | 1628.3 | 55.8832 | 59.8442 | -3.961 | 359.0653 | 55.4 | 58.9884 | -3.5884 | 0.9826 | 13-03-2026 14:10 | 330.964 | 333.295 | 1642.1 | 55.5492 | 59.8442 | -4.295 | 359.0653 | 54.3 | 58.9884 | -4.6884 | 0.99301 | 13-03-2026 14:10 | 328.699 | 337.908 | 1618.6 | 56.318 | 59.8442 | -3.5262 | 359.0653 | 55.6 | 58.9884 | -3.3884 | 0.97275 | 13-03-2026 14:10 | 331.272 | 337.173 | 1629.9 | 56.1955 | 59.8442 | -3.6487 | 359.0653 | 56.1 | 58.9884 | -2.8884 | 0.9825 | 13-03-2026 14:10 | 248.286 | 252.272 | 1219.4 | 42.0453 | 44.329 | -2.2837 | 265.9743 | 42.1 | 43.6951 | -1.5951 | 0.9842 | 13-03-2026 14:10 | 244.277 | 249.255 | 1211 | 41.5425 | 44.329 | -2.7865 | 265.9743 | 40.8 | 43.6951 | -2.8951 | 0.98003 | 13-03-2026 14:10 | 244.061 | 248.902 | 1211.6 | 41.4837 | 44.329 | -2.8454 | 265.9743 | 41.4 | 43.6951 | -2.2951 | 0.98055 | 13-03-2026 14:10 | 246.14 | 253.037 | 1223.8 | 42.1728 | 44.329 | -2.1562 | 265.9743 | 41.3 | 43.6951 | -2.3951 | 0.97274 | 13-03-2026 14:10 | 232.438 | 236.169 | 1157.8 | 39.3615 | 42.1736 | -2.8121 | 253.0416 | 39 | 41.5705 | -2.5705 | 0.9842 | 13-03-2026 14:10 | 430.5517 | 458.8666 | -28.315 | 2753.1997 | 426 | 452.3048 | -26.3048
13-03-2026 14:00 | 1022 | 48.5 | 337.986 | 344.058 | 1572.9 | 57.343 | 60.9239 | -3.5809 | 365.5433 | 51.3 | 60.0527 | -8.7527 | 0.98235 | 13-03-2026 14:00 | 333.023 | 332.897 | 1587.8 | 55.4828 | 60.9239 | -5.441 | 365.5433 | 52.2 | 60.0527 | -7.8527 | 1.0004 | 13-03-2026 14:00 | 335.765 | 345.939 | 1563 | 57.6565 | 60.9239 | -3.2674 | 365.5433 | 51.7 | 60.0527 | -8.3527 | 0.97059 | 13-03-2026 14:00 | 337.671 | 343.686 | 1573.8 | 57.281 | 60.9239 | -3.6429 | 365.5433 | 51.8 | 60.0527 | -8.2527 | 0.9825 | 13-03-2026 14:00 | 253.368 | 257.436 | 1177.3 | 42.906 | 45.1288 | -2.2228 | 270.7728 | 39.8 | 44.4835 | -4.6835 | 0.9842 | 13-03-2026 14:00 | 248.961 | 253.914 | 1170.2 | 42.319 | 45.1288 | -2.8098 | 270.7728 | 39.1 | 44.4835 | -5.3835 | 0.98049 | 13-03-2026 14:00 | 249.946 | 255.536 | 1170.2 | 42.5893 | 45.1288 | -2.5395 | 270.7728 | 39.2 | 44.4835 | -5.2835 | 0.97812 | 13-03-2026 14:00 | 251.575 | 258.912 | 1182.5 | 43.152 | 45.1288 | -1.9768 | 270.7728 | 39.4 | 44.4835 | -5.0835 | 0.97166 | 13-03-2026 14:00 | 237.179 | 240.884 | 1118.8 | 40.1473 | 42.9345 | -2.7871 | 257.6068 | 37.3 | 42.3205 | -5.0205 | 0.98462 | 13-03-2026 14:00 | 438.877 | 467.1452 | -28.2682 | 2802.8712 | 401.8 | 460.465 | -58.665
13-03-2026 13:50 | 1021 | 48.79 | 335.459 | 341.365 | 1521.6 | 56.8942 | 60.797 | -3.9028 | 364.7817 | 56.1 | 59.9276 | -3.8276 | 0.9827 | 13-03-2026 13:50 | 338.32 | 344.381 | 1535.6 | 57.3968 | 60.797 | -3.4001 | 364.7817 | 54.5 | 59.9276 | -5.4276 | 0.9824 | 13-03-2026 13:50 | 339.402 | 349.431 | 1511.3 | 58.2385 | 60.797 | -2.5585 | 364.7817 | 54.4 | 59.9276 | -5.5276 | 0.9713 | 13-03-2026 13:50 | 333.717 | 339.696 | 1522 | 56.616 | 60.797 | -4.181 | 364.7817 | 53.6 | 59.9276 | -6.3276 | 0.9824 | 13-03-2026 13:50 | 251.432 | 255.52 | 1137.5 | 42.5867 | 45.0348 | -2.4481 | 270.2087 | 41.5 | 44.3908 | -2.8908 | 0.984 | 13-03-2026 13:50 | 246.52 | 251.719 | 1131.1 | 41.9532 | 45.0348 | -3.0816 | 270.2087 | 40.9 | 44.3908 | -3.4908 | 0.97935 | 13-03-2026 13:50 | 251.266 | 256.616 | 1131 | 42.7693 | 45.0348 | -2.2654 | 270.2087 | 41.5 | 44.3908 | -2.8908 | 0.97915 | 13-03-2026 13:50 | 252.841 | 260.648 | 1143.1 | 43.4413 | 45.0348 | -1.5934 | 270.2087 | 41.9 | 44.3908 | -2.4908 | 0.97005 | 13-03-2026 13:50 | 238.477 | 242.03 | 1081.5 | 40.3383 | 42.845 | -2.5067 | 257.0701 | 39.5 | 42.2323 | -2.7323 | 0.98532 | 13-03-2026 13:50 | 440.2343 | 466.172 | -25.9376 | 2797.0318 | 423.9 | 459.5057 | -35.6057
13-03-2026 13:40 | 1057 | 48.5 | 335.606 | 340.963 | 1465.5 | 56.8272 | 63.0103 | -6.1831 | 378.0619 | 55 | 62.1093 | -7.1093 | 0.98429 | 13-03-2026 13:40 | 333.512 | 339.038 | 1481.1 | 56.5063 | 63.0103 | -6.504 | 378.0619 | 55.3 | 62.1093 | -6.8093 | 0.9837 | 13-03-2026 13:40 | 329.515 | 339.785 | 1456.9 | 56.6308 | 63.0103 | -6.3795 | 378.0619 | 55.1 | 62.1093 | -7.0093 | 0.96978 | 13-03-2026 13:40 | 332.349 | 337.856 | 1468.4 | 56.3093 | 63.0103 | -6.701 | 378.0619 | 56.2 | 62.1093 | -5.9093 | 0.9837 | 13-03-2026 13:40 | 259.765 | 264.042 | 1096 | 44.007 | 46.6743 | -2.6673 | 280.0458 | 43.3 | 46.0069 | -2.7069 | 0.9838 | 13-03-2026 13:40 | 255.181 | 260.254 | 1090.2 | 43.3757 | 46.6743 | -3.2986 | 280.0458 | 42.7 | 46.0069 | -3.3069 | 0.98051 | 13-03-2026 13:40 | 256.756 | 262.385 | 1089.5 | 43.7308 | 46.6743 | -2.9435 | 280.0458 | 42.4 | 46.0069 | -3.6069 | 0.97855 | 13-03-2026 13:40 | 258.605 | 266.556 | 1101.2 | 44.426 | 46.6743 | -2.2483 | 280.0458 | 42.7 | 46.0069 | -3.3069 | 0.97017 | 13-03-2026 13:40 | 243.568 | 247.554 | 1042 | 41.259 | 44.4048 | -3.1458 | 266.4289 | 40.3 | 43.7698 | -3.4698 | 0.9839 | 13-03-2026 13:40 | 443.0722 | 483.1433 | -40.0711 | 2898.8599 | 433 | 476.2344 | -43.2344
13-03-2026 13:30 | 1050 | 48.5 | 328.472 | 333.711 | 1410.5 | 55.6185 | 62.593 | -6.9745 | 375.5582 | 58.3 | 61.6979 | -3.3979 | 0.9843 | 13-03-2026 13:30 | 329.914 | 335.4 | 1425.8 | 55.9 | 62.593 | -6.693 | 375.5582 | 55.4 | 61.6979 | -6.2979 | 0.98364 | 13-03-2026 13:30 | 329.424 | 339.543 | 1401.8 | 56.5905 | 62.593 | -6.0025 | 375.5582 | 56.2 | 61.6979 | -5.4979 | 0.9702 | 13-03-2026 13:30 | 332.084 | 337.552 | 1412.2 | 56.2587 | 62.593 | -6.3344 | 375.5582 | 53.8 | 61.6979 | -7.8979 | 0.9838 | 13-03-2026 13:30 | 257.046 | 261.305 | 1052.7 | 43.5508 | 46.3652 | -2.8144 | 278.1912 | 43.2 | 45.7022 | -2.5022 | 0.9837 | 13-03-2026 13:30 | 253.976 | 258.832 | 1047.5 | 43.1387 | 46.3652 | -3.2265 | 278.1912 | 42.4 | 45.7022 | -3.3022 | 0.98124 | 13-03-2026 13:30 | 253.918 | 259.565 | 1047.1 | 43.2608 | 46.3652 | -3.1044 | 278.1912 | 42.6 | 45.7022 | -3.1022 | 0.97824 | 13-03-2026 13:30 | 256.029 | 263.509 | 1058.5 | 43.9182 | 46.3652 | -2.447 | 278.1912 | 42.9 | 45.7022 | -2.8022 | 0.97161 | 13-03-2026 13:30 | 242.146 | 246.108 | 1001.7 | 41.018 | 44.1108 | -3.0928 | 264.6645 | 40.5 | 43.48 | -2.98 | 0.9839 | 13-03-2026 13:30 | 439.2542 | 479.9437 | -40.6895 | 2879.6621 | 435.3 | 473.0805 | -37.7805
13-03-2026 13:20 | 1053 | 48.5 | 335.878 | 338.076 | 1352.2 | 56.346 | 62.7719 | -6.4259 | 376.6312 | 55.3 | 61.8742 | -6.5742 | 0.9935 | 13-03-2026 13:20 | 334.683 | 347.229 | 1370.4 | 57.8715 | 62.7719 | -4.9004 | 376.6312 | 57.8 | 61.8742 | -4.0742 | 0.96387 | 13-03-2026 13:20 | 343.043 | 353.003 | 1345.6 | 58.8338 | 62.7719 | -3.938 | 376.6312 | 56.5 | 61.8742 | -5.3742 | 0.97178 | 13-03-2026 13:20 | 338.741 | 344.459 | 1358.4 | 57.4098 | 62.7719 | -5.362 | 376.6312 | 56.6 | 61.8742 | -5.2742 | 0.9834 | 13-03-2026 13:20 | 259.873 | 264.152 | 1009.5 | 44.0253 | 46.4977 | -2.4723 | 278.9861 | 42.3 | 45.8328 | -3.5328 | 0.9838 | 13-03-2026 13:20 | 255.463 | 260.367 | 1005.1 | 43.3945 | 46.4977 | -3.1032 | 278.9861 | 41.7 | 45.8328 | -4.1328 | 0.98117 | 13-03-2026 13:20 | 257.133 | 262.704 | 1004.5 | 43.784 | 46.4977 | -2.7137 | 278.9861 | 41.9 | 45.8328 | -3.9328 | 0.97879 | 13-03-2026 13:20 | 258.549 | 265.884 | 1015.6 | 44.314 | 46.4977 | -2.1837 | 278.9861 | 42.6 | 45.8328 | -3.2328 | 0.97241 | 13-03-2026 13:20 | 243.552 | 247.512 | 961.2 | 41.252 | 44.2368 | -2.9848 | 265.4207 | 40.2 | 43.6042 | -3.4042 | 0.984 | 13-03-2026 13:20 | 447.231 | 481.315 | -34.084 | 2887.8898 | 434.9 | 474.4322 | -39.5322
13-03-2026 13:10 | 1032 | 48.79 | 328.62 | 334.371 | 1296.9 | 55.7285 | 61.452 | -5.7235 | 368.7118 | 54.6 | 60.5732 | -5.9732 | 0.9828 | 13-03-2026 13:10 | 348.956 | 335.706 | 1312.6 | 55.951 | 61.452 | -5.501 | 368.7118 | 55.4 | 60.5732 | -5.1732 | 1.0395 | 13-03-2026 13:10 | 338.518 | 348.76 | 1289.1 | 58.1267 | 61.452 | -3.3253 | 368.7118 | 55.1 | 60.5732 | -5.4732 | 0.97063 | 13-03-2026 13:10 | 338.989 | 345.062 | 1301.8 | 57.5103 | 61.452 | -3.9416 | 368.7118 | 57.2 | 60.5732 | -3.3732 | 0.9824 | 13-03-2026 13:10 | 256.394 | 260.563 | 967.2 | 43.4272 | 45.52 | -2.0928 | 273.1198 | 42.3 | 44.869 | -2.569 | 0.984 | 13-03-2026 13:10 | 251.222 | 256.865 | 963.4 | 42.8108 | 45.52 | -2.7091 | 273.1198 | 41.7 | 44.869 | -3.169 | 0.97803 | 13-03-2026 13:10 | 249.407 | 259.865 | 962.6 | 43.3108 | 45.52 | -2.2091 | 273.1198 | 41.7 | 44.869 | -3.169 | 0.95976 | 13-03-2026 13:10 | 250.614 | 258.917 | 973 | 43.1528 | 45.52 | -2.3671 | 273.1198 | 41.5 | 44.869 | -3.369 | 0.96793 | 13-03-2026 13:10 | 235.131 | 239.061 | 921 | 39.8435 | 43.3066 | -3.4631 | 259.8397 | 39.2 | 42.6873 | -3.4873 | 0.98356 | 13-03-2026 13:10 | 439.8617 | 471.1944 | -31.3327 | 2827.1663 | 428.7 | 464.4563 | -35.7563
13-03-2026 13:00 | 1050 | 48.5 | 341.724 | 347.846 | 1242.3 | 57.9743 | 62.593 | -4.6187 | 375.5582 | 57.6 | 61.6979 | -4.0979 | 0.9824 | 13-03-2026 13:00 | 349.174 | 353.184 | 1257.2 | 58.864 | 62.593 | -3.729 | 375.5582 | 59.3 | 61.6979 | -2.3979 | 0.98865 | 13-03-2026 13:00 | 342.724 | 352.562 | 1234 | 58.7603 | 62.593 | -3.8327 | 375.5582 | 56.9 | 61.6979 | -4.7979 | 0.9721 | 13-03-2026 13:00 | 345.696 | 351.961 | 1244.6 | 58.6602 | 62.593 | -3.9329 | 375.5582 | 56.5 | 61.6979 | -5.1979 | 0.9822 | 13-03-2026 13:00 | 259.312 | 263.502 | 924.9 | 43.917 | 46.3652 | -2.4482 | 278.1912 | 42.8 | 45.7022 | -2.9022 | 0.9841 | 13-03-2026 13:00 | 254.833 | 260.27 | 921.7 | 43.3783 | 46.3652 | -2.9869 | 278.1912 | 42.1 | 45.7022 | -3.6022 | 0.97911 | 13-03-2026 13:00 | 255.632 | 261.259 | 920.9 | 43.5432 | 46.3652 | -2.822 | 278.1912 | 42.2 | 45.7022 | -3.5022 | 0.97846 | 13-03-2026 13:00 | 256.17 | 263.86 | 931.5 | 43.9767 | 46.3652 | -2.3885 | 278.1912 | 42.5 | 45.7022 | -3.2022 | 0.97086 | 13-03-2026 13:00 | 241.778 | 245.734 | 881.8 | 40.9557 | 44.1108 | -3.1551 | 264.6645 | 40.1 | 43.48 | -3.38 | 0.9839 | 13-03-2026 13:00 | 450.0297 | 479.9437 | -29.914 | 2879.6621 | 440 | 473.0805 | -33.0805
13-03-2026 12:50 | 1044 | 48.5 | 340.456 | 346.591 | 1184.7 | 57.7652 | 62.2354 | -4.4702 | 373.4121 | 57.6 | 61.3454 | -3.7454 | 0.9823 | 13-03-2026 12:50 | 345.652 | 351.952 | 1197.9 | 58.6587 | 62.2354 | -3.5767 | 373.4121 | 55.4 | 61.3454 | -5.9454 | 0.9821 | 13-03-2026 12:50 | 338.573 | 348.686 | 1177.1 | 58.1143 | 62.2354 | -4.121 | 373.4121 | 56.3 | 61.3454 | -5.0454 | 0.971 | 13-03-2026 12:50 | 341.469 | 347.693 | 1188.1 | 57.9488 | 62.2354 | -4.2865 | 373.4121 | 56.3 | 61.3454 | -5.0454 | 0.9821 | 13-03-2026 12:50 | 255.378 | 259.583 | 882.1 | 43.2638 | 46.1003 | -2.8364 | 276.6016 | 41.9 | 45.441 | -3.541 | 0.9838 | 13-03-2026 12:50 | 251.257 | 256.049 | 879.6 | 42.6748 | 46.1003 | -3.4254 | 276.6016 | 41.5 | 45.441 | -3.941 | 0.98128 | 13-03-2026 12:50 | 252.119 | 257.684 | 878.7 | 42.9473 | 46.1003 | -3.1529 | 276.6016 | 41.5 | 45.441 | -3.941 | 0.9784 | 13-03-2026 12:50 | 254.131 | 261.504 | 889 | 43.584 | 46.1003 | -2.5163 | 276.6016 | 42.4 | 45.441 | -3.041 | 0.97181 | 13-03-2026 12:50 | 239.471 | 243.39 | 841.7 | 40.565 | 43.8587 | -3.2937 | 263.1521 | 39.7 | 43.2315 | -3.5315 | 0.9839 | 13-03-2026 12:50 | 445.522 | 477.2012 | -31.6792 | 2863.2069 | 432.6 | 470.3772 | -37.7772
13-03-2026 12:40 | 1035 | 48.5 | 339.596 | 345.61 | 1127.1 | 57.6017 | 61.6988 | -4.0972 | 370.1931 | 54.4 | 60.8165 | -6.4165 | 0.9826 | 13-03-2026 12:40 | 345.616 | 351.453 | 1142.5 | 58.5755 | 61.6988 | -3.1233 | 370.1931 | 56.7 | 60.8165 | -4.1165 | 0.98339 | 13-03-2026 12:40 | 335.413 | 345.087 | 1120.8 | 57.5145 | 61.6988 | -4.1843 | 370.1931 | 55 | 60.8165 | -5.8165 | 0.97197 | 13-03-2026 12:40 | 341.559 | 347.678 | 1131.8 | 57.9463 | 61.6988 | -3.7525 | 370.1931 | 55.5 | 60.8165 | -5.3165 | 0.9824 | 13-03-2026 12:40 | 252.621 | 256.755 | 840.2 | 42.7925 | 45.7028 | -2.9103 | 274.2171 | 41.4 | 45.0493 | -3.6493 | 0.9839 | 13-03-2026 12:40 | 251.602 | 256.351 | 838.1 | 42.7252 | 45.7028 | -2.9777 | 274.2171 | 40.9 | 45.0493 | -4.1493 | 0.98147 | 13-03-2026 12:40 | 250.371 | 255.583 | 837.2 | 42.5972 | 45.7028 | -3.1057 | 274.2171 | 41.7 | 45.0493 | -3.3493 | 0.97961 | 13-03-2026 12:40 | 255.981 | 263.307 | 846.6 | 43.8845 | 45.7028 | -1.8183 | 274.2171 | 41.4 | 45.0493 | -3.6493 | 0.97218 | 13-03-2026 12:40 | 240.548 | 244.579 | 802 | 40.7632 | 43.4806 | -2.7174 | 260.8836 | 39.6 | 42.8588 | -3.2588 | 0.98352 | 13-03-2026 12:40 | 444.4005 | 473.0874 | -28.6869 | 2838.5241 | 426.6 | 466.3222 | -39.7222
13-03-2026 12:30 | 994 | 48.5 | 326.478 | 332.259 | 1072.7 | 55.3765 | 59.2547 | -3.8782 | 355.5284 | 55 | 58.4074 | -3.4074 | 0.9826 | 13-03-2026 12:30 | 332.922 | 338.148 | 1085.8 | 56.358 | 59.2547 | -2.8967 | 355.5284 | 56.6 | 58.4074 | -1.8074 | 0.98455 | 13-03-2026 12:30 | 325.677 | 334.788 | 1065.8 | 55.798 | 59.2547 | -3.4567 | 355.5284 | 56.3 | 58.4074 | -2.1074 | 0.97279 | 13-03-2026 12:30 | 328.718 | 334.573 | 1076.3 | 55.7622 | 59.2547 | -3.4926 | 355.5284 | 55.9 | 58.4074 | -2.5074 | 0.9825 | 13-03-2026 12:30 | 245.89 | 249.888 | 798.8 | 41.648 | 43.8924 | -2.2444 | 263.3544 | 41.8 | 43.2647 | -1.4647 | 0.984 | 13-03-2026 12:30 | 242.883 | 247.343 | 797.2 | 41.2238 | 43.8924 | -2.6686 | 263.3544 | 41.4 | 43.2647 | -1.8647 | 0.98197 | 13-03-2026 12:30 | 243.795 | 248.765 | 795.5 | 41.4608 | 43.8924 | -2.4316 | 263.3544 | 40.7 | 43.2647 | -2.5647 | 0.98002 | 13-03-2026 12:30 | 246.021 | 253.182 | 805.2 | 42.197 | 43.8924 | -1.6954 | 263.3544 | 41.1 | 43.2647 | -2.1647 | 0.97172 | 13-03-2026 12:30 | 232.439 | 236.194 | 762.4 | 39.3657 | 41.7582 | -2.3925 | 250.5491 | 38.9 | 41.161 | -2.261 | 0.9841 | 13-03-2026 12:30 | 429.19 | 454.3467 | -25.1567 | 2726.0802 | 427.7 | 447.8495 | -20.1495
13-03-2026 12:20 | 1026 | 48.79 | 340.117 | 346.069 | 1017.7 | 57.6782 | 61.0947 | -3.4165 | 366.5681 | 53.1 | 60.221 | -7.121 | 0.9828 | 13-03-2026 12:20 | 348.291 | 354.423 | 1029.2 | 59.0705 | 61.0947 | -2.0242 | 366.5681 | 52.4 | 60.221 | -7.821 | 0.9827 | 13-03-2026 12:20 | 338.224 | 347.575 | 1009.5 | 57.9292 | 61.0947 | -3.1655 | 366.5681 | 51.6 | 60.221 | -8.621 | 0.9731 | 13-03-2026 12:20 | 342.147 | 348.206 | 1020.4 | 58.0343 | 61.0947 | -3.0604 | 366.5681 | 52.1 | 60.221 | -8.121 | 0.9826 | 13-03-2026 12:20 | 254.08 | 258.145 | 757 | 43.0242 | 45.2553 | -2.2312 | 271.5319 | 39.4 | 44.6082 | -5.2082 | 0.98425 | 13-03-2026 12:20 | 252.483 | 257.39 | 755.8 | 42.8983 | 45.2553 | -2.357 | 271.5319 | 38.8 | 44.6082 | -5.8082 | 0.98094 | 13-03-2026 12:20 | 251.88 | 257.356 | 754.8 | 42.8927 | 45.2553 | -2.3627 | 271.5319 | 39 | 44.6082 | -5.6082 | 0.97872 | 13-03-2026 12:20 | 254.432 | 261.784 | 764.1 | 43.6307 | 45.2553 | -1.6247 | 271.5319 | 39.3 | 44.6082 | -5.3082 | 0.97192 | 13-03-2026 12:20 | 241.037 | 244.857 | 723.5 | 40.8095 | 43.0548 | -2.2453 | 258.329 | 37 | 42.4392 | -5.4392 | 0.9844 | 13-03-2026 12:20 | 445.9675 | 468.4549 | -22.4874 | 2810.7293 | 402.7 | 461.756 | -59.056
13-03-2026 12:10 | 443 | 48.5 | 195.329 | 198.102 | 964.6 | 33.017 | 26.4083 | 6.6087 | 158.4498 | 32.2 | 26.0307 | 6.1693 | 0.986 | 13-03-2026 12:10 | 139.441 | 167.442 | 976.8 | 27.907 | 26.4083 | 1.4987 | 158.4498 | 34.2 | 26.0307 | 8.1693 | 0.83277 | 13-03-2026 12:10 | 168.164 | 170.534 | 957.9 | 28.4223 | 26.4083 | 2.014 | 158.4498 | 32.2 | 26.0307 | 6.1693 | 0.9861 | 13-03-2026 12:10 | 156.122 | 158.339 | 968.3 | 26.3898 | 26.4083 | -0.018463 | 158.4498 | 33.1 | 26.0307 | 7.0693 | 0.986 | 13-03-2026 12:10 | 118.437 | 120.058 | 717.6 | 20.0097 | 19.5617 | 0.44797 | 117.3702 | 24.7 | 19.282 | 5.418 | 0.9865 | 13-03-2026 12:10 | 116.481 | 118.084 | 717 | 19.6807 | 19.5617 | 0.11897 | 117.3702 | 24.5 | 19.282 | 5.218 | 0.98642 | 13-03-2026 12:10 | 120.42 | 122.827 | 715.8 | 20.4712 | 19.5617 | 0.90947 | 117.3702 | 24.4 | 19.282 | 5.118 | 0.9804 | 13-03-2026 12:10 | 124.006 | 128.512 | 724.8 | 21.4187 | 19.5617 | 1.857 | 117.3702 | 24.6 | 19.282 | 5.318 | 0.96494 | 13-03-2026 12:10 | 115.025 | 117.54 | 686.5 | 19.59 | 18.6105 | 0.97946 | 111.6632 | 24 | 18.3444 | 5.6556 | 0.9786 | 13-03-2026 12:10 | 216.9063 | 202.4905 | 14.4158 | 1214.9432 | 253.9 | 199.5949 | 54.3051
13-03-2026 12:00 | 1134 | 48.5 | 352.898 | 358.381 | 932.4 | 59.7302 | 67.6005 | -7.8703 | 405.6028 | 41.3 | 66.6338 | -25.3338 | 0.9847 | 13-03-2026 12:00 | 352.777 | 358.258 | 942.6 | 59.7097 | 67.6005 | -7.8908 | 405.6028 | 40.9 | 66.6338 | -25.7338 | 0.9847 | 13-03-2026 12:00 | 352.794 | 362.688 | 925.7 | 60.448 | 67.6005 | -7.1525 | 405.6028 | 42.1 | 66.6338 | -24.5338 | 0.97272 | 13-03-2026 12:00 | 352.729 | 358.246 | 935.2 | 59.7077 | 67.6005 | -7.8928 | 405.6028 | 42.2 | 66.6338 | -24.4338 | 0.9846 | 13-03-2026 12:00 | 283.977 | 288.624 | 692.9 | 48.104 | 50.0744 | -1.9704 | 300.4465 | 31.9 | 49.3584 | -17.4584 | 0.9839 | 13-03-2026 12:00 | 281.088 | 286.65 | 692.5 | 47.775 | 50.0744 | -2.2994 | 300.4465 | 31.5 | 49.3584 | -17.8584 | 0.9806 | 13-03-2026 12:00 | 281.174 | 287.332 | 691.4 | 47.8887 | 50.0744 | -2.1858 | 300.4465 | 31.5 | 49.3584 | -17.8584 | 0.97857 | 13-03-2026 12:00 | 283.931 | 292.451 | 700.2 | 48.7418 | 50.0744 | -1.3326 | 300.4465 | 31.8 | 49.3584 | -17.5584 | 0.97087 | 13-03-2026 12:00 | 268.466 | 272.859 | 662.5 | 45.4765 | 47.6396 | -2.1631 | 285.8377 | 29.4 | 46.9584 | -17.5584 | 0.9839 | 13-03-2026 12:00 | 477.5815 | 518.3392 | -40.7577 | 3110.0351 | 322.6 | 510.9269 | -188.3269
13-03-2026 11:50 | 942 | 48.5 | 308.38 | 313.649 | 891.1 | 52.2748 | 56.1549 | -3.8801 | 336.9293 | 55.3 | 55.3519 | -0.051874 | 0.9832 | 13-03-2026 11:50 | 298.255 | 314.491 | 901.7 | 52.4152 | 56.1549 | -3.7397 | 336.9293 | 55.6 | 55.3519 | 0.24813 | 0.94837 | 13-03-2026 11:50 | 301.515 | 312.578 | 883.6 | 52.0963 | 56.1549 | -4.0586 | 336.9293 | 53.5 | 55.3519 | -1.8519 | 0.96461 | 13-03-2026 11:50 | 299.502 | 303.636 | 893 | 50.606 | 56.1549 | -5.5489 | 336.9293 | 54.3 | 55.3519 | -1.0519 | 0.98639 | 13-03-2026 11:50 | 230.674 | 234.377 | 661 | 39.0628 | 41.5962 | -2.5334 | 249.5773 | 40.3 | 41.0014 | -0.70139 | 0.9842 | 13-03-2026 11:50 | 220.768 | 226.38 | 661 | 37.73 | 41.5962 | -3.8662 | 249.5773 | 40.1 | 41.0014 | -0.90139 | 0.97521 | 13-03-2026 11:50 | 223.421 | 227.571 | 659.9 | 37.9285 | 41.5962 | -3.6677 | 249.5773 | 40 | 41.0014 | -1.0014 | 0.98176 | 13-03-2026 11:50 | 222.536 | 229.449 | 668.4 | 38.2415 | 41.5962 | -3.3547 | 249.5773 | 40.5 | 41.0014 | -0.50139 | 0.96987 | 13-03-2026 11:50 | 208.978 | 212.483 | 633.1 | 35.4138 | 39.5736 | -4.1598 | 237.4419 | 38.2 | 39.0077 | -0.80774 | 0.9835 | 13-03-2026 11:50 | 395.769 | 430.5781 | -34.8091 | 2583.4683 | 417.8 | 424.4208 | -6.6208
13-03-2026 11:40 | 970 | 48.22 | 318.565 | 324.037 | 835.8 | 54.0062 | 57.8858 | -3.8796 | 347.3147 | 51.3 | 57.058 | -5.758 | 0.98311 | 13-03-2026 11:40 | 324.009 | 329.747 | 846.1 | 54.9578 | 57.8858 | -2.9279 | 347.3147 | 53.6 | 57.058 | -3.458 |  | 13-03-2026 11:40 | 317.25 | 326.44 | 830.1 | 54.4067 | 57.8858 | -3.4791 | 347.3147 | 52.4 | 57.058 | -4.658 | 0.97185 | 13-03-2026 11:40 | 320.919 | 326.602 | 838.7 | 54.4337 | 57.8858 | -3.4521 | 347.3147 | 53.9 | 57.058 | -3.158 | 0.9826 | 13-03-2026 11:40 | 238.836 | 242.695 | 620.7 | 40.4492 | 42.8784 | -2.4292 | 257.2701 | 39.6 | 42.2652 | -2.6652 | 0.9841 | 13-03-2026 11:40 | 237.396 | 242.298 | 620.9 | 40.383 | 42.8784 | -2.4954 | 257.2701 | 39.3 | 42.2652 | -2.9652 | 0.97977 | 13-03-2026 11:40 | 237.27 | 241.998 | 619.9 | 40.333 | 42.8784 | -2.5454 | 257.2701 | 39.3 | 42.2652 | -2.9652 | 0.98046 | 13-03-2026 11:40 | 240.756 | 247.634 | 627.9 | 41.2723 | 42.8784 | -1.606 | 257.2701 | 39.7 | 42.2652 | -2.5652 | 0.97223 | 13-03-2026 11:40 | 227.658 | 231.289 | 594.9 | 38.5482 | 40.7934 | -2.2453 | 244.7607 | 37.7 | 40.2101 | -2.5101 | 0.9843 | 13-03-2026 11:40 | 418.79 | 443.85 | -25.06 | 2663.1 | 406.8 | 437.5029 | -30.7029
13-03-2026 11:30 | 956 | 48.5 | 314.584 | 320.024 | 784.5 | 53.3373 | 56.9895 | -3.6521 | 341.9368 | 53.1 | 56.1745 | -3.0745 | 0.983 | 13-03-2026 11:30 | 320.404 | 326.011 | 792.5 | 54.3352 | 56.9895 | -2.6543 | 341.9368 | 54.7 | 56.1745 | -1.4745 | 0.9828 | 13-03-2026 11:30 | 312.831 | 321.366 | 777.7 | 53.561 | 56.9895 | -3.4285 | 341.9368 | 52 | 56.1745 | -4.1745 | 0.97344 | 13-03-2026 11:30 | 316.553 | 321.943 | 784.8 | 53.6572 | 56.9895 | -3.3323 | 341.9368 | 51.7 | 56.1745 | -4.4745 | 0.98326 | 13-03-2026 11:30 | 235.931 | 239.719 | 581.1 | 39.9532 | 42.2144 | -2.2612 | 253.2865 | 39.1 | 41.6108 | -2.5108 | 0.9842 | 13-03-2026 11:30 | 234.075 | 238.297 | 581.6 | 39.7162 | 42.2144 | -2.4982 | 253.2865 | 38.8 | 41.6108 | -2.8108 | 0.98228 | 13-03-2026 11:30 | 234.03 | 238.994 | 580.6 | 39.8323 | 42.2144 | -2.3821 | 253.2865 | 38.8 | 41.6108 | -2.8108 | 0.97923 | 13-03-2026 11:30 | 236.403 | 243.571 | 588.2 | 40.5952 | 42.2144 | -1.6192 | 253.2865 | 39.3 | 41.6108 | -2.3108 | 0.97057 | 13-03-2026 11:30 | 224.168 | 227.628 | 557.2 | 37.938 | 40.1618 | -2.2238 | 240.9707 | 37.6 | 39.5875 | -1.9875 | 0.9848 | 13-03-2026 11:30 | 412.9255 | 436.9773 | -24.0518 | 2621.8638 | 405.1 | 430.7285 | -25.6285
13-03-2026 11:20 | 943 | 48.79 | 312.712 | 318.088 | 731.4 | 53.0147 | 56.1523 | -3.1377 | 336.914 | 50.8 | 55.3494 | -4.5494 | 0.9831 | 13-03-2026 11:20 | 317.287 | 322.807 | 737.8 | 53.8012 | 56.1523 | -2.3512 | 336.914 | 50 | 55.3494 | -5.3494 | 0.9829 | 13-03-2026 11:20 | 310.961 | 319.748 | 725.7 | 53.2913 | 56.1523 | -2.861 | 336.914 | 50.6 | 55.3494 | -4.7494 | 0.97252 | 13-03-2026 11:20 | 313.946 | 319.408 | 733.1 | 53.2347 | 56.1523 | -2.9177 | 336.914 | 51.8 | 55.3494 | -3.5494 | 0.9829 | 13-03-2026 11:20 | 234.367 | 238.081 | 542 | 39.6802 | 41.5943 | -1.9142 | 249.5659 | 38.6 | 40.9995 | -2.3995 | 0.9844 | 13-03-2026 11:20 | 232.434 | 236.824 | 542.8 | 39.4707 | 41.5943 | -2.1237 | 249.5659 | 38.3 | 40.9995 | -2.6995 | 0.98146 | 13-03-2026 11:20 | 232.875 | 237.29 | 541.8 | 39.5483 | 41.5943 | -2.046 | 249.5659 | 38.4 | 40.9995 | -2.5995 | 0.98139 | 13-03-2026 11:20 | 235.415 | 242.303 | 548.9 | 40.3838 | 41.5943 | -1.2105 | 249.5659 | 38.8 | 40.9995 | -2.1995 | 0.97157 | 13-03-2026 11:20 | 222.634 | 226.07 | 519.6 | 37.6783 | 39.5718 | -1.8935 | 237.4311 | 36.2 | 39.006 | -2.806 | 0.9848 | 13-03-2026 11:20 | 410.1032 | 430.5584 | -20.4553 | 2583.3506 | 393.5 | 424.4014 | -30.9014
13-03-2026 11:10 | 920 | 48.79 | 305.754 | 311.01 | 680.6 | 51.835 | 54.7828 | -2.9478 | 328.6966 | 51.6 | 53.9994 | -2.3994 | 0.9831 | 13-03-2026 11:10 | 310.215 | 315.58 | 687.8 | 52.5967 | 54.7828 | -2.1861 | 328.6966 | 51.8 | 53.9994 | -2.1994 | 0.983 | 13-03-2026 11:10 | 303.341 | 311.895 | 675.1 | 51.9825 | 54.7828 | -2.8003 | 328.6966 | 50.7 | 53.9994 | -3.2994 | 0.97257 | 13-03-2026 11:10 | 306.765 | 312.102 | 681.3 | 52.017 | 54.7828 | -2.7658 | 328.6966 | 50.4 | 53.9994 | -3.5994 | 0.9829 | 13-03-2026 11:10 | 227.639 | 231.27 | 503.4 | 38.545 | 40.5798 | -2.0348 | 243.4789 | 37.5 | 39.9995 | -2.4995 | 0.9843 | 13-03-2026 11:10 | 226.739 | 230.859 | 504.5 | 38.4765 | 40.5798 | -2.1033 | 243.4789 | 37.3 | 39.9995 | -2.6995 | 0.98215 | 13-03-2026 11:10 | 226.797 | 231.298 | 503.4 | 38.5497 | 40.5798 | -2.0302 | 243.4789 | 37.8 | 39.9995 | -2.1995 | 0.98054 | 13-03-2026 11:10 | 229.658 | 236.555 | 510.1 | 39.4258 | 40.5798 | -1.154 | 243.4789 | 38.1 | 39.9995 | -1.8995 | 0.97084 | 13-03-2026 11:10 | 216.944 | 220.337 | 483.4 | 36.7228 | 38.6067 | -1.8838 | 231.6401 | 36 | 38.0546 | -2.0546 | 0.9846 | 13-03-2026 11:10 | 400.151 | 420.057 | -19.906 | 2520.342 | 391.2 | 414.0502 | -22.8502
13-03-2026 11:00 | 899 | 48.79 | 301.51 | 306.568 | 629 | 51.0947 | 53.5323 | -2.4376 | 321.1937 | 49.8 | 52.7668 | -2.9668 | 0.9835 | 13-03-2026 11:00 | 303.284 | 310.988 | 636 | 51.8313 | 53.5323 | -1.701 | 321.1937 | 51.1 | 52.7668 | -1.6668 | 0.97523 | 13-03-2026 11:00 | 299.812 | 307.817 | 624.4 | 51.3028 | 53.5323 | -2.2295 | 321.1937 | 49.4 | 52.7668 | -3.3668 | 0.97399 | 13-03-2026 11:00 | 302.334 | 307.449 | 630.9 | 51.2415 | 53.5323 | -2.2908 | 321.1937 | 50 | 52.7668 | -2.7668 | 0.98336 | 13-03-2026 11:00 | 225.396 | 228.898 | 465.9 | 38.1497 | 39.6535 | -1.5039 | 237.9213 | 37.1 | 39.0865 | -1.9865 | 0.9847 | 13-03-2026 11:00 | 224.259 | 228.055 | 467.2 | 38.0092 | 39.6535 | -1.6444 | 237.9213 | 37 | 39.0865 | -2.0865 | 0.98335 | 13-03-2026 11:00 | 224.05 | 228.409 | 465.6 | 38.0682 | 39.6535 | -1.5854 | 237.9213 | 36.4 | 39.0865 | -2.6865 | 0.98092 | 13-03-2026 11:00 | 225.92 | 232.601 | 472 | 38.7668 | 39.6535 | -0.88671 | 237.9213 | 36.8 | 39.0865 | -2.2865 | 0.97128 | 13-03-2026 11:00 | 214.182 | 217.466 | 447.4 | 36.2443 | 37.7254 | -1.4811 | 226.3526 | 35.4 | 37.186 | -1.786 | 0.9849 | 13-03-2026 11:00 | 394.7085 | 410.4688 | -15.7603 | 2462.8125 | 383 | 404.599 | -21.599
13-03-2026 10:50 | 870 | 48.79 | 293.591 | 298.456 | 579.2 | 49.7427 | 51.8054 | -2.0628 | 310.8326 | 47.4 | 51.0646 | -3.6646 | 0.9837 | 13-03-2026 10:50 | 296.792 | 301.741 | 584.9 | 50.2902 | 51.8054 | -1.5153 | 310.8326 | 48 | 51.0646 | -3.0646 | 0.9836 | 13-03-2026 10:50 | 291.456 | 299.139 | 575 | 49.8565 | 51.8054 | -1.9489 | 310.8326 | 47.6 | 51.0646 | -3.4646 | 0.97432 | 13-03-2026 10:50 | 293.764 | 298.662 | 580.9 | 49.777 | 51.8054 | -2.0284 | 310.8326 | 48 | 51.0646 | -3.0646 | 0.9836 | 13-03-2026 10:50 | 218.279 | 221.603 | 428.8 | 36.9338 | 38.3744 | -1.4406 | 230.2464 | 35.7 | 37.8256 | -2.1256 | 0.985 | 13-03-2026 10:50 | 217.661 | 221.796 | 430.2 | 36.966 | 38.3744 | -1.4084 | 230.2464 | 35.5 | 37.8256 | -2.3256 | 0.98136 | 13-03-2026 10:50 | 216.87 | 220.794 | 429.2 | 36.799 | 38.3744 | -1.5754 | 230.2464 | 35.4 | 37.8256 | -2.4256 | 0.98223 | 13-03-2026 10:50 | 219.205 | 225.703 | 435.2 | 37.6172 | 38.3744 | -0.75723 | 230.2464 | 36.4 | 37.8256 | -1.4256 | 0.97121 | 13-03-2026 10:50 | 208.402 | 211.528 | 412 | 35.2547 | 36.5085 | -1.2538 | 219.0509 | 34 | 35.9864 | -1.9864 | 0.98522 | 13-03-2026 10:50 | 383.237 | 397.2278 | -13.9908 | 2383.3669 | 368 | 391.5475 | -23.5475
13-03-2026 10:40 | 840 | 48.79 | 284.646 | 289.274 | 531.8 | 48.2123 | 50.019 | -1.8067 | 300.1143 | 46.8 | 49.3038 | -2.5038 | 0.984 | 13-03-2026 10:40 | 287.211 | 291.881 | 536.9 | 48.6468 | 50.019 | -1.3722 | 300.1143 | 47.4 | 49.3038 | -1.9038 | 0.984 | 13-03-2026 10:40 | 281.996 | 289.23 | 527.4 | 48.205 | 50.019 | -1.814 | 300.1143 | 45.8 | 49.3038 | -3.5038 | 0.97499 | 13-03-2026 10:40 | 284.222 | 288.932 | 532.9 | 48.1553 | 50.019 | -1.8637 | 300.1143 | 46.9 | 49.3038 | -2.4038 | 0.9837 | 13-03-2026 10:40 | 211.437 | 214.635 | 393.1 | 35.7725 | 37.0511 | -1.2786 | 222.3069 | 34.8 | 36.5213 | -1.7213 | 0.9851 | 13-03-2026 10:40 | 210.079 | 213.824 | 394.7 | 35.6373 | 37.0511 | -1.4138 | 222.3069 | 34.7 | 36.5213 | -1.8213 | 0.98249 | 13-03-2026 10:40 | 210.132 | 213.79 | 393.8 | 35.6317 | 37.0511 | -1.4195 | 222.3069 | 34.7 | 36.5213 | -1.8213 | 0.98289 | 13-03-2026 10:40 | 212.28 | 218.625 | 398.8 | 36.4375 | 37.0511 | -0.61364 | 222.3069 | 34.5 | 36.5213 | -2.0213 | 0.97098 | 13-03-2026 10:40 | 200.925 | 203.947 | 378 | 33.9912 | 35.2496 | -1.2584 | 211.4974 | 32.7 | 34.7455 | -2.0455 | 0.98518 | 13-03-2026 10:40 | 370.6897 | 383.5303 | -12.8406 | 2301.1819 | 358.3 | 378.0458 | -19.7458
13-03-2026 10:30 | 810 | 49.08 | 275.374 | 279.766 | 485 | 46.6277 | 48.1792 | -1.5516 | 289.0755 | 45.1 | 47.4903 | -2.3903 | 0.9843 | 13-03-2026 10:30 | 278.889 | 283.395 | 489.5 | 47.2325 | 48.1792 | -0.94675 | 289.0755 | 45.7 | 47.4903 | -1.7903 | 0.9841 | 13-03-2026 10:30 | 272.883 | 279.955 | 481.6 | 46.6592 | 48.1792 | -1.5201 | 289.0755 | 44.8 | 47.4903 | -2.6903 | 0.97474 | 13-03-2026 10:30 | 275.676 | 280.159 | 486 | 46.6932 | 48.1792 | -1.4861 | 289.0755 | 44.9 | 47.4903 | -2.5903 | 0.984 | 13-03-2026 10:30 | 204.206 | 207.253 | 358.3 | 34.5422 | 35.6883 | -1.1462 | 214.13 | 33.2 | 35.178 | -1.978 | 0.9853 | 13-03-2026 10:30 | 203.938 | 207.305 | 360 | 34.5508 | 35.6883 | -1.1375 | 214.13 | 33.6 | 35.178 | -1.578 | 0.98376 | 13-03-2026 10:30 | 203.273 | 207.131 | 359.1 | 34.5218 | 35.6883 | -1.1665 | 214.13 | 33.5 | 35.178 | -1.678 | 0.98137 | 13-03-2026 10:30 | 205.756 | 211.634 | 364.3 | 35.2723 | 35.6883 | -0.416 | 214.13 | 34 | 35.178 | -1.178 | 0.97223 | 13-03-2026 10:30 | 194.988 | 197.877 | 345.3 | 32.9795 | 33.953 | -0.97353 | 203.7182 | 32.2 | 33.4675 | -1.2675 | 0.9854 | 13-03-2026 10:30 | 359.0792 | 369.4233 | -10.3442 | 2216.54 | 347 | 364.1406 | -17.1406
13-03-2026 10:20 | 779 | 49.36 | 265.158 | 269.305 | 439.9 | 44.8842 | 46.2858 | -1.4016 | 277.7146 | 43.2 | 45.6239 | -2.4239 | 0.9846 | 13-03-2026 10:20 | 269.054 | 273.556 | 443.8 | 45.5927 | 46.2858 | -0.69309 | 277.7146 | 45.1 | 45.6239 | -0.52387 | 0.98354 | 13-03-2026 10:20 | 263.806 | 270.317 | 436.8 | 45.0528 | 46.2858 | -1.2329 | 277.7146 | 43.4 | 45.6239 | -2.2239 | 0.97591 | 13-03-2026 10:20 | 267.271 | 271.534 | 441.1 | 45.2557 | 46.2858 | -1.0301 | 277.7146 | 43.9 | 45.6239 | -1.7239 | 0.9843 | 13-03-2026 10:20 | 197.933 | 200.845 | 325.1 | 33.4742 | 34.2857 | -0.81158 | 205.7145 | 32.6 | 33.7955 | -1.1955 | 0.9855 | 13-03-2026 10:20 | 197.909 | 200.965 | 326.4 | 33.4942 | 34.2857 | -0.79158 | 205.7145 | 32.6 | 33.7955 | -1.1955 | 0.98479 | 13-03-2026 10:20 | 197.891 | 201.265 | 325.6 | 33.5442 | 34.2857 | -0.74158 | 205.7145 | 32.7 | 33.7955 | -1.0955 | 0.98324 | 13-03-2026 10:20 | 200.692 | 206.829 | 330.3 | 34.4715 | 34.2857 | 0.18575 | 205.7145 | 33 | 33.7955 | -0.79546 | 0.97033 | 13-03-2026 10:20 | 190.046 | 192.83 | 313.1 | 32.1383 | 32.6186 | -0.48031 | 195.7119 | 31.7 | 32.1522 | -0.4522 | 0.98556 | 13-03-2026 10:20 | 347.9077 | 354.9047 | -6.997 | 2129.4281 | 338.2 | 349.8295 | -11.6295
13-03-2026 10:10 | 751 | 49.36 | 258.944 | 262.967 | 396.7 | 43.8278 | 44.6221 | -0.79425 | 267.7325 | 42.4 | 43.984 | -1.584 | 0.9847 | 13-03-2026 10:10 | 261.111 | 265.222 | 398.7 | 44.2037 | 44.6221 | -0.41842 | 267.7325 | 41.5 | 43.984 | -2.484 | 0.9845 | 13-03-2026 10:10 | 256.995 | 263.414 | 393.4 | 43.9023 | 44.6221 | -0.71975 | 267.7325 | 42 | 43.984 | -1.984 | 0.97563 | 13-03-2026 10:10 | 259.219 | 263.327 | 397.2 | 43.8878 | 44.6221 | -0.73425 | 267.7325 | 42.4 | 43.984 | -1.584 | 0.9844 | 13-03-2026 10:10 | 192.5 | 195.293 | 292.5 | 32.5488 | 33.0534 | -0.50456 | 198.3204 | 31.4 | 32.5807 | -1.1807 | 0.9857 | 13-03-2026 10:10 | 192.223 | 195.131 | 293.8 | 32.5218 | 33.0534 | -0.53156 | 198.3204 | 31 | 32.5807 | -1.5807 | 0.9851 | 13-03-2026 10:10 | 192.313 | 195.632 | 292.9 | 32.6053 | 33.0534 | -0.44806 | 198.3204 | 30.9 | 32.5807 | -1.6807 | 0.98303 | 13-03-2026 10:10 | 194.387 | 199.776 | 297.3 | 33.296 | 33.0534 | 0.2426 | 198.3204 | 31.3 | 32.5807 | -1.2807 | 0.97302 | 13-03-2026 10:10 | 184.129 | 186.781 | 281.4 | 31.1302 | 31.4462 | -0.31605 | 188.6773 | 29.8 | 30.9965 | -1.1965 | 0.9858 | 13-03-2026 10:10 | 337.9238 | 342.1482 | -4.2243 | 2052.8889 | 322.7 | 337.2554 | -14.5554
13-03-2026 10:00 | 713 | 49.08 | 246.764 | 250.496 | 354.3 | 41.7493 | 42.4096 | -0.6603 | 254.4578 | 41.2 | 41.8032 | -0.60317 | 0.9851 | 13-03-2026 10:00 | 249.47 | 254.068 | 357.2 | 42.3447 | 42.4096 | -0.064965 | 254.4578 | 41.2 | 41.8032 | -0.60317 | 0.9819 | 13-03-2026 10:00 | 245.035 | 250.989 | 351.4 | 41.8315 | 42.4096 | -0.57813 | 254.4578 | 39.9 | 41.8032 | -1.9032 | 0.97628 | 13-03-2026 10:00 | 248.021 | 251.824 | 354.8 | 41.9707 | 42.4096 | -0.43897 | 254.4578 | 40.2 | 41.8032 | -1.6032 | 0.9849 | 13-03-2026 10:00 | 183.119 | 185.7 | 261.1 | 30.95 | 31.4145 | -0.46454 | 188.4873 | 29.8 | 30.9653 | -1.1653 | 0.9861 | 13-03-2026 10:00 | 183.728 | 186.337 | 262.8 | 31.0562 | 31.4145 | -0.35838 | 188.4873 | 29.8 | 30.9653 | -1.1653 | 0.986 | 13-03-2026 10:00 | 182.998 | 185.76 | 262 | 30.96 | 31.4145 | -0.45454 | 188.4873 | 29.8 | 30.9653 | -1.1653 | 0.98513 | 13-03-2026 10:00 | 185.181 | 190.582 | 266 | 31.7637 | 31.4145 | 0.34912 | 188.4873 | 30.6 | 30.9653 | -0.36531 | 0.97166 | 13-03-2026 10:00 | 175.682 | 178.158 | 251.6 | 29.693 | 29.887 | -0.19405 | 179.3223 | 28.1 | 29.4597 | -1.3597 | 0.9861 | 13-03-2026 10:00 | 322.319 | 325.1837 | -2.8647 | 1951.1025 | 310.6 | 320.5336 | -9.9336
13-03-2026 09:50 | 670 | 49.08 | 234.202 | 237.672 | 313.1 | 39.612 | 39.852 | -0.23997 | 239.1118 | 37.2 | 39.2821 | -2.0821 |  | 13-03-2026 09:50 | 236.697 | 240.253 | 316 | 40.0422 | 39.852 | 0.1902 | 239.1118 | 38.2 | 39.2821 | -1.0821 |  | 13-03-2026 09:50 | 232.79 | 237.948 | 311.5 | 39.658 | 39.852 | -0.19397 | 239.1118 | 37.6 | 39.2821 | -1.6821 |  | 13-03-2026 09:50 | 234.74 | 238.218 | 314.6 | 39.703 | 39.852 | -0.14897 | 239.1118 | 38.1 | 39.2821 | -1.1821 |  | 13-03-2026 09:50 | 174.044 | 176.479 | 231.3 | 29.4132 | 29.52 | -0.10681 | 177.1199 | 28.2 | 29.0978 | -0.89784 |  | 13-03-2026 09:50 | 174.061 | 176.479 | 233 | 29.4132 | 29.52 | -0.10681 | 177.1199 | 28.5 | 29.0978 | -0.59784 |  | 13-03-2026 09:50 | 174.213 | 176.764 | 232.2 | 29.4607 | 29.52 | -0.05931 | 177.1199 | 28.4 | 29.0978 | -0.69784 |  | 13-03-2026 09:50 | 176.026 | 180.783 | 235.4 | 30.1305 | 29.52 | 0.61052 | 177.1199 | 28.8 | 29.0978 | -0.29784 |  | 13-03-2026 09:50 | 166.548 | 168.879 | 223.5 | 28.1465 | 28.0846 | 0.061899 | 168.5076 | 27.3 | 27.683 | -0.38299 |  | 13-03-2026 09:50 | 305.5792 | 305.5724 | 0.0067866 | 1833.4343 | 292.3 | 301.2027 | -8.9027
13-03-2026 09:40 | 633 | 49.08 | 223.095 | 226.263 | 275.9 | 37.7105 | 37.6512 | 0.059312 | 225.9071 | 35.7 | 37.1128 | -1.4128 |  | 13-03-2026 09:40 | 225.821 | 229.12 | 277.8 | 38.1867 | 37.6512 | 0.53548 | 225.9071 | 36.6 | 37.1128 | -0.51278 |  | 13-03-2026 09:40 | 221.597 | 226.474 | 273.9 | 37.7457 | 37.6512 | 0.094479 | 225.9071 | 35.9 | 37.1128 | -1.2128 |  | 13-03-2026 09:40 | 224.074 | 227.325 | 276.5 | 37.8875 | 37.6512 | 0.23631 | 225.9071 | 36.3 | 37.1128 | -0.81278 |  | 13-03-2026 09:40 | 165.617 | 167.863 | 203.1 | 27.9772 | 27.8898 | 0.087398 | 167.3386 | 26.8 | 27.4909 | -0.69095 |  | 13-03-2026 09:40 | 166.399 | 168.659 | 204.5 | 28.1098 | 27.8898 | 0.22006 | 167.3386 | 27 | 27.4909 | -0.49095 |  | 13-03-2026 09:40 | 165.77 | 168.139 | 203.8 | 28.0232 | 27.8898 | 0.1334 | 167.3386 | 26.9 | 27.4909 | -0.59095 |  | 13-03-2026 09:40 | 167.827 | 172.556 | 206.6 | 28.7593 | 27.8898 | 0.86956 | 167.3386 | 26.8 | 27.4909 | -0.69095 |  | 13-03-2026 09:40 | 159.136 | 161.314 | 196.2 | 26.8857 | 26.5337 | 0.35201 | 159.202 | 25.8 | 26.1542 | -0.35423 |  | 13-03-2026 09:40 | 291.2855 | 288.6975 | 2.588 | 1732.1849 | 277.8 | 284.5691 | -6.7691
13-03-2026 09:30 | 593 | 49.08 | 209.98 | 213.438 | 240.2 | 35.573 | 35.272 | 0.30103 | 211.6318 | 33.9 | 34.7676 | -0.86758 |  | 13-03-2026 09:30 | 212.331 | 215.324 | 241.2 | 35.8873 | 35.272 | 0.61537 | 211.6318 | 33.6 | 34.7676 | -1.1676 |  | 13-03-2026 09:30 | 208.775 | 213.172 | 238 | 35.5287 | 35.272 | 0.2567 | 211.6318 | 34.1 | 34.7676 | -0.66758 |  | 13-03-2026 09:30 | 210.852 | 213.824 | 240.2 | 35.6373 | 35.272 | 0.36537 | 211.6318 | 34.3 | 34.7676 | -0.46758 |  | 13-03-2026 09:30 | 155.666 | 157.732 | 176.3 | 26.2887 | 26.1274 | 0.16128 | 156.7643 | 25.4 | 25.7538 | -0.35376 |  | 13-03-2026 09:30 | 156.262 | 158.32 | 177.5 | 26.3867 | 26.1274 | 0.25928 | 156.7643 | 25.1 | 25.7538 | -0.65376 |  | 13-03-2026 09:30 | 155.807 | 157.875 | 176.9 | 26.3125 | 26.1274 | 0.18512 | 156.7643 | 25.1 | 25.7538 | -0.65376 |  | 13-03-2026 09:30 | 157.918 | 162.352 | 179.8 | 27.0587 | 26.1274 | 0.93128 | 156.7643 | 25.4 | 25.7538 | -0.35376 |  | 13-03-2026 09:30 | 149.706 | 151.709 | 170.4 | 25.2848 | 24.857 | 0.42787 | 149.1418 | 24.1 | 24.5015 | -0.40151 |  | 13-03-2026 09:30 | 273.9577 | 270.4544 | 3.5033 | 1622.7262 | 261 | 266.5869 | -5.5869
13-03-2026 09:20 | 549 | 48.79 | 197.251 | 199.89 | 206.3 | 33.315 | 32.691 | 0.62398 | 196.1461 | 31.8 | 32.2235 | -0.42354 |  | 13-03-2026 09:20 | 198.169 | 201.165 | 207.6 | 33.5275 | 32.691 | 0.83648 | 196.1461 | 33.3 | 32.2235 | 1.0765 |  | 13-03-2026 09:20 | 195.383 | 199.401 | 203.9 | 33.2335 | 32.691 | 0.54248 | 196.1461 | 31 | 32.2235 | -1.2235 |  | 13-03-2026 09:20 | 196.78 | 199.453 | 205.9 | 33.2422 | 32.691 | 0.55115 | 196.1461 | 31.4 | 32.2235 | -0.82354 |  | 13-03-2026 09:20 | 145.582 | 147.431 | 150.9 | 24.5718 | 24.2156 | 0.35627 | 145.2934 | 23.1 | 23.8693 | -0.76929 |  | 13-03-2026 09:20 | 145.985 | 147.863 | 152.4 | 24.6438 | 24.2156 | 0.42827 | 145.2934 | 23.2 | 23.8693 | -0.66929 |  | 13-03-2026 09:20 | 145.968 | 147.861 | 151.8 | 24.6435 | 24.2156 | 0.42793 | 145.2934 | 23.2 | 23.8693 | -0.66929 |  | 13-03-2026 09:20 | 147.875 | 152.333 | 154.4 | 25.3888 | 24.2156 | 1.1733 | 145.2934 | 23.8 | 23.8693 | -0.069285 |  | 13-03-2026 09:20 | 140.148 | 141.98 | 146.3 | 23.6633 | 23.0381 | 0.62522 | 138.2287 | 22.6 | 22.7087 | -0.10867 |  | 13-03-2026 09:20 | 256.2295 | 250.6645 | 5.565 | 1503.9867 | 243.4 | 247.08 | -3.68
13-03-2026 09:10 | 509 | 48.5 | 182.316 | 184.836 | 174.5 | 30.806 | 30.3427 | 0.46328 | 182.0563 | 29 | 29.9088 | -0.90881 |  | 13-03-2026 09:10 | 183.45 | 185.885 | 174.3 | 30.9808 | 30.3427 | 0.63812 | 182.0563 | 28.4 | 29.9088 | -1.5088 |  | 13-03-2026 09:10 | 181.046 | 184.413 | 172.9 | 30.7355 | 30.3427 | 0.39278 | 182.0563 | 28.8 | 29.9088 | -1.1088 |  | 13-03-2026 09:10 | 182.894 | 185.322 | 174.5 | 30.887 | 30.3427 | 0.54428 | 182.0563 | 29.4 | 29.9088 | -0.50881 |  | 13-03-2026 09:10 | 134.736 | 136.442 | 127.8 | 22.7403 | 22.4761 | 0.26425 | 134.8565 | 21.6 | 22.1547 | -0.55468 |  | 13-03-2026 09:10 | 134.061 | 135.744 | 129.2 | 22.624 | 22.4761 | 0.14791 | 134.8565 | 21.5 | 22.1547 | -0.65468 |  | 13-03-2026 09:10 | 135.322 | 137.007 | 128.6 | 22.8345 | 22.4761 | 0.35841 | 134.8565 | 21.5 | 22.1547 | -0.65468 |  | 13-03-2026 09:10 | 137.275 | 141.019 | 130.6 | 23.5032 | 22.4761 | 1.0271 | 134.8565 | 22.2 | 22.1547 | 0.045322 |  | 13-03-2026 09:10 | 130.084 | 131.731 | 123.7 | 21.9552 | 21.3832 | 0.57195 | 128.2993 | 20.7 | 21.0774 | -0.37743 |  | 13-03-2026 09:10 | 237.0665 | 232.6584 | 4.4081 | 1395.9505 | 223.1 | 229.3314 | -6.2314
13-03-2026 09:00 | 464 | 48.22 | 167.078 | 169.122 | 145.5 | 28.187 | 27.6897 | 0.49731 | 166.1382 | 28.4 | 27.2937 | 1.1063 |  | 13-03-2026 09:00 | 167.081 | 170.223 | 145.9 | 28.3705 | 27.6897 | 0.68081 | 166.1382 | 26.8 | 27.2937 | -0.49373 |  | 13-03-2026 09:00 | 165.483 | 168.36 | 144.1 | 28.06 | 27.6897 | 0.37031 | 166.1382 | 26.4 | 27.2937 | -0.89373 |  | 13-03-2026 09:00 | 166.743 | 168.871 | 145.1 | 28.1452 | 27.6897 | 0.45547 | 166.1382 | 26.3 | 27.2937 | -0.99373 |  | 13-03-2026 09:00 | 122.892 | 124.422 | 106.2 | 20.737 | 20.5109 | 0.22612 | 123.0653 | 19.4 | 20.2176 | -0.81758 |  | 13-03-2026 09:00 | 122.77 | 124.261 | 107.7 | 20.7102 | 20.5109 | 0.19928 | 123.0653 | 19.7 | 20.2176 | -0.51758 |  | 13-03-2026 09:00 | 123.592 | 125.118 | 107.1 | 20.853 | 20.5109 | 0.34212 | 123.0653 | 19.8 | 20.2176 | -0.41758 |  | 13-03-2026 09:00 | 125.542 | 128.868 | 108.4 | 21.478 | 20.5109 | 0.96712 | 123.0653 | 19.7 | 20.2176 | -0.51758 |  | 13-03-2026 09:00 | 119.13 | 120.601 | 103 | 20.1002 | 19.5136 | 0.5866 | 117.0814 | 18.9 | 19.2345 | -0.33452 |  | 13-03-2026 09:00 | 216.641 | 212.3159 | 4.3251 | 1273.8953 | 205.4 | 209.2798 | -3.8798
13-03-2026 08:50 | 420 | 47.93 | 149.625 | 151.407 | 117.1 | 25.2345 | 25.0916 | 0.14286 | 150.5498 | 22.2 | 24.7328 | -2.5328 |  | 13-03-2026 08:50 | 151.726 | 153.615 | 119.1 | 25.6025 | 25.0916 | 0.51086 | 150.5498 | 23.6 | 24.7328 | -1.1328 |  | 13-03-2026 08:50 | 149.651 | 151.74 | 117.7 | 25.29 | 25.0916 | 0.19836 | 150.5498 | 23.8 | 24.7328 | -0.93283 |  | 13-03-2026 08:50 | 151.129 | 152.98 | 118.8 | 25.4967 | 25.0916 | 0.40503 | 150.5498 | 24.1 | 24.7328 | -0.63283 |  | 13-03-2026 08:50 | 111.128 | 112.466 | 86.8 | 18.7443 | 18.5864 | 0.15794 | 111.5184 | 17.6 | 18.3206 | -0.72061 |  | 13-03-2026 08:50 | 111.967 | 113.411 | 88 | 18.9018 | 18.5864 | 0.31544 | 111.5184 | 17.8 | 18.3206 | -0.52061 |  | 13-03-2026 08:50 | 111.466 | 112.808 | 87.3 | 18.8013 | 18.5864 | 0.21494 | 111.5184 | 17.5 | 18.3206 | -0.82061 |  | 13-03-2026 08:50 | 113.809 | 116.82 | 88.7 | 19.47 | 18.5864 | 0.8836 | 111.5184 | 17.8 | 18.3206 | -0.52061 |  | 13-03-2026 08:50 | 106.907 | 108.195 | 84.1 | 18.0325 | 17.6827 | 0.34984 | 106.0959 | 16.8 | 17.4298 | -0.62979 |  | 13-03-2026 08:50 | 195.5737 | 192.3948 | 3.1789 | 1154.3688 | 181.2 | 189.6436 | -8.4436
13-03-2026 08:40 | 376 | 41.61 | 134.926 | 136.523 | 94.9 | 22.7538 | 23.0032 | -0.24939 | 138.0194 | 20.9 | 22.6743 | -1.7743 |  | 13-03-2026 08:40 | 133.941 | 135.554 | 95.5 | 22.5923 | 23.0032 | -0.41089 | 138.0194 | 21.8 | 22.6743 | -0.87428 |  | 13-03-2026 08:40 | 133.897 | 135.676 | 93.9 | 22.6127 | 23.0032 | -0.39056 | 138.0194 | 20.7 | 22.6743 | -1.9743 |  | 13-03-2026 08:40 | 134.951 | 136.562 | 94.7 | 22.7603 | 23.0032 | -0.24289 | 138.0194 | 21.2 | 22.6743 | -1.4743 |  | 13-03-2026 08:40 | 99.156 | 100.32 | 69.2 | 16.72 | 17.0394 | -0.31943 | 102.2366 | 15.6 | 16.7958 | -1.1958 |  | 13-03-2026 08:40 | 100.036 | 101.2 | 70.2 | 16.8667 | 17.0394 | -0.17276 | 102.2366 | 15.7 | 16.7958 | -1.0958 |  | 13-03-2026 08:40 | 99.716 | 100.886 | 69.8 | 16.8143 | 17.0394 | -0.22509 | 102.2366 | 15.7 | 16.7958 | -1.0958 |  | 13-03-2026 08:40 | 100.737 | 103.715 | 70.9 | 17.2858 | 17.0394 | 0.24641 | 102.2366 | 15.9 | 16.7958 | -0.89576 |  | 13-03-2026 08:40 | 96.365 | 97.506 | 67.3 | 16.251 | 16.2109 | 0.040095 | 97.2654 | 15.1 | 15.9791 | -0.87909 |  | 13-03-2026 08:40 | 174.657 | 176.3815 | -1.7245 | 1058.2892 | 162.6 | 173.8593 | -11.2593
13-03-2026 08:30 | 331 | 37.31 | 117.92 | 119.268 | 74 | 19.878 | 20.5738 | -0.69576 | 123.4425 | 18.4 | 20.2796 | -1.8796 |  | 13-03-2026 08:30 | 118.327 | 119.704 | 73.7 | 19.9507 | 20.5738 | -0.62309 | 123.4425 | 17.9 | 20.2796 | -2.3796 |  | 13-03-2026 08:30 | 116.992 | 118.529 | 73.2 | 19.7548 | 20.5738 | -0.81892 | 123.4425 | 18.2 | 20.2796 | -2.0796 |  | 13-03-2026 08:30 | 117.504 | 118.859 | 73.5 | 19.8098 | 20.5738 | -0.76392 | 123.4425 | 18 | 20.2796 | -2.2796 |  | 13-03-2026 08:30 | 86.378 | 87.401 | 53.6 | 14.5668 | 15.2398 | -0.67299 | 91.4389 | 13.2 | 15.0219 | -1.8219 |  | 13-03-2026 08:30 | 87.292 | 88.29 | 54.5 | 14.715 | 15.2398 | -0.52482 | 91.4389 | 13.4 | 15.0219 | -1.6219 |  | 13-03-2026 08:30 | 87.118 | 88.126 | 54.1 | 14.6877 | 15.2398 | -0.55215 | 91.4389 | 13.5 | 15.0219 | -1.5219 |  | 13-03-2026 08:30 | 88.336 | 90.711 | 55 | 15.1185 | 15.2398 | -0.12132 | 91.4389 | 13.8 | 15.0219 | -1.2219 |  | 13-03-2026 08:30 | 84.194 | 85.191 | 52.2 | 14.1985 | 14.4988 | -0.3003 | 86.9928 | 13 | 14.2915 | -1.2915 |  | 13-03-2026 08:30 | 152.6798 | 157.7531 | -5.0733 | 946.5187 | 139.4 | 155.4972 | -16.0972
13-03-2026 08:20 | 286 | 37.31 | 100.514 | 101.632 | 55.6 | 16.9387 | 17.7767 | -0.83805 | 106.6603 | 15.1 | 17.5225 | -2.4225 |  | 13-03-2026 08:20 | 100.028 | 101.161 | 55.8 | 16.8602 | 17.7767 | -0.91655 | 106.6603 | 15.9 | 17.5225 | -1.6225 |  | 13-03-2026 08:20 | 99.574 | 100.927 | 55 | 16.8212 | 17.7767 | -0.95555 | 106.6603 | 15.2 | 17.5225 | -2.3225 |  | 13-03-2026 08:20 | 100.68 | 101.82 | 55.5 | 16.97 | 17.7767 | -0.80672 | 106.6603 | 15.4 | 17.5225 | -2.1225 |  | 13-03-2026 08:20 | 73.568 | 74.462 | 40.4 | 12.4103 | 13.1679 | -0.75761 | 79.0077 | 11.3 | 12.9796 | -1.6796 |  | 13-03-2026 08:20 | 74.699 | 75.576 | 41.1 | 12.596 | 13.1679 | -0.57194 | 79.0077 | 11.4 | 12.9796 | -1.5796 |  | 13-03-2026 08:20 | 74.113 | 75.013 | 40.6 | 12.5022 | 13.1679 | -0.66578 | 79.0077 | 11.2 | 12.9796 | -1.7796 |  | 13-03-2026 08:20 | 74.722 | 76.876 | 41.2 | 12.8127 | 13.1679 | -0.35528 | 79.0077 | 11.3 | 12.9796 | -1.6796 |  | 13-03-2026 08:20 | 71.744 | 72.615 | 39.2 | 12.1025 | 12.5277 | -0.42517 | 75.166 | 10.8 | 12.3485 | -1.5485 |  | 13-03-2026 08:20 | 130.0137 | 136.3063 | -6.2927 | 817.8379 | 117.6 | 134.3571 | -16.7571
13-03-2026 08:10 | 234 | 35.3 | 81.614 | 82.538 | 40.5 | 13.7563 | 14.6515 | -0.89519 | 87.9091 | 13 | 14.442 | -1.442 |  | 13-03-2026 08:10 | 81.633 | 82.591 | 39.9 | 13.7652 | 14.6515 | -0.88635 | 87.9091 | 12.6 | 14.442 | -1.842 |  | 13-03-2026 08:10 | 80.36 | 81.287 | 39.8 | 13.5478 | 14.6515 | -1.1037 | 87.9091 | 12.3 | 14.442 | -2.142 |  | 13-03-2026 08:10 | 81.407 | 82.354 | 40.1 | 13.7257 | 14.6515 | -0.92585 | 87.9091 | 12.4 | 14.442 | -2.042 |  | 13-03-2026 08:10 | 59.432 | 60.196 | 29.1 | 10.0327 | 10.853 | -0.82031 | 65.1179 | 9 | 10.6978 | -1.6978 |  | 13-03-2026 08:10 | 60.48 | 61.215 | 29.7 | 10.2025 | 10.853 | -0.65048 | 65.1179 | 9.2 | 10.6978 | -1.4978 |  | 13-03-2026 08:10 | 60.316 | 61.05 | 29.4 | 10.175 | 10.853 | -0.67798 | 65.1179 | 9.2 | 10.6978 | -1.4978 |  | 13-03-2026 08:10 | 60.881 | 62.532 | 29.9 | 10.422 | 10.853 | -0.43098 | 65.1179 | 9.3 | 10.6978 | -1.3978 |  | 13-03-2026 08:10 | 58.248 | 58.993 | 28.4 | 9.8322 | 10.3253 | -0.4931 | 61.9516 | 8.8 | 10.1776 | -1.3776 |  | 13-03-2026 08:10 | 105.4593 | 112.3432 | -6.8839 | 674.0595 | 95.8 | 110.7367 | -14.9367
13-03-2026 08:00 | 193 | 32.43 | 66.43 | 67.21 | 27.5 | 11.2017 | 12.2103 | -1.0086 | 73.2618 | 9.6 | 12.0357 | -2.4357 |  | 13-03-2026 08:00 | 66.01 | 67.262 | 27.3 | 11.2103 | 12.2103 | -0.99997 | 73.2618 | 9.3 | 12.0357 | -2.7357 |  | 13-03-2026 08:00 | 66.221 | 67.012 | 27.5 | 11.1687 | 12.2103 | -1.0416 | 73.2618 | 9.8 | 12.0357 | -2.2357 |  | 13-03-2026 08:00 | 66.632 | 67.448 | 27.7 | 11.2413 | 12.2103 | -0.96897 | 73.2618 | 9.9 | 12.0357 | -2.1357 |  | 13-03-2026 08:00 | 48.668 | 49.359 | 20.1 | 8.2265 | 9.0447 | -0.81817 | 54.268 | 7.2 | 8.9153 | -1.7153 |  | 13-03-2026 08:00 | 49.542 | 50.225 | 20.5 | 8.3708 | 9.0447 | -0.67383 | 54.268 | 7.4 | 8.9153 | -1.5153 |  | 13-03-2026 08:00 | 49.342 | 49.985 | 20.2 | 8.3308 | 9.0447 | -0.71383 | 54.268 | 7.3 | 8.9153 | -1.6153 |  | 13-03-2026 08:00 | 50.224 | 51.421 | 20.6 | 8.5702 | 9.0447 | -0.4745 | 54.268 | 7.5 | 8.9153 | -1.4153 |  | 13-03-2026 08:00 | 47.296 | 47.987 | 19.6 | 7.9978 | 8.6049 | -0.60705 | 51.6293 | 7.1 | 8.4818 | -1.3818 |  | 13-03-2026 08:00 | 86.3182 | 93.6247 | -7.3066 | 561.7484 | 75.1 | 92.2859 | -17.1859
13-03-2026 07:50 | 152 | 28.99 | 51.862 | 52.515 | 17.9 | 8.7525 | 9.7353 | -0.98277 | 58.4116 | 7.3 | 9.5961 | -2.2961 |  | 13-03-2026 07:50 | 51.474 | 52.566 | 18 | 8.761 | 9.7353 | -0.97427 | 58.4116 | 7.4 | 9.5961 | -2.1961 |  | 13-03-2026 07:50 | 51.169 | 51.869 | 17.7 | 8.6448 | 9.7353 | -1.0904 | 58.4116 | 7.2 | 9.5961 | -2.3961 |  | 13-03-2026 07:50 | 51.666 | 52.378 | 17.8 | 8.7297 | 9.7353 | -1.0056 | 58.4116 | 7.2 | 9.5961 | -2.3961 |  | 13-03-2026 07:50 | 37.607 | 38.203 | 12.9 | 6.3672 | 7.2113 | -0.84415 | 43.2679 | 5.3 | 7.1082 | -1.8082 |  | 13-03-2026 07:50 | 38.458 | 39.04 | 13.1 | 6.5067 | 7.2113 | -0.70465 | 43.2679 | 5.4 | 7.1082 | -1.7082 |  | 13-03-2026 07:50 | 38.322 | 38.921 | 12.9 | 6.4868 | 7.2113 | -0.72448 | 43.2679 | 5.4 | 7.1082 | -1.7082 |  | 13-03-2026 07:50 | 39.023 | 40.035 | 13.1 | 6.6725 | 7.2113 | -0.53881 | 43.2679 | 5.4 | 7.1082 | -1.7082 |  | 13-03-2026 07:50 | 36.993 | 37.575 | 12.5 | 6.2625 | 6.8607 | -0.59817 | 41.164 | 5.1 | 6.7626 | -1.6626 |  | 13-03-2026 07:50 | 67.1837 | 74.647 | -7.4634 | 447.8822 | 55.7 | 73.5796 | -17.8796
13-03-2026 07:40 | 106 | 26.12 | 35.731 | 36.294 | 10.6 | 6.049 | 6.8582 | -0.80923 | 41.1494 | 4.7 | 6.7602 | -2.0602 |  | 13-03-2026 07:40 | 35.531 | 36.137 | 10.6 | 6.0228 | 6.8582 | -0.8354 | 41.1494 | 4.7 | 6.7602 | -2.0602 |  | 13-03-2026 07:40 | 35.383 | 35.947 | 10.5 | 5.9912 | 6.8582 | -0.86707 | 41.1494 | 4.7 | 6.7602 | -2.0602 |  | 13-03-2026 07:40 | 35.589 | 36.168 | 10.6 | 6.028 | 6.8582 | -0.83023 | 41.1494 | 4.8 | 6.7602 | -1.9602 |  | 13-03-2026 07:40 | 26.007 | 26.505 | 7.6 | 4.4175 | 5.0802 | -0.66267 | 30.481 | 3.5 | 5.0075 | -1.5075 |  | 13-03-2026 07:40 | 26.559 | 27.051 | 7.7 | 4.5085 | 5.0802 | -0.57167 | 30.481 | 3.5 | 5.0075 | -1.5075 |  | 13-03-2026 07:40 | 26.523 | 27.028 | 7.5 | 4.5047 | 5.0802 | -0.57551 | 30.481 | 3.5 | 5.0075 | -1.5075 |  | 13-03-2026 07:40 | 26.882 | 27.863 | 7.7 | 4.6438 | 5.0802 | -0.43634 | 30.481 | 3.6 | 5.0075 | -1.4075 |  | 13-03-2026 07:40 | 25.477 | 25.965 | 7.4 | 4.3275 | 4.8332 | -0.50566 | 28.9989 | 3.4 | 4.764 | -1.364 |  | 13-03-2026 07:40 | 46.493 | 52.5868 | -6.0938 | 315.5208 | 36.4 | 51.8348 | -15.4348
13-03-2026 07:30 | 63 | 24.39 | 21.832 | 22.296 | 5.9 | 3.716 | 4.1009 | -0.3849 | 24.6054 | 3 | 4.0423 | -1.0423 |  | 13-03-2026 07:30 | 19.965 | 22.428 | 5.9 | 3.738 | 4.1009 | -0.3629 | 24.6054 | 3 | 4.0423 | -1.0423 |  | 13-03-2026 07:30 | 21.543 | 22.016 | 5.8 | 3.6693 | 4.1009 | -0.43157 | 24.6054 | 2.9 | 4.0423 | -1.1423 |  | 13-03-2026 07:30 | 21.538 | 22.089 | 5.8 | 3.6815 | 4.1009 | -0.4194 | 24.6054 | 2.9 | 4.0423 | -1.1423 |  | 13-03-2026 07:30 | 15.661 | 16.263 | 4.1 | 2.7105 | 3.0377 | -0.3272 | 18.2262 | 2.1 | 2.9943 | -0.89426 |  | 13-03-2026 07:30 | 15.973 | 16.362 | 4.2 | 2.727 | 3.0377 | -0.3107 | 18.2262 | 2.2 | 2.9943 | -0.79426 |  | 13-03-2026 07:30 | 15.992 | 16.387 | 4 | 2.7312 | 3.0377 | -0.30654 | 18.2262 | 2.2 | 2.9943 | -0.79426 |  | 13-03-2026 07:30 | 16.232 | 16.94 | 4.1 | 2.8233 | 3.0377 | -0.21437 | 18.2262 | 2.2 | 2.9943 | -0.79426 |  | 13-03-2026 07:30 | 15.238 | 15.621 | 4 | 2.6035 | 2.89 | -0.2865 | 17.34 | 2.1 | 2.8487 | -0.74867 |  | 13-03-2026 07:30 | 28.4003 | 31.4444 | -3.0441 | 188.6664 | 22.6 | 30.9947 | -8.3947
13-03-2026 07:20 | 40 | 23.53 | 14.888 | 15.524 | 2.9 | 2.5873 | 2.6116 | -0.024233 | 15.6694 | 1.9 | 2.5742 | -0.67422 |  | 13-03-2026 07:20 | 14.973 | 15.853 | 2.9 | 2.6422 | 2.6116 | 0.030601 | 15.6694 | 1.8 | 2.5742 | -0.77422 |  | 13-03-2026 07:20 | 15.099 | 15.493 | 2.9 | 2.5822 | 2.6116 | -0.029399 | 15.6694 | 1.8 | 2.5742 | -0.77422 |  | 13-03-2026 07:20 | 15.113 | 15.692 | 2.9 | 2.6153 | 2.6116 | 0.0037675 | 15.6694 | 1.8 | 2.5742 | -0.77422 |  | 13-03-2026 07:20 | 10.951 | 11.516 | 2 | 1.9193 | 1.9345 | -0.01516 | 11.607 | 1.3 | 1.9068 | -0.60683 |  | 13-03-2026 07:20 | 11.127 | 11.494 | 2 | 1.9157 | 1.9345 | -0.018827 | 11.607 | 1.3 | 1.9068 | -0.60683 |  | 13-03-2026 07:20 | 11.145 | 11.513 | 1.8 | 1.9188 | 1.9345 | -0.01566 | 11.607 | 1.3 | 1.9068 | -0.60683 |  | 13-03-2026 07:20 | 11.356 | 12.075 | 1.9 | 2.0125 | 1.9345 | 0.078007 | 11.607 | 1.4 | 1.9068 | -0.50683 |  | 13-03-2026 07:20 | 10.587 | 10.944 | 1.9 | 1.824 | 1.8404 | -0.016431 | 11.0426 | 1.2 | 1.8141 | -0.61411 |  | 13-03-2026 07:20 | 20.0173 | 20.0247 | -0.0073337 | 120.148 | 13.8 | 19.7383 | -5.9383
13-03-2026 07:10 | 22 | 23.25 | 7.868 | 8.18 | 1 | 1.3633 | 1.4378 | -0.074428 | 8.6266 | 0.8 | 1.4172 | -0.6172 |  | 13-03-2026 07:10 | 8.431 | 9.036 | 1.1 | 1.506 | 1.4378 | 0.068238 | 8.6266 | 0.9 | 1.4172 | -0.5172 |  | 13-03-2026 07:10 | 8.27 | 8.598 | 1.1 | 1.433 | 1.4378 | -0.0047616 | 8.6266 | 0.9 | 1.4172 | -0.5172 |  | 13-03-2026 07:10 | 8.323 | 9.066 | 1.1 | 1.511 | 1.4378 | 0.073238 | 8.6266 | 0.9 | 1.4172 | -0.5172 |  | 13-03-2026 07:10 | 5.97 | 6.586 | 0.7 | 1.0977 | 1.065 | 0.032658 | 6.3901 | 0.6 | 1.0498 | -0.44978 |  | 13-03-2026 07:10 | 5.985 | 6.242 | 0.7 | 1.0403 | 1.065 | -0.024675 | 6.3901 | 0.6 | 1.0498 | -0.44978 |  | 13-03-2026 07:10 | 5.985 | 6.243 | 0.5 | 1.0405 | 1.065 | -0.024509 | 6.3901 | 0.5 | 1.0498 | -0.54978 |  | 13-03-2026 07:10 | 6.101 | 6.749 | 0.5 | 1.1248 | 1.065 | 0.059825 | 6.3901 | 0.5 | 1.0498 | -0.54978 |  | 13-03-2026 07:10 | 5.685 | 5.931 | 0.7 | 0.9885 | 1.0132 | -0.024724 | 6.0793 | 0.6 | 0.99873 | -0.39873 |  | 13-03-2026 07:10 | 11.1052 | 11.0243 | 0.080862 | 66.1458 | 6.3 | 10.8667 | -4.5667
13-03-2026 07:00 | 6 | 23.25 | 2.514 | 2.643 | 0.2 | 0.4405 | 0.39212 | 0.048383 | 2.3527 | 0.2 | 0.38651 | -0.18651 |  | 13-03-2026 07:00 | 2.194 | 3.176 | 0.2 | 0.52933 | 0.39212 | 0.13722 | 2.3527 | 0.2 | 0.38651 | -0.18651 |  | 13-03-2026 07:00 | 2.483 | 2.611 | 0.2 | 0.43517 | 0.39212 | 0.04305 | 2.3527 | 0.2 | 0.38651 | -0.18651 |  | 13-03-2026 07:00 | 2.557 | 3.362 | 0.2 | 0.56033 | 0.39212 | 0.16822 | 2.3527 | 0.2 | 0.38651 | -0.18651 |  | 13-03-2026 07:00 | 1.703 | 2.266 | 0.1 | 0.37767 | 0.29046 | 0.08721 | 1.7427 | 0.1 | 0.2863 | -0.1863 |  | 13-03-2026 07:00 | 1.708 | 1.796 | 0.1 | 0.29933 | 0.29046 | 0.0088764 | 1.7427 | 0.1 | 0.2863 | -0.1863 |  | 13-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.29046 | -0.29046 | 1.7427 | 0 | 0.2863 | -0.2863 |  | 13-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.29046 | -0.29046 | 1.7427 | 0 | 0.2863 | -0.2863 |  | 13-03-2026 07:00 | 1.576 | 1.657 | 0.1 | 0.27617 | 0.27633 | -0.0001671 | 1.658 | 0.1 | 0.27238 | -0.17238 |  | 13-03-2026 07:00 | 2.9185 | 3.0066 | -0.088129 | 18.0398 | 1.1 | 2.9636 | -1.8636
[110 empty] | Total: - | 18806.9373 | 19589.4462 | -782.5089 |  | 18357.7 | 19309.3171 | -951.6171
Sum:- | 42791 |  | 14406.965 |  | 89907 |  |  |  |  | 2385.1 | 2518.2717 | -133.1717 | 0.98382 |  | 14429.235 |  | 86079.8 |  |  |  |  | 2411.9 | 2518.2717 | -106.3717 | 0.97929 |  | 14338.626 |  | 89397.1 |  |  |  |  | 2374.3 | 2518.2717 | -143.9717 | 0.97301 |  | 14407.866 |  | 90023.6 |  |  |  |  | 2387.6 | 2518.2717 | -130.6717 | 0.9834 |  | 10789.484 |  | 67213.9 |  |  |  |  | 1787.4 | 1865.3865 | -77.9865 | 0.98452 |  | 10664.445 |  | 66723.8 |  |  |  |  | 1767.9 | 1865.3865 | -97.4865 | 0.98151 |  | 10700.32 |  | 66752 |  |  |  |  | 1770.7 | 1865.3865 | -94.6865 | 0.97971 |  | 10794.189 |  | 67415.1 |  |  |  |  | 1785.3 | 1865.3865 | -80.0865 | 0.97122 |  | 10189.783 |  | 63759.4 |  |  |  |  | 1687.5 | 1774.6842 | -87.1842 | 0.98438

## 14 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
14-03-2026 19:00 | 0 | 39.03 | 0.067 | 0.081 | 2147.5 | 0.0135 | 0 | 0.0135 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.054 | 0.25 | 2179.9 | 0.041667 | 0 | 0.041667 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.062 | 0.089 | 2145.2 | 0.014833 | 0 | 0.014833 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.083 | 0.137 | 2164.4 | 0.022833 | 0 | 0.022833 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.088 | 0.093 | 1614.6 | 0.0155 | 0 | 0.0155 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.09 | 0.095 | 1594.2 | 0.015833 | 0 | 0.015833 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.104 | 0.109 | 1595.5 | 0.018167 | 0 | 0.018167 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.09 | 0.095 | 1602.9 | 0.015833 | 0 | 0.015833 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.088 | 0.093 | 1513 | 0.0155 | 0 | 0.0155 | 0 | 0 | 0 | 0 |  | 14-03-2026 19:00 | 0.17367 | 0 | 0.17367 | 0 | 0 | 0 | 0 | 1 | 99.18%
14-03-2026 18:50 | 0 | 39.89 | 0.333 | 0.35 | 2147.5 | 0.058333 | 0 | 0.058333 | 0 | 0.3 | 0 | 0.3 |  | 14-03-2026 18:50 | 0.454 | 0.863 | 2179.9 | 0.14383 | 0 | 0.14383 | 0 | 0.3 | 0 | 0.3 |  | 14-03-2026 18:50 | 0.37 | 0.389 | 2145.1 | 0.064833 | 0 | 0.064833 | 0 | 0.3 | 0 | 0.3 |  | 14-03-2026 18:50 | 0.379 | 0.676 | 2164.3 | 0.11267 | 0 | 0.11267 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.087 | 0.173 | 1614.6 | 0.028833 | 0 | 0.028833 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.095 | 0.1 | 1594.2 | 0.016667 | 0 | 0.016667 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.064 | 0.095 | 1595.5 | 0.015833 | 0 | 0.015833 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.203 | 0.437 | 1602.9 | 0.072833 | 0 | 0.072833 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.048 | 0.064 | 1513 | 0.010667 | 0 | 0.010667 | 0 | 0.2 | 0 | 0.2 |  | 14-03-2026 18:50 | 0.5245 | 0 | 0.5245 | 0 | 2.1 | 0 | 2.1 | 2 | 98.38%
14-03-2026 18:40 | 7 | 41.33 | 3.422 | 3.598 | 2147.2 | 0.59967 | 0.4287 | 0.17097 | 2.5722 | 1.1 | 0.42257 | 0.67743 |  | 14-03-2026 18:40 | 3.353 | 3.922 | 2179.6 | 0.65367 | 0.4287 | 0.22497 | 2.5722 | 1.2 | 0.42257 | 0.77743 |  | 14-03-2026 18:40 | 3.208 | 3.377 | 2144.8 | 0.56283 | 0.4287 | 0.13414 | 2.5722 | 1 | 0.42257 | 0.57743 |  | 14-03-2026 18:40 | 3.302 | 3.778 | 2164.1 | 0.62967 | 0.4287 | 0.20097 | 2.5722 | 1.1 | 0.42257 | 0.67743 |  | 14-03-2026 18:40 | 2.096 | 2.542 | 1614.4 | 0.42367 | 0.31755 | 0.10611 | 1.9053 | 0.8 | 0.31301 | 0.48699 |  | 14-03-2026 18:40 | 2.211 | 2.325 | 1594 | 0.3875 | 0.31755 | 0.069947 | 1.9053 | 0.7 | 0.31301 | 0.38699 |  | 14-03-2026 18:40 | 2.21 | 2.324 | 1595.3 | 0.38733 | 0.31755 | 0.06978 | 1.9053 | 0.7 | 0.31301 | 0.38699 |  | 14-03-2026 18:40 | 2.301 | 2.598 | 1602.7 | 0.433 | 0.31755 | 0.11545 | 1.9053 | 0.7 | 0.31301 | 0.38699 |  | 14-03-2026 18:40 | 2.076 | 2.179 | 1512.8 | 0.36317 | 0.30211 | 0.061054 | 1.8127 | 0.7 | 0.29779 | 0.40221 |  | 14-03-2026 18:40 | 4.4405 | 3.2871 | 1.1534 | 19.7227 | 8 | 3.2401 | 4.7599 | 3 | 97.33%
14-03-2026 18:30 | 26 | 42.48 | 10.322 | 10.385 | 2146.1 | 1.7308 | 1.5855 | 0.14533 | 9.513 | 2.2 | 1.5628 | 0.63717 |  | 14-03-2026 18:30 | 10.217 | 10.635 | 2178.4 | 1.7725 | 1.5855 | 0.18699 | 9.513 | 2.2 | 1.5628 | 0.63717 |  | 14-03-2026 18:30 | 9.843 | 10.23 | 2143.8 | 1.705 | 1.5855 | 0.11949 | 9.513 | 2.2 | 1.5628 | 0.63717 |  | 14-03-2026 18:30 | 9.91 | 10.541 | 2163 | 1.7568 | 1.5855 | 0.17133 | 9.513 | 2.2 | 1.5628 | 0.63717 |  | 14-03-2026 18:30 | 7.163 | 7.481 | 1613.6 | 1.2468 | 1.1744 | 0.072384 | 7.0467 | 1.6 | 1.1577 | 0.44235 |  | 14-03-2026 18:30 | 7.022 | 7.331 | 1593.3 | 1.2218 | 1.1744 | 0.047384 | 7.0467 | 1.6 | 1.1577 | 0.44235 |  | 14-03-2026 18:30 | 7.042 | 7.358 | 1594.6 | 1.2263 | 1.1744 | 0.051884 | 7.0467 | 1.6 | 1.1577 | 0.44235 |  | 14-03-2026 18:30 | 7.056 | 7.517 | 1602 | 1.2528 | 1.1744 | 0.078384 | 7.0467 | 1.7 | 1.1577 | 0.54235 |  | 14-03-2026 18:30 | 6.624 | 6.933 | 1512.1 | 1.1555 | 1.1173 | 0.038157 | 6.7041 | 1.5 | 1.1014 | 0.39864 |  | 14-03-2026 18:30 | 13.0685 | 12.1572 | 0.91134 | 72.943 | 16.8 | 11.9833 | 4.8167 | 4 | 98.39%
14-03-2026 18:20 | 43 | 43.91 | 15.998 | 16.445 | 2143.9 | 2.7408 | 2.6082 | 0.13263 | 15.6492 | 3.9 | 2.5709 | 1.3291 |  | 14-03-2026 18:20 | 16.522 | 17.002 | 2176.2 | 2.8337 | 2.6082 | 0.22546 | 15.6492 | 9.2 | 2.5709 | 6.6291 |  | 14-03-2026 18:20 | 16.007 | 16.456 | 2141.6 | 2.7427 | 2.6082 | 0.13446 | 15.6492 | 3.9 | 2.5709 | 1.3291 |  | 14-03-2026 18:20 | 16.072 | 16.528 | 2160.8 | 2.7547 | 2.6082 | 0.14646 | 15.6492 | 3.9 | 2.5709 | 1.3291 |  | 14-03-2026 18:20 | 11.686 | 12.113 | 1612 | 2.0188 | 1.932 | 0.08683 | 11.592 | 2.8 | 1.9044 | 0.89562 |  | 14-03-2026 18:20 | 11.596 | 12.007 | 1591.7 | 2.0012 | 1.932 | 0.069164 | 11.592 | 2.9 | 1.9044 | 0.99562 |  | 14-03-2026 18:20 | 11.593 | 12.006 | 1593 | 2.001 | 1.932 | 0.068997 | 11.592 | 2.9 | 1.9044 | 0.99562 |  | 14-03-2026 18:20 | 11.61 | 12.344 | 1600.3 | 2.0573 | 1.932 | 0.12533 | 11.592 | 2.8 | 1.9044 | 0.89562 |  | 14-03-2026 18:20 | 10.952 | 11.357 | 1510.6 | 1.8928 | 1.8381 | 0.054772 | 11.0284 | 2.6 | 1.8118 | 0.78822 |  | 14-03-2026 18:20 | 21.043 | 19.9989 | 1.0441 | 119.9933 | 34.9 | 19.7129 | 15.1871 | 5 | 98.5%
14-03-2026 18:10 | 78 | 45.35 | 29.322 | 29.917 | 2140 | 4.9862 | 4.7056 | 0.28054 | 28.2338 | 5 | 4.6383 | 0.36166 | [5 empty] | 0 | 4.7056 | -4.7056 | 28.2338 | 0 | 4.6383 | -4.6383 |  | 14-03-2026 18:10 | 29.311 | 29.935 | 2137.7 | 4.9892 | 4.7056 | 0.28354 | 28.2338 | 5.1 | 4.6383 | 0.46166 |  | 14-03-2026 18:10 | 29.355 | 29.963 | 2156.9 | 4.9938 | 4.7056 | 0.28821 | 28.2338 | 5.1 | 4.6383 | 0.46166 |  | 14-03-2026 18:10 | 21.669 | 22.2 | 1609.2 | 3.7 | 3.4856 | 0.21435 | 20.9139 | 3.8 | 3.4358 | 0.3642 |  | 14-03-2026 18:10 | 21.334 | 21.852 | 1588.8 | 3.642 | 3.4856 | 0.15635 | 20.9139 | 3.6 | 3.4358 | 0.1642 |  | 14-03-2026 18:10 | 21.257 | 21.775 | 1590.1 | 3.6292 | 3.4856 | 0.14352 | 20.9139 | 3.6 | 3.4358 | 0.1642 |  | 14-03-2026 18:10 | 21.159 | 21.926 | 1597.5 | 3.6543 | 3.4856 | 0.16868 | 20.9139 | 3.6 | 3.4358 | 0.1642 |  | 14-03-2026 18:10 | 20.065 | 20.575 | 1508 | 3.4292 | 3.3162 | 0.113 | 19.897 | 3.5 | 3.2687 | 0.23126 |  | 14-03-2026 18:10 | 33.0238 | 36.0813 | -3.0574 | 216.4876 | 33.3 | 35.5653 | -2.2653 | 6 | 98.22%
14-03-2026 18:00 | 80 | 45.35 | 29.919 | 30.511 | 2135 | 5.0852 | 4.8263 | 0.25888 | 28.9577 | 4.3 | 4.7573 | -0.45727 |  | 14-03-2026 18:00 | 30.521 | 31.105 | 2167 | 5.1842 | 4.8263 | 0.35788 | 28.9577 | 4.2 | 4.7573 | -0.55727 |  | 14-03-2026 18:00 | 30.312 | 30.902 | 2132.6 | 5.1503 | 4.8263 | 0.32405 | 28.9577 | 4.1 | 4.7573 | -0.65727 |  | 14-03-2026 18:00 | 30.255 | 30.844 | 2151.8 | 5.1407 | 4.8263 | 0.31438 | 28.9577 | 4.1 | 4.7573 | -0.65727 |  | 14-03-2026 18:00 | 22.497 | 23.055 | 1605.4 | 3.8425 | 3.575 | 0.26748 | 21.4501 | 3.1 | 3.5239 | -0.4239 |  | 14-03-2026 18:00 | 21.917 | 22.466 | 1585.2 | 3.7443 | 3.575 | 0.16931 | 21.4501 | 3 | 3.5239 | -0.5239 |  | 14-03-2026 18:00 | 22.075 | 22.595 | 1586.5 | 3.7658 | 3.575 | 0.19081 | 21.4501 | 3 | 3.5239 | -0.5239 |  | 14-03-2026 18:00 | 21.883 | 22.561 | 1593.9 | 3.7602 | 3.575 | 0.18514 | 21.4501 | 3 | 3.5239 | -0.5239 |  | 14-03-2026 18:00 | 20.672 | 21.178 | 1504.5 | 3.5297 | 3.4012 | 0.12847 | 20.4072 | 2.8 | 3.3526 | -0.55256 |  | 14-03-2026 18:00 | 39.2028 | 37.0064 | 2.1964 | 222.0385 | 31.6 | 36.4772 | -4.8772 | 7 | 98.13%
14-03-2026 17:50 | 62 | 46.49 | 23.064 | 23.619 | 2130.7 | 3.9365 | 3.7243 | 0.2122 | 22.3458 | 5.3 | 3.671 | 1.629 |  | 14-03-2026 17:50 | 23.313 | 23.881 | 2162.8 | 3.9802 | 3.7243 | 0.25587 | 22.3458 | 5.4 | 3.671 | 1.729 |  | 14-03-2026 17:50 | 22.359 | 22.943 | 2128.5 | 3.8238 | 3.7243 | 0.099533 | 22.3458 | 5.6 | 3.671 | 1.929 |  | 14-03-2026 17:50 | 22.554 | 23.111 | 2147.7 | 3.8518 | 3.7243 | 0.12753 | 22.3458 | 5.6 | 3.671 | 1.929 |  | 14-03-2026 17:50 | 16.429 | 16.883 | 1602.3 | 2.8138 | 2.7587 | 0.055092 | 16.5524 | 4 | 2.7193 | 1.2807 |  | 14-03-2026 17:50 | 16.285 | 16.741 | 1582.2 | 2.7902 | 2.7587 | 0.031425 | 16.5524 | 4.1 | 2.7193 | 1.3807 |  | 14-03-2026 17:50 | 16.204 | 16.652 | 1583.5 | 2.7753 | 2.7587 | 0.016592 | 16.5524 | 4 | 2.7193 | 1.2807 |  | 14-03-2026 17:50 | 16.418 | 17.212 | 1590.9 | 2.8687 | 2.7587 | 0.10993 | 16.5524 | 4 | 2.7193 | 1.2807 |  | 14-03-2026 17:50 | 15.461 | 15.895 | 1501.7 | 2.6492 | 2.6246 | 0.024566 | 15.7476 | 3.8 | 2.5871 | 1.2129 |  | 14-03-2026 17:50 | 29.4895 | 28.5568 | 0.93273 | 171.3406 | 41.8 | 28.1484 | 13.6516 | 8 | 97.18%
14-03-2026 17:40 | 131 | 47.35 | 45.883 | 46.658 | 2125.4 | 7.7763 | 7.8435 | -0.067141 | 47.0608 | 6.8 | 7.7313 | -0.93131 |  | 14-03-2026 17:40 | 46.755 | 48.414 | 2157.4 | 8.069 | 7.8435 | 0.22553 | 47.0608 | 7.4 | 7.7313 | -0.33131 |  | 14-03-2026 17:40 | 46.439 | 47.233 | 2122.9 | 7.8722 | 7.8435 | 0.028692 | 47.0608 | 7 | 7.7313 | -0.73131 |  | 14-03-2026 17:40 | 46.055 | 46.851 | 2142.1 | 7.8085 | 7.8435 | -0.034975 | 47.0608 | 7 | 7.7313 | -0.73131 |  | 14-03-2026 17:40 | 34.483 | 35.065 | 1598.3 | 5.8442 | 5.81 | 0.034185 | 34.8599 | 5.3 | 5.7269 | -0.4269 |  | 14-03-2026 17:40 | 33.525 | 34.143 | 1578.1 | 5.6905 | 5.81 | -0.11948 | 34.8599 | 5.1 | 5.7269 | -0.6269 |  | 14-03-2026 17:40 | 33.537 | 34.169 | 1579.5 | 5.6948 | 5.81 | -0.11515 | 34.8599 | 5.1 | 5.7269 | -0.6269 |  | 14-03-2026 17:40 | 33.483 | 34.643 | 1586.9 | 5.7738 | 5.81 | -0.036148 | 34.8599 | 5.1 | 5.7269 | -0.6269 |  | 14-03-2026 17:40 | 31.546 | 32.15 | 1497.9 | 5.3583 | 5.5275 | -0.16914 | 33.1649 | 4.8 | 5.4484 | -0.64843 |  | 14-03-2026 17:40 | 59.8877 | 60.1413 | -0.25363 | 360.8478 | 53.6 | 59.2813 | -5.6813 | 9 | 98.54%
14-03-2026 17:30 | 122 | 47.35 | 45.625 | 46.395 | 2118.6 | 7.7325 | 7.3046 | 0.42789 | 43.8277 | 7.3 | 7.2002 | 0.099846 |  | 14-03-2026 17:30 | 40.39 | 42.654 | 2150 | 7.109 | 7.3046 | -0.19561 | 43.8277 | 7 | 7.2002 | -0.20015 |  | 14-03-2026 17:30 | 43.699 | 44.468 | 2115.9 | 7.4113 | 7.3046 | 0.10672 | 43.8277 | 7 | 7.2002 | -0.20015 |  | 14-03-2026 17:30 | 42.724 | 43.485 | 2135.1 | 7.2475 | 7.3046 | -0.05711 | 43.8277 | 7.1 | 7.2002 | -0.10015 |  | 14-03-2026 17:30 | 31.441 | 32.053 | 1593 | 5.3422 | 5.4108 | -0.068655 | 32.4649 | 5.2 | 5.3334 | -0.13345 |  | 14-03-2026 17:30 | 30.747 | 31.336 | 1573 | 5.2227 | 5.4108 | -0.18816 | 32.4649 | 5.1 | 5.3334 | -0.23345 |  | 14-03-2026 17:30 | 30.67 | 31.261 | 1574.4 | 5.2102 | 5.4108 | -0.20066 | 32.4649 | 5.2 | 5.3334 | -0.13345 |  | 14-03-2026 17:30 | 30.864 | 31.801 | 1581.8 | 5.3002 | 5.4108 | -0.11066 | 32.4649 | 5.3 | 5.3334 | -0.033447 |  | 14-03-2026 17:30 | 28.989 | 29.584 | 1493.1 | 4.9307 | 5.1477 | -0.21706 | 30.8864 | 4.9 | 5.0741 | -0.17411 |  | 14-03-2026 17:30 | 55.5062 | 56.0095 | -0.50329 | 336.0567 | 54.1 | 55.2085 | -1.1085
14-03-2026 17:20 | 121 | 47.64 | 43.446 | 44.206 | 2111.3 | 7.3677 | 7.2368 | 0.13091 | 43.4206 | 8.6 | 7.1333 | 1.4667 |  | 14-03-2026 17:20 | 45.244 | 46.045 | 2143 | 7.6742 | 7.2368 | 0.43741 | 43.4206 | 8.4 | 7.1333 | 1.2667 |  | 14-03-2026 17:20 | 43.197 | 43.966 | 2108.9 | 7.3277 | 7.2368 | 0.090908 | 43.4206 | 8.3 | 7.1333 | 1.1667 |  | 14-03-2026 17:20 | 43.312 | 44.092 | 2128 | 7.3487 | 7.2368 | 0.11191 | 43.4206 | 8.3 | 7.1333 | 1.1667 |  | 14-03-2026 17:20 | 31.835 | 32.448 | 1587.8 | 5.408 | 5.3606 | 0.047438 | 32.1634 | 6.1 | 5.2839 | 0.81609 |  | 14-03-2026 17:20 | 31.404 | 32.015 | 1567.9 | 5.3358 | 5.3606 | -0.024729 | 32.1634 | 6.1 | 5.2839 | 0.81609 |  | 14-03-2026 17:20 | 31.133 | 31.739 | 1569.2 | 5.2898 | 5.3606 | -0.070729 | 32.1634 | 6 | 5.2839 | 0.71609 |  | 14-03-2026 17:20 | 31.82 | 32.479 | 1576.5 | 5.4132 | 5.3606 | 0.052605 | 32.1634 | 5.9 | 5.2839 | 0.61609 |  | 14-03-2026 17:20 | 29.715 | 30.321 | 1488.2 | 5.0535 | 5.0999 | -0.046411 | 30.5995 | 5.7 | 5.027 | 0.67302 |  | 14-03-2026 17:20 | 56.2185 | 55.4892 | 0.72931 | 332.9352 | 63.4 | 54.6957 | 8.7043
14-03-2026 17:10 | 149 | 47.93 | 54.543 | 55.413 | 2102.7 | 9.2355 | 8.9016 | 0.33394 | 53.4093 | 13.7 | 8.7743 | 4.9257 |  | 14-03-2026 17:10 | 53.654 | 54.549 | 2134.6 | 9.0915 | 8.9016 | 0.18994 | 53.4093 | 14.1 | 8.7743 | 5.3257 |  | 14-03-2026 17:10 | 52.981 | 53.87 | 2100.6 | 8.9783 | 8.9016 | 0.076776 | 53.4093 | 13.9 | 8.7743 | 5.1257 |  | 14-03-2026 17:10 | 53.33 | 54.214 | 2119.7 | 9.0357 | 8.9016 | 0.13411 | 53.4093 | 13.9 | 8.7743 | 5.1257 |  | 14-03-2026 17:10 | 39.807 | 40.541 | 1581.7 | 6.7568 | 6.5937 | 0.16309 | 39.5625 | 10.3 | 6.4995 | 3.8005 |  | 14-03-2026 17:10 | 38.876 | 39.597 | 1561.8 | 6.5995 | 6.5937 | 0.0057541 | 39.5625 | 10.2 | 6.4995 | 3.7005 |  | 14-03-2026 17:10 | 38.891 | 39.575 | 1563.2 | 6.5958 | 6.5937 | 0.0020874 | 39.5625 | 10.1 | 6.4995 | 3.6005 |  | 14-03-2026 17:10 | 38.905 | 39.964 | 1570.6 | 6.6607 | 6.5937 | 0.066921 | 39.5625 | 10.1 | 6.4995 | 3.6005 |  | 14-03-2026 17:10 | 36.724 | 37.416 | 1482.5 | 6.236 | 6.2731 | -0.037133 | 37.6388 | 9.5 | 6.1834 | 3.3166 |  | 14-03-2026 17:10 | 69.1898 | 68.2543 | 0.93549 | 409.5261 | 105.8 | 67.2783 | 38.5217
14-03-2026 17:00 | 299 | 47.64 | 103.175 | 104.47 | 2089 | 17.4117 | 17.8826 | -0.4709 | 107.2954 | 18.5 | 17.6268 | 0.87315 |  | 14-03-2026 17:00 | 105.639 | 107.265 | 2120.5 | 17.8775 | 17.8826 | -0.0050688 | 107.2954 | 19.1 | 17.6268 | 1.4732 |  | 14-03-2026 17:00 | 104.839 | 106.796 | 2086.7 | 17.7993 | 17.8826 | -0.083236 | 107.2954 | 18.8 | 17.6268 | 1.1732 |  | 14-03-2026 17:00 | 105.471 | 106.839 | 2105.8 | 17.8065 | 17.8826 | -0.076069 | 107.2954 | 18.7 | 17.6268 | 1.0732 |  | 14-03-2026 17:00 | 78.999 | 79.638 | 1571.4 | 13.273 | 13.2463 | 0.026653 | 79.4781 | 14 | 13.0569 | 0.94308 |  | 14-03-2026 17:00 | 77.604 | 78.769 | 1551.6 | 13.1282 | 13.2463 | -0.11818 | 79.4781 | 13.6 | 13.0569 | 0.54308 |  | 14-03-2026 17:00 | 77.537 | 78.574 | 1553.1 | 13.0957 | 13.2463 | -0.15068 | 79.4781 | 13.6 | 13.0569 | 0.54308 |  | 14-03-2026 17:00 | 77.874 | 79.744 | 1560.5 | 13.2907 | 13.2463 | 0.044319 | 79.4781 | 13.8 | 13.0569 | 0.74308 |  | 14-03-2026 17:00 | 73.402 | 74.422 | 1473 | 12.4037 | 12.6023 | -0.19859 | 75.6136 | 13 | 12.422 | 0.57795 |  | 14-03-2026 17:00 | 136.0862 | 137.1179 | -1.0318 | 822.7075 | 143.1 | 135.1571 | 7.9429
14-03-2026 16:50 | 254 | 47.93 | 99.7 | 98.193 | 2070.5 | 16.3655 | 15.1745 | 1.191 | 91.0468 | 42.3 | 14.9575 | 27.3425 |  | 14-03-2026 16:50 | 110.361 | 111.803 | 2101.4 | 18.6338 | 15.1745 | 3.4594 | 91.0468 | 21.1 | 14.9575 | 6.1425 |  | 14-03-2026 16:50 | 89.492 | 91.25 | 2067.9 | 15.2083 | 15.1745 | 0.033867 | 91.0468 | 20.7 | 14.9575 | 5.7425 |  | 14-03-2026 16:50 | 88.086 | 89.282 | 2087.1 | 14.8803 | 15.1745 | -0.29413 | 91.0468 | 20.7 | 14.9575 | 5.7425 |  | 14-03-2026 16:50 | 64.781 | 65.721 | 1557.4 | 10.9535 | 11.2403 | -0.28685 | 67.4421 | 15.4 | 11.0796 | 4.3204 |  | 14-03-2026 16:50 | 63.211 | 64.122 | 1538 | 10.687 | 11.2403 | -0.55335 | 67.4421 | 15 | 11.0796 | 3.9204 |  | 14-03-2026 16:50 | 63.079 | 63.994 | 1539.5 | 10.6657 | 11.2403 | -0.57468 | 67.4421 | 15 | 11.0796 | 3.9204 |  | 14-03-2026 16:50 | 63.448 | 65.348 | 1546.7 | 10.8913 | 11.2403 | -0.34901 | 67.4421 | 15 | 11.0796 | 3.9204 |  | 14-03-2026 16:50 | 60.159 | 61.05 | 1460 | 10.175 | 10.6938 | -0.5188 | 64.1628 | 14 | 10.5409 | 3.4591 |  | 14-03-2026 16:50 | 118.4605 | 116.353 | 2.1075 | 698.1183 | 179.2 | 114.6892 | 64.5108
14-03-2026 16:40 | 367 | 48.22 | 129.888 | 131.572 | 2049.7 | 21.9287 | 21.9011 | 0.027551 | 131.4067 | 0 | 21.5879 | -21.5879 |  | 14-03-2026 16:40 | 136.29 | 137.517 | 2080.3 | 22.9195 | 21.9011 | 1.0184 | 131.4067 | 22.5 | 21.5879 | 0.91207 |  | 14-03-2026 16:40 | 132.308 | 136.226 | 2047.2 | 22.7043 | 21.9011 | 0.80322 | 131.4067 | 21.7 | 21.5879 | 0.11207 |  | 14-03-2026 16:40 | 133.524 | 135.296 | 2066.4 | 22.5493 | 21.9011 | 0.64822 | 131.4067 | 21.8 | 21.5879 | 0.21207 |  | 14-03-2026 16:40 | 104.542 | 105.876 | 1542 | 17.646 | 16.223 | 1.423 | 97.3383 | 16.2 | 15.9911 | 0.20894 |  | 14-03-2026 16:40 | 102.084 | 103.459 | 1523 | 17.2432 | 16.223 | 1.0201 | 97.3383 | 15.9 | 15.9911 | -0.091059 |  | 14-03-2026 16:40 | 104.648 | 105.962 | 1524.5 | 17.6603 | 16.223 | 1.4373 | 97.3383 | 15.9 | 15.9911 | -0.091059 |  | 14-03-2026 16:40 | 102.126 | 106.445 | 1531.7 | 17.7408 | 16.223 | 1.5178 | 97.3383 | 15.7 | 15.9911 | -0.29106 |  | 14-03-2026 16:40 | 96.704 | 97.948 | 1446 | 16.3247 | 15.4342 | 0.89045 | 92.6053 | 15.3 | 15.2135 | 0.086488 |  | 14-03-2026 16:40 | 176.7168 | 167.9309 | 8.786 | 1007.5853 | 145 | 165.5295 | -20.5295
14-03-2026 16:30 | 385 | 48.5 | 129.804 | 131.474 | 2028.2 | 21.9123 | 22.9508 | -1.0384 | 137.7047 | 25 | 22.6226 | 2.3774 |  | 14-03-2026 16:30 | 0 | 136.914 | 2057.8 | 22.819 | 22.9508 | -0.13178 | 137.7047 | 24.3 | 22.6226 | 1.6774 |  | 14-03-2026 16:30 | 137.481 | 140.873 | 2025.5 | 23.4788 | 22.9508 | 0.52806 | 137.7047 | 24.8 | 22.6226 | 2.1774 |  | 14-03-2026 16:30 | 138.383 | 139.364 | 2044.6 | 23.2273 | 22.9508 | 0.27656 | 137.7047 | 24.9 | 22.6226 | 2.2774 |  | 14-03-2026 16:30 | 106.188 | 107.554 | 1525.8 | 17.9257 | 17.0006 | 0.92509 | 102.0035 | 18.7 | 16.7575 | 1.9425 |  | 14-03-2026 16:30 | 103.959 | 105.31 | 1507.1 | 17.5517 | 17.0006 | 0.55109 | 102.0035 | 18.4 | 16.7575 | 1.6425 |  | 14-03-2026 16:30 | 104.399 | 105.742 | 1508.6 | 17.6237 | 17.0006 | 0.62309 | 102.0035 | 18.7 | 16.7575 | 1.9425 |  | 14-03-2026 16:30 | 104.919 | 107.793 | 1516 | 17.9655 | 17.0006 | 0.96492 | 102.0035 | 18.8 | 16.7575 | 2.0425 |  | 14-03-2026 16:30 | 96.722 | 97.966 | 1430.7 | 16.3277 | 16.1739 | 0.15372 | 97.0437 | 17.4 | 15.9427 | 1.4573 |  | 14-03-2026 16:30 | 178.8317 | 175.9794 | 2.8523 | 1055.8761 | 191 | 173.4628 | 17.5372
14-03-2026 16:20 | 453 | 48.5 | 158.967 | 161.093 | 2003.2 | 26.8488 | 27.0044 | -0.15559 | 162.0265 | 27.5 | 26.6183 | 0.88174 |  | 14-03-2026 16:20 | 162.014 | 161.761 | 2033.5 | 26.9602 | 27.0044 | -0.044254 | 162.0265 | 28.4 | 26.6183 | 1.7817 |  | 14-03-2026 16:20 | 156.984 | 159.224 | 2000.7 | 26.5373 | 27.0044 | -0.46709 | 162.0265 | 28 | 26.6183 | 1.3817 |  | 14-03-2026 16:20 | 157.497 | 159.636 | 2019.7 | 26.606 | 27.0044 | -0.39842 | 162.0265 | 28.1 | 26.6183 | 1.4817 |  | 14-03-2026 16:20 | 118.505 | 120.054 | 1507.1 | 20.009 | 20.0033 | 0.0057253 | 120.0196 | 21.1 | 19.7172 | 1.3828 |  | 14-03-2026 16:20 | 116.499 | 118.021 | 1488.7 | 19.6702 | 20.0033 | -0.33311 | 120.0196 | 20.9 | 19.7172 | 1.1828 |  | 14-03-2026 16:20 | 116.994 | 118.523 | 1489.9 | 19.7538 | 20.0033 | -0.24944 | 120.0196 | 20.7 | 19.7172 | 0.98277 |  | 14-03-2026 16:20 | 117.714 | 120.98 | 1497.2 | 20.1633 | 20.0033 | 0.16006 | 120.0196 | 20.7 | 19.7172 | 0.98277 |  | 14-03-2026 16:20 | 110.707 | 112.165 | 1413.3 | 18.6942 | 19.0306 | -0.33647 | 114.1838 | 19.5 | 18.7585 | 0.7415 |  | 14-03-2026 16:20 | 205.2428 | 207.0614 | -1.8186 | 1242.3685 | 214.9 | 204.1004 | 10.7996
14-03-2026 16:10 | 496 | 48.5 | 171.589 | 173.884 | 1975.7 | 28.9807 | 29.5678 | -0.58709 | 177.4065 | 31.7 | 29.1449 | 2.5551 |  | 14-03-2026 16:10 | 176.29 | 177.851 | 2005.1 | 29.6418 | 29.5678 | 0.074079 | 177.4065 | 32.8 | 29.1449 | 3.6551 |  | 14-03-2026 16:10 | 172.459 | 175.863 | 1972.7 | 29.3105 | 29.5678 | -0.25725 | 177.4065 | 31.7 | 29.1449 | 2.5551 |  | 14-03-2026 16:10 | 173.488 | 175.88 | 1991.6 | 29.3133 | 29.5678 | -0.25442 | 177.4065 | 31.7 | 29.1449 | 2.5551 |  | 14-03-2026 16:10 | 129.461 | 131.178 | 1486 | 21.863 | 21.902 | -0.03904 | 131.4122 | 23.7 | 21.5888 | 2.1112 |  | 14-03-2026 16:10 | 127.191 | 128.879 | 1467.8 | 21.4798 | 21.902 | -0.42221 | 131.4122 | 22.9 | 21.5888 | 1.3112 |  | 14-03-2026 16:10 | 126.927 | 128.733 | 1469.2 | 21.4555 | 21.902 | -0.44654 | 131.4122 | 22.8 | 21.5888 | 1.2112 |  | 14-03-2026 16:10 | 126.62 | 130.176 | 1476.5 | 21.696 | 21.902 | -0.20604 | 131.4122 | 22.8 | 21.5888 | 1.2112 |  | 14-03-2026 16:10 | 119.815 | 121.405 | 1393.8 | 20.2342 | 20.8371 | -0.60291 | 125.0225 | 22.1 | 20.5391 | 1.5609 |  | 14-03-2026 16:10 | 223.9748 | 226.7163 | -2.7414 | 1360.2975 | 242.2 | 223.4742 | 18.7258
14-03-2026 16:00 | 600 | 47.93 | 209.047 | 211.952 | 1944 | 35.3253 | 35.8452 | -0.51986 | 215.0712 | 1944 | 35.3326 | 1908.6674 |  | 14-03-2026 16:00 | 210.294 | 213.258 | 1972.3 | 35.543 | 35.8452 | -0.3022 | 215.0712 | 27.6 | 35.3326 | -7.7326 |  | 14-03-2026 16:00 | 209.858 | 214.371 | 1941 | 35.7285 | 35.8452 | -0.1167 | 215.0712 | 28.7 | 35.3326 | -6.6326 |  | 14-03-2026 16:00 | 211.004 | 214 | 1959.9 | 35.6667 | 35.8452 | -0.17853 | 215.0712 | 28.8 | 35.3326 | -6.5326 |  | 14-03-2026 16:00 | 157.093 | 159.26 | 1462.3 | 26.5433 | 26.552 | -0.0086637 | 159.312 | 21.8 | 26.1723 | -4.3723 |  | 14-03-2026 16:00 | 154.637 | 156.726 | 1444.9 | 26.121 | 26.552 | -0.431 | 159.312 | 21.4 | 26.1723 | -4.7723 |  | 14-03-2026 16:00 | 154.03 | 156.426 | 1446.4 | 26.071 | 26.552 | -0.481 | 159.312 | 21.6 | 26.1723 | -4.5723 |  | 14-03-2026 16:00 | 154.279 | 158.328 | 1453.7 | 26.388 | 26.552 | -0.164 | 159.312 | 21.8 | 26.1723 | -4.3723 |  | 14-03-2026 16:00 | 146.555 | 148.515 | 1371.7 | 24.7525 | 25.2609 | -0.50844 | 151.5656 | 20.2 | 24.8997 | -4.6997 |  | 14-03-2026 16:00 | 272.1393 | 274.8497 | -2.7104 | 1649.0983 | 2135.9 | 270.9194 | 1864.9806
14-03-2026 15:50 | 594 | 47.64 |  |  |  | 0 | 35.5259 | -35.5259 | 213.1554 | -1886 | 35.0179 | -1921.0179 |  | 14-03-2026 15:50 | 154.285 | 156.381 | 1944.7 | 26.0635 | 35.5259 | -9.4624 | 213.1554 | 31.5 | 35.0179 | -3.5179 |  | 14-03-2026 15:50 | 214.864 | 222.076 | 1912.3 | 37.0127 | 35.5259 | 1.4868 | 213.1554 | 30.5 | 35.0179 | -4.5179 |  | 14-03-2026 15:50 | 196.614 | 203.583 | 1931.1 | 33.9305 | 35.5259 | -1.5954 | 213.1554 | 30.8 | 35.0179 | -4.2179 |  | 14-03-2026 15:50 | 166.264 | 168.471 | 1440.5 | 28.0785 | 26.3155 | 1.763 | 157.8929 | 23.3 | 25.9392 | -2.6392 |  | 14-03-2026 15:50 | 157.099 | 160.468 | 1423.5 | 26.7447 | 26.3155 | 0.42918 | 157.8929 | 22.7 | 25.9392 | -3.2392 |  | 14-03-2026 15:50 | 161.429 | 163.555 | 1424.8 | 27.2592 | 26.3155 | 0.94368 | 157.8929 | 23.4 | 25.9392 | -2.5392 |  | 14-03-2026 15:50 | 157.343 | 161.089 | 1431.9 | 26.8482 | 26.3155 | 0.53268 | 157.8929 | 23.3 | 25.9392 | -2.6392 |  | 14-03-2026 15:50 | 136.594 | 139.206 | 1351.5 | 23.201 | 25.0359 | -1.8349 | 150.2156 | 21.5 | 24.6779 | -3.1779 |  | 14-03-2026 15:50 | 229.1382 | 272.4015 | -43.2633 | 1634.409 | -1679 | 268.5062 | -1947.5062
14-03-2026 15:40 | 560 | 47.64 | 201.599 | 208.841 | 1886 | 34.8068 | 33.4924 | 1.3144 | 200.9546 | 25.2 | 33.0135 | -7.8135 |  | 14-03-2026 15:40 | 197.277 | 200.017 | 1913.2 | 33.3362 | 33.4924 | -0.15627 | 200.9546 | 25.1 | 33.0135 | -7.9135 |  | 14-03-2026 15:40 | 197.081 | 212.595 | 1881.8 | 35.4325 | 33.4924 | 1.9401 | 200.9546 | 25.5 | 33.0135 | -7.5135 |  | 14-03-2026 15:40 | 202.921 | 205.74 | 1900.3 | 34.29 | 33.4924 | 0.79756 | 200.9546 | 25.5 | 33.0135 | -7.5135 |  | 14-03-2026 15:40 | 133.822 | 135.585 | 1417.2 | 22.5975 | 24.8092 | -2.2117 | 148.8553 | 19.1 | 24.4544 | -5.3544 |  | 14-03-2026 15:40 | 144.178 | 146.033 | 1400.8 | 24.3388 | 24.8092 | -0.47038 | 148.8553 | 18.8 | 24.4544 | -5.6544 |  | 14-03-2026 15:40 | 133.195 | 138.149 | 1401.4 | 23.0248 | 24.8092 | -1.7844 | 148.8553 | 18.5 | 24.4544 | -5.9544 |  | 14-03-2026 15:40 | 127.818 | 132.511 | 1408.6 | 22.0852 | 24.8092 | -2.724 | 148.8553 | 18.5 | 24.4544 | -5.9544 |  | 14-03-2026 15:40 | 116.999 | 118.916 | 1330 | 19.8193 | 23.6029 | -3.7836 | 141.6174 | 17.4 | 23.2654 | -5.8654 |  | 14-03-2026 15:40 | 249.7312 | 256.8095 | -7.0783 | 1540.8569 | 193.6 | 253.1371 | -59.5371
14-03-2026 15:30 | 272 | 47.35 | 102.582 | 103.902 | 1860.8 | 17.317 | 16.2857 | 1.0313 | 97.7141 | 15.5 | 16.0528 | -0.5528 |  | 14-03-2026 15:30 | 103.352 | 104.703 | 1888.1 | 17.4505 | 16.2857 | 1.1648 | 97.7141 | 15.5 | 16.0528 | -0.5528 |  | 14-03-2026 15:30 | 103.517 | 105.302 | 1856.3 | 17.5503 | 16.2857 | 1.2646 | 97.7141 | 14.9 | 16.0528 | -1.1528 |  | 14-03-2026 15:30 | 105.375 | 106.752 | 1874.8 | 17.792 | 16.2857 | 1.5063 | 97.7141 | 15 | 16.0528 | -1.0528 |  | 14-03-2026 15:30 | 78.499 | 79.565 | 1398.1 | 13.2608 | 12.0635 | 1.1974 | 72.3808 | 11.2 | 11.891 | -0.69096 |  | 14-03-2026 15:30 | 78.506 | 79.564 | 1382 | 13.2607 | 12.0635 | 1.1972 | 72.3808 | 10.9 | 11.891 | -0.99096 |  | 14-03-2026 15:30 | 78.749 | 79.819 | 1382.9 | 13.3032 | 12.0635 | 1.2397 | 72.3808 | 10.9 | 11.891 | -0.99096 |  | 14-03-2026 15:30 | 79.713 | 81.671 | 1390.1 | 13.6118 | 12.0635 | 1.5484 | 72.3808 | 11 | 11.891 | -0.89096 |  | 14-03-2026 15:30 | 75.303 | 76.341 | 1312.6 | 12.7235 | 11.4769 | 1.2466 | 68.8614 | 10.5 | 11.3128 | -0.81278 |  | 14-03-2026 15:30 | 136.2698 | 124.8735 | 11.3963 | 749.2412 | 115.4 | 123.0878 | -7.6878
14-03-2026 15:20 | 235 | 47.35 | 92.696 | 93.888 | 1845.3 | 15.648 | 14.0704 | 1.5776 | 84.4221 | 18.3 | 13.8691 | 4.4309 |  | 14-03-2026 15:20 | 96.73 | 92.935 | 1872.6 | 15.4892 | 14.0704 | 1.4188 | 84.4221 | 17.5 | 13.8691 | 3.6309 |  | 14-03-2026 15:20 | 88.522 | 90.233 | 1841.4 | 15.0388 | 14.0704 | 0.96848 | 84.4221 | 17.8 | 13.8691 | 3.9309 |  | 14-03-2026 15:20 | 89.355 | 90.569 | 1859.8 | 15.0948 | 14.0704 | 1.0245 | 84.4221 | 18 | 13.8691 | 4.1309 |  | 14-03-2026 15:20 | 66.016 | 66.96 | 1386.9 | 11.16 | 10.4225 | 0.73751 | 62.5349 | 13.5 | 10.2734 | 3.2266 |  | 14-03-2026 15:20 | 65.438 | 66.374 | 1371.1 | 11.0623 | 10.4225 | 0.63985 | 62.5349 | 13.4 | 10.2734 | 3.1266 |  | 14-03-2026 15:20 | 65.157 | 66.082 | 1372 | 11.0137 | 10.4225 | 0.59118 | 62.5349 | 13.4 | 10.2734 | 3.1266 |  | 14-03-2026 15:20 | 65.538 | 67.591 | 1379.1 | 11.2652 | 10.4225 | 0.84268 | 62.5349 | 13.4 | 10.2734 | 3.1266 |  | 14-03-2026 15:20 | 62.182 | 63.097 | 1302.1 | 10.5162 | 9.9157 | 0.60046 | 59.4942 | 12.6 | 9.7739 | 2.8261 |  | 14-03-2026 15:20 | 116.2882 | 107.8871 | 8.4011 | 647.3224 | 137.9 | 106.3443 | 31.5557
14-03-2026 15:10 | 364 | 47.35 | 169.833 | 153.505 | 1827 | 25.5842 | 21.7941 | 3.7901 | 130.7645 | 16.1 | 21.4824 | -5.3824 |  | 14-03-2026 15:10 | 175.026 | 177.421 | 1855.1 | 29.5702 | 21.7941 | 7.7761 | 130.7645 | 17.3 | 21.4824 | -4.1824 |  | 14-03-2026 15:10 | 129.425 | 132.002 | 1823.6 | 22.0003 | 21.7941 | 0.20625 | 130.7645 | 16.7 | 21.4824 | -4.7824 |  | 14-03-2026 15:10 | 132.011 | 133.79 | 1841.8 | 22.2983 | 21.7941 | 0.50425 | 130.7645 | 17.1 | 21.4824 | -4.3824 |  | 14-03-2026 15:10 | 100.295 | 101.585 | 1373.4 | 16.9308 | 16.1438 | 0.78707 | 96.8626 | 12.5 | 15.9129 | -3.4129 |  | 14-03-2026 15:10 | 100.667 | 102.705 | 1357.7 | 17.1175 | 16.1438 | 0.97374 | 96.8626 | 12.3 | 15.9129 | -3.6129 |  | 14-03-2026 15:10 | 97.145 | 98.385 | 1358.6 | 16.3975 | 16.1438 | 0.25374 | 96.8626 | 12.2 | 15.9129 | -3.7129 |  | 14-03-2026 15:10 | 98.905 | 101.804 | 1365.7 | 16.9673 | 16.1438 | 0.82357 | 96.8626 | 12.2 | 15.9129 | -3.7129 |  | 14-03-2026 15:10 | 93.483 | 94.705 | 1289.5 | 15.7842 | 15.3588 | 0.42537 | 92.1528 | 11.5 | 15.1392 | -3.6392 |  | 14-03-2026 15:10 | 182.6503 | 167.1102 | 15.5402 | 1002.6611 | 127.9 | 164.7205 | -36.8205
14-03-2026 15:00 | 352 | 48.5 | 143.497 | 119.047 | 1810.9 | 19.8412 | 20.9836 | -1.1424 | 125.9014 | 41.9 | 20.6835 | 21.2165 | 1.2054 | 14-03-2026 15:00 | 135.934 | 137.85 | 1837.8 | 22.975 | 20.9836 | 1.9914 | 125.9014 | 40.6 | 20.6835 | 19.9165 | 0.9861 | 14-03-2026 15:00 | 119.559 | 122.31 | 1806.9 | 20.385 | 20.9836 | -0.59857 | 125.9014 | 39.5 | 20.6835 | 18.8165 | 0.97751 | 14-03-2026 15:00 | 133.301 | 135.18 | 1824.7 | 22.53 | 20.9836 | 1.5464 | 125.9014 | 40 | 20.6835 | 19.3165 | 0.9861 | 14-03-2026 15:00 | 89.944 | 91.193 | 1360.9 | 15.1988 | 15.5434 | -0.34455 | 93.2603 | 29.7 | 15.3211 | 14.3789 | 0.9863 | 14-03-2026 15:00 | 93.226 | 94.502 | 1345.4 | 15.7503 | 15.5434 | 0.20695 | 93.2603 | 29.2 | 15.3211 | 13.8789 | 0.9865 | 14-03-2026 15:00 | 88.296 | 89.714 | 1346.4 | 14.9523 | 15.5434 | -0.59105 | 93.2603 | 29 | 15.3211 | 13.6789 | 0.98419 | 14-03-2026 15:00 | 92.225 | 95.468 | 1353.5 | 15.9113 | 15.5434 | 0.36795 | 93.2603 | 29.2 | 15.3211 | 13.8789 | 0.96603 | 14-03-2026 15:00 | 87.933 | 89.182 | 1278 | 14.8637 | 14.7876 | 0.076062 | 88.7256 | 27.7 | 14.5761 | 13.1239 | 0.98599 | 14-03-2026 15:00 | 162.4077 | 160.8954 | 1.5123 | 965.3725 | 306.8 | 158.5946 | 148.2054
14-03-2026 14:50 | 685 | 48.5 | 244.071 | 247.788 | 1769 | 41.298 | 40.8345 | 0.4635 | 245.007 | 43.7 | 40.2506 | 3.4494 | 0.985 | 14-03-2026 14:50 | 243.577 | 247.362 | 1797.2 | 41.227 | 40.8345 | 0.3925 | 245.007 | 47.2 | 40.2506 | 6.9494 | 0.9847 | 14-03-2026 14:50 | 217.266 | 225.83 | 1767.4 | 37.6383 | 40.8345 | -3.1962 | 245.007 | 46.7 | 40.2506 | 6.4494 | 0.96208 | 14-03-2026 14:50 | 229.662 | 233.159 | 1784.7 | 38.8598 | 40.8345 | -1.9747 | 245.007 | 46.9 | 40.2506 | 6.6494 | 0.985 | 14-03-2026 14:50 | 174.302 | 178.039 | 1331.2 | 29.6732 | 30.2478 | -0.57461 | 181.4867 | 35.1 | 29.8152 | 5.2848 | 0.97901 | 14-03-2026 14:50 | 162.101 | 168.238 | 1316.2 | 28.0397 | 30.2478 | -2.2081 | 181.4867 | 34.6 | 29.8152 | 4.7848 | 0.96352 | 14-03-2026 14:50 | 161.319 | 163.593 | 1317.4 | 27.2655 | 30.2478 | -2.9823 | 181.4867 | 34.6 | 29.8152 | 4.7848 | 0.9861 | 14-03-2026 14:50 | 152.018 | 154.161 | 1324.3 | 25.6935 | 30.2478 | -4.5543 | 181.4867 | 34.8 | 29.8152 | 4.9848 | 0.9861 | 14-03-2026 14:50 | 158.569 | 160.82 | 1250.3 | 26.8033 | 28.777 | -1.9737 | 172.6621 | 32.8 | 28.3655 | 4.4345 | 0.986 | 14-03-2026 14:50 | 296.4983 | 313.1061 | -16.6078 | 1878.6367 | 356.4 | 308.6287 | 47.7713
14-03-2026 14:40 | 881 | 48.5 | 295.963 | 300.775 | 1725.3 | 50.1292 | 52.5185 | -2.3894 | 315.1112 | 49.2 | 51.7675 | -2.5675 | 0.984 | 14-03-2026 14:40 | 301.685 | 306.684 | 1750 | 51.114 | 52.5185 | -1.4045 | 315.1112 | 49.3 | 51.7675 | -2.4675 | 0.9837 | 14-03-2026 14:40 | 296.208 | 304.285 | 1720.7 | 50.7142 | 52.5185 | -1.8044 | 315.1112 | 48.4 | 51.7675 | -3.3675 | 0.97346 | 14-03-2026 14:40 | 298.932 | 303.916 | 1737.8 | 50.6527 | 52.5185 | -1.8659 | 315.1112 | 48.7 | 51.7675 | -3.0675 | 0.9836 | 14-03-2026 14:40 | 224.19 | 227.497 | 1296.1 | 37.9162 | 38.9026 | -0.98645 | 233.4157 | 36.4 | 38.3463 | -1.9463 | 0.98546 | 14-03-2026 14:40 | 220.446 | 224.377 | 1281.6 | 37.3962 | 38.9026 | -1.5064 | 233.4157 | 35.7 | 38.3463 | -2.6463 | 0.98248 | 14-03-2026 14:40 | 221.5 | 225.646 | 1282.8 | 37.6077 | 38.9026 | -1.2949 | 233.4157 | 36.5 | 38.3463 | -1.8463 | 0.98163 | 14-03-2026 14:40 | 222.818 | 229.4 | 1289.5 | 38.2333 | 38.9026 | -0.66928 | 233.4157 | 36.7 | 38.3463 | -1.6463 | 0.97131 | 14-03-2026 14:40 | 209.555 | 212.66 | 1217.5 | 35.4433 | 37.011 | -1.5677 | 222.0661 | 34.5 | 36.4818 | -1.9818 | 0.9854 | 14-03-2026 14:40 | 389.2067 | 402.6956 | -13.4889 | 2416.1737 | 375.4 | 396.9371 | -21.5371
14-03-2026 14:30 | 876 | 48.5 | 296.161 | 300.915 | 1676.1 | 50.1525 | 52.2205 | -2.068 | 313.3228 | 49.9 | 51.4737 | -1.5737 | 0.9842 | 14-03-2026 14:30 | 301.547 | 306.544 | 1700.7 | 51.0907 | 52.2205 | -1.1298 | 313.3228 | 52.8 | 51.4737 | 1.3263 | 0.9837 | 14-03-2026 14:30 | 294.676 | 302.68 | 1672.3 | 50.4467 | 52.2205 | -1.7738 | 313.3228 | 49.8 | 51.4737 | -1.6737 | 0.97356 | 14-03-2026 14:30 | 296.292 | 301.202 | 1689.1 | 50.2003 | 52.2205 | -2.0201 | 313.3228 | 50.1 | 51.4737 | -1.3737 | 0.9837 | 14-03-2026 14:30 | 221.513 | 224.841 | 1259.7 | 37.4735 | 38.6818 | -1.2083 | 232.091 | 37.5 | 38.1287 | -0.62868 | 0.9852 | 14-03-2026 14:30 | 216.672 | 220.507 | 1245.9 | 36.7512 | 38.6818 | -1.9307 | 232.091 | 36.8 | 38.1287 | -1.3287 | 0.98261 | 14-03-2026 14:30 | 217.357 | 221.87 | 1246.3 | 36.9783 | 38.6818 | -1.7035 | 232.091 | 36.2 | 38.1287 | -1.9287 | 0.97966 | 14-03-2026 14:30 | 217.923 | 224.241 | 1252.8 | 37.3735 | 38.6818 | -1.3083 | 232.091 | 36.8 | 38.1287 | -1.3287 | 0.97182 | 14-03-2026 14:30 | 204.907 | 207.964 | 1183 | 34.6607 | 36.801 | -2.1403 | 220.8058 | 34.8 | 36.2747 | -1.4747 | 0.9853 | 14-03-2026 14:30 | 385.1273 | 400.4102 | -15.2828 | 2402.461 | 384.7 | 394.6843 | -9.9843
14-03-2026 14:20 | 884 | 48.5 | 298.786 | 303.644 | 1626.2 | 50.6073 | 52.6974 | -2.09 | 316.1842 | 49.7 | 51.9438 | -2.2438 | 0.984 | 14-03-2026 14:20 | 302.114 | 308.594 | 1647.9 | 51.4323 | 52.6974 | -1.265 | 316.1842 | 49.1 | 51.9438 | -2.8438 | 0.979 | 14-03-2026 14:20 | 297.656 | 305.583 | 1622.5 | 50.9305 | 52.6974 | -1.7669 | 316.1842 | 49.6 | 51.9438 | -2.3438 | 0.97406 | 14-03-2026 14:20 | 300.207 | 305.181 | 1639 | 50.8635 | 52.6974 | -1.8339 | 316.1842 | 50 | 51.9438 | -1.9438 | 0.9837 | 14-03-2026 14:20 | 224.041 | 227.384 | 1222.2 | 37.8973 | 39.0351 | -1.1378 | 234.2105 | 37.9 | 38.4769 | -0.57689 | 0.9853 | 14-03-2026 14:20 | 219.824 | 223.802 | 1209.1 | 37.3003 | 39.0351 | -1.7348 | 234.2105 | 37.3 | 38.4769 | -1.1769 | 0.98223 | 14-03-2026 14:20 | 220.206 | 224.276 | 1210.1 | 37.3793 | 39.0351 | -1.6558 | 234.2105 | 37.3 | 38.4769 | -1.1769 | 0.98185 | 14-03-2026 14:20 | 220.577 | 226.717 | 1216 | 37.7862 | 39.0351 | -1.2489 | 234.2105 | 37 | 38.4769 | -1.4769 | 0.97292 | 14-03-2026 14:20 | 208.105 | 211.21 | 1148.2 | 35.2017 | 37.1371 | -1.9354 | 222.8223 | 34.8 | 36.606 | -1.806 | 0.9853 | 14-03-2026 14:20 | 389.3985 | 404.0669 | -14.6684 | 2424.4013 | 382.7 | 398.2887 | -15.5887
14-03-2026 14:10 | 905 | 48.22 | 308.634 | 309.531 | 1576.5 | 51.5885 | 54.0068 | -2.4183 | 324.041 | 51.2 | 53.2345 | -2.0345 | 0.9971 | 14-03-2026 14:10 | 313.518 | 318.778 | 1598.8 | 53.1297 | 54.0068 | -0.87717 | 324.041 | 52.7 | 53.2345 | -0.53454 | 0.9835 | 14-03-2026 14:10 | 304.037 | 312.548 | 1572.9 | 52.0913 | 54.0068 | -1.9155 | 324.041 | 51.2 | 53.2345 | -2.0345 | 0.97277 | 14-03-2026 14:10 | 307.076 | 312.296 | 1589 | 52.0493 | 54.0068 | -1.9575 | 324.041 | 51.5 | 53.2345 | -1.7345 | 0.98329 | 14-03-2026 14:10 | 229.8 | 233.305 | 1184.3 | 38.8842 | 40.0051 | -1.1209 | 240.0304 | 38.1 | 39.433 | -1.333 | 0.98498 | 14-03-2026 14:10 | 226.224 | 230.119 | 1171.8 | 38.3532 | 40.0051 | -1.6519 | 240.0304 | 37.9 | 39.433 | -1.533 | 0.98307 | 14-03-2026 14:10 | 226.132 | 230.402 | 1172.8 | 38.4003 | 40.0051 | -1.6047 | 240.0304 | 38.1 | 39.433 | -1.333 | 0.98147 | 14-03-2026 14:10 | 227.298 | 234.072 | 1179 | 39.012 | 40.0051 | -0.99307 | 240.0304 | 38.3 | 39.433 | -1.133 | 0.97106 | 14-03-2026 14:10 | 214.576 | 217.977 | 1113.4 | 36.3295 | 38.0599 | -1.7304 | 228.3592 | 36.1 | 37.5156 | -1.4156 | 0.9844 | 14-03-2026 14:10 | 399.838 | 414.1075 | -14.2695 | 2484.6449 | 395.1 | 408.1857 | -13.0857
14-03-2026 14:00 | 917 | 48.5 | 307.565 | 312.491 | 1525.3 | 52.0818 | 54.6646 | -2.5827 | 327.9875 | 53.2 | 53.8829 | -0.68287 | 0.98424 | 14-03-2026 14:00 | 312.717 | 318.028 | 1546.1 | 53.0047 | 54.6646 | -1.6599 | 327.9875 | 52.7 | 53.8829 | -1.1829 | 0.9833 | 14-03-2026 14:00 | 308.08 | 316.738 | 1521.7 | 52.7897 | 54.6646 | -1.8749 | 327.9875 | 53.2 | 53.8829 | -0.68287 | 0.97267 | 14-03-2026 14:00 | 309.564 | 314.758 | 1537.5 | 52.4597 | 54.6646 | -2.2049 | 327.9875 | 53.6 | 53.8829 | -0.28287 | 0.9835 | 14-03-2026 14:00 | 232.407 | 235.994 | 1146.2 | 39.3323 | 40.4923 | -1.1599 | 242.9537 | 40.3 | 39.9132 | 0.38676 | 0.9848 | 14-03-2026 14:00 | 227.698 | 232.164 | 1133.9 | 38.694 | 40.4923 | -1.7983 | 242.9537 | 39 | 39.9132 | -0.91324 | 0.98076 | 14-03-2026 14:00 | 229.015 | 233.451 | 1134.7 | 38.9085 | 40.4923 | -1.5838 | 242.9537 | 39.1 | 39.9132 | -0.81324 | 0.981 | 14-03-2026 14:00 | 230.243 | 236.968 | 1140.7 | 39.4947 | 40.4923 | -0.99761 | 242.9537 | 39.9 | 39.9132 | -0.013241 | 0.97162 | 14-03-2026 14:00 | 216.741 | 219.997 | 1077.3 | 36.6662 | 38.5234 | -1.8572 | 231.1403 | 37.6 | 37.9725 | -0.37251 | 0.9852 | 14-03-2026 14:00 | 403.4315 | 419.1508 | -15.7193 | 2514.9049 | 408.6 | 413.157 | -4.557
14-03-2026 13:50 | 923 | 48.5 | 311.448 | 315.88 | 1472.1 | 52.6467 | 55.0223 | -2.3756 | 330.1335 | 52.6 | 54.2354 | -1.6354 | 0.98597 | 14-03-2026 13:50 | 314.718 | 320.031 | 1493.4 | 53.3385 | 55.0223 | -1.6838 | 330.1335 | 54.4 | 54.2354 | 0.16457 | 0.9834 | 14-03-2026 13:50 | 309.878 | 318.531 | 1468.5 | 53.0885 | 55.0223 | -1.9338 | 330.1335 | 53.6 | 54.2354 | -0.63543 | 0.97283 | 14-03-2026 13:50 | 312.405 | 317.711 | 1483.9 | 52.9518 | 55.0223 | -2.0704 | 330.1335 | 53.3 | 54.2354 | -0.93543 | 0.9833 | 14-03-2026 13:50 | 235.869 | 239.51 | 1105.9 | 39.9183 | 40.7572 | -0.83889 | 244.5433 | 40 | 40.1744 | -0.1744 | 0.9848 | 14-03-2026 13:50 | 230.771 | 235.27 | 1094.9 | 39.2117 | 40.7572 | -1.5456 | 244.5433 | 39.3 | 40.1744 | -0.8744 | 0.98088 | 14-03-2026 13:50 | 232.364 | 238.184 | 1095.6 | 39.6973 | 40.7572 | -1.0599 | 244.5433 | 39.5 | 40.1744 | -0.6744 | 0.97557 | 14-03-2026 13:50 | 233.634 | 240.601 | 1100.8 | 40.1002 | 40.7572 | -0.65706 | 244.5433 | 39.1 | 40.1744 | -1.0744 | 0.97104 | 14-03-2026 13:50 | 219.099 | 222.39 | 1039.7 | 37.065 | 38.7755 | -1.7105 | 232.6527 | 37.2 | 38.221 | -1.021 | 0.9852 | 14-03-2026 13:50 | 408.018 | 421.8934 | -13.8754 | 2531.3602 | 409 | 415.8603 | -6.8603
14-03-2026 13:40 | 941 | 48.5 | 316.91 | 322.194 | 1419.5 | 53.699 | 56.0953 | -2.3963 | 336.5717 | 53.8 | 55.2931 | -1.4931 | 0.9836 | 14-03-2026 13:40 | 321.844 | 327.31 | 1439 | 54.5517 | 56.0953 | -1.5436 | 336.5717 | 53.8 | 55.2931 | -1.4931 | 0.9833 | 14-03-2026 13:40 | 315.989 | 324.404 | 1414.9 | 54.0673 | 56.0953 | -2.0279 | 336.5717 | 52 | 55.2931 | -3.2931 | 0.97406 | 14-03-2026 13:40 | 317.774 | 323.173 | 1430.6 | 53.8622 | 56.0953 | -2.2331 | 336.5717 | 53.1 | 55.2931 | -2.1931 | 0.98329 | 14-03-2026 13:40 | 238.964 | 242.677 | 1065.9 | 40.4462 | 41.5521 | -1.1059 | 249.3123 | 39.8 | 40.9579 | -1.1579 | 0.9847 | 14-03-2026 13:40 | 233.973 | 238.248 | 1055.6 | 39.708 | 41.5521 | -1.8441 | 249.3123 | 39 | 40.9579 | -1.9579 | 0.98206 | 14-03-2026 13:40 | 236.066 | 240.574 | 1056.1 | 40.0957 | 41.5521 | -1.4564 | 249.3123 | 39.8 | 40.9579 | -1.1579 | 0.98126 | 14-03-2026 13:40 | 237.211 | 243.863 | 1061.7 | 40.6438 | 41.5521 | -0.90822 | 249.3123 | 39.6 | 40.9579 | -1.3579 | 0.97272 | 14-03-2026 13:40 | 222.198 | 225.582 | 1002.5 | 37.597 | 39.5316 | -1.9346 | 237.1898 | 36.8 | 38.9663 | -2.1663 | 0.985 | 14-03-2026 13:40 | 414.6708 | 430.121 | -15.4501 | 2580.7258 | 407.7 | 423.9702 | -16.2702
14-03-2026 13:30 | 977 | 48.79 | 328.025 | 333.528 | 1365.7 | 55.588 | 58.1769 | -2.5889 | 349.0615 | 55 | 57.345 | -2.345 | 0.9835 | 14-03-2026 13:30 | 331.679 | 337.381 | 1385.2 | 56.2302 | 58.1769 | -1.9467 | 349.0615 | 54.4 | 57.345 | -2.945 | 0.9831 | 14-03-2026 13:30 | 327.311 | 336.769 | 1362.9 | 56.1282 | 58.1769 | -2.0487 | 349.0615 | 53.5 | 57.345 | -3.845 | 0.97192 | 14-03-2026 13:30 | 328.426 | 334.072 | 1377.5 | 55.6787 | 58.1769 | -2.4982 | 349.0615 | 54.7 | 57.345 | -2.645 | 0.9831 | 14-03-2026 13:30 | 246.791 | 250.626 | 1026.1 | 41.771 | 43.094 | -1.323 | 258.564 | 40.6 | 42.4778 | -1.8778 | 0.9847 | 14-03-2026 13:30 | 241.79 | 246.3 | 1016.6 | 41.05 | 43.094 | -2.044 | 258.564 | 40.3 | 42.4778 | -2.1778 | 0.98169 | 14-03-2026 13:30 | 242.499 | 247.758 | 1016.3 | 41.293 | 43.094 | -1.801 | 258.564 | 39.9 | 42.4778 | -2.5778 | 0.97877 | 14-03-2026 13:30 | 243.573 | 250.881 | 1022.1 | 41.8135 | 43.094 | -1.2805 | 258.564 | 40.5 | 42.4778 | -1.9778 | 0.97087 | 14-03-2026 13:30 | 229.223 | 232.805 | 965.7 | 38.8008 | 40.9986 | -2.1978 | 245.9917 | 38.2 | 40.4123 | -2.2123 | 0.98461 | 14-03-2026 13:30 | 428.3533 | 446.0823 | -17.7289 | 2676.4937 | 417.1 | 439.7033 | -22.6033
14-03-2026 13:20 | 938 | 48.5 | 315.361 | 320.619 | 1310.7 | 53.4365 | 55.9164 | -2.4799 | 335.4986 | 51.9 | 55.1168 | -3.2168 | 0.9836 | 14-03-2026 13:20 | 320.638 | 326.084 | 1330.8 | 54.3473 | 55.9164 | -1.5691 | 335.4986 | 55.1 | 55.1168 | -0.016834 | 0.9833 | 14-03-2026 13:20 | 315.679 | 324.829 | 1309.4 | 54.1382 | 55.9164 | -1.7783 | 335.4986 | 54.8 | 55.1168 | -0.31683 | 0.97183 | 14-03-2026 13:20 | 317.778 | 323.175 | 1322.8 | 53.8625 | 55.9164 | -2.0539 | 335.4986 | 54.5 | 55.1168 | -0.61683 | 0.9833 | 14-03-2026 13:20 | 238.005 | 241.679 | 985.5 | 40.2798 | 41.4196 | -1.1398 | 248.5175 | 41.3 | 40.8273 | 0.47272 | 0.9848 | 14-03-2026 13:20 | 233.572 | 238.109 | 976.3 | 39.6848 | 41.4196 | -1.7348 | 248.5175 | 40.1 | 40.8273 | -0.72728 | 0.98095 | 14-03-2026 13:20 | 234.813 | 239.805 | 976.4 | 39.9675 | 41.4196 | -1.4521 | 248.5175 | 40.3 | 40.8273 | -0.52728 | 0.97918 | 14-03-2026 13:20 | 236.011 | 243.049 | 981.6 | 40.5082 | 41.4196 | -0.91142 | 248.5175 | 40.6 | 40.8273 | -0.22728 | 0.97104 | 14-03-2026 13:20 | 221.728 | 225.105 | 927.5 | 37.5175 | 39.4056 | -1.8881 | 236.4336 | 38.1 | 38.8421 | -0.7421 | 0.985 | 14-03-2026 13:20 | 413.7423 | 428.7497 | -15.0074 | 2572.4982 | 416.7 | 422.6186 | -5.9186
14-03-2026 13:10 | 952 | 48.79 | 319.829 | 325.228 | 1258.8 | 54.2047 | 56.6882 | -2.4836 | 340.1295 | 56.6 | 55.8776 | 0.72239 | 0.9834 | 14-03-2026 13:10 | 326.535 | 332.115 | 1275.7 | 55.3525 | 56.6882 | -1.3357 | 340.1295 | 55.1 | 55.8776 | -0.77761 | 0.9832 | 14-03-2026 13:10 | 319.306 | 328.481 | 1254.6 | 54.7468 | 56.6882 | -1.9414 | 340.1295 | 53.6 | 55.8776 | -2.2776 | 0.97207 | 14-03-2026 13:10 | 322.965 | 328.534 | 1268.3 | 54.7557 | 56.6882 | -1.9326 | 340.1295 | 54 | 55.8776 | -1.8776 | 0.98305 | 14-03-2026 13:10 | 243.383 | 247.009 | 944.2 | 41.1682 | 41.9913 | -0.82313 | 251.9478 | 40.7 | 41.3908 | -0.69082 | 0.98532 | 14-03-2026 13:10 | 238.257 | 242.914 | 936.2 | 40.4857 | 41.9913 | -1.5056 | 251.9478 | 39.9 | 41.3908 | -1.4908 | 0.98083 | 14-03-2026 13:10 | 240.303 | 245.514 | 936.1 | 40.919 | 41.9913 | -1.0723 | 251.9478 | 40.1 | 41.3908 | -1.2908 | 0.97878 | 14-03-2026 13:10 | 241.258 | 248.44 | 941 | 41.4067 | 41.9913 | -0.58463 | 251.9478 | 40.6 | 41.3908 | -0.79082 | 0.97109 | 14-03-2026 13:10 | 226.734 | 230.234 | 889.4 | 38.3723 | 39.9495 | -1.5772 | 239.6971 | 38.3 | 39.3782 | -1.0782 | 0.9848 | 14-03-2026 13:10 | 421.4115 | 434.6677 | -13.2562 | 2608.0061 | 418.9 | 428.4519 | -9.5519
14-03-2026 13:00 | 950 | 48.5 | 321.539 | 326.867 | 1202.2 | 54.4778 | 56.6318 | -2.154 | 339.7907 | 53.1 | 55.822 | -2.722 | 0.9837 | 14-03-2026 13:00 | 325.536 | 331.065 | 1220.6 | 55.1775 | 56.6318 | -1.4543 | 339.7907 | 54.6 | 55.822 | -1.222 | 0.9833 | 14-03-2026 13:00 | 317.47 | 326.507 | 1201 | 54.4178 | 56.6318 | -2.214 | 339.7907 | 54.3 | 55.822 | -1.522 | 0.97232 | 14-03-2026 13:00 | 321.494 | 327.096 | 1214.3 | 54.516 | 56.6318 | -2.1158 | 339.7907 | 54.7 | 55.822 | -1.122 | 0.98287 | 14-03-2026 13:00 | 239.99 | 243.694 | 903.5 | 40.6157 | 41.9495 | -1.3338 | 251.6968 | 41 | 41.3496 | -0.34959 | 0.9848 | 14-03-2026 13:00 | 236.835 | 241.163 | 896.3 | 40.1938 | 41.9495 | -1.7556 | 251.6968 | 40.9 | 41.3496 | -0.44959 | 0.98205 | 14-03-2026 13:00 | 237.117 | 242.031 | 896 | 40.3385 | 41.9495 | -1.611 | 251.6968 | 40.6 | 41.3496 | -0.74959 | 0.9797 | 14-03-2026 13:00 | 238.399 | 245.368 | 900.4 | 40.8947 | 41.9495 | -1.0548 | 251.6968 | 40.4 | 41.3496 | -0.94959 | 0.9716 | 14-03-2026 13:00 | 225.306 | 228.784 | 851.1 | 38.1307 | 39.9097 | -1.7791 | 239.4584 | 38.4 | 39.339 | -0.93902 | 0.9848 | 14-03-2026 13:00 | 418.7625 | 434.2348 | -15.4723 | 2605.4086 | 418 | 428.0252 | -10.0252
14-03-2026 12:50 | 935 | 48.5 | 315.303 | 320.495 | 1149.1 | 53.4158 | 55.7376 | -2.3218 | 334.4256 | 54 | 54.9406 | -0.94055 | 0.9838 | 14-03-2026 12:50 | 320.689 | 326.102 | 1166 | 54.3503 | 55.7376 | -1.3873 | 334.4256 | 54.8 | 54.9406 | -0.14055 | 0.9834 | 14-03-2026 12:50 | 315.337 | 324.108 | 1146.7 | 54.018 | 55.7376 | -1.7196 | 334.4256 | 53.8 | 54.9406 | -1.1406 | 0.97294 | 14-03-2026 12:50 | 318.021 | 323.422 | 1159.6 | 53.9037 | 55.7376 | -1.8339 | 334.4256 | 54.3 | 54.9406 | -0.64055 | 0.9833 | 14-03-2026 12:50 | 238.152 | 241.828 | 862.5 | 40.3047 | 41.2871 | -0.98245 | 247.7227 | 40.6 | 40.6967 | -0.096707 | 0.9848 | 14-03-2026 12:50 | 234.414 | 238.495 | 855.4 | 39.7492 | 41.2871 | -1.5379 | 247.7227 | 40 | 40.6967 | -0.69671 | 0.98289 | 14-03-2026 12:50 | 235.307 | 239.779 | 855.4 | 39.9632 | 41.2871 | -1.3239 | 247.7227 | 40.1 | 40.6967 | -0.59671 | 0.98135 | 14-03-2026 12:50 | 235.948 | 242.883 | 860 | 40.4805 | 41.2871 | -0.80661 | 247.7227 | 40.3 | 40.6967 | -0.39671 | 0.97145 | 14-03-2026 12:50 | 222.388 | 225.706 | 812.7 | 37.6177 | 39.2796 | -1.6619 | 235.6774 | 38.1 | 38.7179 | -0.61788 | 0.9853 | 14-03-2026 12:50 | 413.803 | 427.3784 | -13.5754 | 2564.2706 | 416 | 421.2669 | -5.2669
14-03-2026 12:40 | 980 | 48.79 | 330.347 | 335.889 | 1095.1 | 55.9815 | 58.3555 | -2.374 | 350.1333 | 54 | 57.5211 | -3.5211 | 0.9835 | 14-03-2026 12:40 | 328.948 | 340.764 | 1111.2 | 56.794 | 58.3555 | -1.5615 | 350.1333 | 55.5 | 57.5211 | -2.0211 | 0.96532 | 14-03-2026 12:40 | 328.727 | 338.087 | 1092.9 | 56.3478 | 58.3555 | -2.0077 | 350.1333 | 53.9 | 57.5211 | -3.6211 | 0.97231 | 14-03-2026 12:40 | 330.874 | 336.562 | 1105.3 | 56.0937 | 58.3555 | -2.2619 | 350.1333 | 54.2 | 57.5211 | -3.3211 | 0.9831 | 14-03-2026 12:40 | 248.986 | 252.806 | 821.9 | 42.1343 | 43.2263 | -1.092 | 259.358 | 40.6 | 42.6082 | -2.0082 | 0.98489 | 14-03-2026 12:40 | 244.583 | 249.151 | 815.4 | 41.5252 | 43.2263 | -1.7012 | 259.358 | 39.4 | 42.6082 | -3.2082 | 0.98167 | 14-03-2026 12:40 | 246.19 | 251.179 | 815.3 | 41.8632 | 43.2263 | -1.3632 | 259.358 | 40.5 | 42.6082 | -2.1082 | 0.98014 | 14-03-2026 12:40 | 247.457 | 254.555 | 819.7 | 42.4258 | 43.2263 | -0.8005 | 259.358 | 40.7 | 42.6082 | -1.9082 | 0.97212 | 14-03-2026 12:40 | 233.276 | 236.877 | 774.6 | 39.4795 | 41.1245 | -1.645 | 246.747 | 37.9 | 40.5364 | -2.6364 | 0.9848 | 14-03-2026 12:40 | 432.645 | 447.452 | -14.807 | 2684.7122 | 416.7 | 441.0535 | -24.3535
14-03-2026 12:30 | 971 | 48.5 | 327.766 | 333.265 | 1041.1 | 55.5442 | 57.8836 | -2.3395 | 347.3019 | 53.8 | 57.0559 | -3.2559 | 0.9835 | 14-03-2026 12:30 | 332.372 | 338.017 | 1055.7 | 56.3362 | 57.8836 | -1.5475 | 347.3019 | 54.7 | 57.0559 | -2.3559 | 0.9833 | 14-03-2026 12:30 | 326.054 | 334.966 | 1039 | 55.8277 | 57.8836 | -2.056 | 347.3019 | 54.2 | 57.0559 | -2.8559 | 0.97339 | 14-03-2026 12:30 | 328.787 | 334.405 | 1051.1 | 55.7342 | 57.8836 | -2.1495 | 347.3019 | 54.7 | 57.0559 | -2.3559 | 0.9832 | 14-03-2026 12:30 | 246.715 | 250.523 | 781.3 | 41.7538 | 42.8768 | -1.1229 | 257.2607 | 41 | 42.2636 | -1.2636 | 0.9848 | 14-03-2026 12:30 | 242.66 | 246.945 | 776 | 41.1575 | 42.8768 | -1.7193 | 257.2607 | 41 | 42.2636 | -1.2636 | 0.98265 | 14-03-2026 12:30 | 243.553 | 248.522 | 774.8 | 41.4203 | 42.8768 | -1.4564 | 257.2607 | 40.7 | 42.2636 | -1.5636 | 0.98001 | 14-03-2026 12:30 | 244.108 | 251.644 | 779 | 41.9407 | 42.8768 | -0.93611 | 257.2607 | 40.9 | 42.2636 | -1.3636 | 0.97005 | 14-03-2026 12:30 | 230.102 | 233.63 | 736.7 | 38.9383 | 40.7919 | -1.8536 | 244.7517 | 38.5 | 40.2086 | -1.7086 | 0.9849 | 14-03-2026 12:30 | 428.6528 | 443.8336 | -15.1808 | 2663.0018 | 419.5 | 437.4868 | -17.9868
14-03-2026 12:20 | 982 | 48.5 | 329.759 | 335.325 | 987.3 | 55.8875 | 58.5394 | -2.6519 | 351.2363 | 54 | 57.7023 | -3.7023 | 0.9834 | 14-03-2026 12:20 | 334.799 | 340.554 | 1001 | 56.759 | 58.5394 | -1.7804 | 351.2363 | 55.7 | 57.7023 | -2.0023 | 0.9831 | 14-03-2026 12:20 | 326.182 | 335.133 | 984.8 | 55.8555 | 58.5394 | -2.6839 | 351.2363 | 54 | 57.7023 | -3.7023 | 0.97329 | 14-03-2026 12:20 | 330.341 | 336.02 | 996.4 | 56.0033 | 58.5394 | -2.5361 | 351.2363 | 54.5 | 57.7023 | -3.2023 | 0.9831 | 14-03-2026 12:20 | 245.783 | 249.602 | 740.3 | 41.6003 | 43.3625 | -1.7622 | 260.175 | 40.6 | 42.7424 | -2.1424 | 0.9847 | 14-03-2026 12:20 | 242.577 | 247.053 | 735 | 41.1755 | 43.3625 | -2.187 | 260.175 | 39.5 | 42.7424 | -3.2424 | 0.98188 | 14-03-2026 12:20 | 242.479 | 247.145 | 734.1 | 41.1908 | 43.3625 | -2.1717 | 260.175 | 39.4 | 42.7424 | -3.3424 | 0.98112 | 14-03-2026 12:20 | 244.615 | 251.752 | 738.1 | 41.9587 | 43.3625 | -1.4038 | 260.175 | 39.7 | 42.7424 | -3.0424 | 0.97165 | 14-03-2026 12:20 | 230.435 | 233.968 | 698.2 | 38.9947 | 41.2541 | -2.2594 | 247.5243 | 38 | 40.6641 | -2.6641 | 0.9849 | 14-03-2026 12:20 | 429.4253 | 448.8616 | -19.4363 | 2693.1697 | 415.4 | 442.4429 | -27.0429
14-03-2026 12:10 | 959 | 48.79 | 323.703 | 329.134 | 933.3 | 54.8557 | 57.1051 | -2.2494 | 342.6304 | 53.2 | 56.2885 | -3.0885 | 0.9835 | 14-03-2026 12:10 | 326.26 | 331.869 | 945.3 | 55.3115 | 57.1051 | -1.7936 | 342.6304 | 105.8 | 56.2885 | 49.5115 | 0.9831 | 14-03-2026 12:10 | 323.099 | 332.113 | 930.8 | 55.3522 | 57.1051 | -1.7529 | 342.6304 | 53.2 | 56.2885 | -3.0885 | 0.97286 | 14-03-2026 12:10 | 325.517 | 331.079 | 941.9 | 55.1798 | 57.1051 | -1.9252 | 342.6304 | 53.8 | 56.2885 | -2.4885 | 0.9832 | 14-03-2026 12:10 | 243.31 | 247.065 | 699.7 | 41.1775 | 42.3001 | -1.1226 | 253.8003 | 40.2 | 41.6952 | -1.4952 | 0.9848 | 14-03-2026 12:10 | 239.477 | 244.251 | 695.5 | 40.7085 | 42.3001 | -1.5916 | 253.8003 | 39.6 | 41.6952 | -2.0952 | 0.98045 | 14-03-2026 12:10 | 239.731 | 244.669 | 694.7 | 40.7782 | 42.3001 | -1.5219 | 253.8003 | 39.6 | 41.6952 | -2.0952 | 0.97982 | 14-03-2026 12:10 | 239.995 | 247.126 | 698.4 | 41.1877 | 42.3001 | -1.1124 | 253.8003 | 40.3 | 41.6952 | -1.3952 | 0.97114 | 14-03-2026 12:10 | 226.703 | 230.179 | 660.2 | 38.3632 | 40.2433 | -1.8801 | 241.4596 | 37.5 | 39.6678 | -2.1678 | 0.9849 | 14-03-2026 12:10 | 422.9142 | 437.8638 | -14.9496 | 2627.1826 | 463.2 | 431.6023 | 31.5977
14-03-2026 12:00 | 947 | 48.5 | 319.475 | 324.693 | 880.1 | 54.1155 | 56.453 | -2.3375 | 338.7177 | 51.8 | 55.6457 | -3.8457 | 0.98393 |  |  |  |  | 0 | 56.453 | -56.453 | 338.7177 | 0 | 55.6457 | -55.6457 |  | 14-03-2026 12:00 | 319.007 | 328.014 | 877.6 | 54.669 | 56.453 | -1.784 | 338.7177 | 52.4 | 55.6457 | -3.2457 | 0.97254 | 14-03-2026 12:00 | 322.259 | 327.732 | 888.1 | 54.622 | 56.453 | -1.831 | 338.7177 | 53 | 55.6457 | -2.6457 | 0.9833 | 14-03-2026 12:00 | 241.281 | 245 | 659.5 | 40.8333 | 41.817 | -0.98367 | 250.902 | 39.6 | 41.219 | -1.619 | 0.98482 | 14-03-2026 12:00 | 237.67 | 242.053 | 655.9 | 40.3422 | 41.817 | -1.4748 | 250.902 | 39.1 | 41.219 | -2.119 | 0.98189 | 14-03-2026 12:00 | 238.719 | 243.472 | 655.1 | 40.5787 | 41.817 | -1.2383 | 250.902 | 39.2 | 41.219 | -2.019 | 0.98048 | 14-03-2026 12:00 | 240.228 | 247.131 | 658.1 | 41.1885 | 41.817 | -0.6285 | 250.902 | 38.9 | 41.219 | -2.319 | 0.97207 | 14-03-2026 12:00 | 226.35 | 229.82 | 622.7 | 38.3033 | 39.7837 | -1.4804 | 238.7022 | 36.6 | 39.2148 | -2.6148 | 0.9849 | 14-03-2026 12:00 | 364.6525 | 432.8635 | -68.211 | 2597.181 | 350.6 | 426.6736 | -76.0736
14-03-2026 11:50 | 965 | 48.5 | 318.424 | 323.602 | 828.3 | 53.9337 | 57.526 | -3.5923 | 345.1558 | 50.4 | 56.7034 | -6.3034 | 0.984 | 14-03-2026 11:50 | 321.81 | 320.254 | 839.5 | 53.3757 | 57.526 | -4.1503 | 345.1558 | 50.6 | 56.7034 | -6.1034 | 1.0049 | 14-03-2026 11:50 | 326.565 | 338.229 | 825.2 | 56.3715 | 57.526 | -1.1545 | 345.1558 | 48.8 | 56.7034 | -7.9034 | 0.96551 | 14-03-2026 11:50 | 324.447 | 329.957 | 835.1 | 54.9928 | 57.526 | -2.5331 | 345.1558 | 49.5 | 56.7034 | -7.2034 | 0.9833 | 14-03-2026 11:50 | 245.686 | 249.427 | 619.9 | 41.5712 | 42.6118 | -1.0407 | 255.671 | 37.6 | 42.0025 | -4.4025 | 0.985 | 14-03-2026 11:50 | 244.519 | 248.761 | 616.8 | 41.4602 | 42.6118 | -1.1517 | 255.671 | 37.3 | 42.0025 | -4.7025 | 0.98295 | 14-03-2026 11:50 | 240.922 | 245.68 | 615.9 | 40.9467 | 42.6118 | -1.6652 | 255.671 | 37.3 | 42.0025 | -4.7025 | 0.98063 | 14-03-2026 11:50 | 241.868 | 248.967 | 619.2 | 41.4945 | 42.6118 | -1.1173 | 255.671 | 37.6 | 42.0025 | -4.4025 | 0.97149 | 14-03-2026 11:50 | 228.456 | 231.888 | 586.1 | 38.648 | 40.5399 | -1.8919 | 243.2393 | 35.6 | 39.9602 | -4.3602 | 0.9852 | 14-03-2026 11:50 | 422.7942 | 441.0911 | -18.2969 | 2646.5466 | 384.7 | 434.7835 | -50.0835
14-03-2026 11:40 | 710 | 48.5 | 236.741 | 240.297 | 777.9 | 40.0495 | 42.3248 | -2.2753 | 253.9489 | 48.3 | 41.7196 | 6.5804 | 0.9852 | 14-03-2026 11:40 | 243.497 | 247.23 | 788.9 | 41.205 | 42.3248 | -1.1198 | 253.9489 | 51.9 | 41.7196 | 10.1804 | 0.9849 | 14-03-2026 11:40 | 244.725 | 251.497 | 776.4 | 41.9162 | 42.3248 | -0.40864 | 253.9489 | 50.3 | 41.7196 | 8.5804 | 0.97307 | 14-03-2026 11:40 | 238.914 | 242.528 | 785.6 | 40.4213 | 42.3248 | -1.9035 | 253.9489 | 50.8 | 41.7196 | 9.0804 | 0.9851 | 14-03-2026 11:40 | 179.033 | 182.181 | 582.3 | 30.3635 | 31.3517 | -0.98821 | 188.1103 | 37.4 | 30.9034 | 6.4966 | 0.98272 | 14-03-2026 11:40 | 175.178 | 178.74 | 579.5 | 29.79 | 31.3517 | -1.5617 | 188.1103 | 36.9 | 30.9034 | 5.9966 | 0.98007 | 14-03-2026 11:40 | 178.723 | 183.812 | 578.6 | 30.6353 | 31.3517 | -0.71638 | 188.1103 | 36.9 | 30.9034 | 5.9966 | 0.97231 | 14-03-2026 11:40 | 181.645 | 187.894 | 581.6 | 31.3157 | 31.3517 | -0.036044 | 188.1103 | 37 | 30.9034 | 6.0966 | 0.96674 | 14-03-2026 11:40 | 170.029 | 172.478 | 550.5 | 28.7463 | 29.8273 | -1.0809 | 178.9636 | 35 | 29.4007 | 5.5993 | 0.9858 | 14-03-2026 11:40 | 314.4428 | 324.5334 | -10.0905 | 1947.2001 | 384.5 | 319.8925 | 64.6075
14-03-2026 11:30 | 895 | 48.5 | 304.801 | 309.726 | 729.6 | 51.621 | 53.3531 | -1.7321 | 320.1186 | 50.3 | 52.5902 | -2.2902 | 0.9841 | 14-03-2026 11:30 | 309.409 | 314.536 | 737 | 52.4227 | 53.3531 | -0.93044 | 320.1186 | 50.3 | 52.5902 | -2.2902 | 0.9837 | 14-03-2026 11:30 | 303.99 | 312.17 | 726.1 | 52.0283 | 53.3531 | -1.3248 | 320.1186 | 49.4 | 52.5902 | -3.1902 | 0.9738 | 14-03-2026 11:30 | 306.966 | 312.02 | 734.8 | 52.0033 | 53.3531 | -1.3498 | 320.1186 | 49.9 | 52.5902 | -2.6902 | 0.9838 | 14-03-2026 11:30 | 229.103 | 232.545 | 544.9 | 38.7575 | 39.5208 | -0.76332 | 237.1249 | 37.2 | 38.9557 | -1.7557 | 0.9852 | 14-03-2026 11:30 | 226.402 | 230.494 | 542.6 | 38.4157 | 39.5208 | -1.1052 | 237.1249 | 36.9 | 38.9557 | -2.0557 | 0.98225 | 14-03-2026 11:30 | 226.274 | 230.685 | 541.7 | 38.4475 | 39.5208 | -1.0733 | 237.1249 | 37.4 | 38.9557 | -1.5557 | 0.98088 | 14-03-2026 11:30 | 226.893 | 233.41 | 544.6 | 38.9017 | 39.5208 | -0.61915 | 237.1249 | 37.5 | 38.9557 | -1.4557 | 0.97208 | 14-03-2026 11:30 | 214.609 | 217.789 | 515.5 | 36.2982 | 37.5992 | -1.301 | 225.595 | 35.5 | 37.0615 | -1.5615 | 0.9854 | 14-03-2026 11:30 | 398.8958 | 409.0949 | -10.199 | 2454.5692 | 384.4 | 403.2448 | -18.8448
14-03-2026 11:20 | 877 | 48.22 | 298.76 | 303.587 | 679.3 | 50.5978 | 52.3359 | -1.7381 | 314.0154 | 49.7 | 51.5875 | -1.8875 | 0.9841 | 14-03-2026 11:20 | 303.005 | 308.086 | 686.7 | 51.3477 | 52.3359 | -0.98824 | 314.0154 | 49.2 | 51.5875 | -2.3875 | 0.98351 | 14-03-2026 11:20 | 298.404 | 306.514 | 676.7 | 51.0857 | 52.3359 | -1.2502 | 314.0154 | 49 | 51.5875 | -2.5875 | 0.97354 | 14-03-2026 11:20 | 301.37 | 306.301 | 684.9 | 51.0502 | 52.3359 | -1.2857 | 314.0154 | 49.5 | 51.5875 | -2.0875 | 0.9839 | 14-03-2026 11:20 | 225.117 | 228.476 | 507.7 | 38.0793 | 38.7673 | -0.68801 | 232.604 | 37 | 38.213 | -1.213 | 0.9853 | 14-03-2026 11:20 | 222.31 | 225.79 | 505.7 | 37.6317 | 38.7673 | -1.1357 | 232.604 | 36.5 | 38.213 | -1.713 | 0.98459 | 14-03-2026 11:20 | 222.192 | 226.367 | 504.3 | 37.7278 | 38.7673 | -1.0395 | 232.604 | 36.5 | 38.213 | -1.713 | 0.98156 | 14-03-2026 11:20 | 222.828 | 229.253 | 507.1 | 38.2088 | 38.7673 | -0.55851 | 232.604 | 36.7 | 38.213 | -1.513 | 0.97197 | 14-03-2026 11:20 | 210.799 | 213.901 | 480 | 35.6502 | 36.8823 | -1.2322 | 221.2939 | 34.7 | 36.3549 | -1.6549 | 0.9855 | 14-03-2026 11:20 | 391.3792 | 401.2953 | -9.9161 | 2407.7719 | 378.8 | 395.5568 | -16.7568
14-03-2026 11:10 | 850 | 48.5 | 291.437 | 296.452 | 629.6 | 49.4087 | 50.6705 | -1.2619 | 304.0233 | 48.5 | 49.946 | -1.446 | 0.98308 | 14-03-2026 11:10 | 295.647 | 301.088 | 637.5 | 50.1813 | 50.6705 | -0.48921 | 304.0233 | 49.7 | 49.946 | -0.24596 | 0.98193 | 14-03-2026 11:10 | 291.819 | 299.45 | 627.7 | 49.9083 | 50.6705 | -0.76221 | 304.0233 | 48.2 | 49.946 | -1.746 | 0.97452 | 14-03-2026 11:10 | 293.367 | 298.137 | 635.4 | 49.6895 | 50.6705 | -0.98105 | 304.0233 | 49.2 | 49.946 | -0.74596 | 0.984 | 14-03-2026 11:10 | 219.72 | 222.93 | 470.7 | 37.155 | 37.5337 | -0.37874 | 225.2024 | 36.6 | 36.997 | -0.39701 | 0.9856 | 14-03-2026 11:10 | 216.157 | 220.499 | 469.2 | 36.7498 | 37.5337 | -0.78391 | 225.2024 | 36.3 | 36.997 | -0.69701 | 0.98031 | 14-03-2026 11:10 | 217.155 | 221.046 | 467.8 | 36.841 | 37.5337 | -0.69274 | 225.2024 | 35.8 | 36.997 | -1.197 | 0.9824 | 14-03-2026 11:10 | 217.943 | 224.476 | 470.4 | 37.4127 | 37.5337 | -0.12107 | 225.2024 | 36 | 36.997 | -0.99701 | 0.9709 | 14-03-2026 11:10 | 205.673 | 208.678 | 445.3 | 34.7797 | 35.7087 | -0.92904 | 214.2522 | 34 | 35.1981 | -1.1981 | 0.9856 | 14-03-2026 11:10 | 382.126 | 388.5258 | -6.3998 | 2331.1551 | 374.3 | 382.9699 | -8.6699
14-03-2026 11:00 | 839 | 48.5 | 288.753 | 293.157 | 581.1 | 48.8595 | 50.0148 | -1.1553 | 300.0889 | 47.7 | 49.2996 | -1.5996 | 0.98498 | 14-03-2026 11:00 | 293.302 | 298.041 | 587.8 | 49.6735 | 50.0148 | -0.34131 | 300.0889 | 47.8 | 49.2996 | -1.4996 | 0.9841 | 14-03-2026 11:00 | 287.833 | 294.992 | 579.5 | 49.1653 | 50.0148 | -0.84948 | 300.0889 | 47.6 | 49.2996 | -1.6996 | 0.97573 | 14-03-2026 11:00 | 290.996 | 295.638 | 586.2 | 49.273 | 50.0148 | -0.74181 | 300.0889 | 47.5 | 49.2996 | -1.7996 | 0.9843 | 14-03-2026 11:00 | 216.72 | 219.842 | 434.1 | 36.6403 | 37.048 | -0.40767 | 222.288 | 35.4 | 36.5182 | -1.1182 | 0.9858 | 14-03-2026 11:00 | 215.029 | 218.449 | 432.9 | 36.4082 | 37.048 | -0.63984 | 222.288 | 35 | 36.5182 | -1.5182 | 0.98434 | 14-03-2026 11:00 | 214.83 | 218.431 | 432 | 36.4052 | 37.048 | -0.64284 | 222.288 | 35.1 | 36.5182 | -1.4182 | 0.98351 | 14-03-2026 11:00 | 215.784 | 222.261 | 434.4 | 37.0435 | 37.048 | -0.0045077 | 222.288 | 35.7 | 36.5182 | -0.81822 | 0.97086 | 14-03-2026 11:00 | 204.202 | 207.143 | 411.3 | 34.5238 | 35.2466 | -0.72276 | 211.4795 | 33.8 | 34.7426 | -0.94256 | 0.9858 | 14-03-2026 11:00 | 377.9923 | 383.4979 | -5.5055 | 2300.9872 | 365.6 | 378.0138 | -12.4138
14-03-2026 10:50 | 808 | 48.5 | 278.862 | 283.195 | 533.4 | 47.1992 | 48.1668 | -0.96766 | 289.001 | 46.1 | 47.478 | -1.378 | 0.9847 | 14-03-2026 10:50 | 282.809 | 287.349 | 540 | 47.8915 | 48.1668 | -0.27533 | 289.001 | 47.3 | 47.478 | -0.17804 | 0.9842 | 14-03-2026 10:50 | 277.767 | 284.703 | 531.9 | 47.4505 | 48.1668 | -0.71633 | 289.001 | 46.1 | 47.478 | -1.378 | 0.97564 | 14-03-2026 10:50 | 280.698 | 285.175 | 538.7 | 47.5292 | 48.1668 | -0.63766 | 289.001 | 46.6 | 47.478 | -0.87804 | 0.9843 | 14-03-2026 10:50 | 209.333 | 212.348 | 398.7 | 35.3913 | 35.6791 | -0.2878 | 214.0748 | 34.7 | 35.1689 | -0.46892 | 0.9858 | 14-03-2026 10:50 | 207.204 | 210.727 | 397.9 | 35.1212 | 35.6791 | -0.55796 | 214.0748 | 34.4 | 35.1689 | -0.76892 | 0.98328 | 14-03-2026 10:50 | 207.514 | 211.325 | 396.9 | 35.2208 | 35.6791 | -0.4583 | 214.0748 | 34.4 | 35.1689 | -0.76892 | 0.98197 | 14-03-2026 10:50 | 208.527 | 214.754 | 398.7 | 35.7923 | 35.6791 | 0.1132 | 214.0748 | 34.1 | 35.1689 | -1.0689 | 0.971 | 14-03-2026 10:50 | 196.825 | 199.68 | 377.5 | 33.28 | 33.9443 | -0.66427 | 203.6656 | 32.2 | 33.4589 | -1.2589 | 0.9857 | 14-03-2026 10:50 | 364.876 | 369.3281 | -4.4521 | 2215.9686 | 355.9 | 364.0467 | -8.1467
14-03-2026 10:40 | 787 | 48.5 | 273.107 | 277.266 | 487.3 | 46.211 | 46.915 | -0.70397 | 281.4898 | 44 | 46.2441 | -2.2441 | 0.985 | 14-03-2026 10:40 | 276.503 | 280.828 | 492.7 | 46.8047 | 46.915 | -0.1103 | 281.4898 | 46.6 | 46.2441 | 0.35592 | 0.9846 | 14-03-2026 10:40 | 272.306 | 278.926 | 485.8 | 46.4877 | 46.915 | -0.4273 | 281.4898 | 44.4 | 46.2441 | -1.8441 | 0.97627 | 14-03-2026 10:40 | 274.602 | 278.897 | 492.1 | 46.4828 | 46.915 | -0.43213 | 281.4898 | 45.4 | 46.2441 | -0.84408 | 0.9846 | 14-03-2026 10:40 | 204.295 | 207.196 | 364 | 34.5327 | 34.7518 | -0.21916 | 208.511 | 33.9 | 34.2549 | -0.35487 | 0.986 | 14-03-2026 10:40 | 202.752 | 205.847 | 363.5 | 34.3078 | 34.7518 | -0.44399 | 208.511 | 33.5 | 34.2549 | -0.75487 | 0.98496 | 14-03-2026 10:40 | 202.473 | 206.017 | 362.5 | 34.3362 | 34.7518 | -0.41566 | 208.511 | 33.5 | 34.2549 | -0.75487 | 0.9828 | 14-03-2026 10:40 | 203.141 | 208.878 | 364.6 | 34.813 | 34.7518 | 0.061174 | 208.511 | 33.6 | 34.2549 | -0.65487 | 0.97253 | 14-03-2026 10:40 | 192.627 | 195.382 | 345.3 | 32.5637 | 33.0621 | -0.49839 | 198.3724 | 31.8 | 32.5893 | -0.78927 | 0.9859 | 14-03-2026 10:40 | 356.5395 | 359.7292 | -3.1897 | 2158.3753 | 346.7 | 354.5851 | -7.8851
14-03-2026 10:30 | 760 | 48.5 | 265.166 | 269.149 | 443.3 | 44.8582 | 45.3054 | -0.44726 | 271.8326 | 43.8 | 44.6576 | -0.85756 | 0.9852 | 14-03-2026 10:30 | 267.743 | 271.876 | 446.1 | 45.3127 | 45.3054 | 0.0072365 | 271.8326 | 42.1 | 44.6576 | -2.5576 | 0.9848 | 14-03-2026 10:30 | 264.692 | 271.099 | 441.4 | 45.1832 | 45.3054 | -0.12226 | 271.8326 | 43.8 | 44.6576 | -0.85756 | 0.97637 | 14-03-2026 10:30 | 267.141 | 271.264 | 446.7 | 45.2107 | 45.3054 | -0.094764 | 271.8326 | 43.6 | 44.6576 | -1.0576 | 0.9848 | 14-03-2026 10:30 | 198.605 | 201.384 | 330.1 | 33.564 | 33.5596 | 0.0044221 | 201.3575 | 32.5 | 33.0797 | -0.57968 | 0.9862 | 14-03-2026 10:30 | 196.939 | 199.749 | 330 | 33.2915 | 33.5596 | -0.26808 | 201.3575 | 32.3 | 33.0797 | -0.77968 | 0.98593 | 14-03-2026 10:30 | 196.78 | 199.786 | 329 | 33.2977 | 33.5596 | -0.26191 | 201.3575 | 32.2 | 33.0797 | -0.87968 | 0.98495 | 14-03-2026 10:30 | 197.373 | 202.999 | 331 | 33.8332 | 33.5596 | 0.27359 | 201.3575 | 32.3 | 33.0797 | -0.77968 | 0.97229 | 14-03-2026 10:30 | 186.808 | 189.403 | 313.5 | 31.5672 | 31.9278 | -0.36062 | 191.5667 | 30.6 | 31.4712 | -0.87121 | 0.9863 | 14-03-2026 10:30 | 346.1182 | 347.3878 | -1.2696 | 2084.3269 | 333.2 | 342.4202 | -9.2202
14-03-2026 10:20 | 721 | 48.79 | 252.605 | 256.322 | 399.5 | 42.7203 | 42.933 | -0.21268 | 257.5981 | 41.4 | 42.3191 | -0.91907 | 0.9855 | 14-03-2026 10:20 | 255.742 | 259.584 | 404 | 43.264 | 42.933 | 0.33099 | 257.5981 | 42.5 | 42.3191 | 0.18093 | 0.9852 | 14-03-2026 10:20 | 252.489 | 258.521 | 397.6 | 43.0868 | 42.933 | 0.15382 | 257.5981 | 40.8 | 42.3191 | -1.5191 | 0.97667 | 14-03-2026 10:20 | 254.849 | 258.651 | 403.1 | 43.1085 | 42.933 | 0.17549 | 257.5981 | 41.8 | 42.3191 | -0.51907 | 0.9853 | 14-03-2026 10:20 | 189.957 | 192.557 | 297.6 | 32.0928 | 31.8022 | 0.2906 | 190.8134 | 31 | 31.3475 | -0.34746 | 0.9865 | 14-03-2026 10:20 | 188.183 | 190.837 | 297.7 | 31.8062 | 31.8022 | 0.0039361 | 190.8134 | 30.7 | 31.3475 | -0.64746 | 0.98609 | 14-03-2026 10:20 | 188.504 | 191.361 | 296.8 | 31.8935 | 31.8022 | 0.091269 | 190.8134 | 30.7 | 31.3475 | -0.64746 | 0.98507 | 14-03-2026 10:20 | 188.615 | 194.078 | 298.7 | 32.3463 | 31.8022 | 0.5441 | 190.8134 | 30.8 | 31.3475 | -0.54746 | 0.97185 | 14-03-2026 10:20 | 178.391 | 180.887 | 282.9 | 30.1478 | 30.2559 | -0.10805 | 181.5353 | 29.1 | 29.8232 | -0.72322 | 0.9862 | 14-03-2026 10:20 | 330.4663 | 329.1969 | 1.2695 | 1975.1811 | 318.8 | 324.4893 | -5.6893
14-03-2026 10:10 | 679 | 48.5 | 239.2 | 242.646 | 358.1 | 40.441 | 40.4768 | -0.035825 | 242.861 | 40 | 39.898 | 0.10199 | 0.9858 | 14-03-2026 10:10 | 242.611 | 246.108 | 361.5 | 41.018 | 40.4768 | 0.54117 | 242.861 | 40 | 39.898 | 0.10199 | 0.98579 | 14-03-2026 10:10 | 238.712 | 244.787 | 356.8 | 40.7978 | 40.4768 | 0.32101 | 242.861 | 39.8 | 39.898 | -0.098007 | 0.97518 | 14-03-2026 10:10 | 241.304 | 244.83 | 361.3 | 40.805 | 40.4768 | 0.32817 | 242.861 | 39.8 | 39.898 | -0.098007 | 0.9856 | 14-03-2026 10:10 | 179.47 | 181.908 | 266.6 | 30.318 | 29.9828 | 0.33517 | 179.897 | 29.6 | 29.5541 | 0.045921 | 0.9866 | 14-03-2026 10:10 | 178.111 | 180.512 | 267 | 30.0853 | 29.9828 | 0.1025 | 179.897 | 29.5 | 29.5541 | -0.054079 | 0.9867 | 14-03-2026 10:10 | 178.121 | 180.715 | 266.1 | 30.1192 | 29.9828 | 0.13633 | 179.897 | 29.4 | 29.5541 | -0.15408 | 0.98565 | 14-03-2026 10:10 | 178.239 | 183.075 | 267.9 | 30.5125 | 29.9828 | 0.52967 | 179.897 | 29.3 | 29.5541 | -0.25408 | 0.97358 | 14-03-2026 10:10 | 168.816 | 171.126 | 253.8 | 28.521 | 28.525 | -0.0039525 | 171.1497 | 28.2 | 28.117 | 0.082954 | 0.9865 | 14-03-2026 10:10 | 312.6178 | 310.3636 | 2.2542 | 1862.1815 | 305.6 | 305.9254 | -0.32539
14-03-2026 10:00 | 651 | 48.5 | 230.076 | 233.319 | 318.1 | 38.8865 | 38.8077 | 0.078822 | 232.8461 | 37 | 38.2527 | -1.2527 | 0.9861 | 14-03-2026 10:00 | 233.48 | 236.805 | 321.5 | 39.4675 | 38.8077 | 0.65982 | 232.8461 | 38.7 | 38.2527 | 0.44727 | 0.98596 | 14-03-2026 10:00 | 229.738 | 234.669 | 317 | 39.1115 | 38.8077 | 0.30382 | 232.8461 | 37.5 | 38.2527 | -0.75273 | 0.97899 | 14-03-2026 10:00 | 232.244 | 235.589 | 321.5 | 39.2648 | 38.8077 | 0.45716 | 232.8461 | 37.9 | 38.2527 | -0.35273 | 0.9858 | 14-03-2026 10:00 | 172.386 | 174.71 | 237 | 29.1183 | 28.7464 | 0.37191 | 172.4786 | 28 | 28.3354 | -0.33535 | 0.9867 | 14-03-2026 10:00 | 171.521 | 173.815 | 237.5 | 28.9692 | 28.7464 | 0.22274 | 172.4786 | 27.9 | 28.3354 | -0.43535 | 0.9868 | 14-03-2026 10:00 | 171.166 | 173.446 | 236.7 | 28.9077 | 28.7464 | 0.16124 | 172.4786 | 27.9 | 28.3354 | -0.43535 | 0.98685 | 14-03-2026 10:00 | 171.564 | 176.623 | 238.6 | 29.4372 | 28.7464 | 0.69074 | 172.4786 | 28.1 | 28.3354 | -0.23535 | 0.97136 | 14-03-2026 10:00 | 162.649 | 164.841 | 225.6 | 27.4735 | 27.3487 | 0.12483 | 164.092 | 26.6 | 26.9576 | -0.35758 | 0.9867 | 14-03-2026 10:00 | 300.6362 | 297.5651 | 3.0711 | 1785.3905 | 289.6 | 293.3099 | -3.7099
14-03-2026 09:50 | 627 | 48.5 | 222.233 | 225.297 | 281.1 | 37.5495 | 37.377 | 0.17252 | 224.2619 | 36.9 | 36.8425 | 0.057511 |  | 14-03-2026 09:50 | 224.967 | 228.066 | 282.8 | 38.011 | 37.377 | 0.63402 | 224.2619 | 35.3 | 36.8425 | -1.5425 |  | 14-03-2026 09:50 | 221.929 | 226.902 | 279.5 | 37.817 | 37.377 | 0.44002 | 224.2619 | 35.4 | 36.8425 | -1.4425 |  | 14-03-2026 09:50 | 224.5 | 227.641 | 283.6 | 37.9402 | 37.377 | 0.56319 | 224.2619 | 36.3 | 36.8425 | -0.54249 |  | 14-03-2026 09:50 | 166.455 | 168.647 | 209 | 28.1078 | 27.6867 | 0.42118 | 166.1199 | 27 | 27.2907 | -0.29073 |  | 14-03-2026 09:50 | 165.897 | 168.082 | 209.6 | 28.0137 | 27.6867 | 0.32701 | 166.1199 | 26.8 | 27.2907 | -0.49073 |  | 14-03-2026 09:50 | 165.325 | 167.724 | 208.8 | 27.954 | 27.6867 | 0.26735 | 166.1199 | 26.7 | 27.2907 | -0.59073 |  | 14-03-2026 09:50 | 166.135 | 170.59 | 210.5 | 28.4317 | 27.6867 | 0.74501 | 166.1199 | 26.9 | 27.2907 | -0.39073 |  | 14-03-2026 09:50 | 157.204 | 159.291 | 199 | 26.5485 | 26.3404 | 0.20808 | 158.0425 | 25.1 | 25.9638 | -0.86375 |  | 14-03-2026 09:50 | 290.3733 | 286.5949 | 3.7784 | 1719.5697 | 276.4 | 282.4966 | -6.0966
14-03-2026 09:40 | 594 | 48.5 | 210.537 | 213.397 | 244.2 | 35.5662 | 35.4098 | 0.1564 | 212.4586 | 31.9 | 34.9034 | -3.0034 |  | 14-03-2026 09:40 | 213.979 | 216.951 | 247.5 | 36.1585 | 35.4098 | 0.74873 | 212.4586 | 34.8 | 34.9034 | -0.10341 |  | 14-03-2026 09:40 | 210.519 | 215.075 | 244.1 | 35.8458 | 35.4098 | 0.43606 | 212.4586 | 33.3 | 34.9034 | -1.6034 |  | 14-03-2026 09:40 | 212.904 | 215.861 | 247.3 | 35.9768 | 35.4098 | 0.56706 | 212.4586 | 33.7 | 34.9034 | -1.2034 |  | 14-03-2026 09:40 | 157.488 | 159.507 | 182 | 26.5845 | 26.2295 | 0.35504 | 157.3768 | 24.9 | 25.8544 | -0.95438 |  | 14-03-2026 09:40 | 156.903 | 158.954 | 182.8 | 26.4923 | 26.2295 | 0.26287 | 157.3768 | 24.9 | 25.8544 | -0.95438 |  | 14-03-2026 09:40 | 156.354 | 158.45 | 182.1 | 26.4083 | 26.2295 | 0.17887 | 157.3768 | 24.8 | 25.8544 | -1.0544 |  | 14-03-2026 09:40 | 156.885 | 161.148 | 183.6 | 26.858 | 26.2295 | 0.62854 | 157.3768 | 24.9 | 25.8544 | -0.95438 |  | 14-03-2026 09:40 | 149.058 | 151.021 | 173.9 | 25.1702 | 24.9541 | 0.21608 | 149.7245 | 23.6 | 24.5972 | -0.99724 |  | 14-03-2026 09:40 | 275.0607 | 271.511 | 3.5497 | 1629.066 | 256.8 | 267.6284 | -10.8284
|  |  | 197.379 | 200.019 | 212.3 | 33.3365 | 0 | 33.3365 | 0 | 32.2 | 0 | 32.2 |  | 14-03-2026 09:30 | 199.526 | 202.236 | 212.7 | 33.706 | 0 | 33.706 | 0 | 32.1 | 0 | 32.1 |  | 14-03-2026 09:30 | 197.005 | 200.526 | 210.8 | 33.421 | 0 | 33.421 | 0 | 32.1 | 0 | 32.1 |  | 14-03-2026 09:30 | 199.473 | 202.182 | 213.6 | 33.697 | 0 | 33.697 | 0 | 31.9 | 0 | 31.9 |  | 14-03-2026 09:30 | 147.145 | 149.023 | 157.1 | 24.8372 | 0 | 24.8372 | 0 | 23.5 | 0 | 23.5 |  | 14-03-2026 09:30 | 147.156 | 149.064 | 157.9 | 24.844 | 0 | 24.844 | 0 | 23.6 | 0 | 23.6 |  | 14-03-2026 09:30 | 146.33 | 148.291 | 157.3 | 24.7152 | 0 | 24.7152 | 0 | 23.5 | 0 | 23.5 |  | 14-03-2026 09:30 | 147.164 | 151.139 | 158.7 | 25.1898 | 0 | 25.1898 | 0 | 23.9 | 0 | 23.9 |  | 14-03-2026 09:30 | 139.729 | 141.541 | 150.3 | 23.5902 | 0 | 23.5902 | 0 | 22.7 | 0 | 22.7 |  | 0 | 257.3368 | 0 | 257.3368 | 0 | 245.5 | 0 | 245.5
14-03-2026 09:20 | 524 | 48.22 | 186.016 | 189.681 | 180.1 | 31.6135 | 31.2703 | 0.34324 | 187.6215 | 28.2 | 30.8231 | -2.6231 |  | 14-03-2026 09:20 | 189.751 | 192.289 | 180.6 | 32.0482 | 31.2703 | 0.77791 | 187.6215 | 28.3 | 30.8231 | -2.5231 |  | 14-03-2026 09:20 | 187.256 | 190.628 | 178.7 | 31.7713 | 31.2703 | 0.50108 | 187.6215 | 27.4 | 30.8231 | -3.4231 |  | 14-03-2026 09:20 | 189.266 | 191.798 | 181.7 | 31.9663 | 31.2703 | 0.69608 | 187.6215 | 27.8 | 30.8231 | -3.0231 |  | 14-03-2026 09:20 | 139.603 | 141.356 | 133.6 | 23.5593 | 23.1632 | 0.39618 | 138.9789 | 20.5 | 22.8319 | -2.3319 |  | 14-03-2026 09:20 | 139.654 | 141.407 | 134.3 | 23.5678 | 23.1632 | 0.40468 | 138.9789 | 20.4 | 22.8319 | -2.4319 |  | 14-03-2026 09:20 | 139.044 | 140.79 | 133.8 | 23.465 | 23.1632 | 0.30185 | 138.9789 | 20.3 | 22.8319 | -2.5319 |  | 14-03-2026 09:20 | 139.495 | 143.142 | 134.8 | 23.857 | 23.1632 | 0.69385 | 138.9789 | 20.1 | 22.8319 | -2.7319 |  | 14-03-2026 09:20 | 132.279 | 133.967 | 127.6 | 22.3278 | 22.0369 | 0.29096 | 132.2212 | 19.1 | 21.7217 | -2.6217 |  | 14-03-2026 09:20 | 244.1763 | 239.7705 | 4.4058 | 1438.6231 | 212.1 | 236.3418 | -24.2418
14-03-2026 09:10 | 441 | 47.93 | 141.077 | 142.834 | 151.9 | 23.8057 | 26.3462 | -2.5406 | 158.0773 | 20.5 | 25.9695 | -5.4695 |  | 14-03-2026 09:10 | 130.478 | 133.078 | 152.3 | 22.1797 | 26.3462 | -4.1666 | 158.0773 | 20.8 | 25.9695 | -5.1695 |  | 14-03-2026 09:10 | 157.035 | 159.682 | 151.3 | 26.6137 | 26.3462 | 0.26745 | 158.0773 | 21.1 | 25.9695 | -4.8695 |  | 14-03-2026 09:10 | 160.596 | 162.645 | 153.9 | 27.1075 | 26.3462 | 0.76128 | 158.0773 | 21.4 | 25.9695 | -4.5695 |  | 14-03-2026 09:10 | 117.589 | 119.041 | 113.1 | 19.8402 | 19.5157 | 0.32445 | 117.0943 | 15.7 | 19.2366 | -3.5366 |  | 14-03-2026 09:10 | 118.233 | 119.657 | 113.9 | 19.9428 | 19.5157 | 0.42712 | 117.0943 | 15.9 | 19.2366 | -3.3366 |  | 14-03-2026 09:10 | 117.112 | 118.558 | 113.5 | 19.7597 | 19.5157 | 0.24395 | 117.0943 | 15.8 | 19.2366 | -3.4366 |  | 14-03-2026 09:10 | 118.235 | 121.397 | 114.7 | 20.2328 | 19.5157 | 0.71712 | 117.0943 | 16.2 | 19.2366 | -3.0366 |  | 14-03-2026 09:10 | 112.133 | 113.506 | 108.5 | 18.9177 | 18.5668 | 0.35088 | 111.4007 | 15.3 | 18.3013 | -3.0013 |  | 14-03-2026 09:10 | 198.3997 | 202.0145 | -3.6149 | 1212.0872 | 162.7 | 199.1257 | -36.4257
14-03-2026 09:00 | 404 | 47.64 | 142.914 | 144.08 | 131.4 | 24.0133 | 24.1624 | -0.14907 | 144.9744 | 26.7 | 23.8169 | 2.8831 |  | 14-03-2026 09:00 | 145.777 | 147.652 | 131.5 | 24.6087 | 24.1624 | 0.44627 | 144.9744 | 27.8 | 23.8169 | 3.9831 |  | 14-03-2026 09:00 | 144.962 | 147.348 | 130.2 | 24.558 | 24.1624 | 0.3956 | 144.9744 | 26.9 | 23.8169 | 3.0831 |  | 14-03-2026 09:00 | 144.727 | 146.589 | 132.5 | 24.4315 | 24.1624 | 0.2691 | 144.9744 | 27.3 | 23.8169 | 3.4831 |  | 14-03-2026 09:00 | 104.134 | 105.441 | 97.4 | 17.5735 | 17.8981 | -0.32457 | 107.3884 | 20.1 | 17.6421 | 2.4579 |  | 14-03-2026 09:00 | 105.74 | 107.035 | 98 | 17.8392 | 17.8981 | -0.058908 | 107.3884 | 20.1 | 17.6421 | 2.4579 |  | 14-03-2026 09:00 | 101.723 | 103.748 | 97.7 | 17.2913 | 17.8981 | -0.60674 | 107.3884 | 19.9 | 17.6421 | 2.2579 |  | 14-03-2026 09:00 | 106.772 | 109.455 | 98.5 | 18.2425 | 17.8981 | 0.34443 | 107.3884 | 19.8 | 17.6421 | 2.1579 |  | 14-03-2026 09:00 | 101.808 | 103.076 | 93.2 | 17.1793 | 17.0278 | 0.15153 | 102.1668 | 18.9 | 16.7843 | 2.1157 |  | 14-03-2026 09:00 | 185.7373 | 185.2697 | 0.46763 | 1111.6182 | 207.5 | 182.6203 | 24.8797
14-03-2026 08:50 | 453 | 47.35 | 157.415 | 159.375 | 104.7 | 26.5625 | 27.1229 | -0.56035 | 162.7371 | 24.6 | 26.735 | -2.135 |  | 14-03-2026 08:50 | 128.35 | 138.375 | 103.7 | 23.0625 | 27.1229 | -4.0604 | 162.7371 | 23.1 | 26.735 | -3.635 |  | 14-03-2026 08:50 | 160.66 | 163.806 | 103.3 | 27.301 | 27.1229 | 0.17815 | 162.7371 | 23.7 | 26.735 | -3.035 |  | 14-03-2026 08:50 | 162.517 | 164.574 | 105.2 | 27.429 | 27.1229 | 0.30615 | 162.7371 | 24.2 | 26.735 | -2.535 |  | 14-03-2026 08:50 | 120.95 | 122.419 | 77.3 | 20.4032 | 20.091 | 0.31216 | 120.546 | 17.8 | 19.8037 | -2.0037 |  | 14-03-2026 08:50 | 121.07 | 122.528 | 77.9 | 20.4213 | 20.091 | 0.33033 | 120.546 | 17.9 | 19.8037 | -1.9037 |  | 14-03-2026 08:50 | 121.029 | 122.443 | 77.8 | 20.4072 | 20.091 | 0.31616 | 120.546 | 17.8 | 19.8037 | -2.0037 |  | 14-03-2026 08:50 | 122.062 | 125.411 | 78.7 | 20.9018 | 20.091 | 0.81083 | 120.546 | 18 | 19.8037 | -1.8037 |  | 14-03-2026 08:50 | 115.634 | 117.05 | 74.3 | 19.5083 | 19.1141 | 0.39423 | 114.6846 | 17 | 18.8408 | -1.8408 |  | 14-03-2026 08:50 | 205.9968 | 207.9695 | -1.9727 | 1247.8172 | 184.1 | 204.9956 | -20.8956
14-03-2026 08:40 | 382 | 45.92 | 135.388 | 137.019 | 80.1 | 22.8365 | 22.996 | -0.1595 | 137.976 | 20.4 | 22.6672 | -2.2672 |  | 14-03-2026 08:40 | 136.971 | 138.663 | 80.6 | 23.1105 | 22.996 | 0.1145 | 137.976 | 20.8 | 22.6672 | -1.8672 |  | 14-03-2026 08:40 | 134.138 | 136.39 | 79.6 | 22.7317 | 22.996 | -0.26433 | 137.976 | 20.3 | 22.6672 | -2.3672 |  | 14-03-2026 08:40 | 137.01 | 138.688 | 81 | 23.1147 | 22.996 | 0.11867 | 137.976 | 20.7 | 22.6672 | -1.9672 |  | 14-03-2026 08:40 | 101.14 | 102.348 | 59.5 | 17.058 | 17.0341 | 0.023926 | 102.2044 | 15.3 | 16.7905 | -1.4905 |  | 14-03-2026 08:40 | 101.477 | 102.668 | 60 | 17.1113 | 17.0341 | 0.07726 | 102.2044 | 15.3 | 16.7905 | -1.4905 |  | 14-03-2026 08:40 | 101.285 | 102.494 | 60 | 17.0823 | 17.0341 | 0.04826 | 102.2044 | 15.4 | 16.7905 | -1.3905 |  | 14-03-2026 08:40 | 102.357 | 105.32 | 60.7 | 17.5533 | 17.0341 | 0.51926 | 102.2044 | 15.6 | 16.7905 | -1.1905 |  | 14-03-2026 08:40 | 96.788 | 97.934 | 57.3 | 16.3223 | 16.2058 | 0.11652 | 97.2349 | 14.8 | 15.9741 | -1.1741 |  | 14-03-2026 08:40 | 176.9207 | 176.3261 | 0.59456 | 1057.9566 | 158.6 | 173.8046 | -15.2046
14-03-2026 08:30 | 313 | 41.61 | 110.162 | 111.444 | 59.7 | 18.574 | 19.149 | -0.57496 | 114.8938 | 17 | 18.8751 | -1.8751 |  | 14-03-2026 08:30 | 110.009 | 111.334 | 59.8 | 18.5557 | 19.149 | -0.5933 | 114.8938 | 16.8 | 18.8751 | -2.0751 |  | 14-03-2026 08:30 | 109.974 | 111.52 | 59.3 | 18.5867 | 19.149 | -0.5623 | 114.8938 | 16.8 | 18.8751 | -2.0751 |  | 14-03-2026 08:30 | 112.342 | 113.683 | 60.3 | 18.9472 | 19.149 | -0.2018 | 114.8938 | 17.2 | 18.8751 | -1.6751 |  | 14-03-2026 08:30 | 82.805 | 83.802 | 44.2 | 13.967 | 14.1844 | -0.21742 | 85.1065 | 12.8 | 13.9816 | -1.1816 |  | 14-03-2026 08:30 | 83.337 | 84.306 | 44.7 | 14.051 | 14.1844 | -0.13342 | 85.1065 | 12.8 | 13.9816 | -1.1816 |  | 14-03-2026 08:30 | 83.223 | 84.242 | 44.6 | 14.0403 | 14.1844 | -0.14408 | 85.1065 | 12.7 | 13.9816 | -1.2816 |  | 14-03-2026 08:30 | 83.886 | 86.169 | 45.1 | 14.3615 | 14.1844 | 0.17708 | 85.1065 | 12.7 | 13.9816 | -1.2816 |  | 14-03-2026 08:30 | 79.092 | 80.085 | 42.5 | 13.3475 | 13.4947 | -0.14722 | 80.9683 | 12 | 13.3017 | -1.3017 |  | 14-03-2026 08:30 | 144.4308 | 146.8282 | -2.3974 | 880.9694 | 130.8 | 144.7286 | -13.9286
14-03-2026 08:20 | 263 | 37.88 | 92.627 | 93.646 | 42.7 | 15.6077 | 16.313 | -0.70538 | 97.8783 | 14.7 | 16.0798 | -1.3798 |  | 14-03-2026 08:20 | 93.215 | 94.309 | 43 | 15.7182 | 16.313 | -0.59488 | 97.8783 | 14.1 | 16.0798 | -1.9798 |  | 14-03-2026 08:20 | 92.091 | 93.153 | 42.5 | 15.5255 | 16.313 | -0.78754 | 97.8783 | 13.9 | 16.0798 | -2.1798 |  | 14-03-2026 08:20 | 93.033 | 94.125 | 43.1 | 15.6875 | 16.313 | -0.62554 | 97.8783 | 14.1 | 16.0798 | -1.9798 |  | 14-03-2026 08:20 | 68.758 | 69.635 | 31.4 | 11.6058 | 12.0837 | -0.4779 | 72.5024 | 10.4 | 11.9109 | -1.5109 |  | 14-03-2026 08:20 | 69.471 | 70.336 | 31.9 | 11.7227 | 12.0837 | -0.36107 | 72.5024 | 10.6 | 11.9109 | -1.3109 |  | 14-03-2026 08:20 | 69.261 | 70.145 | 31.9 | 11.6908 | 12.0837 | -0.3929 | 72.5024 | 10.6 | 11.9109 | -1.3109 |  | 14-03-2026 08:20 | 70.095 | 72.028 | 32.4 | 12.0047 | 12.0837 | -0.07907 | 72.5024 | 10.8 | 11.9109 | -1.1109 |  | 14-03-2026 08:20 | 66.318 | 67.171 | 30.5 | 11.1952 | 11.4962 | -0.30101 | 68.9771 | 10.1 | 11.3318 | -1.2318 |  | 14-03-2026 08:20 | 120.758 | 125.0833 | -4.3253 | 750.4998 | 109.3 | 123.2946 | -13.9946
14-03-2026 08:10 | 217 | 34.15 | 73.181 | 74.07 | 28 | 12.345 | 13.6438 | -1.2988 | 81.863 | 10.7 | 13.4487 | -2.7487 |  | 14-03-2026 08:10 | 74.35 | 76.105 | 28.9 | 12.6842 | 13.6438 | -0.95966 | 81.863 | 12 | 13.4487 | -1.4487 |  | 14-03-2026 08:10 | 74.819 | 75.7 | 28.6 | 12.6167 | 13.6438 | -1.0272 | 81.863 | 11.3 | 13.4487 | -2.1487 |  | 14-03-2026 08:10 | 76.245 | 77.194 | 29 | 12.8657 | 13.6438 | -0.77816 | 81.863 | 11.6 | 13.4487 | -1.8487 |  | 14-03-2026 08:10 | 55.672 | 56.44 | 21 | 9.4067 | 10.1065 | -0.69987 | 60.6392 | 8.3 | 9.962 | -1.662 |  | 14-03-2026 08:10 | 56.328 | 57.087 | 21.3 | 9.5145 | 10.1065 | -0.59204 | 60.6392 | 8.5 | 9.962 | -1.462 |  | 14-03-2026 08:10 | 56.239 | 56.982 | 21.3 | 9.497 | 10.1065 | -0.60954 | 60.6392 | 8.5 | 9.962 | -1.462 |  | 14-03-2026 08:10 | 56.845 | 58.593 | 21.6 | 9.7655 | 10.1065 | -0.34104 | 60.6392 | 8.5 | 9.962 | -1.462 |  | 14-03-2026 08:10 | 53.708 | 54.471 | 20.4 | 9.0785 | 9.6151 | -0.53662 | 57.6907 | 8.1 | 9.4776 | -1.3776 |  | 14-03-2026 08:10 | 97.7737 | 104.6166 | -6.8429 | 627.6994 | 87.5 | 103.1206 | -15.6206
14-03-2026 08:00 | 179 | 31.86 | 61.027 | 62.2 | 17.3 | 10.3667 | 11.3478 | -0.98111 | 68.0866 | 9 | 11.1855 | -2.1855 |  | 14-03-2026 08:00 | 60.784 | 61.622 | 16.9 | 10.2703 | 11.3478 | -1.0774 | 68.0866 | 8.5 | 11.1855 | -2.6855 |  | 14-03-2026 08:00 | 60.891 | 61.668 | 17.3 | 10.278 | 11.3478 | -1.0698 | 68.0866 | 9 | 11.1855 | -2.1855 |  | 14-03-2026 08:00 | 61.856 | 62.658 | 17.4 | 10.443 | 11.3478 | -0.90477 | 68.0866 | 9 | 11.1855 | -2.1855 |  | 14-03-2026 08:00 | 44.883 | 45.658 | 12.7 | 7.6097 | 8.4058 | -0.79609 | 50.4346 | 6.6 | 8.2856 | -1.6856 |  | 14-03-2026 08:00 | 45.937 | 46.627 | 12.8 | 7.7712 | 8.4058 | -0.63459 | 50.4346 | 6.8 | 8.2856 | -1.4856 |  | 14-03-2026 08:00 | 45.787 | 46.48 | 12.8 | 7.7467 | 8.4058 | -0.65909 | 50.4346 | 6.7 | 8.2856 | -1.5856 |  | 14-03-2026 08:00 | 46.229 | 47.616 | 13.1 | 7.936 | 8.4058 | -0.46976 | 50.4346 | 6.9 | 8.2856 | -1.3856 |  | 14-03-2026 08:00 | 43.839 | 44.525 | 12.3 | 7.4208 | 7.997 | -0.5762 | 47.9822 | 6.5 | 7.8827 | -1.3827 |  | 14-03-2026 08:00 | 79.8423 | 87.0112 | -7.1688 | 522.067 | 69 | 85.7669 | -16.7669
14-03-2026 07:50 | 141 | 30.14 | 47.297 | 47.998 | 8.3 | 7.9997 | 8.9939 | -0.99422 | 53.9633 | 4.7 | 8.8653 | -4.1653 |  | 14-03-2026 07:50 | 47.616 | 48.331 | 8.4 | 8.0552 | 8.9939 | -0.93872 | 53.9633 | 4.8 | 8.8653 | -4.0653 |  | 14-03-2026 07:50 | 47.194 | 47.893 | 8.3 | 7.9822 | 8.9939 | -1.0117 | 53.9633 | 4.7 | 8.8653 | -4.1653 |  | 14-03-2026 07:50 | 47.843 | 48.572 | 8.4 | 8.0953 | 8.9939 | -0.89855 | 53.9633 | 4.8 | 8.8653 | -4.0653 |  | 14-03-2026 07:50 | 35.019 | 35.603 | 6.1 | 5.9338 | 6.6621 | -0.7283 | 39.9728 | 3.6 | 6.5669 | -2.9669 |  | 14-03-2026 07:50 | 35.454 | 36.041 | 6 | 6.0068 | 6.6621 | -0.6553 | 39.9728 | 3.5 | 6.5669 | -3.0669 |  | 14-03-2026 07:50 | 35.319 | 35.912 | 6.1 | 5.9853 | 6.6621 | -0.6768 | 39.9728 | 3.5 | 6.5669 | -3.0669 |  | 14-03-2026 07:50 | 35.725 | 36.81 | 6.2 | 6.135 | 6.6621 | -0.52714 | 39.9728 | 3.6 | 6.5669 | -2.9669 |  | 14-03-2026 07:50 | 33.745 | 34.322 | 5.8 | 5.7203 | 6.3382 | -0.61786 | 38.0292 | 3.4 | 6.2476 | -2.8476 |  | 14-03-2026 07:50 | 61.9137 | 68.9623 | -7.0486 | 413.7737 | 36.6 | 67.9761 | -31.3761
14-03-2026 07:40 | 108 | 28.13 | 0 | 0 | 3.6 | 0 | 6.9383 | -6.9383 | 41.6297 | 0 | 6.8391 | -6.8391 |  | 14-03-2026 07:40 | 0 | 0 | 3.6 | 0 | 6.9383 | -6.9383 | 41.6297 | 0 | 6.8391 | -6.8391 |  | 14-03-2026 07:40 | 0 | 0 | 3.6 | 0 | 6.9383 | -6.9383 | 41.6297 | 0 | 6.8391 | -6.8391 |  | 14-03-2026 07:40 | 0 | 0 | 3.6 | 0 | 6.9383 | -6.9383 | 41.6297 | 0 | 6.8391 | -6.8391 |  | 14-03-2026 07:40 | 0 | 0 | 2.5 | 0 | 5.1395 | -5.1395 | 30.8368 | 0 | 5.066 | -5.066 |  | 14-03-2026 07:40 | 0 | 0 | 2.5 | 0 | 5.1395 | -5.1395 | 30.8368 | 0 | 5.066 | -5.066 |  | 14-03-2026 07:40 | 0 | 0 | 2.6 | 0 | 5.1395 | -5.1395 | 30.8368 | 0 | 5.066 | -5.066 |  | 14-03-2026 07:40 | 0 | 0 | 2.6 | 0 | 5.1395 | -5.1395 | 30.8368 | 0 | 5.066 | -5.066 |  | 14-03-2026 07:40 | 0 | 0 | 2.4 | 0 | 4.8896 | -4.8896 | 29.3374 | 0 | 4.8196 | -4.8196 |  | 14-03-2026 07:40 | 0 | 53.2006 | -53.2006 | 319.2035 | 0 | 52.4398 | -52.4398
14-03-2026 07:30 | 75 | 24.68 | 0 | 0 | 3.6 | 0 | 4.8771 | -4.8771 | 29.2625 | 0.4 | 4.8073 | -4.4073 |  | 14-03-2026 07:30 | 0 | 0 | 3.6 | 0 | 4.8771 | -4.8771 | 29.2625 | 0.4 | 4.8073 | -4.4073 |  | 14-03-2026 07:30 | 0 | 0 | 3.6 | 0 | 4.8771 | -4.8771 | 29.2625 | 0.5 | 4.8073 | -4.3073 |  | 14-03-2026 07:30 | 0 | 0 | 3.6 | 0 | 4.8771 | -4.8771 | 29.2625 | 0.5 | 4.8073 | -4.3073 |  | 14-03-2026 07:30 | 0 | 0 | 2.5 | 0 | 3.6127 | -3.6127 | 21.6759 | 0.3 | 3.561 | -3.261 |  | 14-03-2026 07:30 | 0 | 0 | 2.5 | 0 | 3.6127 | -3.6127 | 21.6759 | 0.3 | 3.561 | -3.261 |  | 14-03-2026 07:30 | 0 | 0 | 2.6 | 0 | 3.6127 | -3.6127 | 21.6759 | 0.3 | 3.561 | -3.261 |  | 14-03-2026 07:30 | 0 | 0 | 2.6 | 0 | 3.6127 | -3.6127 | 21.6759 | 0.3 | 3.561 | -3.261 |  | 14-03-2026 07:30 | 0 | 0 | 2.4 | 0 | 3.437 | -3.437 | 20.6219 | 0.3 | 3.3878 | -3.0878 |  | 14-03-2026 07:30 | 0 | 37.3959 | -37.3959 | 224.3754 | 3.3 | 36.8611 | -33.5611
14-03-2026 07:20 | 43 | 22.39 | 15.877 | 16.265 | 3.2 | 2.7108 | 2.8186 | -0.10774 | 16.9115 | 2 | 2.7783 | -0.77827 |  | 14-03-2026 07:20 | 15.919 | 16.569 | 3.2 | 2.7615 | 2.8186 | -0.057078 | 16.9115 | 2 | 2.7783 | -0.77827 |  | 14-03-2026 07:20 | 15.624 | 16.034 | 3.1 | 2.6723 | 2.8186 | -0.14624 | 16.9115 | 1.9 | 2.7783 | -0.87827 |  | 14-03-2026 07:20 | 15.551 | 16.257 | 3.1 | 2.7095 | 2.8186 | -0.10908 | 16.9115 | 1.9 | 2.7783 | -0.87827 |  | 14-03-2026 07:20 | 11.439 | 12.007 | 2.2 | 2.0012 | 2.0878 | -0.086669 | 12.527 | 1.4 | 2.058 | -0.65798 |  | 14-03-2026 07:20 | 10.96 | 11.328 | 2.2 | 1.888 | 2.0878 | -0.19984 | 12.527 | 1.4 | 2.058 | -0.65798 |  | 14-03-2026 07:20 | 11.59 | 11.973 | 2.3 | 1.9955 | 2.0878 | -0.092335 | 12.527 | 1.5 | 2.058 | -0.55798 |  | 14-03-2026 07:20 | 11.718 | 12.242 | 2.3 | 2.0403 | 2.0878 | -0.047502 | 12.527 | 1.5 | 2.058 | -0.55798 |  | 14-03-2026 07:20 | 10.977 | 11.354 | 2.1 | 1.8923 | 1.9863 | -0.093983 | 11.9179 | 1.3 | 1.9579 | -0.65791 |  | 14-03-2026 07:20 | 20.6715 | 21.612 | -0.94047 | 129.6718 | 14.9 | 21.3029 | -6.4029
14-03-2026 07:10 | 22 | 22.67 | 8.391 | 8.724 | 1.2 | 1.454 | 1.4407 | 0.013337 | 8.644 | 1 | 1.4201 | -0.42006 |  | 14-03-2026 07:10 | 8.302 | 9.041 | 1.2 | 1.5068 | 1.4407 | 0.066171 | 8.644 | 1 | 1.4201 | -0.42006 |  | 14-03-2026 07:10 | 8.284 | 8.614 | 1.2 | 1.4357 | 1.4407 | -0.0049959 | 8.644 | 1 | 1.4201 | -0.42006 |  | 14-03-2026 07:10 | 8.379 | 9.242 | 1.2 | 1.5403 | 1.4407 | 0.099671 | 8.644 | 1 | 1.4201 | -0.42006 |  | 14-03-2026 07:10 | 6.01 | 6.631 | 0.8 | 1.1052 | 1.0672 | 0.038009 | 6.4029 | 0.7 | 1.0519 | -0.3519 |  | 14-03-2026 07:10 | 5.709 | 5.961 | 0.8 | 0.9935 | 1.0672 | -0.073657 | 6.4029 | 0.7 | 1.0519 | -0.3519 |  | 14-03-2026 07:10 | 6.078 | 6.343 | 0.8 | 1.0572 | 1.0672 | -0.0099908 | 6.4029 | 0.7 | 1.0519 | -0.3519 |  | 14-03-2026 07:10 | 6.178 | 6.629 | 0.8 | 1.1048 | 1.0672 | 0.037676 | 6.4029 | 0.7 | 1.0519 | -0.3519 |  | 14-03-2026 07:10 | 5.785 | 6.042 | 0.8 | 1.007 | 1.0153 | -0.0082681 | 6.0916 | 0.7 | 1.0007 | -0.30075 |  | 14-03-2026 07:10 | 11.2045 | 11.0465 | 0.15795 | 66.2793 | 7.5 | 10.8886 | -3.3886
14-03-2026 07:00 | 8 | 23.25 | 3.255 | 3.421 | 0.2 | 0.57017 | 0.52282 | 0.047344 | 3.1369 | 0.2 | 0.51535 | -0.31535 |  | 14-03-2026 07:00 | 2.877 | 3.544 | 0.2 | 0.59067 | 0.52282 | 0.067844 | 3.1369 | 0.2 | 0.51535 | -0.31535 |  | 14-03-2026 07:00 | 3.349 | 3.497 | 0.2 | 0.58283 | 0.52282 | 0.060011 | 3.1369 | 0.2 | 0.51535 | -0.31535 |  | 14-03-2026 07:00 | 3.297 | 4.158 | 0.2 | 0.693 | 0.52282 | 0.17018 | 3.1369 | 0.2 | 0.51535 | -0.31535 |  | 14-03-2026 07:00 | 2.3 | 2.779 | 0.1 | 0.46317 | 0.38728 | 0.075891 | 2.3237 | 0.1 | 0.38174 | -0.28174 |  | 14-03-2026 07:00 | 2.352 | 2.473 | 0.1 | 0.41217 | 0.38728 | 0.024891 | 2.3237 | 0.1 | 0.38174 | -0.28174 |  | 14-03-2026 07:00 | 2.292 | 2.41 | 0.1 | 0.40167 | 0.38728 | 0.014391 | 2.3237 | 0.1 | 0.38174 | -0.28174 |  | 14-03-2026 07:00 | 2.404 | 2.849 | 0.1 | 0.47483 | 0.38728 | 0.087557 | 2.3237 | 0.1 | 0.38174 | -0.28174 |  | 14-03-2026 07:00 | 2.18 | 2.292 | 0.1 | 0.382 | 0.36845 | 0.013555 | 2.2107 | 0.1 | 0.36318 | -0.26318 |  | 14-03-2026 07:00 | 4.5705 | 4.0088 | 0.56166 | 24.053 | 1.3 | 3.9515 | -2.6515
[110 empty] | Total: - | 16704.3087 | 16951.3372 | -247.0286 |  | 16557 | 16708.9331 | -151.9331
Sum:- | 36989 |  | 12707.674 |  | 81318.7 |  |  |  |  | 2147.5 | 2179.1363 | -31.6363 | 0.99184 |  | 12501.574 |  | 81359.5 |  |  |  |  | 2179.9 | 2179.1363 | 0.76368 | 0.98385 |  | 12830.909 |  | 83079.5 |  |  |  |  | 2145.1 | 2179.1363 | -34.0363 | 0.97335 |  | 12939.172 |  | 83916.5 |  |  |  |  | 2164.3 | 2179.1363 | -14.8363 | 0.98393 |  | 9657.987 |  | 62518 |  |  |  |  | 1614.6 | 1614.1751 | 0.42495 | 0.98504 |  | 9538.928 |  | 61873.1 |  |  |  |  | 1594.2 | 1614.1751 | -19.9751 | 0.98224 |  | 9533.68 |  | 61892 |  |  |  |  | 1595.5 | 1614.1751 | -18.6751 | 0.98131 |  | 9564.233 |  | 62207.1 |  |  |  |  | 1602.9 | 1614.1751 | -11.2751 | 0.97175 |  | 9025.674 |  | 58751 |  |  |  |  | 1513 | 1535.6876 | -22.6876 | 0.9854

## 15 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
15-03-2026 19:00 | 0 | 37.6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.061 | 0.25 | 1996 | 0.041667 | 0 | 0.041667 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.078 | 0.082 | 1960.4 | 0.013667 | 0 | 0.013667 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.052 | 0.06 | 1984.6 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.011 | 0.053 | 1480.7 | 0.0088333 | 0 | 0.0088333 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.075 | 0.079 | 1465.5 | 0.013167 | 0 | 0.013167 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.091 | 0.096 | 1462.4 | 0.016 | 0 | 0.016 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.074 | 0.087 | 1465.7 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.059 | 0.095 | 1385 | 0.015833 | 0 | 0.015833 | 0 | 0 | 0 | 0 |  | 15-03-2026 19:00 | 0.13367 | 0 | 0.13367 | 0 | 0 | 0 | 0 | 1 | 98.36%
15-03-2026 18:50 | 0 | 38.75 | 0.07 | 0.074 | 1976.6 | 0.012333 | 0 | 0.012333 | 0 | 0.3 | 0 | 0.3 |  | 15-03-2026 18:50 | 0.375 | 0.612 | 1996 | 0.102 | 0 | 0.102 | 0 | 0.3 | 0 | 0.3 |  | 15-03-2026 18:50 | 0.132 | 0.156 | 1960.4 | 0.026 | 0 | 0.026 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.149 | 0.567 | 1984.6 | 0.0945 | 0 | 0.0945 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.021 | 0.086 | 1480.7 | 0.014333 | 0 | 0.014333 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.013 | 0.1 | 1465.5 | 0.016667 | 0 | 0.016667 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.083 | 0.087 | 1462.4 | 0.0145 | 0 | 0.0145 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.124 | 0.341 | 1465.7 | 0.056833 | 0 | 0.056833 | 0 | 0.2 | 0 | 0.2 |  | 15-03-2026 18:50 | 0.083 | 0.087 | 1385 | 0.0145 | 0 | 0.0145 | 0 | 0.1 | 0 | 0.1 |  | 15-03-2026 18:50 | 0.35167 | 0 | 0.35167 | 0 | 1.9 | 0 | 1.9 | 2 | 98.29%
15-03-2026 18:40 | 7 | 39.61 | 3.534 | 3.716 | 1976.3 | 0.61933 | 0.43143 | 0.1879 | 2.5886 | 0.9 | 0.42526 | 0.47474 |  | 15-03-2026 18:40 | 3.864 | 4.192 | 1995.7 | 0.69867 | 0.43143 | 0.26723 | 2.5886 | 1 | 0.42526 | 0.57474 |  | 15-03-2026 18:40 | 3.528 | 3.709 | 1960.2 | 0.61817 | 0.43143 | 0.18673 | 2.5886 | 1 | 0.42526 | 0.57474 |  | 15-03-2026 18:40 | 3.586 | 3.903 | 1984.4 | 0.6505 | 0.43143 | 0.21907 | 2.5886 | 1 | 0.42526 | 0.57474 |  | 15-03-2026 18:40 | 2.535 | 2.614 | 1480.5 | 0.43567 | 0.31958 | 0.11609 | 1.9175 | 0.7 | 0.31501 | 0.38499 |  | 15-03-2026 18:40 | 2.486 | 2.614 | 1465.3 | 0.43567 | 0.31958 | 0.11609 | 1.9175 | 0.7 | 0.31501 | 0.38499 |  | 15-03-2026 18:40 | 2.497 | 2.625 | 1462.2 | 0.4375 | 0.31958 | 0.11792 | 1.9175 | 0.7 | 0.31501 | 0.38499 |  | 15-03-2026 18:40 | 2.445 | 2.915 | 1465.5 | 0.48583 | 0.31958 | 0.16625 | 1.9175 | 0.7 | 0.31501 | 0.38499 |  | 15-03-2026 18:40 | 2.337 | 2.457 | 1384.9 | 0.4095 | 0.30404 | 0.10546 | 1.8243 | 0.7 | 0.29969 | 0.40031 |  | 15-03-2026 18:40 | 4.7908 | 3.3081 | 1.4827 | 19.8486 | 7.4 | 3.2608 | 4.1392 | 3 | 97.34%
15-03-2026 18:30 | 22 | 40.75 | 8.732 | 9.092 | 1975.4 | 1.5153 | 1.3502 | 0.1651 | 8.1014 | 1.8 | 1.3309 | 0.46907 |  | 15-03-2026 18:30 | 9.061 | 9.428 | 1994.7 | 1.5713 | 1.3502 | 0.2211 | 8.1014 | 1.8 | 1.3309 | 0.46907 |  | 15-03-2026 18:30 | 8.709 | 9.073 | 1959.2 | 1.5122 | 1.3502 | 0.16193 | 8.1014 | 1.8 | 1.3309 | 0.46907 |  | 15-03-2026 18:30 | 8.845 | 9.275 | 1983.4 | 1.5458 | 1.3502 | 0.1956 | 8.1014 | 1.8 | 1.3309 | 0.46907 |  | 15-03-2026 18:30 | 6.394 | 6.686 | 1479.8 | 1.1143 | 1.0002 | 0.11416 | 6.001 | 1.3 | 0.98587 | 0.31413 |  | 15-03-2026 18:30 | 6.316 | 6.603 | 1464.6 | 1.1005 | 1.0002 | 0.10033 | 6.001 | 1.3 | 0.98587 | 0.31413 |  | 15-03-2026 18:30 | 6.325 | 6.615 | 1461.5 | 1.1025 | 1.0002 | 0.10233 | 6.001 | 1.3 | 0.98587 | 0.31413 |  | 15-03-2026 18:30 | 6.376 | 6.925 | 1464.8 | 1.1542 | 1.0002 | 0.15399 | 6.001 | 1.3 | 0.98587 | 0.31413 |  | 15-03-2026 18:30 | 5.952 | 6.231 | 1384.2 | 1.0385 | 0.95154 | 0.086958 | 5.7092 | 1.2 | 0.93793 | 0.26207 |  | 15-03-2026 18:30 | 11.6547 | 10.3532 | 1.3015 | 62.1191 | 13.6 | 10.2051 | 3.3949 | 4 | 98.33%
15-03-2026 18:20 | 31 | 41.61 | 12.131 | 12.554 | 1973.6 | 2.0923 | 1.8965 | 0.19579 | 11.3793 | 2.1 | 1.8694 | 0.23058 |  | 15-03-2026 18:20 | 12.511 | 12.98 | 1992.9 | 2.1633 | 1.8965 | 0.26679 | 11.3793 | 2.2 | 1.8694 | 0.33058 |  | 15-03-2026 18:20 | 12.152 | 12.572 | 1957.4 | 2.0953 | 1.8965 | 0.19879 | 11.3793 | 2.1 | 1.8694 | 0.23058 |  | 15-03-2026 18:20 | 12.281 | 12.709 | 1981.6 | 2.1182 | 1.8965 | 0.22162 | 11.3793 | 2.2 | 1.8694 | 0.33058 |  | 15-03-2026 18:20 | 8.978 | 9.339 | 1478.5 | 1.5565 | 1.4048 | 0.15165 | 8.4291 | 1.5 | 1.3848 | 0.11524 |  | 15-03-2026 18:20 | 8.829 | 9.183 | 1463.3 | 1.5305 | 1.4048 | 0.12565 | 8.4291 | 1.5 | 1.3848 | 0.11524 |  | 15-03-2026 18:20 | 8.827 | 9.18 | 1460.2 | 1.53 | 1.4048 | 0.12515 | 8.4291 | 1.5 | 1.3848 | 0.11524 |  | 15-03-2026 18:20 | 8.674 | 9.093 | 1463.5 | 1.5155 | 1.4048 | 0.11065 | 8.4291 | 1.6 | 1.3848 | 0.21524 |  | 15-03-2026 18:20 | 8.204 | 8.545 | 1383 | 1.4242 | 1.3365 | 0.087629 | 8.0192 | 1.5 | 1.3174 | 0.18258 |  | 15-03-2026 18:20 | 16.0258 | 14.5421 | 1.4837 | 87.2526 | 16.2 | 14.3341 | 1.8659 | 5 | 98.48%
15-03-2026 18:10 | 36 | 43.05 | 13.687 | 13.78 | 1971.5 | 2.2967 | 2.1907 | 0.10602 | 13.1439 | 3 | 2.1593 | 0.84068 |  | 15-03-2026 18:10 | 15.13 | 15.27 | 1990.7 | 2.545 | 2.1907 | 0.35435 | 13.1439 | 3 | 2.1593 | 0.84068 |  | 15-03-2026 18:10 | 13.326 | 13.765 | 1955.3 | 2.2942 | 2.1907 | 0.10352 | 13.1439 | 2.9 | 2.1593 | 0.74068 |  | 15-03-2026 18:10 | 13.442 | 13.889 | 1979.4 | 2.3148 | 2.1907 | 0.12418 | 13.1439 | 2.9 | 2.1593 | 0.74068 |  | 15-03-2026 18:10 | 9.817 | 10.198 | 1477 | 1.6997 | 1.6227 | 0.076962 | 9.7362 | 2.3 | 1.5995 | 0.7005 |  | 15-03-2026 18:10 | 9.661 | 10.034 | 1461.8 | 1.6723 | 1.6227 | 0.049629 | 9.7362 | 2.2 | 1.5995 | 0.6005 |  | 15-03-2026 18:10 | 9.765 | 10.148 | 1458.7 | 1.6913 | 1.6227 | 0.068629 | 9.7362 | 2.2 | 1.5995 | 0.6005 |  | 15-03-2026 18:10 | 9.799 | 10.383 | 1461.9 | 1.7305 | 1.6227 | 0.1078 | 9.7362 | 2 | 1.5995 | 0.4005 |  | 15-03-2026 18:10 | 9.175 | 9.544 | 1381.5 | 1.5907 | 1.5438 | 0.046864 | 9.2628 | 2 | 1.5217 | 0.47827 |  | 15-03-2026 18:10 | 17.8352 | 16.7972 | 1.0379 | 100.7834 | 22.5 | 16.557 | 5.943 | 6 | 98.27%
15-03-2026 18:00 | 52 | 45.06 | 21.29 | 21.807 | 1968.5 | 3.6345 | 3.1405 | 0.49399 | 18.8431 | 5.2 | 3.0956 | 2.1044 |  | 15-03-2026 18:00 | 21.848 | 22.333 | 1987.7 | 3.7222 | 3.1405 | 0.58165 | 18.8431 | 5.3 | 3.0956 | 2.2044 |  | 15-03-2026 18:00 | 21.398 | 21.92 | 1952.4 | 3.6533 | 3.1405 | 0.51282 | 18.8431 | 5.2 | 3.0956 | 2.1044 |  | 15-03-2026 18:00 | 21.471 | 21.999 | 1976.5 | 3.6665 | 3.1405 | 0.52599 | 18.8431 | 5.2 | 3.0956 | 2.1044 |  | 15-03-2026 18:00 | 15.98 | 16.417 | 1474.7 | 2.7362 | 2.3263 | 0.40986 | 13.9578 | 3.8 | 2.293 | 1.507 |  | 15-03-2026 18:00 | 15.568 | 15.992 | 1459.6 | 2.6653 | 2.3263 | 0.33903 | 13.9578 | 3.7 | 2.293 | 1.407 |  | 15-03-2026 18:00 | 15.609 | 16.039 | 1456.5 | 2.6732 | 2.3263 | 0.34686 | 13.9578 | 3.7 | 2.293 | 1.407 |  | 15-03-2026 18:00 | 15.18 | 15.892 | 1459.9 | 2.6487 | 2.3263 | 0.32236 | 13.9578 | 3.7 | 2.293 | 1.407 |  | 15-03-2026 18:00 | 14.552 | 14.996 | 1379.5 | 2.4993 | 2.2132 | 0.28614 | 13.2791 | 3.5 | 2.1815 | 1.3185 |  | 15-03-2026 18:00 | 27.8992 | 24.0805 | 3.8187 | 144.4828 | 39.3 | 23.7361 | 15.5639 | 7 | 98.16%
15-03-2026 17:50 | 106 | 47.07 | 41.747 | 38.16 | 1963.3 | 6.36 | 6.3534 | 0.0066242 | 38.1203 | 8.1 | 6.2625 | 1.8375 |  | 15-03-2026 17:50 | 38.01 | 38.703 | 1982.4 | 6.4505 | 6.3534 | 0.097124 | 38.1203 | 8.4 | 6.2625 | 2.1375 |  | 15-03-2026 17:50 | 37.842 | 38.528 | 1947.2 | 6.4213 | 6.3534 | 0.067958 | 38.1203 | 8.4 | 6.2625 | 2.1375 |  | 15-03-2026 17:50 | 37.925 | 38.616 | 1971.3 | 6.436 | 6.3534 | 0.082624 | 38.1203 | 8.5 | 6.2625 | 2.2375 |  | 15-03-2026 17:50 | 28.408 | 28.997 | 1470.9 | 4.8328 | 4.7062 | 0.12663 | 28.2372 | 6.3 | 4.6389 | 1.6611 |  | 15-03-2026 17:50 | 27.738 | 28.313 | 1455.9 | 4.7188 | 4.7062 | 0.012629 | 28.2372 | 6.1 | 4.6389 | 1.4611 |  | 15-03-2026 17:50 | 27.755 | 28.327 | 1452.8 | 4.7212 | 4.7062 | 0.014962 | 28.2372 | 6.2 | 4.6389 | 1.5611 |  | 15-03-2026 17:50 | 27.32 | 27.957 | 1456.2 | 4.6595 | 4.7062 | -0.046704 | 28.2372 | 6.1 | 4.6389 | 1.4611 |  | 15-03-2026 17:50 | 25.763 | 26.326 | 1376 | 4.3877 | 4.4774 | -0.089704 | 26.8642 | 5.6 | 4.4133 | 1.1867 |  | 15-03-2026 17:50 | 48.9878 | 48.7157 | 0.27214 | 292.2941 | 63.7 | 48.0191 | 15.6809 | 8 | 97.16%
15-03-2026 17:40 | 165 | 47.35 | 56.321 | 57.645 | 1955.2 | 9.6075 | 9.8792 | -0.27169 | 59.2751 | 10.8 | 9.7379 | 1.0621 |  | 15-03-2026 17:40 | 62.536 | 56.098 | 1974 | 9.3497 | 9.8792 | -0.52952 | 59.2751 | 11 | 9.7379 | 1.2621 |  | 15-03-2026 17:40 | 56.87 | 57.73 | 1938.8 | 9.6217 | 9.8792 | -0.25752 | 59.2751 | 10.5 | 9.7379 | 0.76209 |  | 15-03-2026 17:40 | 56.832 | 57.692 | 1962.8 | 9.6153 | 9.8792 | -0.26385 | 59.2751 | 10.5 | 9.7379 | 0.76209 |  | 15-03-2026 17:40 | 42.731 | 43.466 | 1464.6 | 7.2443 | 7.3179 | -0.073582 | 43.9075 | 7.9 | 7.2133 | 0.68673 |  | 15-03-2026 17:40 | 41.577 | 42.279 | 1449.8 | 7.0465 | 7.3179 | -0.27142 | 43.9075 | 7.7 | 7.2133 | 0.48673 |  | 15-03-2026 17:40 | 41.735 | 42.448 | 1446.6 | 7.0747 | 7.3179 | -0.24325 | 43.9075 | 7.7 | 7.2133 | 0.48673 |  | 15-03-2026 17:40 | 40.664 | 41.819 | 1450.1 | 6.9698 | 7.3179 | -0.34808 | 43.9075 | 7.5 | 7.2133 | 0.28673 |  | 15-03-2026 17:40 | 38.899 | 39.58 | 1370.4 | 6.5967 | 6.9621 | -0.36542 | 41.7725 | 7.2 | 6.8625 | 0.33747 |  | 15-03-2026 17:40 | 73.1262 | 75.7505 | -2.6243 | 454.503 | 80.8 | 74.6673 | 6.1327 | 9 | 98.5%
15-03-2026 17:30 | 164 | 47.64 | 56.417 | 57.27 | 1944.4 | 9.545 | 9.8085 | -0.2635 | 58.851 | 10.7 | 9.6682 | 1.0318 |  | 15-03-2026 17:30 | 48.182 | 55.641 | 1963 | 9.2735 | 9.8085 | -0.535 | 58.851 | 10.6 | 9.6682 | 0.93176 |  | 15-03-2026 17:30 | 56.779 | 57.632 | 1928.3 | 9.6053 | 9.8085 | -0.20317 | 58.851 | 10.7 | 9.6682 | 1.0318 |  | 15-03-2026 17:30 | 56.866 | 57.738 | 1952.3 | 9.623 | 9.8085 | -0.1855 | 58.851 | 10.7 | 9.6682 | 1.0318 |  | 15-03-2026 17:30 | 42.636 | 43.369 | 1456.7 | 7.2282 | 7.2656 | -0.037388 | 43.5933 | 8 | 7.1617 | 0.83834 |  | 15-03-2026 17:30 | 41.625 | 42.341 | 1442.1 | 7.0568 | 7.2656 | -0.20872 | 43.5933 | 7.9 | 7.1617 | 0.73834 |  | 15-03-2026 17:30 | 41.733 | 42.45 | 1438.9 | 7.075 | 7.2656 | -0.19056 | 43.5933 | 8 | 7.1617 | 0.83834 |  | 15-03-2026 17:30 | 41.028 | 42.026 | 1442.6 | 7.0043 | 7.2656 | -0.26122 | 43.5933 | 7.8 | 7.1617 | 0.63834 |  | 15-03-2026 17:30 | 38.449 | 39.138 | 1363.2 | 6.523 | 6.9123 | -0.38928 | 41.4737 | 7.4 | 6.8134 | 0.58657 |  | 15-03-2026 17:30 | 72.9342 | 75.2085 | -2.2743 | 451.251 | 81.8 | 74.133 | 7.667
15-03-2026 17:20 | 247 | 47.35 | 84.376 | 85.453 | 1933.7 | 14.2422 | 14.7888 | -0.54667 | 88.733 | 16 | 14.5774 | 1.4226 |  | 15-03-2026 17:20 | 85.18 | 86.302 | 1952.4 | 14.3837 | 14.7888 | -0.40517 | 88.733 | 15.6 | 14.5774 | 1.0226 |  | 15-03-2026 17:20 | 84.372 | 85.677 | 1917.6 | 14.2795 | 14.7888 | -0.50934 | 88.733 | 15.5 | 14.5774 | 0.92264 |  | 15-03-2026 17:20 | 84.544 | 85.656 | 1941.6 | 14.276 | 14.7888 | -0.51284 | 88.733 | 15.5 | 14.5774 | 0.92264 |  | 15-03-2026 17:20 | 63.5 | 64.402 | 1448.7 | 10.7337 | 10.9547 | -0.22103 | 65.7282 | 11.7 | 10.798 | 0.90195 |  | 15-03-2026 17:20 | 61.936 | 62.796 | 1434.2 | 10.466 | 10.9547 | -0.4887 | 65.7282 | 11.4 | 10.798 | 0.60195 |  | 15-03-2026 17:20 | 62.258 | 63.129 | 1430.9 | 10.5215 | 10.9547 | -0.4332 | 65.7282 | 11.2 | 10.798 | 0.40195 |  | 15-03-2026 17:20 | 61.007 | 63.035 | 1434.8 | 10.5058 | 10.9547 | -0.44886 | 65.7282 | 11.2 | 10.798 | 0.40195 |  | 15-03-2026 17:20 | 57.285 | 58.157 | 1355.8 | 9.6928 | 10.422 | -0.7292 | 62.5322 | 10.6 | 10.273 | 0.327 |  | 15-03-2026 17:20 | 109.1012 | 113.3962 | -4.295 | 680.3772 | 118.7 | 111.7746 | 6.9254
15-03-2026 17:10 | 293 | 47.64 | 102.291 | 103.554 | 1917.7 | 17.259 | 17.5237 | -0.26472 | 105.1423 | 17.3 | 17.2731 | 0.026868 |  | 15-03-2026 17:10 | 102.138 | 103.452 | 1936.8 | 17.242 | 17.5237 | -0.28172 | 105.1423 | 19.1 | 17.2731 | 1.8269 |  | 15-03-2026 17:10 | 100.894 | 102.614 | 1902.1 | 17.1023 | 17.5237 | -0.42139 | 105.1423 | 18 | 17.2731 | 0.72687 |  | 15-03-2026 17:10 | 101.232 | 102.524 | 1926.1 | 17.0873 | 17.5237 | -0.43639 | 105.1423 | 18.1 | 17.2731 | 0.82687 |  | 15-03-2026 17:10 | 75.83 | 76.86 | 1437 | 12.81 | 12.9805 | -0.17053 | 77.8832 | 13.5 | 12.7949 | 0.70509 |  | 15-03-2026 17:10 | 74.086 | 75.085 | 1422.8 | 12.5142 | 12.9805 | -0.46637 | 77.8832 | 13.2 | 12.7949 | 0.40509 |  | 15-03-2026 17:10 | 73.805 | 74.807 | 1419.7 | 12.4678 | 12.9805 | -0.5127 | 77.8832 | 13.5 | 12.7949 | 0.70509 |  | 15-03-2026 17:10 | 72.996 | 75.176 | 1423.6 | 12.5293 | 12.9805 | -0.4512 | 77.8832 | 13.2 | 12.7949 | 0.40509 |  | 15-03-2026 17:10 | 68.254 | 69.209 | 1345.2 | 11.5348 | 12.3494 | -0.81454 | 74.0962 | 12.4 | 12.1728 | 0.22723 |  | 15-03-2026 17:10 | 130.5468 | 134.3664 | -3.8196 | 806.1984 | 138.3 | 132.445 | 5.855
15-03-2026 17:00 | 334 | 47.64 | 115.602 | 117.053 | 1900.4 | 19.5088 | 19.9758 | -0.46701 | 119.8551 | 20.1 | 19.6902 | 0.40981 |  | 15-03-2026 17:00 | 114.413 | 115.896 | 1917.7 | 19.316 | 19.9758 | -0.65985 | 119.8551 | 19.2 | 19.6902 | -0.49019 |  | 15-03-2026 17:00 | 115.028 | 117.037 | 1884.1 | 19.5062 | 19.9758 | -0.46968 | 119.8551 | 20.1 | 19.6902 | 0.40981 |  | 15-03-2026 17:00 | 115.71 | 117.21 | 1908 | 19.535 | 19.9758 | -0.44085 | 119.8551 | 20.2 | 19.6902 | 0.50981 |  | 15-03-2026 17:00 | 86.588 | 87.728 | 1423.5 | 14.6213 | 14.7969 | -0.17559 | 88.7815 | 15.2 | 14.5853 | 0.61467 |  | 15-03-2026 17:00 | 84.494 | 85.598 | 1409.6 | 14.2663 | 14.7969 | -0.53059 | 88.7815 | 15 | 14.5853 | 0.41467 |  | 15-03-2026 17:00 | 84.943 | 86.036 | 1406.2 | 14.3393 | 14.7969 | -0.45759 | 88.7815 | 14.8 | 14.5853 | 0.21467 |  | 15-03-2026 17:00 | 83.76 | 85.939 | 1410.4 | 14.3232 | 14.7969 | -0.47376 | 88.7815 | 14.6 | 14.5853 | 0.014673 |  | 15-03-2026 17:00 | 79.084 | 80.15 | 1332.8 | 13.3583 | 14.0774 | -0.71911 | 84.4646 | 13.8 | 13.8761 | -0.076132 |  | 15-03-2026 17:00 | 148.7745 | 153.1685 | -4.394 | 919.0111 | 153 | 150.9782 | 2.0218
15-03-2026 16:50 | 376 | 47.93 | 131.267 | 132.942 | 1880.3 | 22.157 | 22.463 | -0.30599 | 134.7779 | 48 | 22.1418 | 25.8582 |  | 15-03-2026 16:50 | 132.429 | 134.16 | 1898.5 | 22.36 | 22.463 | -0.10299 | 134.7779 | 23.1 | 22.1418 | 0.95823 |  | 15-03-2026 16:50 | 130.346 | 132.925 | 1864 | 22.1542 | 22.463 | -0.30882 | 134.7779 | 22.7 | 22.1418 | 0.55823 |  | 15-03-2026 16:50 | 131.114 | 132.841 | 1887.8 | 22.1402 | 22.463 | -0.32282 | 134.7779 | 22.9 | 22.1418 | 0.75823 |  | 15-03-2026 16:50 | 97.865 | 99.114 | 1408.3 | 16.519 | 16.6393 | -0.12025 | 99.8355 | 17.1 | 16.4013 | 0.69869 |  | 15-03-2026 16:50 | 96.279 | 97.508 | 1394.6 | 16.2513 | 16.6393 | -0.38792 | 99.8355 | 16.6 | 16.4013 | 0.19869 |  | 15-03-2026 16:50 | 96.376 | 97.606 | 1391.4 | 16.2677 | 16.6393 | -0.37158 | 99.8355 | 16.5 | 16.4013 | 0.09869 |  | 15-03-2026 16:50 | 95.199 | 97.964 | 1395.8 | 16.3273 | 16.6393 | -0.31192 | 99.8355 | 16.4 | 16.4013 | -0.0013102 |  | 15-03-2026 16:50 | 89.941 | 91.116 | 1319 | 15.186 | 15.8302 | -0.64419 | 94.9811 | 15.7 | 15.6038 | 0.096185 |  | 15-03-2026 16:50 | 169.3627 | 172.2392 | -2.8765 | 1033.4349 | 199 | 169.7761 | 29.2239
15-03-2026 16:40 | 420 | 47.93 | 147.08 | 148.987 | 1857.4 | 24.8312 | 25.0916 | -0.26047 | 150.5498 | 0 | 24.7328 | -24.7328 |  | 15-03-2026 16:40 | 147.5 | 149.473 | 1875.4 | 24.9122 | 25.0916 | -0.17947 | 150.5498 | 26.2 | 24.7328 | 1.4672 |  | 15-03-2026 16:40 | 146.11 | 148.982 | 1841.3 | 24.8303 | 25.0916 | -0.2613 | 150.5498 | 25.1 | 24.7328 | 0.36717 |  | 15-03-2026 16:40 | 146.602 | 148.578 | 1864.9 | 24.763 | 25.0916 | -0.32864 | 150.5498 | 25.7 | 24.7328 | 0.96717 |  | 15-03-2026 16:40 | 110.083 | 111.488 | 1391.2 | 18.5813 | 18.5864 | -0.0050646 | 111.5184 | 19.3 | 18.3206 | 0.97939 |  | 15-03-2026 16:40 | 107.406 | 108.788 | 1378 | 18.1313 | 18.5864 | -0.45506 | 111.5184 | 18.8 | 18.3206 | 0.47939 |  | 15-03-2026 16:40 | 107.549 | 108.932 | 1374.9 | 18.1553 | 18.5864 | -0.43106 | 111.5184 | 18.8 | 18.3206 | 0.47939 |  | 15-03-2026 16:40 | 106.274 | 108.981 | 1379.4 | 18.1635 | 18.5864 | -0.4229 | 111.5184 | 18.7 | 18.3206 | 0.37939 |  | 15-03-2026 16:40 | 100.552 | 101.845 | 1303.3 | 16.9742 | 17.6827 | -0.70849 | 106.0959 | 17.4 | 17.4298 | -0.029794 |  | 15-03-2026 16:40 | 189.3423 | 192.3948 | -3.0525 | 1154.3688 | 170 | 189.6436 | -19.6436
15-03-2026 16:30 | 458 | 47.93 | 160.907 | 163.01 | 1832.3 | 27.1683 | 27.3618 | -0.1935 | 164.171 | 25 | 26.9706 | -1.9706 |  | 15-03-2026 16:30 | 167.168 | 169.421 | 1849.2 | 28.2368 | 27.3618 | 0.875 | 164.171 | 24 | 26.9706 | -2.9706 |  | 15-03-2026 16:30 | 162.042 | 161.034 | 1816.2 | 26.839 | 27.3618 | -0.52283 | 164.171 | 24.7 | 26.9706 | -2.2706 |  | 15-03-2026 16:30 | 163.748 | 165.955 | 1839.2 | 27.6592 | 27.3618 | 0.29733 | 164.171 | 24.3 | 26.9706 | -2.6706 |  | 15-03-2026 16:30 | 121.976 | 123.558 | 1371.9 | 20.593 | 20.268 | 0.32498 | 121.6081 | 18.5 | 19.9782 | -1.4782 |  | 15-03-2026 16:30 | 119.09 | 120.634 | 1359.2 | 20.1057 | 20.268 | -0.16236 | 121.6081 | 18.1 | 19.9782 | -1.8782 |  | 15-03-2026 16:30 | 118.25 | 120.165 | 1356.1 | 20.0275 | 20.268 | -0.24052 | 121.6081 | 18.1 | 19.9782 | -1.8782 |  | 15-03-2026 16:30 | 117.584 | 120.854 | 1360.7 | 20.1423 | 20.268 | -0.12569 | 121.6081 | 18 | 19.9782 | -1.9782 |  | 15-03-2026 16:30 | 111.56 | 113.018 | 1285.9 | 18.8363 | 19.2825 | -0.44618 | 115.6951 | 17 | 19.0068 | -2.0068 |  | 15-03-2026 16:30 | 209.6082 | 209.8019 | -0.19378 | 1258.8117 | 187.7 | 206.8018 | -19.1018
15-03-2026 16:20 | 471 | 48.22 | 167.84 | 170.102 | 1807.3 | 28.3503 | 28.1074 | 0.24291 | 168.6446 | 29.2 | 27.7055 | 1.4945 |  | 15-03-2026 16:20 | 177.345 | 179.808 | 1825.2 | 29.968 | 28.1074 | 1.8606 | 168.6446 | 29.8 | 27.7055 | 2.0945 |  | 15-03-2026 16:20 | 163.033 | 165.545 | 1791.5 | 27.5908 | 28.1074 | -0.51659 | 168.6446 | 29.2 | 27.7055 | 1.4945 |  | 15-03-2026 16:20 | 162.799 | 165.594 | 1814.9 | 27.599 | 28.1074 | -0.50843 | 168.6446 | 29.5 | 27.7055 | 1.7945 |  | 15-03-2026 16:20 | 123.955 | 125.575 | 1353.4 | 20.9292 | 20.8203 | 0.10885 | 124.9219 | 21.7 | 20.5226 | 1.1774 |  | 15-03-2026 16:20 | 120.808 | 122.721 | 1341.1 | 20.4535 | 20.8203 | -0.36682 | 124.9219 | 21.3 | 20.5226 | 0.77741 |  | 15-03-2026 16:20 | 120.073 | 121.642 | 1338 | 20.2737 | 20.8203 | -0.54665 | 124.9219 | 21.2 | 20.5226 | 0.67741 |  | 15-03-2026 16:20 | 118.681 | 121.834 | 1342.7 | 20.3057 | 20.8203 | -0.51465 | 124.9219 | 21.4 | 20.5226 | 0.87741 |  | 15-03-2026 16:20 | 112.037 | 113.536 | 1268.9 | 18.9227 | 19.808 | -0.88529 | 118.8477 | 20.3 | 19.5247 | 0.7753 |  | 15-03-2026 16:20 | 214.3928 | 215.5189 | -1.1261 | 1293.1135 | 223.6 | 212.437 | 11.163
15-03-2026 16:10 | 567 | 48.5 | 196.712 | 199.538 | 1778.1 | 33.2563 | 33.8002 | -0.5439 | 202.8014 | 24.7 | 33.3169 | -8.6169 |  | 15-03-2026 16:10 | 198.681 | 201.522 | 1795.4 | 33.587 | 33.8002 | -0.21324 | 202.8014 | 24.9 | 33.3169 | -8.4169 |  | 15-03-2026 16:10 | 196 | 200.186 | 1762.3 | 33.3643 | 33.8002 | -0.4359 | 202.8014 | 24.8 | 33.3169 | -8.5169 |  | 15-03-2026 16:10 | 197.445 | 200.269 | 1785.4 | 33.3782 | 33.8002 | -0.42207 | 202.8014 | 24.9 | 33.3169 | -8.4169 |  | 15-03-2026 16:10 | 147.694 | 149.7 | 1331.7 | 24.95 | 25.0372 | -0.087211 | 150.2233 | 19.3 | 24.6792 | -5.3792 |  | 15-03-2026 16:10 | 144.844 | 146.842 | 1319.8 | 24.4737 | 25.0372 | -0.56354 | 150.2233 | 19 | 24.6792 | -5.6792 |  | 15-03-2026 16:10 | 144.351 | 146.312 | 1316.8 | 24.3853 | 25.0372 | -0.65188 | 150.2233 | 19 | 24.6792 | -5.6792 |  | 15-03-2026 16:10 | 143.899 | 148.003 | 1321.3 | 24.6672 | 25.0372 | -0.37004 | 150.2233 | 19.8 | 24.6792 | -4.8792 |  | 15-03-2026 16:10 | 136.204 | 138.026 | 1248.6 | 23.0043 | 23.8198 | -0.81547 | 142.9188 | 17.7 | 23.4792 | -5.7792 |  | 15-03-2026 16:10 | 255.0663 | 259.1696 | -4.1033 | 1555.0176 | 194.1 | 255.4635 | -61.3635
15-03-2026 16:00 | 604 | 48.5 | 0 | 0 | 1753.4 | 0 | 36.0059 | -36.0059 | 216.0354 | 0 | 35.491 | -35.491 |  | 15-03-2026 16:00 | 0 | 0 | 1770.5 | 0 | 36.0059 | -36.0059 | 216.0354 | 0 | 35.491 | -35.491 |  | 15-03-2026 16:00 | 0 | 0 | 1737.5 | 0 | 36.0059 | -36.0059 | 216.0354 | 0 | 35.491 | -35.491 |  | 15-03-2026 16:00 | 0 | 0 | 1760.5 | 0 | 36.0059 | -36.0059 | 216.0354 | 0 | 35.491 | -35.491 |  | 15-03-2026 16:00 | 0 | 0 | 1312.4 | 0 | 26.671 | -26.671 | 160.0262 | 0 | 26.2896 | -26.2896 |  | 15-03-2026 16:00 | 0 | 0 | 1300.8 | 0 | 26.671 | -26.671 | 160.0262 | 0 | 26.2896 | -26.2896 |  | 15-03-2026 16:00 | 0 | 0 | 1297.8 | 0 | 26.671 | -26.671 | 160.0262 | 0 | 26.2896 | -26.2896 |  | 15-03-2026 16:00 | 0 | 0 | 1301.5 | 0 | 26.671 | -26.671 | 160.0262 | 0 | 26.2896 | -26.2896 |  | 15-03-2026 16:00 | 0 | 0 | 1230.9 | 0 | 25.3742 | -25.3742 | 152.2451 | 0 | 25.0113 | -25.0113 |  | 15-03-2026 16:00 | 0 | 276.0819 | -276.0819 | 1656.4914 | 0 | 272.1339 | -272.1339
15-03-2026 15:50 | 624 | 48.5 | 0 | 0 | 1753.4 | 0 | 37.1981 | -37.1981 | 223.1889 | 0 | 36.6662 | -36.6662 |  | 15-03-2026 15:50 | 0 | 0 | 1770.5 | 0 | 37.1981 | -37.1981 | 223.1889 | 0 | 36.6662 | -36.6662 |  | 15-03-2026 15:50 | 0 | 0 | 1737.5 | 0 | 37.1981 | -37.1981 | 223.1889 | 0 | 36.6662 | -36.6662 |  | 15-03-2026 15:50 | 0 | 0 | 1760.5 | 0 | 37.1981 | -37.1981 | 223.1889 | 0 | 36.6662 | -36.6662 |  | 15-03-2026 15:50 | 0 | 0 | 1312.4 | 0 | 27.5542 | -27.5542 | 165.3251 | 0 | 27.1602 | -27.1602 |  | 15-03-2026 15:50 | 0 | 0 | 1300.8 | 0 | 27.5542 | -27.5542 | 165.3251 | 0 | 27.1602 | -27.1602 |  | 15-03-2026 15:50 | 0 | 0 | 1297.8 | 0 | 27.5542 | -27.5542 | 165.3251 | 0 | 27.1602 | -27.1602 |  | 15-03-2026 15:50 | 0 | 0 | 1301.5 | 0 | 27.5542 | -27.5542 | 165.3251 | 0 | 27.1602 | -27.1602 |  | 15-03-2026 15:50 | 0 | 0 | 1230.9 | 0 | 26.2144 | -26.2144 | 157.2863 | 0 | 25.8395 | -25.8395 |  | 15-03-2026 15:50 | 0 | 285.2237 | -285.2237 | 1711.3421 | 0 | 281.145 | -281.145
15-03-2026 15:40 | 668 | 48.79 | 0 | 0 | 1753.4 | 0 | 39.777 | -39.777 | 238.6623 | 0 | 39.2082 | -39.2082 |  | 15-03-2026 15:40 | 0 | 0 | 1770.5 | 0 | 39.777 | -39.777 | 238.6623 | 0 | 39.2082 | -39.2082 |  | 15-03-2026 15:40 | 0 | 0 | 1737.5 | 0 | 39.777 | -39.777 | 238.6623 | 0 | 39.2082 | -39.2082 |  | 15-03-2026 15:40 | 0 | 0 | 1760.5 | 0 | 39.777 | -39.777 | 238.6623 | 0 | 39.2082 | -39.2082 |  | 15-03-2026 15:40 | 0 | 0 | 1312.4 | 0 | 29.4645 | -29.4645 | 176.7869 | 0 | 29.0431 | -29.0431 |  | 15-03-2026 15:40 | 0 | 0 | 1300.8 | 0 | 29.4645 | -29.4645 | 176.7869 | 0 | 29.0431 | -29.0431 |  | 15-03-2026 15:40 | 0 | 0 | 1297.8 | 0 | 29.4645 | -29.4645 | 176.7869 | 0 | 29.0431 | -29.0431 |  | 15-03-2026 15:40 | 0 | 0 | 1301.5 | 0 | 29.4645 | -29.4645 | 176.7869 | 0 | 29.0431 | -29.0431 |  | 15-03-2026 15:40 | 0 | 0 | 1230.9 | 0 | 28.0318 | -28.0318 | 168.1908 | 0 | 27.6309 | -27.6309 |  | 15-03-2026 15:40 | 0 | 304.9979 | -304.9979 | 1829.9875 | 0 | 300.6364 | -300.6364
15-03-2026 15:30 | 709 | 48.5 | 0 | 0 | 1753.4 | 0 | 42.2652 | -42.2652 | 253.5912 | 0 | 41.6608 | -41.6608 |  | 15-03-2026 15:30 | 0 | 0 | 1770.5 | 0 | 42.2652 | -42.2652 | 253.5912 | 0 | 41.6608 | -41.6608 |  | 15-03-2026 15:30 | 0 | 0 | 1737.5 | 0 | 42.2652 | -42.2652 | 253.5912 | 0 | 41.6608 | -41.6608 |  | 15-03-2026 15:30 | 0 | 0 | 1760.5 | 0 | 42.2652 | -42.2652 | 253.5912 | 0 | 41.6608 | -41.6608 |  | 15-03-2026 15:30 | 0 | 0 | 1312.4 | 0 | 31.3076 | -31.3076 | 187.8453 | 0 | 30.8599 | -30.8599 |  | 15-03-2026 15:30 | 0 | 0 | 1300.8 | 0 | 31.3076 | -31.3076 | 187.8453 | 0 | 30.8599 | -30.8599 |  | 15-03-2026 15:30 | 0 | 0 | 1297.8 | 0 | 31.3076 | -31.3076 | 187.8453 | 0 | 30.8599 | -30.8599 |  | 15-03-2026 15:30 | 0 | 0 | 1301.5 | 0 | 31.3076 | -31.3076 | 187.8453 | 0 | 30.8599 | -30.8599 |  | 15-03-2026 15:30 | 0 | 0 | 1230.9 | 0 | 29.7853 | -29.7853 | 178.7116 | 0 | 29.3593 | -29.3593 |  | 15-03-2026 15:30 | 0 | 324.0763 | -324.0763 | 1944.4576 | 0 | 319.442 | -319.442
15-03-2026 15:20 | 754 | 48.5 | 0 | 0 | 1753.4 | 0 | 44.9478 | -44.9478 | 269.6865 | 0 | 44.305 | -44.305 |  | 15-03-2026 15:20 | 0 | 0 | 1770.5 | 0 | 44.9478 | -44.9478 | 269.6865 | 0 | 44.305 | -44.305 |  | 15-03-2026 15:20 | 0 | 0 | 1737.5 | 0 | 44.9478 | -44.9478 | 269.6865 | 0 | 44.305 | -44.305 |  | 15-03-2026 15:20 | 0 | 0 | 1760.5 | 0 | 44.9478 | -44.9478 | 269.6865 | 0 | 44.305 | -44.305 |  | 15-03-2026 15:20 | 0 | 0 | 1312.4 | 0 | 33.2946 | -33.2946 | 199.7678 | 0 | 32.8185 | -32.8185 |  | 15-03-2026 15:20 | 0 | 0 | 1300.8 | 0 | 33.2946 | -33.2946 | 199.7678 | 0 | 32.8185 | -32.8185 |  | 15-03-2026 15:20 | 0 | 0 | 1297.8 | 0 | 33.2946 | -33.2946 | 199.7678 | 0 | 32.8185 | -32.8185 |  | 15-03-2026 15:20 | 0 | 0 | 1301.5 | 0 | 33.2946 | -33.2946 | 199.7678 | 0 | 32.8185 | -32.8185 |  | 15-03-2026 15:20 | 0 | 0 | 1230.9 | 0 | 31.6757 | -31.6757 | 190.0543 | 0 | 31.2228 | -31.2228 |  | 15-03-2026 15:20 | 0 | 344.6453 | -344.6453 | 2067.8717 | 0 | 339.7169 | -339.7169
15-03-2026 15:10 | 763 | 48.79 | 0 | 0 | 1753.4 | 0 | 45.434 | -45.434 | 272.6038 | 0 | 44.7843 | -44.7843 |  | 15-03-2026 15:10 | 0 | 0 | 1770.5 | 0 | 45.434 | -45.434 | 272.6038 | 0 | 44.7843 | -44.7843 |  | 15-03-2026 15:10 | 0 | 0 | 1737.5 | 0 | 45.434 | -45.434 | 272.6038 | 0 | 44.7843 | -44.7843 |  | 15-03-2026 15:10 | 0 | 0 | 1760.5 | 0 | 45.434 | -45.434 | 272.6038 | 0 | 44.7843 | -44.7843 |  | 15-03-2026 15:10 | 0 | 0 | 1312.4 | 0 | 33.6548 | -33.6548 | 201.9287 | 0 | 33.1735 | -33.1735 |  | 15-03-2026 15:10 | 0 | 0 | 1300.8 | 0 | 33.6548 | -33.6548 | 201.9287 | 0 | 33.1735 | -33.1735 |  | 15-03-2026 15:10 | 0 | 0 | 1297.8 | 0 | 33.6548 | -33.6548 | 201.9287 | 0 | 33.1735 | -33.1735 |  | 15-03-2026 15:10 | 0 | 0 | 1301.5 | 0 | 33.6548 | -33.6548 | 201.9287 | 0 | 33.1735 | -33.1735 |  | 15-03-2026 15:10 | 0 | 0 | 1230.9 | 0 | 32.0184 | -32.0184 | 192.1102 | 0 | 31.5605 | -31.5605 |  | 15-03-2026 15:10 | 0 | 348.3734 | -348.3734 | 2090.2402 | 0 | 343.3916 | -343.3916
15-03-2026 15:00 | 818 | 48.79 | 0 | 0 | 1753.4 | 0 | 48.709 | -48.709 | 292.2541 | 0 | 48.0125 | -48.0125 |  | 15-03-2026 15:00 | 0 | 0 | 1770.5 | 0 | 48.709 | -48.709 | 292.2541 | 0 | 48.0125 | -48.0125 |  | 15-03-2026 15:00 | 0 | 0 | 1737.5 | 0 | 48.709 | -48.709 | 292.2541 | 0 | 48.0125 | -48.0125 |  | 15-03-2026 15:00 | 0 | 0 | 1760.5 | 0 | 48.709 | -48.709 | 292.2541 | 0 | 48.0125 | -48.0125 |  | 15-03-2026 15:00 | 0 | 0 | 1312.4 | 0 | 36.0808 | -36.0808 | 216.4845 | 0 | 35.5648 | -35.5648 |  | 15-03-2026 15:00 | 0 | 0 | 1300.8 | 0 | 36.0808 | -36.0808 | 216.4845 | 0 | 35.5648 | -35.5648 |  | 15-03-2026 15:00 | 0 | 0 | 1297.8 | 0 | 36.0808 | -36.0808 | 216.4845 | 0 | 35.5648 | -35.5648 |  | 15-03-2026 15:00 | 0 | 0 | 1301.5 | 0 | 36.0808 | -36.0808 | 216.4845 | 0 | 35.5648 | -35.5648 |  | 15-03-2026 15:00 | 0 | 0 | 1230.9 | 0 | 34.3264 | -34.3264 | 205.9582 | 0 | 33.8355 | -33.8355 |  | 15-03-2026 15:00 | 0 | 373.4855 | -373.4855 | 2240.9128 | 0 | 368.1446 | -368.1446
15-03-2026 14:50 | 875 | 48.79 | 0 | 0 | 1753.4 | 0 | 52.1032 | -52.1032 | 312.619 | 0 | 51.3581 | -51.3581 |  | 15-03-2026 14:50 | 0 | 0 | 1770.5 | 0 | 52.1032 | -52.1032 | 312.619 | 0 | 51.3581 | -51.3581 |  | 15-03-2026 14:50 | 0 | 0 | 1737.5 | 0 | 52.1032 | -52.1032 | 312.619 | 0 | 51.3581 | -51.3581 |  | 15-03-2026 14:50 | 0 | 0 | 1760.5 | 0 | 52.1032 | -52.1032 | 312.619 | 0 | 51.3581 | -51.3581 |  | 15-03-2026 14:50 | 0 | 0 | 1312.4 | 0 | 38.5949 | -38.5949 | 231.5696 | 0 | 38.043 | -38.043 |  | 15-03-2026 14:50 | 0 | 0 | 1300.8 | 0 | 38.5949 | -38.5949 | 231.5696 | 0 | 38.043 | -38.043 |  | 15-03-2026 14:50 | 0 | 0 | 1297.8 | 0 | 38.5949 | -38.5949 | 231.5696 | 0 | 38.043 | -38.043 |  | 15-03-2026 14:50 | 0 | 0 | 1301.5 | 0 | 38.5949 | -38.5949 | 231.5696 | 0 | 38.043 | -38.043 |  | 15-03-2026 14:50 | 0 | 0 | 1230.9 | 0 | 36.7183 | -36.7183 | 220.3098 | 0 | 36.1932 | -36.1932 |  | 15-03-2026 14:50 | 0 | 399.5107 | -399.5107 | 2397.0644 | 0 | 393.7977 | -393.7977
15-03-2026 14:40 | 903 | 48.5 | 0 | 0 | 1753.4 | 0 | 53.83 | -53.83 | 322.98 | 0 | 53.0602 | -53.0602 |  | 15-03-2026 14:40 | 0 | 0 | 1770.5 | 0 | 53.83 | -53.83 | 322.98 | 0 | 53.0602 | -53.0602 |  | 15-03-2026 14:40 | 0 | 0 | 1737.5 | 0 | 53.83 | -53.83 | 322.98 | 0 | 53.0602 | -53.0602 |  | 15-03-2026 14:40 | 0 | 0 | 1760.5 | 0 | 53.83 | -53.83 | 322.98 | 0 | 53.0602 | -53.0602 |  | 15-03-2026 14:40 | 0 | 0 | 1312.4 | 0 | 39.8741 | -39.8741 | 239.2445 | 0 | 39.3039 | -39.3039 |  | 15-03-2026 14:40 | 0 | 0 | 1300.8 | 0 | 39.8741 | -39.8741 | 239.2445 | 0 | 39.3039 | -39.3039 |  | 15-03-2026 14:40 | 0 | 0 | 1297.8 | 0 | 39.8741 | -39.8741 | 239.2445 | 0 | 39.3039 | -39.3039 |  | 15-03-2026 14:40 | 0 | 0 | 1301.5 | 0 | 39.8741 | -39.8741 | 239.2445 | 0 | 39.3039 | -39.3039 |  | 15-03-2026 14:40 | 0 | 0 | 1230.9 | 0 | 37.9352 | -37.9352 | 227.6115 | 0 | 37.3928 | -37.3928 |  | 15-03-2026 14:40 | 0 | 412.7516 | -412.7516 | 2476.5094 | 0 | 406.8492 | -406.8492
15-03-2026 14:30 | 920 | 48.5 | 0 | 0 | 1753.4 | 0 | 54.8434 | -54.8434 | 329.0605 | 40 | 54.0592 | -14.0592 |  | 15-03-2026 14:30 | 0 | 0 | 1770.5 | 0 | 54.8434 | -54.8434 | 329.0605 | 41.3 | 54.0592 | -12.7592 |  | 15-03-2026 14:30 | 0 | 0 | 1737.5 | 0 | 54.8434 | -54.8434 | 329.0605 | 40.3 | 54.0592 | -13.7592 |  | 15-03-2026 14:30 | 0 | 0 | 1760.5 | 0 | 54.8434 | -54.8434 | 329.0605 | 40.7 | 54.0592 | -13.3592 |  | 15-03-2026 14:30 | 0 | 0 | 1312.4 | 0 | 40.6248 | -40.6248 | 243.7485 | 30.4 | 40.0438 | -9.6438 |  | 15-03-2026 14:30 | 0 | 0 | 1300.8 | 0 | 40.6248 | -40.6248 | 243.7485 | 29.8 | 40.0438 | -10.2438 |  | 15-03-2026 14:30 | 0 | 0 | 1297.8 | 0 | 40.6248 | -40.6248 | 243.7485 | 29.7 | 40.0438 | -10.3438 |  | 15-03-2026 14:30 | 0 | 0 | 1301.5 | 0 | 40.6248 | -40.6248 | 243.7485 | 29.6 | 40.0438 | -10.4438 |  | 15-03-2026 14:30 | 0 | 0 | 1230.9 | 0 | 38.6494 | -38.6494 | 231.8965 | 28 | 38.0967 | -10.0967 |  | 15-03-2026 14:30 | 0 | 420.5221 | -420.5221 | 2523.1325 | 309.8 | 414.5086 | -104.7086
15-03-2026 14:20 | 949 | 48.79 | 314.28 | 319.511 | 1713.4 | 53.2518 | 56.5096 | -3.2578 | 339.0577 | 53 | 55.7015 | -2.7015 | 0.98363 | 15-03-2026 14:20 | 318.065 | 323.566 | 1729.2 | 53.9277 | 56.5096 | -2.5819 | 339.0577 | 55.7 | 55.7015 | -0.001521 | 0.983 | 15-03-2026 14:20 | 312.585 | 321.222 | 1697.2 | 53.537 | 56.5096 | -2.9726 | 339.0577 | 51.8 | 55.7015 | -3.9015 | 0.97311 | 15-03-2026 14:20 | 315.526 | 321.048 | 1719.8 | 53.508 | 56.5096 | -3.0016 | 339.0577 | 53.2 | 55.7015 | -2.5015 | 0.9828 | 15-03-2026 14:20 | 236.998 | 240.803 | 1282 | 40.1338 | 41.859 | -1.7251 | 251.1538 | 39.9 | 41.2604 | -1.3604 | 0.9842 | 15-03-2026 14:20 | 232.561 | 237.069 | 1271 | 39.5115 | 41.859 | -2.3475 | 251.1538 | 39.2 | 41.2604 | -2.0604 | 0.98098 | 15-03-2026 14:20 | 232.651 | 236.997 | 1268.1 | 39.4995 | 41.859 | -2.3595 | 251.1538 | 39.2 | 41.2604 | -2.0604 | 0.98166 | 15-03-2026 14:20 | 232.202 | 239.17 | 1271.9 | 39.8617 | 41.859 | -1.9973 | 251.1538 | 39.2 | 41.2604 | -2.0604 | 0.97087 | 15-03-2026 14:20 | 219.335 | 222.743 | 1202.9 | 37.1238 | 39.8236 | -2.6998 | 238.9417 | 37 | 39.2541 | -2.2541 | 0.9847 | 15-03-2026 14:20 | 410.3548 | 433.2979 | -22.9431 | 2599.7876 | 408.2 | 427.1018 | -18.9018
15-03-2026 14:10 | 961 | 48.79 | 320.006 | 325.474 | 1660.4 | 54.2457 | 57.2242 | -2.9785 | 343.345 | 54.7 | 56.4059 | -1.7059 | 0.9832 | 15-03-2026 14:10 | 324.455 | 330.066 | 1673.5 | 55.011 | 57.2242 | -2.2132 | 343.345 | 52.5 | 56.4059 | -3.9059 | 0.983 | 15-03-2026 14:10 | 317.137 | 326.129 | 1645.4 | 54.3548 | 57.2242 | -2.8693 | 343.345 | 53.6 | 56.4059 | -2.8059 | 0.97243 | 15-03-2026 14:10 | 321.663 | 327.226 | 1666.6 | 54.5377 | 57.2242 | -2.6865 | 343.345 | 53.6 | 56.4059 | -2.8059 | 0.983 | 15-03-2026 14:10 | 239.903 | 243.775 | 1242.1 | 40.6292 | 42.3883 | -1.7591 | 254.3296 | 40.1 | 41.7821 | -1.6821 | 0.98412 | 15-03-2026 14:10 | 236.907 | 241.369 | 1231.8 | 40.2282 | 42.3883 | -2.1601 | 254.3296 | 39.5 | 41.7821 | -2.2821 | 0.98151 | 15-03-2026 14:10 | 235.774 | 240.64 | 1228.9 | 40.1067 | 42.3883 | -2.2816 | 254.3296 | 39.9 | 41.7821 | -1.8821 | 0.97978 | 15-03-2026 14:10 | 236.188 | 243.314 | 1232.7 | 40.5523 | 42.3883 | -1.8359 | 254.3296 | 39.9 | 41.7821 | -1.8821 | 0.97071 | 15-03-2026 14:10 | 224.074 | 227.534 | 1165.9 | 37.9223 | 40.3272 | -2.4049 | 241.9631 | 37.8 | 39.7505 | -1.9505 | 0.98479 | 15-03-2026 14:10 | 417.5878 | 438.7769 | -21.1891 | 2632.6616 | 411.6 | 432.5024 | -20.9024
15-03-2026 14:00 | 974 | 48.79 | 324.921 | 330.507 | 1605.7 | 55.0845 | 57.9983 | -2.9138 | 347.9896 | 53.4 | 57.1689 | -3.7689 | 0.9831 | 15-03-2026 14:00 | 329.221 | 334.915 | 1621 | 55.8192 | 57.9983 | -2.1791 | 347.9896 | 54.3 | 57.1689 | -2.8689 | 0.983 | 15-03-2026 14:00 | 322.565 | 331.783 | 1591.8 | 55.2972 | 57.9983 | -2.7011 | 347.9896 | 54.5 | 57.1689 | -2.6689 | 0.97222 | 15-03-2026 14:00 | 325.993 | 331.664 | 1613 | 55.2773 | 57.9983 | -2.7209 | 347.9896 | 55.9 | 57.1689 | -1.2689 | 0.9829 | 15-03-2026 14:00 | 244.09 | 247.933 | 1202 | 41.3222 | 42.9617 | -1.6395 | 257.7701 | 41.2 | 42.3473 | -1.1473 | 0.9845 | 15-03-2026 14:00 | 241.003 | 245.52 | 1192.3 | 40.92 | 42.9617 | -2.0417 | 257.7701 | 40.8 | 42.3473 | -1.5473 | 0.9816 | 15-03-2026 14:00 | 240.285 | 245.407 | 1189 | 40.9012 | 42.9617 | -2.0605 | 257.7701 | 40.1 | 42.3473 | -2.2473 | 0.97913 | 15-03-2026 14:00 | 241.673 | 248.718 | 1192.8 | 41.453 | 42.9617 | -1.5087 | 257.7701 | 40.4 | 42.3473 | -1.9473 | 0.97167 | 15-03-2026 14:00 | 228.991 | 232.573 | 1128.1 | 38.7622 | 40.8727 | -2.1106 | 245.2363 | 38.2 | 40.2882 | -2.0882 | 0.9846 | 15-03-2026 14:00 | 424.8367 | 444.7125 | -19.8759 | 2668.2752 | 418.8 | 438.3531 | -19.5531
15-03-2026 13:50 | 986 | 48.5 | 329.926 | 335.556 | 1552.3 | 55.926 | 58.7778 | -2.8518 | 352.667 | 55.1 | 57.9373 | -2.8373 | 0.98322 | 15-03-2026 13:50 | 334.833 | 340.682 | 1566.7 | 56.7803 | 58.7778 | -1.9975 | 352.667 | 55.8 | 57.9373 | -2.1373 | 0.98283 | 15-03-2026 13:50 | 326.935 | 336.409 | 1537.3 | 56.0682 | 58.7778 | -2.7097 | 352.667 | 53.8 | 57.9373 | -4.1373 | 0.97184 | 15-03-2026 13:50 | 331.37 | 337.101 | 1557.1 | 56.1835 | 58.7778 | -2.5943 | 352.667 | 53.7 | 57.9373 | -4.2373 | 0.983 | 15-03-2026 13:50 | 247.104 | 251.089 | 1160.8 | 41.8482 | 43.5391 | -1.691 | 261.2348 | 40.7 | 42.9165 | -2.2165 | 0.98413 | 15-03-2026 13:50 | 244.327 | 248.799 | 1151.5 | 41.4665 | 43.5391 | -2.0726 | 261.2348 | 40.8 | 42.9165 | -2.1165 | 0.98203 | 15-03-2026 13:50 | 243.199 | 247.801 | 1148.9 | 41.3002 | 43.5391 | -2.239 | 261.2348 | 40.7 | 42.9165 | -2.2165 | 0.98143 | 15-03-2026 13:50 | 244.124 | 251.302 | 1152.4 | 41.8837 | 43.5391 | -1.6555 | 261.2348 | 40.8 | 42.9165 | -2.1165 | 0.97144 | 15-03-2026 13:50 | 231.087 | 234.654 | 1089.9 | 39.109 | 41.4221 | -2.3131 | 248.5326 | 38.6 | 40.8298 | -2.2298 | 0.9848 | 15-03-2026 13:50 | 430.5655 | 450.69 | -20.1245 | 2704.1399 | 420 | 444.2451 | -24.2451
15-03-2026 13:40 | 983 | 48.79 | 326.568 | 332.216 | 1497.2 | 55.3693 | 58.5342 | -3.1649 | 351.2051 | 55.4 | 57.6971 | -2.2971 | 0.983 | 15-03-2026 13:40 | 330.569 | 336.389 | 1510.9 | 56.0648 | 58.5342 | -2.4694 | 351.2051 | 56.3 | 57.6971 | -1.3971 | 0.9827 | 15-03-2026 13:40 | 326.088 | 335.988 | 1483.5 | 55.998 | 58.5342 | -2.5362 | 351.2051 | 54.4 | 57.6971 | -3.2971 | 0.97053 | 15-03-2026 13:40 | 327.387 | 333.151 | 1503.4 | 55.5252 | 58.5342 | -3.009 | 351.2051 | 55.2 | 57.6971 | -2.4971 | 0.9827 | 15-03-2026 13:40 | 247.162 | 251.113 | 1120.1 | 41.8522 | 43.3587 | -1.5065 | 260.1519 | 41.7 | 42.7386 | -1.0386 | 0.98427 | 15-03-2026 13:40 | 241.401 | 245.921 | 1110.7 | 40.9868 | 43.3587 | -2.3718 | 260.1519 | 40.4 | 42.7386 | -2.3386 | 0.98162 | 15-03-2026 13:40 | 242.845 | 247.747 | 1108.2 | 41.2912 | 43.3587 | -2.0675 | 260.1519 | 40.3 | 42.7386 | -2.4386 | 0.98021 | 15-03-2026 13:40 | 242.968 | 250.078 | 1111.6 | 41.6797 | 43.3587 | -1.679 | 260.1519 | 40.4 | 42.7386 | -2.3386 | 0.97157 | 15-03-2026 13:40 | 228.588 | 232.187 | 1051.3 | 38.6978 | 41.2504 | -2.5526 | 247.5024 | 38.2 | 40.6605 | -2.4605 | 0.9845 | 15-03-2026 13:40 | 427.465 | 448.8218 | -21.3568 | 2692.9307 | 422.3 | 442.4036 | -20.1036
15-03-2026 13:30 | 1017 | 48.79 | 336.196 | 342.045 | 1441.8 | 57.0075 | 60.5588 | -3.5513 | 363.3526 | 56.2 | 59.6928 | -3.4928 | 0.9829 | 15-03-2026 13:30 | 341.301 | 347.092 | 1454.6 | 57.8487 | 60.5588 | -2.7101 | 363.3526 | 57 | 59.6928 | -2.6928 | 0.98332 | 15-03-2026 13:30 | 333.472 | 343.42 | 1429.1 | 57.2367 | 60.5588 | -3.3221 | 363.3526 | 55.7 | 59.6928 | -3.9928 | 0.97103 | 15-03-2026 13:30 | 338.041 | 344.076 | 1448.2 | 57.346 | 60.5588 | -3.2128 | 363.3526 | 56.4 | 59.6928 | -3.2928 | 0.98246 | 15-03-2026 13:30 | 251.942 | 256.013 | 1078.4 | 42.6688 | 44.8583 | -2.1895 | 269.1501 | 41.7 | 44.2169 | -2.5169 | 0.9841 | 15-03-2026 13:30 | 248.806 | 253.633 | 1070.3 | 42.2722 | 44.8583 | -2.5862 | 269.1501 | 41.1 | 44.2169 | -3.1169 | 0.98097 | 15-03-2026 13:30 | 247.911 | 252.992 | 1067.9 | 42.1653 | 44.8583 | -2.693 | 269.1501 | 41.1 | 44.2169 | -3.1169 | 0.97992 | 15-03-2026 13:30 | 248.826 | 256.132 | 1071.2 | 42.6887 | 44.8583 | -2.1697 | 269.1501 | 41.2 | 44.2169 | -3.0169 | 0.97148 | 15-03-2026 13:30 | 234.951 | 238.72 | 1013.1 | 39.7867 | 42.6772 | -2.8905 | 256.063 | 39.4 | 42.0669 | -2.6669 | 0.98421 | 15-03-2026 13:30 | 439.0205 | 464.3456 | -25.3251 | 2786.0738 | 429.8 | 457.7055 | -27.9055
15-03-2026 13:20 | 1015 | 49.08 | 331.778 | 337.653 | 1385.6 | 56.2755 | 60.3728 | -4.0973 | 362.2365 | 53.7 | 59.5094 | -5.8094 | 0.9826 | 15-03-2026 13:20 | 337.283 | 343.291 | 1397.6 | 57.2152 | 60.3728 | -3.1576 | 362.2365 | 54.4 | 59.5094 | -5.1094 | 0.9825 | 15-03-2026 13:20 | 329.147 | 339.17 | 1373.4 | 56.5283 | 60.3728 | -3.8444 | 362.2365 | 53.8 | 59.5094 | -5.7094 | 0.97045 | 15-03-2026 13:20 | 334.125 | 340.146 | 1391.8 | 56.691 | 60.3728 | -3.6818 | 362.2365 | 55.5 | 59.5094 | -4.0094 | 0.9823 | 15-03-2026 13:20 | 249.612 | 253.697 | 1036.7 | 42.2828 | 44.7206 | -2.4377 | 268.3234 | 41.4 | 44.0811 | -2.6811 | 0.9839 | 15-03-2026 13:20 | 245.864 | 250.751 | 1029.2 | 41.7918 | 44.7206 | -2.9287 | 268.3234 | 41 | 44.0811 | -3.0811 | 0.98051 | 15-03-2026 13:20 | 245.742 | 250.754 | 1026.8 | 41.7923 | 44.7206 | -2.9282 | 268.3234 | 40.9 | 44.0811 | -3.1811 | 0.98001 | 15-03-2026 13:20 | 246.188 | 253.464 | 1030 | 42.244 | 44.7206 | -2.4766 | 268.3234 | 41 | 44.0811 | -3.0811 | 0.97129 | 15-03-2026 13:20 | 232.621 | 236.379 | 973.7 | 39.3965 | 42.5461 | -3.1496 | 255.2765 | 38.3 | 41.9377 | -3.6377 | 0.9841 | 15-03-2026 13:20 | 434.2175 | 462.9194 | -28.7019 | 2777.5161 | 420 | 456.2996 | -36.2996
15-03-2026 13:10 | 1010 | 49.08 | 332.481 | 338.369 | 1331.9 | 56.3948 | 60.0754 | -3.6805 | 360.4521 | 55.3 | 59.2163 | -3.9163 | 0.9826 | 15-03-2026 13:10 | 337.02 | 343.109 | 1343.2 | 57.1848 | 60.0754 | -2.8905 | 360.4521 | 57.6 | 59.2163 | -1.6163 | 0.98225 | 15-03-2026 13:10 | 328.114 | 337.253 | 1319.6 | 56.2088 | 60.0754 | -3.8665 | 360.4521 | 55 | 59.2163 | -4.2163 | 0.9729 | 15-03-2026 13:10 | 333.568 | 339.579 | 1336.3 | 56.5965 | 60.0754 | -3.4789 | 360.4521 | 54.8 | 59.2163 | -4.4163 | 0.9823 | 15-03-2026 13:10 | 248.945 | 253.044 | 995.3 | 42.174 | 44.5003 | -2.3263 | 267.0016 | 41.1 | 43.8639 | -2.7639 | 0.9838 | 15-03-2026 13:10 | 246.224 | 250.876 | 988.2 | 41.8127 | 44.5003 | -2.6876 | 267.0016 | 41.1 | 43.8639 | -2.7639 | 0.98146 | 15-03-2026 13:10 | 245.141 | 249.985 | 985.9 | 41.6642 | 44.5003 | -2.8361 | 267.0016 | 41 | 43.8639 | -2.8639 | 0.98062 | 15-03-2026 13:10 | 245.715 | 252.927 | 989 | 42.1545 | 44.5003 | -2.3458 | 267.0016 | 41.3 | 43.8639 | -2.5639 | 0.97149 | 15-03-2026 13:10 | 232.518 | 236.251 | 935.4 | 39.3752 | 42.3365 | -2.9613 | 254.0189 | 39 | 41.7311 | -2.7311 | 0.9842 | 15-03-2026 13:10 | 433.5655 | 460.639 | -27.0735 | 2763.8338 | 426.2 | 454.0518 | -27.8518
15-03-2026 13:00 | 1013 | 48.79 | 332.54 | 338.394 | 1276.6 | 56.399 | 60.3206 | -3.9216 | 361.9235 | 56.3 | 59.458 | -3.158 | 0.9827 | 15-03-2026 13:00 | 337.52 | 343.567 | 1285.6 | 57.2612 | 60.3206 | -3.0594 | 361.9235 | 54.8 | 59.458 | -4.658 | 0.9824 | 15-03-2026 13:00 | 329.03 | 338.592 | 1264.6 | 56.432 | 60.3206 | -3.8886 | 361.9235 | 55 | 59.458 | -4.458 | 0.97176 | 15-03-2026 13:00 | 334.639 | 340.634 | 1281.5 | 56.7723 | 60.3206 | -3.5482 | 361.9235 | 56.7 | 59.458 | -2.758 | 0.9824 | 15-03-2026 13:00 | 249.83 | 253.866 | 954.2 | 42.311 | 44.6819 | -2.3709 | 268.0915 | 41.9 | 44.043 | -2.143 | 0.9841 | 15-03-2026 13:00 | 247.646 | 252.201 | 947.1 | 42.0335 | 44.6819 | -2.6484 | 268.0915 | 40.8 | 44.043 | -3.243 | 0.98194 | 15-03-2026 13:00 | 246.919 | 251.752 | 944.9 | 41.9587 | 44.6819 | -2.7232 | 268.0915 | 40.7 | 44.043 | -3.343 | 0.9808 | 15-03-2026 13:00 | 247.626 | 255.194 | 947.7 | 42.5323 | 44.6819 | -2.1496 | 268.0915 | 40.8 | 44.043 | -3.243 | 0.97034 | 15-03-2026 13:00 | 234.657 | 238.351 | 896.4 | 39.7252 | 42.5093 | -2.7841 | 255.0558 | 39 | 41.9014 | -2.9014 | 0.9845 | 15-03-2026 13:00 | 435.4252 | 462.5193 | -27.0941 | 2775.1158 | 426 | 455.9053 | -29.9053
15-03-2026 12:50 | 1002 | 49.08 | 329.685 | 335.529 | 1220.3 | 55.9215 | 59.5995 | -3.678 | 357.5971 | 54.2 | 58.7472 | -4.5472 | 0.98258 | 15-03-2026 12:50 | 334.296 | 341.61 | 1230.8 | 56.935 | 59.5995 | -2.6645 | 357.5971 | 55.8 | 58.7472 | -2.9472 | 0.97859 | 15-03-2026 12:50 | 328.742 | 338.451 | 1209.6 | 56.4085 | 59.5995 | -3.191 | 357.5971 | 54.6 | 58.7472 | -4.1472 | 0.97131 | 15-03-2026 12:50 | 333.199 | 339.168 | 1224.8 | 56.528 | 59.5995 | -3.0715 | 357.5971 | 54.5 | 58.7472 | -4.2472 | 0.9824 | 15-03-2026 12:50 | 249.812 | 253.874 | 912.3 | 42.3123 | 44.1478 | -1.8355 | 264.8867 | 41.4 | 43.5165 | -2.1165 | 0.984 | 15-03-2026 12:50 | 246.946 | 251.561 | 906.3 | 41.9268 | 44.1478 | -2.221 | 264.8867 | 40.9 | 43.5165 | -2.6165 | 0.98165 | 15-03-2026 12:50 | 246.029 | 251.197 | 904.2 | 41.8662 | 44.1478 | -2.2816 | 264.8867 | 40.9 | 43.5165 | -2.6165 | 0.97943 | 15-03-2026 12:50 | 246.572 | 253.979 | 906.9 | 42.3298 | 44.1478 | -1.818 | 264.8867 | 41.6 | 43.5165 | -1.9165 | 0.97084 | 15-03-2026 12:50 | 234.147 | 237.745 | 857.4 | 39.6242 | 42.0012 | -2.377 | 252.0069 | 38.9 | 41.4005 | -2.5005 | 0.98487 | 15-03-2026 12:50 | 433.8523 | 456.9903 | -23.138 | 2741.942 | 422.8 | 450.4554 | -27.6554
15-03-2026 12:40 | 1005 | 48.79 | 331.7 | 337.539 | 1166.1 | 56.2565 | 59.8442 | -3.5877 | 359.0653 | 55 | 58.9884 | -3.9884 | 0.9827 | 15-03-2026 12:40 | 336.98 | 342.982 | 1175 | 57.1637 | 59.8442 | -2.6805 | 359.0653 | 112.3 | 58.9884 | 53.3116 | 0.9825 | 15-03-2026 12:40 | 329.393 | 339.172 | 1155 | 56.5287 | 59.8442 | -3.3155 | 359.0653 | 55.3 | 58.9884 | -3.6884 | 0.97117 | 15-03-2026 12:40 | 334.062 | 340.012 | 1170.3 | 56.6687 | 59.8442 | -3.1755 | 359.0653 | 56 | 58.9884 | -2.9884 | 0.9825 | 15-03-2026 12:40 | 250.248 | 254.24 | 870.9 | 42.3733 | 44.329 | -1.9557 | 265.9743 | 42 | 43.6951 | -1.6951 | 0.9843 | 15-03-2026 12:40 | 246.651 | 251.232 | 865.4 | 41.872 | 44.329 | -2.457 | 265.9743 | 41.9 | 43.6951 | -1.7951 | 0.98177 | 15-03-2026 12:40 | 247.586 | 252.915 | 863.3 | 42.1525 | 44.329 | -2.1765 | 265.9743 | 41.6 | 43.6951 | -2.0951 | 0.97893 | 15-03-2026 12:40 | 248.331 | 255.551 | 865.3 | 42.5918 | 44.329 | -1.7372 | 265.9743 | 41.1 | 43.6951 | -2.5951 | 0.97175 | 15-03-2026 12:40 | 234.108 | 237.818 | 818.5 | 39.6363 | 42.1736 | -2.5373 | 253.0416 | 38.8 | 41.5705 | -2.7705 | 0.9844 | 15-03-2026 12:40 | 435.2435 | 458.8666 | -23.6231 | 2753.1997 | 484 | 452.3048 | 31.6952
15-03-2026 12:30 | 990 | 49.08 | 329.79 | 335.493 | 1111.1 | 55.9155 | 58.8857 | -2.9702 | 353.3145 | 55.1 | 58.0437 | -2.9437 | 0.983 |  |  |  |  | 0 | 58.8857 | -58.8857 | 353.3145 | 0 | 58.0437 | -58.0437 |  | 15-03-2026 12:30 | 328.329 | 337.942 | 1099.7 | 56.3237 | 58.8857 | -2.5621 | 353.3145 | 54.2 | 58.0437 | -3.8437 | 0.97155 | 15-03-2026 12:30 | 330.934 | 336.76 | 1114.3 | 56.1267 | 58.8857 | -2.7591 | 353.3145 | 54.8 | 58.0437 | -3.2437 | 0.9827 | 15-03-2026 12:30 | 249.975 | 253.936 | 828.9 | 42.3227 | 43.6191 | -1.2964 | 261.7144 | 41.2 | 42.9953 | -1.7953 | 0.9844 | 15-03-2026 12:30 | 244.908 | 249.519 | 823.5 | 41.5865 | 43.6191 | -2.0326 | 261.7144 | 40.6 | 42.9953 | -2.3953 | 0.98152 | 15-03-2026 12:30 | 246.752 | 251.914 | 821.7 | 41.9857 | 43.6191 | -1.6334 | 261.7144 | 41 | 42.9953 | -1.9953 | 0.97951 | 15-03-2026 12:30 | 247.533 | 255.069 | 824.2 | 42.5115 | 43.6191 | -1.1076 | 261.7144 | 41.1 | 42.9953 | -1.8953 | 0.97046 | 15-03-2026 12:30 | 232.9 | 236.567 | 779.7 | 39.4278 | 41.4981 | -2.0703 | 248.9889 | 38.8 | 40.9047 | -2.1047 | 0.9845 | 15-03-2026 12:30 | 376.2 | 451.5174 | -75.3174 | 2709.1044 | 366.8 | 445.0607 | -78.2607
15-03-2026 12:20 | 987 | 48.79 | 328.844 | 334.497 | 1056 | 55.7495 | 58.7724 | -3.0229 | 352.6342 | 55.3 | 57.9319 | -2.6319 | 0.9831 | 15-03-2026 12:20 | 336.079 | 342.235 | 1062.7 | 57.0392 | 58.7724 | -1.7332 | 352.6342 | 55.2 | 57.9319 | -2.7319 | 0.98201 | 15-03-2026 12:20 | 327.036 | 336.171 | 1045.5 | 56.0285 | 58.7724 | -2.7439 | 352.6342 | 54.8 | 57.9319 | -3.1319 | 0.97283 | 15-03-2026 12:20 | 331.878 | 337.721 | 1059.5 | 56.2868 | 58.7724 | -2.4855 | 352.6342 | 55.5 | 57.9319 | -2.4319 | 0.9827 | 15-03-2026 12:20 | 247.799 | 251.726 | 787.7 | 41.9543 | 43.5351 | -1.5808 | 261.2106 | 41.5 | 42.9125 | -1.4125 | 0.9844 | 15-03-2026 12:20 | 245.729 | 250.357 | 782.9 | 41.7262 | 43.5351 | -1.8089 | 261.2106 | 40.4 | 42.9125 | -2.5125 | 0.98151 | 15-03-2026 12:20 | 244.469 | 249.386 | 780.7 | 41.5643 | 43.5351 | -1.9708 | 261.2106 | 40.4 | 42.9125 | -2.5125 | 0.98028 | 15-03-2026 12:20 | 244.964 | 252.281 | 783.1 | 42.0468 | 43.5351 | -1.4883 | 261.2106 | 41.2 | 42.9125 | -1.7125 | 0.971 | 15-03-2026 12:20 | 232.152 | 235.817 | 740.9 | 39.3028 | 41.4182 | -2.1154 | 248.5095 | 39 | 40.826 | -1.826 | 0.98446 | 15-03-2026 12:20 | 431.6985 | 450.6481 | -18.9496 | 2703.8887 | 423.3 | 444.2038 | -20.9038
15-03-2026 12:10 | 982 | 48.79 | 329.91 | 335.615 | 1000.7 | 55.9358 | 58.4746 | -2.5388 | 350.8479 | 54.6 | 57.6385 | -3.0385 | 0.983 | 15-03-2026 12:10 | 332.832 | 338.588 | 1007.5 | 56.4313 | 58.4746 | -2.0433 | 350.8479 | 55.2 | 57.6385 | -2.4385 | 0.983 | 15-03-2026 12:10 | 327.556 | 336.58 | 990.7 | 56.0967 | 58.4746 | -2.378 | 350.8479 | 54.3 | 57.6385 | -3.3385 | 0.97319 | 15-03-2026 12:10 | 330.603 | 336.389 | 1004 | 56.0648 | 58.4746 | -2.4098 | 350.8479 | 54.8 | 57.6385 | -2.8385 | 0.9828 | 15-03-2026 12:10 | 247.613 | 251.511 | 746.2 | 41.9185 | 43.3145 | -1.396 | 259.8873 | 41 | 42.6952 | -1.6952 | 0.9845 | 15-03-2026 12:10 | 244.14 | 248.664 | 742.5 | 41.444 | 43.3145 | -1.8705 | 259.8873 | 40.5 | 42.6952 | -2.1952 | 0.98181 | 15-03-2026 12:10 | 243.767 | 248.519 | 740.3 | 41.4198 | 43.3145 | -1.8947 | 259.8873 | 40.5 | 42.6952 | -2.1952 | 0.98088 | 15-03-2026 12:10 | 244.349 | 251.487 | 741.9 | 41.9145 | 43.3145 | -1.4 | 259.8873 | 40.5 | 42.6952 | -2.1952 | 0.97162 | 15-03-2026 12:10 | 230.876 | 234.415 | 701.9 | 39.0692 | 41.2084 | -2.1393 | 247.2506 | 37.7 | 40.6191 | -2.9191 | 0.9849 | 15-03-2026 12:10 | 430.2947 | 448.3652 | -18.0705 | 2690.1912 | 419.1 | 441.9536 | -22.8536
15-03-2026 12:00 | 969 | 48.5 | 327.211 | 332.768 | 946.1 | 55.4613 | 57.7644 | -2.3031 | 346.5865 | 54.2 | 56.9384 | -2.7384 | 0.9833 | 15-03-2026 12:00 | 329.076 | 336.119 | 952.3 | 56.0198 | 57.7644 | -1.7446 | 346.5865 | 54.8 | 56.9384 | -2.1384 | 0.97905 | 15-03-2026 12:00 | 324.303 | 332.923 | 936.4 | 55.4872 | 57.7644 | -2.2773 | 346.5865 | 53.2 | 56.9384 | -3.7384 | 0.97411 | 15-03-2026 12:00 | 328.023 | 333.685 | 949.2 | 55.6142 | 57.7644 | -2.1503 | 346.5865 | 54.4 | 56.9384 | -2.5384 | 0.98303 | 15-03-2026 12:00 | 244.846 | 248.676 | 705.2 | 41.446 | 42.7885 | -1.3425 | 256.7308 | 40.7 | 42.1766 | -1.4766 | 0.9846 | 15-03-2026 12:00 | 242.048 | 246.835 | 702 | 41.1392 | 42.7885 | -1.6493 | 256.7308 | 40.3 | 42.1766 | -1.8766 | 0.98061 | 15-03-2026 12:00 | 241.087 | 245.726 | 699.8 | 40.9543 | 42.7885 | -1.8341 | 256.7308 | 40.1 | 42.1766 | -2.0766 | 0.98112 | 15-03-2026 12:00 | 241.757 | 248.605 | 701.4 | 41.4342 | 42.7885 | -1.3543 | 256.7308 | 39.6 | 42.1766 | -2.5766 | 0.97245 | 15-03-2026 12:00 | 229.082 | 232.688 | 664.2 | 38.7813 | 40.7079 | -1.9266 | 244.2475 | 38 | 40.1258 | -2.1258 | 0.9845 | 15-03-2026 12:00 | 426.3375 | 442.9195 | -16.582 | 2657.5168 | 415.3 | 436.5857 | -21.2857
15-03-2026 11:50 | 950 | 48.79 | 321.291 | 326.737 | 891.9 | 54.4562 | 56.5692 | -2.113 | 339.4149 | 52.9 | 55.7602 | -2.8602 | 0.98333 | 15-03-2026 11:50 | 325.08 | 330.585 | 897.5 | 55.0975 | 56.5692 | -1.4717 | 339.4149 | 55.8 | 55.7602 | 0.039784 | 0.98335 | 15-03-2026 11:50 | 318.955 | 327.405 | 883.2 | 54.5675 | 56.5692 | -2.0017 | 339.4149 | 53.3 | 55.7602 | -2.4602 | 0.97419 | 15-03-2026 11:50 | 322.931 | 328.473 | 894.8 | 54.7455 | 56.5692 | -1.8237 | 339.4149 | 53.3 | 55.7602 | -2.4602 | 0.98313 | 15-03-2026 11:50 | 241.388 | 245.139 | 664.5 | 40.8565 | 41.9031 | -1.0466 | 251.4185 | 40.4 | 41.3039 | -0.90386 | 0.9847 | 15-03-2026 11:50 | 238.71 | 242.993 | 661.7 | 40.4988 | 41.9031 | -1.4042 | 251.4185 | 39.9 | 41.3039 | -1.4039 | 0.98237 | 15-03-2026 11:50 | 238.131 | 242.605 | 659.7 | 40.4342 | 41.9031 | -1.4689 | 251.4185 | 39.8 | 41.3039 | -1.5039 | 0.98156 | 15-03-2026 11:50 | 238.815 | 245.742 | 661.8 | 40.957 | 41.9031 | -0.94608 | 251.4185 | 39.9 | 41.3039 | -1.4039 | 0.97181 | 15-03-2026 11:50 | 225.437 | 228.94 | 626.2 | 38.1567 | 39.8656 | -1.7089 | 239.1935 | 37.7 | 39.2955 | -1.5955 | 0.9847 | 15-03-2026 11:50 | 419.7698 | 433.7545 | -13.9847 | 2602.5271 | 413 | 427.5518 | -14.5518
15-03-2026 11:40 | 943 | 49.08 | 320.818 | 326.134 | 839 | 54.3557 | 56.0902 | -1.7345 | 336.5409 | 53.6 | 55.2881 | -1.6881 | 0.9837 | 15-03-2026 11:40 | 323.237 | 329.427 | 841.7 | 54.9045 | 56.0902 | -1.1857 | 336.5409 | 51.7 | 55.2881 | -3.5881 | 0.98121 | 15-03-2026 11:40 | 318.412 | 327.348 | 829.9 | 54.558 | 56.0902 | -1.5322 | 336.5409 | 52.4 | 55.2881 | -2.8881 | 0.9727 | 15-03-2026 11:40 | 321.972 | 327.44 | 841.5 | 54.5733 | 56.0902 | -1.5168 | 336.5409 | 53.6 | 55.2881 | -1.6881 | 0.9833 | 15-03-2026 11:40 | 240.719 | 244.41 | 624.1 | 40.735 | 41.5483 | -0.81327 | 249.2896 | 39.5 | 40.9541 | -1.4541 | 0.9849 | 15-03-2026 11:40 | 238.543 | 242.523 | 621.8 | 40.4205 | 41.5483 | -1.1278 | 249.2896 | 39.1 | 40.9541 | -1.8541 | 0.98359 | 15-03-2026 11:40 | 237.855 | 242.352 | 619.9 | 40.392 | 41.5483 | -1.1563 | 249.2896 | 39 | 40.9541 | -1.9541 | 0.98144 | 15-03-2026 11:40 | 238.52 | 245.34 | 621.9 | 40.89 | 41.5483 | -0.65827 | 249.2896 | 39.1 | 40.9541 | -1.8541 | 0.9722 | 15-03-2026 11:40 | 225.305 | 228.759 | 588.5 | 38.1265 | 39.528 | -1.4015 | 237.1682 | 36.9 | 38.9628 | -2.0628 | 0.9849 | 15-03-2026 11:40 | 418.9555 | 430.0817 | -11.1262 | 2580.4903 | 404.9 | 423.9316 | -19.0316
15-03-2026 11:30 | 919 | 48.79 | 313.414 | 318.642 | 785.4 | 53.107 | 54.7232 | -1.6162 | 328.3393 | 51.4 | 53.9407 | -2.5407 | 0.98359 | 15-03-2026 11:30 | 316.382 | 321.723 | 790 | 53.6205 | 54.7232 | -1.1027 | 328.3393 | 52.7 | 53.9407 | -1.2407 | 0.9834 | 15-03-2026 11:30 | 310.949 | 319.289 | 777.5 | 53.2148 | 54.7232 | -1.5084 | 328.3393 | 51.7 | 53.9407 | -2.2407 | 0.97388 | 15-03-2026 11:30 | 314.11 | 319.38 | 787.9 | 53.23 | 54.7232 | -1.4932 | 328.3393 | 51.7 | 53.9407 | -2.2407 | 0.9835 | 15-03-2026 11:30 | 234.934 | 238.512 | 584.6 | 39.752 | 40.5357 | -0.78371 | 243.2143 | 39.1 | 39.9561 | -0.85605 | 0.985 | 15-03-2026 11:30 | 232.278 | 236.337 | 582.7 | 39.3895 | 40.5357 | -1.1462 | 243.2143 | 38.7 | 39.9561 | -1.2561 | 0.98283 | 15-03-2026 11:30 | 232.022 | 235.934 | 580.9 | 39.3223 | 40.5357 | -1.2134 | 243.2143 | 38.7 | 39.9561 | -1.2561 | 0.98342 | 15-03-2026 11:30 | 232.435 | 238.85 | 582.8 | 39.8083 | 40.5357 | -0.72738 | 243.2143 | 38.8 | 39.9561 | -1.1561 | 0.97314 | 15-03-2026 11:30 | 219.545 | 222.82 | 551.6 | 37.1367 | 38.5647 | -1.428 | 231.3883 | 36.6 | 38.0132 | -1.4132 | 0.9853 | 15-03-2026 11:30 | 408.5812 | 419.6004 | -11.0193 | 2517.6025 | 399.4 | 413.6001 | -14.2001
15-03-2026 11:20 | 905 | 48.79 | 310.557 | 315.567 | 734 | 52.5945 | 53.8896 | -1.2951 | 323.3374 | 52.1 | 53.1189 | -1.0189 | 0.98412 | 15-03-2026 11:20 | 312.704 | 317.918 | 737.3 | 52.9863 | 53.8896 | -0.90323 | 323.3374 | 51.7 | 53.1189 | -1.4189 | 0.9836 | 15-03-2026 11:20 | 307.848 | 315.906 | 725.8 | 52.651 | 53.8896 | -1.2386 | 323.3374 | 50.8 | 53.1189 | -2.3189 | 0.97449 | 15-03-2026 11:20 | 311.708 | 316.958 | 736.2 | 52.8263 | 53.8896 | -1.0632 | 323.3374 | 51.5 | 53.1189 | -1.6189 | 0.98344 | 15-03-2026 11:20 | 232.532 | 236.049 | 545.5 | 39.3415 | 39.9182 | -0.5767 | 239.5092 | 37.8 | 39.3474 | -1.5474 | 0.9851 | 15-03-2026 11:20 | 230.519 | 234.159 | 544 | 39.0265 | 39.9182 | -0.8917 | 239.5092 | 37.5 | 39.3474 | -1.8474 | 0.98446 | 15-03-2026 11:20 | 229.997 | 234.325 | 542.2 | 39.0542 | 39.9182 | -0.86403 | 239.5092 | 37.9 | 39.3474 | -1.4474 | 0.98153 | 15-03-2026 11:20 | 230.571 | 237.416 | 544 | 39.5693 | 39.9182 | -0.34886 | 239.5092 | 38 | 39.3474 | -1.3474 | 0.97117 | 15-03-2026 11:20 | 217.822 | 221.072 | 515 | 36.8453 | 37.9772 | -1.1319 | 227.8633 | 35.9 | 37.4341 | -1.5341 | 0.9853 | 15-03-2026 11:20 | 404.895 | 413.2083 | -8.3133 | 2479.2495 | 393.2 | 407.2994 | -14.0994
15-03-2026 11:10 | 887 | 49.36 | 305.921 | 310.895 | 681.9 | 51.8158 | 52.7028 | -0.88695 | 316.2167 | 49.6 | 51.9491 | -2.3491 | 0.984 | 15-03-2026 11:10 | 308.632 | 313.714 | 685.6 | 52.2857 | 52.7028 | -0.41712 | 316.2167 | 50.9 | 51.9491 | -1.0491 | 0.9838 | 15-03-2026 11:10 | 302.585 | 310.674 | 675 | 51.779 | 52.7028 | -0.92378 | 316.2167 | 49.9 | 51.9491 | -2.0491 | 0.97396 | 15-03-2026 11:10 | 307.197 | 312.256 | 684.7 | 52.0427 | 52.7028 | -0.66012 | 316.2167 | 50.5 | 51.9491 | -1.4491 | 0.9838 | 15-03-2026 11:10 | 229.029 | 232.47 | 507.7 | 38.745 | 39.0391 | -0.2941 | 234.2346 | 38.3 | 38.4808 | -0.18084 | 0.9852 | 15-03-2026 11:10 | 227.133 | 230.75 | 506.5 | 38.4583 | 39.0391 | -0.58077 | 234.2346 | 37.9 | 38.4808 | -0.58084 | 0.98433 | 15-03-2026 11:10 | 226.746 | 230.754 | 504.3 | 38.459 | 39.0391 | -0.5801 | 234.2346 | 37.4 | 38.4808 | -1.0808 | 0.98263 | 15-03-2026 11:10 | 226.904 | 233.567 | 506 | 38.9278 | 39.0391 | -0.11127 | 234.2346 | 37.5 | 38.4808 | -0.98084 | 0.97147 | 15-03-2026 11:10 | 214.481 | 217.659 | 479.1 | 36.2765 | 37.1409 | -0.86437 | 222.8452 | 35.4 | 36.6098 | -1.2098 | 0.9854 | 15-03-2026 11:10 | 398.7898 | 404.1084 | -5.3186 | 2424.6504 | 387.4 | 398.3297 | -10.9297
15-03-2026 11:00 | 862 | 49.08 | 299.891 | 304.674 | 632.3 | 50.779 | 51.2722 | -0.49323 | 307.6334 | 49.8 | 50.539 | -0.73904 | 0.9843 | 15-03-2026 11:00 | 301.967 | 306.815 | 634.7 | 51.1358 | 51.2722 | -0.1364 | 307.6334 | 49.5 | 50.539 | -1.039 | 0.9842 | 15-03-2026 11:00 | 297.158 | 304.65 | 625.1 | 50.775 | 51.2722 | -0.49723 | 307.6334 | 49.4 | 50.539 | -1.139 | 0.97541 | 15-03-2026 11:00 | 300.772 | 305.663 | 634.2 | 50.9438 | 51.2722 | -0.3284 | 307.6334 | 49.9 | 50.539 | -0.63904 | 0.984 | 15-03-2026 11:00 | 224.397 | 227.676 | 469.4 | 37.946 | 37.9794 | -0.033432 | 227.8766 | 36.8 | 37.4363 | -0.63633 | 0.9856 | 15-03-2026 11:00 | 222.58 | 226.418 | 468.6 | 37.7363 | 37.9794 | -0.2431 | 227.8766 | 36.5 | 37.4363 | -0.93633 | 0.98305 | 15-03-2026 11:00 | 222.131 | 226.177 | 466.9 | 37.6962 | 37.9794 | -0.28327 | 227.8766 | 36.4 | 37.4363 | -1.0363 | 0.98211 | 15-03-2026 11:00 | 222.634 | 229.042 | 468.5 | 38.1737 | 37.9794 | 0.19423 | 227.8766 | 36.4 | 37.4363 | -1.0363 | 0.97202 | 15-03-2026 11:00 | 210.448 | 213.501 | 443.7 | 35.5835 | 36.1327 | -0.54923 | 216.7964 | 35 | 35.616 | -0.61603 | 0.9857 | 15-03-2026 11:00 | 390.7693 | 393.1394 | -2.3701 | 2358.8363 | 379.7 | 387.5175 | -7.8175
15-03-2026 10:50 | 841 | 48.79 | 294.028 | 298.597 | 582.5 | 49.7662 | 50.0786 | -0.31242 | 300.4715 | 48.1 | 49.3625 | -1.2625 | 0.9847 | 15-03-2026 10:50 | 296.061 | 301.177 | 585.2 | 50.1962 | 50.0786 | 0.11758 | 300.4715 | 49.2 | 49.3625 | -0.16246 | 0.98301 | 15-03-2026 10:50 | 291.082 | 298.613 | 575.7 | 49.7688 | 50.0786 | -0.30976 | 300.4715 | 47.7 | 49.3625 | -1.6625 | 0.97478 | 15-03-2026 10:50 | 295.377 | 300.027 | 584.3 | 50.0045 | 50.0786 | -0.074089 | 300.4715 | 48.4 | 49.3625 | -0.96246 | 0.9845 | 15-03-2026 10:50 | 220.014 | 223.138 | 432.6 | 37.1897 | 37.0953 | 0.094416 | 222.5715 | 36.6 | 36.5648 | 0.035211 | 0.986 | 15-03-2026 10:50 | 218.339 | 221.656 | 432.1 | 36.9427 | 37.0953 | -0.15258 | 222.5715 | 36.3 | 36.5648 | -0.26479 | 0.98504 | 15-03-2026 10:50 | 217.457 | 220.992 | 430.5 | 36.832 | 37.0953 | -0.26325 | 222.5715 | 36.2 | 36.5648 | -0.36479 | 0.984 | 15-03-2026 10:50 | 217.574 | 223.79 | 432.1 | 37.2983 | 37.0953 | 0.20308 | 222.5715 | 36.1 | 36.5648 | -0.46479 | 0.97222 | 15-03-2026 10:50 | 206.045 | 208.992 | 408.7 | 34.832 | 35.2915 | -0.45954 | 211.7492 | 34.2 | 34.7869 | -0.58687 | 0.9859 | 15-03-2026 10:50 | 382.8303 | 383.9869 | -1.1566 | 2303.9214 | 372.8 | 378.4959 | -5.6959
15-03-2026 10:40 | 810 | 48.5 | 284.512 | 288.874 | 534.4 | 48.1457 | 48.2861 | -0.14038 | 289.7163 | 48 | 47.5956 | 0.40444 | 0.9849 | 15-03-2026 10:40 | 286.788 | 291.244 | 536 | 48.5407 | 48.2861 | 0.25462 | 289.7163 | 46.4 | 47.5956 | -1.1956 | 0.9847 | 15-03-2026 10:40 | 282.42 | 289.584 | 528 | 48.264 | 48.2861 | -0.022051 | 289.7163 | 47 | 47.5956 | -0.59556 | 0.97526 | 15-03-2026 10:40 | 285.834 | 290.275 | 535.9 | 48.3792 | 48.2861 | 0.093116 | 289.7163 | 47.7 | 47.5956 | 0.10444 | 0.9847 | 15-03-2026 10:40 | 213.342 | 216.371 | 396 | 36.0618 | 35.7674 | 0.29439 | 214.6047 | 35 | 35.256 | -0.25597 | 0.986 | 15-03-2026 10:40 | 211.95 | 215.242 | 395.8 | 35.8737 | 35.7674 | 0.10622 | 214.6047 | 34.9 | 35.256 | -0.35597 | 0.98471 | 15-03-2026 10:40 | 211.372 | 214.654 | 394.3 | 35.7757 | 35.7674 | 0.0082218 | 214.6047 | 34.8 | 35.256 | -0.45597 | 0.98471 | 15-03-2026 10:40 | 211.093 | 217.3 | 396 | 36.2167 | 35.7674 | 0.44922 | 214.6047 | 34.7 | 35.256 | -0.55597 | 0.97144 | 15-03-2026 10:40 | 199.854 | 202.671 | 374.5 | 33.7785 | 34.0283 | -0.24979 | 204.1698 | 32.4 | 33.5417 | -1.1417 | 0.9861 | 15-03-2026 10:40 | 371.0358 | 370.2423 | 0.79356 | 2221.4537 | 360.9 | 364.9478 | -4.0478
15-03-2026 10:30 | 789 | 48.79 | 277.125 | 281.345 | 486.4 | 46.8908 | 46.9822 | -0.091338 | 281.893 | 44.4 | 46.3103 | -1.9103 | 0.985 | 15-03-2026 10:30 | 279.883 | 284.203 | 489.6 | 47.3672 | 46.9822 | 0.38499 | 281.893 | 48.4 | 46.3103 | 2.0897 | 0.9848 | 15-03-2026 10:30 | 275.217 | 281.608 | 481 | 46.9347 | 46.9822 | -0.047505 | 281.893 | 45.1 | 46.3103 | -1.2103 | 0.97731 | 15-03-2026 10:30 | 278.812 | 283.115 | 488.2 | 47.1858 | 46.9822 | 0.20366 | 281.893 | 45.6 | 46.3103 | -0.71033 | 0.9848 | 15-03-2026 10:30 | 207.854 | 210.784 | 361 | 35.1307 | 34.8016 | 0.32906 | 208.8097 | 34 | 34.3039 | -0.30395 | 0.9861 | 15-03-2026 10:30 | 206.532 | 209.443 | 360.9 | 34.9072 | 34.8016 | 0.10556 | 208.8097 | 33.7 | 34.3039 | -0.60395 | 0.9861 | 15-03-2026 10:30 | 206.216 | 209.246 | 359.5 | 34.8743 | 34.8016 | 0.072725 | 208.8097 | 33.7 | 34.3039 | -0.60395 | 0.98552 | 15-03-2026 10:30 | 206.502 | 212.424 | 361.3 | 35.404 | 34.8016 | 0.60239 | 208.8097 | 33.8 | 34.3039 | -0.50395 | 0.97212 | 15-03-2026 10:30 | 195.45 | 198.205 | 342.1 | 33.0342 | 33.1094 | -0.075254 | 198.6565 | 31.9 | 32.636 | -0.73596 | 0.9861 | 15-03-2026 10:30 | 361.7288 | 360.2445 | 1.4843 | 2161.4673 | 350.6 | 355.093 | -4.493
15-03-2026 10:20 | 758 | 48.79 | 269.496 | 273.517 | 442 | 45.5862 | 45.1362 | 0.44994 | 270.8174 | 86.4 | 44.4908 | 41.9092 | 0.9853 | 15-03-2026 10:20 | 270.406 | 274.496 | 441.2 | 45.7493 | 45.1362 | 0.6131 | 270.8174 | 85.5 | 44.4908 | 41.0092 | 0.9851 | 15-03-2026 10:20 | 266.075 | 272.5 | 435.9 | 45.4167 | 45.1362 | 0.28044 | 270.8174 | 84.3 | 44.4908 | 39.8092 | 0.97642 | 15-03-2026 10:20 | 269.462 | 273.565 | 442.6 | 45.5942 | 45.1362 | 0.45794 | 270.8174 | 85.5 | 44.4908 | 41.0092 | 0.985 | 15-03-2026 10:20 | 200.84 | 203.588 | 327 | 33.9313 | 33.4342 | 0.49709 | 200.6055 | 64.1 | 32.9561 | 31.1439 | 0.9865 | 15-03-2026 10:20 | 199.645 | 202.419 | 327.2 | 33.7365 | 33.4342 | 0.30225 | 200.6055 | 63.8 | 32.9561 | 30.8439 | 0.9863 | 15-03-2026 10:20 | 199.398 | 202.443 | 325.8 | 33.7405 | 33.4342 | 0.30625 | 200.6055 | 63.6 | 32.9561 | 30.6439 | 0.98496 | 15-03-2026 10:20 | 199.631 | 205.365 | 327.5 | 34.2275 | 33.4342 | 0.79325 | 200.6055 | 63.7 | 32.9561 | 30.7439 | 0.97208 | 15-03-2026 10:20 | 188.786 | 191.389 | 310.2 | 31.8982 | 31.8085 | 0.089623 | 190.8513 | 60.3 | 31.3537 | 28.9463 | 0.9864 | 15-03-2026 10:20 | 349.8803 | 346.0904 | 3.7899 | 2076.5427 | 657.2 | 341.1414 | 316.0586
15-03-2026 10:10 | 724 | 48.79 |  |  |  | 0 | 43.1117 | -43.1117 | 258.6699 | 0 | 42.4952 | -42.4952 | [5 empty] | 0 | 43.1117 | -43.1117 | 258.6699 | 0 | 42.4952 | -42.4952 | [5 empty] | 0 | 43.1117 | -43.1117 | 258.6699 | 0 | 42.4952 | -42.4952 | [5 empty] | 0 | 43.1117 | -43.1117 | 258.6699 | 0 | 42.4952 | -42.4952 | [5 empty] | 0 | 31.9346 | -31.9346 | 191.6073 | 0 | 31.4779 | -31.4779 | [5 empty] | 0 | 31.9346 | -31.9346 | 191.6073 | 0 | 31.4779 | -31.4779 | [5 empty] | 0 | 31.9346 | -31.9346 | 191.6073 | 0 | 31.4779 | -31.4779 | [5 empty] | 0 | 31.9346 | -31.9346 | 191.6073 | 0 | 31.4779 | -31.4779 | [5 empty] | 0 | 30.3818 | -30.3818 | 182.2906 | 0 | 29.9473 | -29.9473 |  | 15-03-2026 10:10 | 0 | 330.5666 | -330.5666 | 1983.3996 | 0 | 325.8395 | -325.8395
15-03-2026 10:00 | 686 | 48.5 | 245.517 | 249.003 | 355.6 | 41.5005 | 40.8941 | 0.60639 | 245.3647 | 39.9 | 40.3093 | -0.40933 | 0.986 | 15-03-2026 10:00 | 247.885 | 251.456 | 355.7 | 41.9093 | 40.8941 | 1.0152 | 245.3647 | 39.1 | 40.3093 | -1.2093 | 0.9858 | 15-03-2026 10:00 | 243.171 | 248.363 | 351.6 | 41.3938 | 40.8941 | 0.49972 | 245.3647 | 40 | 40.3093 | -0.30933 | 0.9791 | 15-03-2026 10:00 | 247.211 | 250.772 | 357.1 | 41.7953 | 40.8941 | 0.90122 | 245.3647 | 40.7 | 40.3093 | 0.39067 | 0.9858 | 15-03-2026 10:00 | 183.504 | 185.921 | 262.9 | 30.9868 | 30.2919 | 0.6949 | 181.7516 | 29.8 | 29.8588 | -0.05876 | 0.987 | 15-03-2026 10:00 | 183.245 | 185.708 | 263.4 | 30.9513 | 30.2919 | 0.6594 | 181.7516 | 29.8 | 29.8588 | -0.05876 | 0.98674 | 15-03-2026 10:00 | 182.457 | 184.951 | 262.2 | 30.8252 | 30.2919 | 0.53323 | 181.7516 | 29.6 | 29.8588 | -0.25876 | 0.98652 | 15-03-2026 10:00 | 182.649 | 187.659 | 263.8 | 31.2765 | 30.2919 | 0.98457 | 181.7516 | 29.6 | 29.8588 | -0.25876 | 0.9733 | 15-03-2026 10:00 | 173.02 | 175.317 | 249.9 | 29.2195 | 28.819 | 0.40048 | 172.9141 | 28.5 | 28.4069 | 0.093088 | 0.9869 | 15-03-2026 10:00 | 319.8583 | 313.5632 | 6.2951 | 1881.3793 | 307 | 309.0793 | -2.0793
15-03-2026 09:50 | 650 | 48.5 | 233.966 | 237.216 | 315.7 | 39.536 | 38.7481 | 0.78793 | 232.4884 | 37.9 | 38.194 | -0.29397 |  | 15-03-2026 09:50 | 235.529 | 238.849 | 316.6 | 39.8082 | 38.7481 | 1.0601 | 232.4884 | 38.1 | 38.194 | -0.093968 |  | 15-03-2026 09:50 | 231.276 | 236.215 | 311.6 | 39.3692 | 38.7481 | 0.6211 | 232.4884 | 37.6 | 38.194 | -0.59397 |  | 15-03-2026 09:50 | 235.34 | 238.657 | 316.4 | 39.7762 | 38.7481 | 1.0281 | 232.4884 | 38.1 | 38.194 | -0.093968 |  | 15-03-2026 09:50 | 174.513 | 176.794 | 233.1 | 29.4657 | 28.7023 | 0.7634 | 172.2136 | 28.7 | 28.2918 | 0.40817 |  | 15-03-2026 09:50 | 174.294 | 176.554 | 233.6 | 29.4257 | 28.7023 | 0.7234 | 172.2136 | 28.6 | 28.2918 | 0.30817 |  | 15-03-2026 09:50 | 173.428 | 175.659 | 232.6 | 29.2765 | 28.7023 | 0.57423 | 172.2136 | 28.5 | 28.2918 | 0.20817 |  | 15-03-2026 09:50 | 173.413 | 178.311 | 234.2 | 29.7185 | 28.7023 | 1.0162 | 172.2136 | 28.5 | 28.2918 | 0.20817 |  | 15-03-2026 09:50 | 164.26 | 166.424 | 221.4 | 27.7373 | 27.3067 | 0.43068 | 163.8399 | 26.6 | 26.9162 | -0.31617 |  | 15-03-2026 09:50 | 304.1132 | 297.108 | 7.0052 | 1782.648 | 292.6 | 292.8594 | -0.25935
15-03-2026 09:40 | 615 | 48.79 | 221.865 | 224.856 | 277.8 | 37.476 | 36.6211 | 0.85492 | 219.7265 | 35.9 | 36.0974 | -0.1974 |  | 15-03-2026 09:40 | 223.1 | 226.704 | 278.5 | 37.784 | 36.6211 | 1.1629 | 219.7265 | 36.1 | 36.0974 | 0.002597 |  | 15-03-2026 09:40 | 219.924 | 224.483 | 274 | 37.4138 | 36.6211 | 0.79275 | 219.7265 | 35.5 | 36.0974 | -0.5974 |  | 15-03-2026 09:40 | 223.704 | 226.765 | 278.3 | 37.7942 | 36.6211 | 1.1731 | 219.7265 | 36.7 | 36.0974 | 0.6026 |  | 15-03-2026 09:40 | 165.754 | 167.869 | 204.4 | 27.9782 | 27.1267 | 0.85144 | 162.7604 | 26.8 | 26.7388 | 0.061183 |  | 15-03-2026 09:40 | 165.564 | 167.677 | 205 | 27.9462 | 27.1267 | 0.81944 | 162.7604 | 26.8 | 26.7388 | 0.061183 |  | 15-03-2026 09:40 | 164.609 | 166.726 | 204.1 | 27.7877 | 27.1267 | 0.66094 | 162.7604 | 26.6 | 26.7388 | -0.13882 |  | 15-03-2026 09:40 | 164.61 | 168.918 | 205.7 | 28.153 | 27.1267 | 1.0263 | 162.7604 | 26.7 | 26.7388 | -0.038817 |  | 15-03-2026 09:40 | 156.119 | 158.127 | 194.8 | 26.3545 | 25.8077 | 0.54678 | 154.8463 | 25.2 | 25.4387 | -0.23867 |  | 15-03-2026 09:40 | 288.6875 | 280.799 | 7.8885 | 1684.7939 | 276.3 | 276.7836 | -0.48355
15-03-2026 09:30 | 579 | 48.79 | 209.687 | 212.47 | 241.9 | 35.4117 | 34.4774 | 0.93426 | 206.8645 | 33.7 | 33.9844 | -0.28438 |  | 15-03-2026 09:30 | 209.425 | 212.248 | 242.4 | 35.3747 | 34.4774 | 0.89726 | 206.8645 | 35.4 | 33.9844 | 1.4156 |  | 15-03-2026 09:30 | 207.097 | 211.531 | 238.5 | 35.2552 | 34.4774 | 0.77776 | 206.8645 | 33.4 | 33.9844 | -0.58438 |  | 15-03-2026 09:30 | 210.305 | 213.036 | 241.6 | 35.506 | 34.4774 | 1.0286 | 206.8645 | 33.4 | 33.9844 | -0.58438 |  | 15-03-2026 09:30 | 155.969 | 157.927 | 177.6 | 26.3212 | 25.5388 | 0.78234 | 153.2329 | 25 | 25.1736 | -0.17362 |  | 15-03-2026 09:30 | 155.879 | 157.836 | 178.2 | 26.306 | 25.5388 | 0.76718 | 153.2329 | 25 | 25.1736 | -0.17362 |  | 15-03-2026 09:30 | 154.893 | 156.84 | 177.5 | 26.14 | 25.5388 | 0.60118 | 153.2329 | 24.9 | 25.1736 | -0.27362 |  | 15-03-2026 09:30 | 155.361 | 159.57 | 179 | 26.595 | 25.5388 | 1.0562 | 153.2329 | 24.9 | 25.1736 | -0.27362 |  | 15-03-2026 09:30 | 147.184 | 149.047 | 169.6 | 24.8412 | 24.297 | 0.54414 | 145.7822 | 23.6 | 23.9496 | -0.34958 |  | 15-03-2026 09:30 | 271.7508 | 264.362 | 7.3889 | 1586.1718 | 259.3 | 260.5816 | -1.2816
15-03-2026 09:20 | 535 | 48.5 | 194.663 | 197.054 | 208.2 | 32.8423 | 31.8926 | 0.94969 | 191.3558 | 31.8 | 31.4366 | 0.36343 |  | 15-03-2026 09:20 | 194.902 | 197.429 | 207 | 32.9048 | 31.8926 | 1.0122 | 191.3558 | 32.1 | 31.4366 | 0.66343 |  | 15-03-2026 09:20 | 191.941 | 195.637 | 205.1 | 32.6062 | 31.8926 | 0.71353 | 191.3558 | 31 | 31.4366 | -0.43657 |  | 15-03-2026 09:20 | 195.277 | 197.829 | 208.2 | 32.9715 | 31.8926 | 1.0789 | 191.3558 | 31.5 | 31.4366 | 0.063426 |  | 15-03-2026 09:20 | 144.286 | 146.031 | 152.6 | 24.3385 | 23.6242 | 0.71432 | 141.7451 | 23 | 23.2864 | -0.28635 |  | 15-03-2026 09:20 | 144.564 | 146.349 | 153.2 | 24.3915 | 23.6242 | 0.76732 | 141.7451 | 22.9 | 23.2864 | -0.38635 |  | 15-03-2026 09:20 | 142.437 | 144.182 | 152.6 | 24.0303 | 23.6242 | 0.40616 | 141.7451 | 23.1 | 23.2864 | -0.18635 |  | 15-03-2026 09:20 | 143.649 | 147.482 | 154.1 | 24.5803 | 23.6242 | 0.95616 | 141.7451 | 23.1 | 23.2864 | -0.18635 |  | 15-03-2026 09:20 | 136.263 | 137.96 | 146 | 22.9933 | 22.4755 | 0.51786 | 134.8529 | 22 | 22.1541 | -0.15408 |  | 15-03-2026 09:20 | 251.6588 | 244.5427 | 7.1161 | 1467.2564 | 240.5 | 241.0458 | -0.54578
15-03-2026 09:10 | 497 | 46.21 | 179.894 | 182.153 | 176.4 | 30.3588 | 29.8861 | 0.47272 | 179.3167 | 28.3 | 29.4587 | -1.1587 |  | 15-03-2026 09:10 | 180.607 | 182.93 | 174.9 | 30.4883 | 29.8861 | 0.60222 | 179.3167 | 27.5 | 29.4587 | -1.9587 |  | 15-03-2026 09:10 | 178.35 | 181.581 | 174.1 | 30.2635 | 29.8861 | 0.37739 | 179.3167 | 28.7 | 29.4587 | -0.75874 |  | 15-03-2026 09:10 | 181.515 | 183.831 | 176.7 | 30.6385 | 29.8861 | 0.75239 | 179.3167 | 29.3 | 29.4587 | -0.15874 |  | 15-03-2026 09:10 | 133.929 | 135.542 | 129.6 | 22.5903 | 22.1379 | 0.45247 | 132.8272 | 21.6 | 21.8213 | -0.22129 |  | 15-03-2026 09:10 | 133.309 | 134.928 | 130.3 | 22.488 | 22.1379 | 0.35014 | 132.8272 | 21.5 | 21.8213 | -0.32129 |  | 15-03-2026 09:10 | 133.012 | 134.628 | 129.5 | 22.438 | 22.1379 | 0.30014 | 132.8272 | 21.2 | 21.8213 | -0.62129 |  | 15-03-2026 09:10 | 133.563 | 137.01 | 131 | 22.835 | 22.1379 | 0.69714 | 132.8272 | 21.4 | 21.8213 | -0.42129 |  | 15-03-2026 09:10 | 126.781 | 128.354 | 124 | 21.3923 | 21.0614 | 0.3309 | 126.3686 | 20.2 | 20.7603 | -0.56025 |  | 15-03-2026 09:10 | 233.4928 | 229.1573 | 4.3355 | 1374.9439 | 219.7 | 225.8804 | -6.1804
15-03-2026 09:00 | 458 | 45.92 | 165.406 | 167.432 | 148.1 | 27.9053 | 27.5711 | 0.33421 | 165.4267 | 26.8 | 27.1769 | -0.37685 |  | 15-03-2026 09:00 | 166.087 | 168.189 | 147.4 | 28.0315 | 27.5711 | 0.46038 | 165.4267 | 26.8 | 27.1769 | -0.37685 |  | 15-03-2026 09:00 | 163.367 | 166.08 | 145.4 | 27.68 | 27.5711 | 0.10888 | 165.4267 | 26 | 27.1769 | -1.1769 |  | 15-03-2026 09:00 | 166.451 | 168.524 | 147.4 | 28.0873 | 27.5711 | 0.51621 | 165.4267 | 26.2 | 27.1769 | -0.97685 |  | 15-03-2026 09:00 | 122.768 | 124.247 | 108 | 20.7078 | 20.4231 | 0.28478 | 122.5383 | 19.4 | 20.131 | -0.731 |  | 15-03-2026 09:00 | 122.236 | 123.683 | 108.8 | 20.6138 | 20.4231 | 0.19078 | 122.5383 | 19.5 | 20.131 | -0.631 |  | 15-03-2026 09:00 | 122.147 | 123.618 | 108.3 | 20.603 | 20.4231 | 0.17995 | 122.5383 | 19.4 | 20.131 | -0.731 |  | 15-03-2026 09:00 | 122.69 | 125.974 | 109.6 | 20.9957 | 20.4231 | 0.57262 | 122.5383 | 19.5 | 20.131 | -0.631 |  | 15-03-2026 09:00 | 116.323 | 117.736 | 103.8 | 19.6227 | 19.43 | 0.19266 | 116.58 | 18.6 | 19.1522 | -0.55216 |  | 15-03-2026 09:00 | 214.2472 | 211.4067 | 2.8405 | 1268.4401 | 202.2 | 208.3836 | -6.1836
15-03-2026 08:50 | 416 | 44.2 | 149.669 | 151.456 | 121.3 | 25.2427 | 25.2054 | 0.037235 | 151.2326 | 23.9 | 24.845 | -0.94499 |  | 15-03-2026 08:50 | 149.131 | 150.958 | 120.6 | 25.1597 | 25.2054 | -0.045765 | 151.2326 | 23.3 | 24.845 | -1.545 |  | 15-03-2026 08:50 | 147.981 | 150.381 | 119.4 | 25.0635 | 25.2054 | -0.14193 | 151.2326 | 23.3 | 24.845 | -1.545 |  | 15-03-2026 08:50 | 151.009 | 152.843 | 121.2 | 25.4738 | 25.2054 | 0.2684 | 151.2326 | 24 | 24.845 | -0.84499 |  | 15-03-2026 08:50 | 111.301 | 112.619 | 88.6 | 18.7698 | 18.6707 | 0.099143 | 112.0241 | 17.7 | 18.4037 | -0.7037 |  | 15-03-2026 08:50 | 111.51 | 112.819 | 89.3 | 18.8032 | 18.6707 | 0.13248 | 112.0241 | 17.4 | 18.4037 | -1.0037 |  | 15-03-2026 08:50 | 110.025 | 111.328 | 88.9 | 18.5547 | 18.6707 | -0.11602 | 112.0241 | 17.4 | 18.4037 | -1.0037 |  | 15-03-2026 08:50 | 111.375 | 114.126 | 90.1 | 19.021 | 18.6707 | 0.35031 | 112.0241 | 17.6 | 18.4037 | -0.8037 |  | 15-03-2026 08:50 | 105.633 | 106.884 | 85.2 | 17.814 | 17.7628 | 0.051151 | 106.5771 | 16.6 | 17.5088 | -0.90884 |  | 15-03-2026 08:50 | 193.9023 | 193.2673 | 0.635 | 1159.604 | 181.2 | 190.5036 | -9.3036
15-03-2026 08:40 | 374 | 42.19 | 133.972 | 135.558 | 97.4 | 22.593 | 22.8316 | -0.23855 | 136.9893 | 20.4 | 22.5051 | -2.1051 |  | 15-03-2026 08:40 | 133.177 | 136.053 | 97.3 | 22.6755 | 22.8316 | -0.15605 | 136.9893 | 20.7 | 22.5051 | -1.8051 |  | 15-03-2026 08:40 | 132.46 | 134.551 | 96.1 | 22.4252 | 22.8316 | -0.40639 | 136.9893 | 20.7 | 22.5051 | -1.8051 |  | 15-03-2026 08:40 | 134.677 | 136.285 | 97.2 | 22.7142 | 22.8316 | -0.11739 | 136.9893 | 21 | 22.5051 | -1.5051 |  | 15-03-2026 08:40 | 99.338 | 100.504 | 70.9 | 16.7507 | 16.9123 | -0.1616 | 101.4736 | 15.5 | 16.6704 | -1.1704 |  | 15-03-2026 08:40 | 97.787 | 98.885 | 71.9 | 16.4808 | 16.9123 | -0.43143 | 101.4736 | 15.5 | 16.6704 | -1.1704 |  | 15-03-2026 08:40 | 98.792 | 99.941 | 71.5 | 16.6568 | 16.9123 | -0.25543 | 101.4736 | 15.4 | 16.6704 | -1.2704 |  | 15-03-2026 08:40 | 99.742 | 102.304 | 72.5 | 17.0507 | 16.9123 | 0.1384 | 101.4736 | 15.6 | 16.6704 | -1.0704 |  | 15-03-2026 08:40 | 94.567 | 95.677 | 68.6 | 15.9462 | 16.0899 | -0.14376 | 96.5395 | 14.8 | 15.8598 | -1.0598 |  | 15-03-2026 08:40 | 173.293 | 175.0652 | -1.7722 | 1050.3912 | 159.6 | 172.5618 | -12.9618
15-03-2026 08:30 | 330 | 39.03 | 117.663 | 119.263 | 77 | 19.8772 | 20.3826 | -0.5054 | 122.2954 | 18.7 | 20.0911 | -1.3911 |  | 15-03-2026 08:30 | 117.941 | 119.337 | 76.6 | 19.8895 | 20.3826 | -0.49306 | 122.2954 | 18.9 | 20.0911 | -1.1911 |  | 15-03-2026 08:30 | 115.883 | 117.673 | 75.4 | 19.6122 | 20.3826 | -0.7704 | 122.2954 | 18 | 20.0911 | -2.0911 |  | 15-03-2026 08:30 | 117.178 | 118.565 | 76.2 | 19.7608 | 20.3826 | -0.62173 | 122.2954 | 18.3 | 20.0911 | -1.7911 |  | 15-03-2026 08:30 | 86.179 | 87.199 | 55.4 | 14.5332 | 15.0982 | -0.56503 | 90.5892 | 13.2 | 14.8823 | -1.6823 |  | 15-03-2026 08:30 | 86.827 | 87.837 | 56.4 | 14.6395 | 15.0982 | -0.45869 | 90.5892 | 13.5 | 14.8823 | -1.3823 |  | 15-03-2026 08:30 | 86.266 | 87.287 | 56.1 | 14.5478 | 15.0982 | -0.55036 | 90.5892 | 13.4 | 14.8823 | -1.4823 |  | 15-03-2026 08:30 | 87.276 | 89.278 | 56.9 | 14.8797 | 15.0982 | -0.21853 | 90.5892 | 13.5 | 14.8823 | -1.3823 |  | 15-03-2026 08:30 | 82.932 | 83.931 | 53.8 | 13.9885 | 14.3641 | -0.37556 | 86.1844 | 12.8 | 14.1587 | -1.3587 |  | 15-03-2026 08:30 | 151.7283 | 156.2871 | -4.5588 | 937.7225 | 140.3 | 154.0522 | -13.7522
15-03-2026 08:20 | 288 | 38.17 | 100.156 | 102.105 | 58.3 | 17.0175 | 17.8447 | -0.82723 | 107.0684 | 15.2 | 17.5895 | -2.3895 |  | 15-03-2026 08:20 | 100.618 | 101.789 | 57.7 | 16.9648 | 17.8447 | -0.87989 | 107.0684 | 14.8 | 17.5895 | -2.7895 |  | 15-03-2026 08:20 | 99.682 | 101.112 | 57.4 | 16.852 | 17.8447 | -0.99273 | 107.0684 | 15.1 | 17.5895 | -2.4895 |  | 15-03-2026 08:20 | 101.603 | 102.775 | 57.9 | 17.1292 | 17.8447 | -0.71556 | 107.0684 | 15.3 | 17.5895 | -2.2895 |  | 15-03-2026 08:20 | 73.845 | 74.725 | 42.2 | 12.4542 | 13.2183 | -0.76415 | 79.3099 | 11.2 | 13.0293 | -1.8293 |  | 15-03-2026 08:20 | 74.901 | 75.788 | 42.9 | 12.6313 | 13.2183 | -0.58698 | 79.3099 | 11.3 | 13.0293 | -1.7293 |  | 15-03-2026 08:20 | 74.499 | 75.411 | 42.7 | 12.5685 | 13.2183 | -0.64982 | 79.3099 | 11.3 | 13.0293 | -1.7293 |  | 15-03-2026 08:20 | 75.466 | 77.431 | 43.4 | 12.9052 | 13.2183 | -0.31315 | 79.3099 | 11.5 | 13.0293 | -1.5293 |  | 15-03-2026 08:20 | 71.429 | 72.324 | 41 | 12.054 | 12.5756 | -0.52159 | 75.4535 | 10.9 | 12.3958 | -1.4958 |  | 15-03-2026 08:20 | 130.5767 | 136.8278 | -6.2511 | 820.9665 | 116.6 | 134.8711 | -18.2711
15-03-2026 08:10 | 243 | 37.31 | 84.471 | 85.445 | 43.1 | 14.2408 | 15.104 | -0.86316 | 90.624 | 12.8 | 14.888 | -2.088 |  | 15-03-2026 08:10 | 84.125 | 85.104 | 42.9 | 14.184 | 15.104 | -0.92 | 90.624 | 13.1 | 14.888 | -1.788 |  | 15-03-2026 08:10 | 82.98 | 83.945 | 42.3 | 13.9908 | 15.104 | -1.1132 | 90.624 | 12.4 | 14.888 | -2.488 |  | 15-03-2026 08:10 | 83.801 | 84.793 | 42.6 | 14.1322 | 15.104 | -0.97183 | 90.624 | 12.5 | 14.888 | -2.388 |  | 15-03-2026 08:10 | 61.607 | 62.399 | 31 | 10.3998 | 11.1881 | -0.78831 | 67.1289 | 9.2 | 11.0282 | -1.8282 |  | 15-03-2026 08:10 | 62.479 | 63.209 | 31.6 | 10.5348 | 11.1881 | -0.65331 | 67.1289 | 9.4 | 11.0282 | -1.6282 |  | 15-03-2026 08:10 | 61.937 | 62.727 | 31.4 | 10.4545 | 11.1881 | -0.73365 | 67.1289 | 9.3 | 11.0282 | -1.7282 |  | 15-03-2026 08:10 | 62.817 | 64.67 | 31.9 | 10.7783 | 11.1881 | -0.40981 | 67.1289 | 9.5 | 11.0282 | -1.5282 |  | 15-03-2026 08:10 | 59.631 | 60.416 | 30.1 | 10.0693 | 10.6441 | -0.5748 | 63.8648 | 9 | 10.4919 | -1.4919 |  | 15-03-2026 08:10 | 108.7847 | 115.8127 | -7.028 | 694.8763 | 97.2 | 114.1566 | -16.9566
15-03-2026 08:00 | 197 | 34.15 | 67.695 | 68.51 | 30.3 | 11.4183 | 12.3863 | -0.968 | 74.318 | 10 | 12.2092 | -2.2092 |  | 15-03-2026 08:00 | 67.033 | 67.875 | 29.8 | 11.3125 | 12.3863 | -1.0738 | 74.318 | 9.5 | 12.2092 | -2.7092 |  | 15-03-2026 08:00 | 66.912 | 67.744 | 29.9 | 11.2907 | 12.3863 | -1.0957 | 74.318 | 9.9 | 12.2092 | -2.3092 |  | 15-03-2026 08:00 | 67.229 | 68.059 | 30.1 | 11.3432 | 12.3863 | -1.0432 | 74.318 | 10 | 12.2092 | -2.2092 |  | 15-03-2026 08:00 | 49.33 | 50.041 | 21.8 | 8.3402 | 9.1751 | -0.83489 | 55.0504 | 7.2 | 9.0439 | -1.8439 |  | 15-03-2026 08:00 | 50.154 | 50.861 | 22.2 | 8.4768 | 9.1751 | -0.69823 | 55.0504 | 7.4 | 9.0439 | -1.6439 |  | 15-03-2026 08:00 | 49.821 | 50.544 | 22.1 | 8.424 | 9.1751 | -0.75106 | 55.0504 | 7.4 | 9.0439 | -1.6439 |  | 15-03-2026 08:00 | 50.536 | 51.886 | 22.4 | 8.6477 | 9.1751 | -0.52739 | 55.0504 | 7.4 | 9.0439 | -1.6439 |  | 15-03-2026 08:00 | 47.932 | 48.637 | 21.1 | 8.1062 | 8.7289 | -0.62277 | 52.3736 | 7.1 | 8.6041 | -1.5041 |  | 15-03-2026 08:00 | 87.3595 | 94.9745 | -7.615 | 569.8469 | 75.9 | 93.6164 | -17.7164
15-03-2026 07:50 | 154 | 31.86 | 52.509 | 53.233 | 20.3 | 8.8722 | 9.7629 | -0.89072 | 58.5773 | 7.6 | 9.6233 | -2.0233 |  | 15-03-2026 07:50 | 51.626 | 52.354 | 20.3 | 8.7257 | 9.7629 | -1.0372 | 58.5773 | 7.9 | 9.6233 | -1.7233 |  | 15-03-2026 07:50 | 51.744 | 52.473 | 20 | 8.7455 | 9.7629 | -1.0174 | 58.5773 | 7.5 | 9.6233 | -2.1233 |  | 15-03-2026 07:50 | 52.278 | 53.015 | 20.1 | 8.8358 | 9.7629 | -0.92706 | 58.5773 | 7.6 | 9.6233 | -2.0233 |  | 15-03-2026 07:50 | 38.025 | 38.635 | 14.6 | 6.4392 | 7.2318 | -0.7926 | 43.3906 | 5.5 | 7.1284 | -1.6284 |  | 15-03-2026 07:50 | 38.64 | 39.399 | 14.8 | 6.5665 | 7.2318 | -0.66527 | 43.3906 | 5.6 | 7.1284 | -1.5284 |  | 15-03-2026 07:50 | 38.492 | 39.11 | 14.7 | 6.5183 | 7.2318 | -0.71344 | 43.3906 | 5.5 | 7.1284 | -1.6284 |  | 15-03-2026 07:50 | 39.076 | 40.159 | 15 | 6.6932 | 7.2318 | -0.5386 | 43.3906 | 5.6 | 7.1284 | -1.5284 |  | 15-03-2026 07:50 | 37.008 | 37.578 | 14 | 6.263 | 6.8801 | -0.61713 | 41.2808 | 5.3 | 6.7817 | -1.4817 |  | 15-03-2026 07:50 | 67.6593 | 74.8588 | -7.1994 | 449.1526 | 58.1 | 73.7883 | -15.6883
15-03-2026 07:40 | 116 | 30.71 | 38.843 | 39.455 | 12.7 | 6.5758 | 7.3842 | -0.80836 | 44.3052 | 5.4 | 7.2786 | -1.8786 |  | 15-03-2026 07:40 | 38.078 | 38.722 | 12.4 | 6.4537 | 7.3842 | -0.93053 | 44.3052 | 5.2 | 7.2786 | -2.0786 |  | 15-03-2026 07:40 | 38.197 | 38.818 | 12.5 | 6.4697 | 7.3842 | -0.91453 | 44.3052 | 5.3 | 7.2786 | -1.9786 |  | 15-03-2026 07:40 | 38.528 | 39.15 | 12.5 | 6.525 | 7.3842 | -0.85919 | 44.3052 | 5.3 | 7.2786 | -1.9786 |  | 15-03-2026 07:40 | 27.971 | 28.501 | 9.1 | 4.7502 | 5.4698 | -0.71961 | 32.8186 | 4 | 5.3916 | -1.3916 |  | 15-03-2026 07:40 | 28.539 | 29.056 | 9.2 | 4.8427 | 5.4698 | -0.62711 | 32.8186 | 4 | 5.3916 | -1.3916 |  | 15-03-2026 07:40 | 28.38 | 28.906 | 9.2 | 4.8177 | 5.4698 | -0.65211 | 32.8186 | 4 | 5.3916 | -1.3916 |  | 15-03-2026 07:40 | 28.919 | 29.814 | 9.4 | 4.969 | 5.4698 | -0.50077 | 32.8186 | 4.1 | 5.3916 | -1.2916 |  | 15-03-2026 07:40 | 27.162 | 27.68 | 8.7 | 4.6133 | 5.2038 | -0.59048 | 31.2229 | 3.8 | 5.1294 | -1.3294 |  | 15-03-2026 07:40 | 50.017 | 56.6197 | -6.6027 | 339.718 | 41.1 | 55.81 | -14.71
15-03-2026 07:30 | 80 | 29.85 | 27.372 | 27.891 | 7.3 | 4.6485 | 5.1082 | -0.45969 | 30.6491 | 3.8 | 5.0351 | -1.2351 |  | 15-03-2026 07:30 | 26.247 | 27.442 | 7.2 | 4.5737 | 5.1082 | -0.53452 | 30.6491 | 3.6 | 5.0351 | -1.4351 |  | 15-03-2026 07:30 | 26.792 | 27.316 | 7.2 | 4.5527 | 5.1082 | -0.55552 | 30.6491 | 3.7 | 5.0351 | -1.3351 |  | 15-03-2026 07:30 | 26.678 | 27.324 | 7.2 | 4.554 | 5.1082 | -0.55419 | 30.6491 | 3.7 | 5.0351 | -1.3351 |  | 15-03-2026 07:30 | 19.424 | 19.944 | 5.1 | 3.324 | 3.7838 | -0.45984 | 22.7031 | 2.6 | 3.7297 | -1.1297 |  | 15-03-2026 07:30 | 19.782 | 20.226 | 5.2 | 3.371 | 3.7838 | -0.41284 | 22.7031 | 2.7 | 3.7297 | -1.0297 |  | 15-03-2026 07:30 | 19.676 | 20.137 | 5.2 | 3.3562 | 3.7838 | -0.42768 | 22.7031 | 2.7 | 3.7297 | -1.0297 |  | 15-03-2026 07:30 | 20.087 | 20.916 | 5.3 | 3.486 | 3.7838 | -0.29784 | 22.7031 | 2.7 | 3.7297 | -1.0297 |  | 15-03-2026 07:30 | 18.805 | 19.254 | 4.9 | 3.209 | 3.5999 | -0.39086 | 21.5991 | 2.5 | 3.5484 | -1.0484 |  | 15-03-2026 07:30 | 35.075 | 39.168 | -4.093 | 235.0079 | 28 | 38.6079 | -10.6079
15-03-2026 07:20 | 45 | 29.27 | 16.542 | 17.356 | 3.5 | 2.8927 | 2.8793 | 0.013378 | 17.2757 | 2.1 | 2.8381 | -0.73812 |  | 15-03-2026 07:20 | 16.895 | 17.642 | 3.6 | 2.9403 | 2.8793 | 0.061044 | 17.2757 | 2.2 | 2.8381 | -0.63812 |  | 15-03-2026 07:20 | 16.76 | 17.183 | 3.5 | 2.8638 | 2.8793 | -0.015456 | 17.2757 | 2.1 | 2.8381 | -0.73812 |  | 15-03-2026 07:20 | 16.757 | 17.449 | 3.5 | 2.9082 | 2.8793 | 0.028878 | 17.2757 | 2.1 | 2.8381 | -0.73812 |  | 15-03-2026 07:20 | 12.137 | 12.792 | 2.5 | 2.132 | 2.1328 | -0.00080671 | 12.7968 | 1.5 | 2.1023 | -0.60231 |  | 15-03-2026 07:20 | 12.315 | 12.706 | 2.5 | 2.1177 | 2.1328 | -0.01514 | 12.7968 | 1.5 | 2.1023 | -0.60231 |  | 15-03-2026 07:20 | 12.33 | 12.727 | 2.5 | 2.1212 | 2.1328 | -0.01164 | 12.7968 | 1.5 | 2.1023 | -0.60231 |  | 15-03-2026 07:20 | 12.53 | 13.027 | 2.6 | 2.1712 | 2.1328 | 0.03836 | 12.7968 | 1.6 | 2.1023 | -0.50231 |  | 15-03-2026 07:20 | 11.677 | 12.059 | 2.4 | 2.0098 | 2.0291 | -0.019268 | 12.1746 | 1.5 | 2.0001 | -0.50009 |  | 15-03-2026 07:20 | 22.1568 | 22.0775 | 0.079349 | 132.4649 | 16.1 | 21.7618 | -5.6618
15-03-2026 07:10 | 25 | 28.41 | 9.372 | 9.722 | 1.4 | 1.6203 | 1.6045 | 0.01584 | 9.627 | 1.1 | 1.5815 | -0.48155 |  | 15-03-2026 07:10 | 9.345 | 9.945 | 1.4 | 1.6575 | 1.6045 | 0.053007 | 9.627 | 1.1 | 1.5815 | -0.48155 |  | 15-03-2026 07:10 | 9.238 | 9.594 | 1.4 | 1.599 | 1.6045 | -0.0054929 | 9.627 | 1.1 | 1.5815 | -0.48155 |  | 15-03-2026 07:10 | 9.275 | 10.093 | 1.4 | 1.6822 | 1.6045 | 0.077674 | 9.627 | 1.1 | 1.5815 | -0.48155 |  | 15-03-2026 07:10 | 6.551 | 7.24 | 1 | 1.2067 | 1.1885 | 0.018153 | 7.1311 | 0.8 | 1.1715 | -0.37152 |  | 15-03-2026 07:10 | 6.636 | 6.918 | 1 | 1.153 | 1.1885 | -0.035513 | 7.1311 | 0.8 | 1.1715 | -0.37152 |  | 15-03-2026 07:10 | 6.647 | 6.931 | 1 | 1.1552 | 1.1885 | -0.033347 | 7.1311 | 0.8 | 1.1715 | -0.37152 |  | 15-03-2026 07:10 | 6.787 | 7.456 | 1 | 1.2427 | 1.1885 | 0.054153 | 7.1311 | 0.8 | 1.1715 | -0.37152 |  | 15-03-2026 07:10 | 6.316 | 6.593 | 0.9 | 1.0988 | 1.1307 | -0.03189 | 6.7843 | 0.7 | 1.1146 | -0.41455 |  | 15-03-2026 07:10 | 12.4153 | 12.3027 | 0.11259 | 73.8165 | 8.3 | 12.1268 | -3.8268
15-03-2026 07:00 | 10 | 28.41 | 3.967 | 4.163 | 0.3 | 0.69383 | 0.6418 | 0.052036 | 3.8508 | 0.3 | 0.63262 | -0.33262 |  | 15-03-2026 07:00 | 3.931 | 4.699 | 0.3 | 0.78317 | 0.6418 | 0.14137 | 3.8508 | 0.3 | 0.63262 | -0.33262 |  | 15-03-2026 07:00 | 3.981 | 4.179 | 0.3 | 0.6965 | 0.6418 | 0.054703 | 3.8508 | 0.3 | 0.63262 | -0.33262 |  | 15-03-2026 07:00 | 4.047 | 4.79 | 0.3 | 0.79833 | 0.6418 | 0.15654 | 3.8508 | 0.3 | 0.63262 | -0.33262 |  | 15-03-2026 07:00 | 2.782 | 3.379 | 0.2 | 0.56317 | 0.47541 | 0.087761 | 2.8524 | 0.2 | 0.46861 | -0.26861 |  | 15-03-2026 07:00 | 2.813 | 2.958 | 0.2 | 0.493 | 0.47541 | 0.017595 | 2.8524 | 0.2 | 0.46861 | -0.26861 |  | 15-03-2026 07:00 | 2.795 | 2.939 | 0.2 | 0.48983 | 0.47541 | 0.014428 | 2.8524 | 0.2 | 0.46861 | -0.26861 |  | 15-03-2026 07:00 | 2.924 | 3.381 | 0.2 | 0.5635 | 0.47541 | 0.088095 | 2.8524 | 0.2 | 0.46861 | -0.26861 |  | 15-03-2026 07:00 | 2.64 | 2.776 | 0.2 | 0.46267 | 0.45229 | 0.010377 | 2.7137 | 0.2 | 0.44582 | -0.24582 |  | 15-03-2026 07:00 | 5.544 | 4.9211 | 0.6229 | 29.5266 | 2.2 | 4.8507 | -2.6507
[110 empty] | Total: - | 14916.1557 | 19192.6537 | -4276.4981 |  | 15176.9 | 18918.1988 | -3741.2988
Sum:- | 41916 |  | 11496.122 |  | 78917.6 |  |  |  |  | 1976.6 | 2467.2631 | -490.6631 | 0.9836 |  | 11272.784 |  | 80470.7 |  |  |  |  | 1996 | 2467.2631 | -471.2631 | 0.98292 |  | 11397.508 |  | 80155.3 |  |  |  |  | 1960.4 | 2467.2631 | -506.8631 | 0.97338 |  | 11536.692 |  | 81199.8 |  |  |  |  | 1984.6 | 2467.2631 | -482.6631 | 0.98331 |  | 8605.143 |  | 60479.6 |  |  |  |  | 1480.7 | 1827.6023 | -346.9023 | 0.98482 |  | 8515.695 |  | 59996.4 |  |  |  |  | 1465.5 | 1827.6023 | -362.1023 | 0.98273 |  | 8496.15 |  | 59849.1 |  |  |  |  | 1462.4 | 1827.6023 | -365.2023 | 0.98162 |  | 8508.249 |  | 60031.7 |  |  |  |  | 1465.7 | 1827.6023 | -361.9023 | 0.97161 |  | 8047.332 |  | 56760.5 |  |  |  |  | 1385 | 1738.7372 | -353.7372 | 0.98503

## 16 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
16-03-2026 19:00 | 0 | 39.32 | 0.092 | 0.079 | 2442.2 | 0.013167 | 0 | 0.013167 | 0 | 0.1 | 0 | 0.1 |  | 16-03-2026 19:00 | 0 | 0 | 2460.5 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 16-03-2026 19:00 | 0.086 | 0.09 | 2430.4 | 0.015 | 0 | 0.015 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.09 | 0.235 | 2440.5 | 0.039167 | 0 | 0.039167 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.075 | 0.083 | 1840.5 | 0.013833 | 0 | 0.013833 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.099 | 0.104 | 1820.7 | 0.017333 | 0 | 0.017333 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.076 | 0.083 | 1820.8 | 0.013833 | 0 | 0.013833 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.066 | 0.088 | 1834.2 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.054 | 0.066 | 1733.3 | 0.011 | 0 | 0.011 | 0 | 0 | 0 | 0 |  | 16-03-2026 19:00 | 0.138 | 0 | 0.138 | 0 | 0.2 | 0 | 0.2 | 1 | 98.49%
16-03-2026 18:50 | 0 | 40.47 | 1.209 | 1.271 | 2442.1 | 0.21183 | 0 | 0.21183 | 0 | 0.4 | 0 | 0.4 |  | 16-03-2026 18:50 | 1.461 | 1.647 | 2460.4 | 0.2745 | 0 | 0.2745 | 0 | 0.5 | 0 | 0.5 |  | 16-03-2026 18:50 | 1.232 | 1.295 | 2430.3 | 0.21583 | 0 | 0.21583 | 0 | 0.4 | 0 | 0.4 |  | 16-03-2026 18:50 | 1.247 | 1.72 | 2440.4 | 0.28667 | 0 | 0.28667 | 0 | 0.4 | 0 | 0.4 |  | 16-03-2026 18:50 | 0.796 | 0.905 | 1840.4 | 0.15083 | 0 | 0.15083 | 0 | 0.3 | 0 | 0.3 |  | 16-03-2026 18:50 | 0.706 | 0.742 | 1820.6 | 0.12367 | 0 | 0.12367 | 0 | 0.2 | 0 | 0.2 |  | 16-03-2026 18:50 | 0.697 | 0.73 | 1820.7 | 0.12167 | 0 | 0.12167 | 0 | 0.3 | 0 | 0.3 |  | 16-03-2026 18:50 | 0.845 | 1.162 | 1834.1 | 0.19367 | 0 | 0.19367 | 0 | 0.3 | 0 | 0.3 |  | 16-03-2026 18:50 | 0.661 | 0.695 | 1733.3 | 0.11583 | 0 | 0.11583 | 0 | 0.3 | 0 | 0.3 |  | 16-03-2026 18:50 | 1.6945 | 0 | 1.6945 | 0 | 3.1 | 0 | 3.1 | 2 | 98.3%
16-03-2026 18:40 | 11 | 42.19 | 5.088 | 5.332 | 2441.7 | 0.88867 | 0.67152 | 0.21715 | 4.0291 | 1.4 | 0.66191 | 0.73809 |  | 16-03-2026 18:40 | 5.134 | 5.572 | 2459.9 | 0.92867 | 0.67152 | 0.25715 | 4.0291 | 4.6 | 0.66191 | 3.9381 |  | 16-03-2026 18:40 | 4.904 | 5.145 | 2429.9 | 0.8575 | 0.67152 | 0.18598 | 4.0291 | 1.4 | 0.66191 | 0.73809 |  | 16-03-2026 18:40 | 4.951 | 5.439 | 2440 | 0.9065 | 0.67152 | 0.23498 | 4.0291 | 1.4 | 0.66191 | 0.73809 |  | 16-03-2026 18:40 | 3.51 | 3.69 | 1840.1 | 0.615 | 0.49742 | 0.11758 | 2.9845 | 0.9 | 0.49031 | 0.40969 |  | 16-03-2026 18:40 | 3.4 | 3.574 | 1820.4 | 0.59567 | 0.49742 | 0.098247 | 2.9845 | 1 | 0.49031 | 0.50969 |  | 16-03-2026 18:40 | 3.42 | 3.596 | 1820.4 | 0.59933 | 0.49742 | 0.10191 | 2.9845 | 0.9 | 0.49031 | 0.40969 |  | 16-03-2026 18:40 | 3.476 | 3.743 | 1833.8 | 0.62383 | 0.49742 | 0.12641 | 2.9845 | 0.9 | 0.49031 | 0.40969 |  | 16-03-2026 18:40 | 3.038 | 3.201 | 1733 | 0.5335 | 0.47323 | 0.060267 | 2.8394 | 0.9 | 0.46647 | 0.43353 |  | 16-03-2026 18:40 | 6.5487 | 5.149 | 1.3997 | 30.8939 | 13.4 | 5.0753 | 8.3247 | 3 | 97.26%
16-03-2026 18:30 | 31 | 43.05 | 11.92 | 12.334 | 2440.3 | 2.0557 | 1.8864 | 0.16927 | 11.3184 | 3.1 | 1.8594 | 1.2406 | [5 empty] | 0 | 1.8864 | -1.8864 | 11.3184 | 0 | 1.8594 | -1.8594 |  | 16-03-2026 18:30 | 11.767 | 12.19 | 2428.5 | 2.0317 | 1.8864 | 0.14527 | 11.3184 | 3 | 1.8594 | 1.1406 |  | 16-03-2026 18:30 | 11.829 | 12.285 | 2438.6 | 2.0475 | 1.8864 | 0.16111 | 11.3184 | 3.1 | 1.8594 | 1.2406 |  | 16-03-2026 18:30 | 8.553 | 8.947 | 1839.2 | 1.4912 | 1.3973 | 0.093838 | 8.384 | 2.3 | 1.3773 | 0.92265 |  | 16-03-2026 18:30 | 8.433 | 8.775 | 1819.4 | 1.4625 | 1.3973 | 0.065171 | 8.384 | 2.2 | 1.3773 | 0.82265 |  | 16-03-2026 18:30 | 8.386 | 8.734 | 1819.5 | 1.4557 | 1.3973 | 0.058338 | 8.384 | 2.2 | 1.3773 | 0.82265 |  | 16-03-2026 18:30 | 8.363 | 8.708 | 1832.9 | 1.4513 | 1.3973 | 0.054004 | 8.384 | 2.2 | 1.3773 | 0.82265 |  | 16-03-2026 18:30 | 7.926 | 8.264 | 1732.1 | 1.3773 | 1.3294 | 0.047948 | 7.9763 | 2.1 | 1.3104 | 0.78962 |  | 16-03-2026 18:30 | 13.3728 | 14.4643 | -1.0914 | 86.7857 | 20.2 | 14.2574 | 5.9426 | 4 | 98.37%
16-03-2026 18:20 | 62 | 43.62 | 24.457 | 25.019 | 2437.2 | 4.1698 | 3.7648 | 0.40508 | 22.5885 | 4.1 | 3.7109 | 0.38908 |  | 16-03-2026 18:20 | 25.064 | 25.636 | 2455.3 | 4.2727 | 3.7648 | 0.50791 | 22.5885 | 4 | 3.7109 | 0.28908 |  | 16-03-2026 18:20 | 24.456 | 25.011 | 2425.5 | 4.1685 | 3.7648 | 0.40375 | 22.5885 | 4.2 | 3.7109 | 0.48908 |  | 16-03-2026 18:20 | 24.562 | 25.047 | 2435.5 | 4.1745 | 3.7648 | 0.40975 | 22.5885 | 4.1 | 3.7109 | 0.38908 |  | 16-03-2026 18:20 | 18.047 | 18.517 | 1836.9 | 3.0862 | 2.7887 | 0.29746 | 16.7322 | 3.1 | 2.7488 | 0.35117 |  | 16-03-2026 18:20 | 17.644 | 18.098 | 1817.2 | 3.0163 | 2.7887 | 0.22763 | 16.7322 | 3 | 2.7488 | 0.25117 |  | 16-03-2026 18:20 | 17.608 | 18.067 | 1817.3 | 3.0112 | 2.7887 | 0.22246 | 16.7322 | 3 | 2.7488 | 0.25117 |  | 16-03-2026 18:20 | 16.912 | 17.68 | 1830.7 | 2.9467 | 2.7887 | 0.15796 | 16.7322 | 2.9 | 2.7488 | 0.15117 |  | 16-03-2026 18:20 | 16.34 | 16.78 | 1730 | 2.7967 | 2.6531 | 0.14356 | 15.9187 | 2.7 | 2.6152 | 0.08483 |  | 16-03-2026 18:20 | 31.6425 | 28.867 | 2.7755 | 173.2017 | 31.1 | 28.4542 | 2.6458 | 5 | 98.45%
16-03-2026 18:10 | 69 | 44.2 | 26.06 | 26.635 | 2433.1 | 4.4392 | 4.1807 | 0.25846 | 25.0843 | 4.9 | 4.1209 | 0.77908 |  | 16-03-2026 18:10 | 26.494 | 27.076 | 2451.3 | 4.5127 | 4.1807 | 0.33196 | 25.0843 | 5.1 | 4.1209 | 0.97908 |  | 16-03-2026 18:10 | 26.094 | 26.681 | 2421.3 | 4.4468 | 4.1807 | 0.26612 | 25.0843 | 4.9 | 4.1209 | 0.77908 |  | 16-03-2026 18:10 | 26.234 | 26.813 | 2431.4 | 4.4688 | 4.1807 | 0.28812 | 25.0843 | 4.9 | 4.1209 | 0.77908 |  | 16-03-2026 18:10 | 19.309 | 19.804 | 1833.8 | 3.3007 | 3.0968 | 0.20385 | 18.5809 | 3.6 | 3.0525 | 0.54746 |  | 16-03-2026 18:10 | 19.013 | 19.493 | 1814.2 | 3.2488 | 3.0968 | 0.15201 | 18.5809 | 3.6 | 3.0525 | 0.54746 |  | 16-03-2026 18:10 | 18.967 | 19.451 | 1814.3 | 3.2418 | 3.0968 | 0.14501 | 18.5809 | 3.6 | 3.0525 | 0.54746 |  | 16-03-2026 18:10 | 18.747 | 19.535 | 1827.8 | 3.2558 | 3.0968 | 0.15901 | 18.5809 | 3.6 | 3.0525 | 0.54746 |  | 16-03-2026 18:10 | 17.862 | 18.333 | 1727.3 | 3.0555 | 2.9462 | 0.10926 | 17.6775 | 3.4 | 2.9041 | 0.49589 |  | 16-03-2026 18:10 | 33.9702 | 32.0564 | 1.9138 | 192.3382 | 37.6 | 31.598 | 6.002 | 6 | 98.17%
16-03-2026 18:00 | 80 | 44.77 | 30.767 | 31.353 | 2428.2 | 5.2255 | 4.8368 | 0.38867 | 29.021 | 5.4 | 4.7677 | 0.63234 |  | 16-03-2026 18:00 | 31.252 | 31.857 | 2446.2 | 5.3095 | 4.8368 | 0.47267 | 29.021 | 5.4 | 4.7677 | 0.63234 |  | 16-03-2026 18:00 | 30.912 | 31.514 | 2416.4 | 5.2523 | 4.8368 | 0.4155 | 29.021 | 5.5 | 4.7677 | 0.73234 |  | 16-03-2026 18:00 | 30.911 | 31.513 | 2426.5 | 5.2522 | 4.8368 | 0.41534 | 29.021 | 5.5 | 4.7677 | 0.73234 |  | 16-03-2026 18:00 | 22.89 | 23.431 | 1830.2 | 3.9052 | 3.5828 | 0.32233 | 21.497 | 4.1 | 3.5316 | 0.5684 |  | 16-03-2026 18:00 | 22.466 | 22.997 | 1810.6 | 3.8328 | 3.5828 | 0.25 | 21.497 | 4 | 3.5316 | 0.4684 |  | 16-03-2026 18:00 | 22.469 | 22.998 | 1810.7 | 3.833 | 3.5828 | 0.25016 | 21.497 | 3.9 | 3.5316 | 0.3684 |  | 16-03-2026 18:00 | 22.37 | 23.26 | 1824.2 | 3.8767 | 3.5828 | 0.29383 | 21.497 | 3.9 | 3.5316 | 0.3684 |  | 16-03-2026 18:00 | 21.146 | 21.664 | 1723.9 | 3.6107 | 3.4086 | 0.20204 | 20.4518 | 3.7 | 3.3599 | 0.34012 |  | 16-03-2026 18:00 | 40.0978 | 37.0873 | 3.0105 | 222.5238 | 41.4 | 36.557 | 4.843 | 7 | 98.09%
16-03-2026 17:50 | 97 | 45.35 | 35.563 | 36.215 | 2422.8 | 6.0358 | 5.8519 | 0.18397 | 35.1112 | 5.9 | 5.7682 | 0.13181 |  | 16-03-2026 17:50 | 36.319 | 37.014 | 2440.8 | 6.169 | 5.8519 | 0.31713 | 35.1112 | 6.1 | 5.7682 | 0.33181 |  | 16-03-2026 17:50 | 35.864 | 36.544 | 2410.9 | 6.0907 | 5.8519 | 0.2388 | 35.1112 | 5.9 | 5.7682 | 0.13181 |  | 16-03-2026 17:50 | 35.797 | 36.461 | 2421 | 6.0768 | 5.8519 | 0.22497 | 35.1112 | 5.9 | 5.7682 | 0.13181 |  | 16-03-2026 17:50 | 26.565 | 27.132 | 1826.1 | 4.522 | 4.3347 | 0.18728 | 26.0083 | 4.4 | 4.2727 | 0.12727 |  | 16-03-2026 17:50 | 26.059 | 26.623 | 1806.6 | 4.4372 | 4.3347 | 0.10245 | 26.0083 | 4.3 | 4.2727 | 0.027269 |  | 16-03-2026 17:50 | 26.009 | 26.598 | 1806.8 | 4.433 | 4.3347 | 0.098283 | 26.0083 | 4.4 | 4.2727 | 0.12727 |  | 16-03-2026 17:50 | 26.036 | 26.879 | 1820.3 | 4.4798 | 4.3347 | 0.14512 | 26.0083 | 4.4 | 4.2727 | 0.12727 |  | 16-03-2026 17:50 | 24.521 | 25.08 | 1720.2 | 4.18 | 4.1239 | 0.056054 | 24.7437 | 4.2 | 4.065 | 0.13503 |  | 16-03-2026 17:50 | 46.4243 | 44.8703 | 1.554 | 269.2217 | 45.5 | 44.2286 | 1.2714 | 8 | 97.13%
16-03-2026 17:40 | 99 | 46.21 | 35.654 | 36.332 | 2416.9 | 6.0553 | 5.9532 | 0.10216 | 35.719 | 6.5 | 5.868 | 0.63196 |  | 16-03-2026 17:40 | 36.577 | 37.259 | 2434.7 | 6.2098 | 5.9532 | 0.25666 | 35.719 | 6.4 | 5.868 | 0.53196 |  | 16-03-2026 17:40 | 35.723 | 36.393 | 2405 | 6.0655 | 5.9532 | 0.11233 | 35.719 | 6.4 | 5.868 | 0.53196 |  | 16-03-2026 17:40 | 35.783 | 36.457 | 2415.1 | 6.0762 | 5.9532 | 0.123 | 35.719 | 6.4 | 5.868 | 0.53196 |  | 16-03-2026 17:40 | 26.549 | 27.132 | 1821.7 | 4.522 | 4.4098 | 0.11225 | 26.4585 | 4.7 | 4.3467 | 0.3533 |  | 16-03-2026 17:40 | 26.202 | 26.63 | 1802.3 | 4.4383 | 4.4098 | 0.028578 | 26.4585 | 4.6 | 4.3467 | 0.2533 |  | 16-03-2026 17:40 | 26.084 | 26.669 | 1802.4 | 4.4448 | 4.4098 | 0.035078 | 26.4585 | 4.6 | 4.3467 | 0.2533 |  | 16-03-2026 17:40 | 26.161 | 26.891 | 1815.9 | 4.4818 | 4.4098 | 0.072078 | 26.4585 | 4.5 | 4.3467 | 0.1533 |  | 16-03-2026 17:40 | 24.682 | 25.24 | 1716 | 4.2067 | 4.1953 | 0.011331 | 25.172 | 4.3 | 4.1353 | 0.16466 |  | 16-03-2026 17:40 | 46.5005 | 45.647 | 0.85347 | 273.8822 | 48.4 | 44.9943 | 3.4057 | 9 | 98.47%
16-03-2026 17:30 | 106 | 47.64 | 37.358 | 38.027 | 2410.4 | 6.3378 | 6.3396 | -0.0018065 | 38.0378 | 8.7 | 6.249 | 2.451 |  | 16-03-2026 17:30 | 38.155 | 38.854 | 2428.3 | 6.4757 | 6.3396 | 0.13603 | 38.0378 | 8.9 | 6.249 | 2.651 |  | 16-03-2026 17:30 | 37.774 | 38.474 | 2398.6 | 6.4123 | 6.3396 | 0.072694 | 38.0378 | 8.7 | 6.249 | 2.451 |  | 16-03-2026 17:30 | 37.732 | 38.435 | 2408.7 | 6.4058 | 6.3396 | 0.066194 | 38.0378 | 8.7 | 6.249 | 2.451 |  | 16-03-2026 17:30 | 28.031 | 28.611 | 1817 | 4.7685 | 4.696 | 0.072471 | 28.1762 | 6.5 | 4.6289 | 1.8711 |  | 16-03-2026 17:30 | 27.505 | 28.086 | 1797.7 | 4.681 | 4.696 | -0.015029 | 28.1762 | 6.4 | 4.6289 | 1.7711 |  | 16-03-2026 17:30 | 27.482 | 28.074 | 1797.8 | 4.679 | 4.696 | -0.017029 | 28.1762 | 6.4 | 4.6289 | 1.7711 |  | 16-03-2026 17:30 | 27.567 | 28.52 | 1811.4 | 4.7533 | 4.696 | 0.057304 | 28.1762 | 6.5 | 4.6289 | 1.8711 |  | 16-03-2026 17:30 | 25.945 | 26.512 | 1711.7 | 4.4187 | 4.4677 | -0.049024 | 26.8061 | 6.1 | 4.4038 | 1.6962 |  | 16-03-2026 17:30 | 48.9322 | 48.6104 | 0.3218 | 291.6622 | 66.9 | 47.9152 | 18.9848
16-03-2026 17:20 | 195 | 48.22 | 70.623 | 71.56 | 2401.7 | 11.9267 | 11.6368 | 0.28983 | 69.821 | 11.6 | 11.4704 | 0.12957 |  | 16-03-2026 17:20 | 73.605 | 74.605 | 2419.4 | 12.4342 | 11.6368 | 0.79733 | 69.821 | 12.2 | 11.4704 | 0.72957 |  | 16-03-2026 17:20 | 69.232 | 70.179 | 2389.9 | 11.6965 | 11.6368 | 0.059668 | 69.821 | 12 | 11.4704 | 0.52957 |  | 16-03-2026 17:20 | 69.128 | 70.088 | 2400 | 11.6813 | 11.6368 | 0.044501 | 69.821 | 11.9 | 11.4704 | 0.42957 |  | 16-03-2026 17:20 | 51.68 | 52.504 | 1810.5 | 8.7507 | 8.6199 | 0.13079 | 51.7193 | 8.8 | 8.4966 | 0.30339 |  | 16-03-2026 17:20 | 50.58 | 51.376 | 1791.3 | 8.5627 | 8.6199 | -0.057209 | 51.7193 | 8.7 | 8.4966 | 0.20339 |  | 16-03-2026 17:20 | 50.754 | 51.553 | 1791.4 | 8.5922 | 8.6199 | -0.027709 | 51.7193 | 8.6 | 8.4966 | 0.10339 |  | 16-03-2026 17:20 | 50.881 | 52.173 | 1804.9 | 8.6955 | 8.6199 | 0.075624 | 51.7193 | 8.6 | 8.4966 | 0.10339 |  | 16-03-2026 17:20 | 47.982 | 48.786 | 1705.6 | 8.131 | 8.2007 | -0.069744 | 49.2045 | 8.1 | 8.0835 | 0.016526 |  | 16-03-2026 17:20 | 90.4707 | 89.2276 | 1.2431 | 535.3655 | 90.5 | 87.9516 | 2.5484
16-03-2026 17:10 | 159 | 48.22 | 54.444 | 55.296 | 2390.1 | 9.216 | 9.4885 | -0.27249 | 56.931 | 17 | 9.3528 | 7.6472 |  | 16-03-2026 17:10 | 56.102 | 56.997 | 2407.2 | 9.4995 | 9.4885 | 0.011006 | 56.931 | 16.4 | 9.3528 | 7.0472 |  | 16-03-2026 17:10 | 55.307 | 56.2 | 2377.9 | 9.3667 | 9.4885 | -0.12183 | 56.931 | 16.3 | 9.3528 | 6.9472 |  | 16-03-2026 17:10 | 55.407 | 56.291 | 2388.1 | 9.3818 | 9.4885 | -0.10666 | 56.931 | 16.3 | 9.3528 | 6.9472 |  | 16-03-2026 17:10 | 41.041 | 41.776 | 1801.7 | 6.9627 | 7.0285 | -0.065848 | 42.1711 | 12.2 | 6.928 | 5.272 |  | 16-03-2026 17:10 | 40.49 | 41.18 | 1782.6 | 6.8633 | 7.0285 | -0.16518 | 42.1711 | 11.8 | 6.928 | 4.872 |  | 16-03-2026 17:10 | 40.414 | 41.134 | 1782.8 | 6.8557 | 7.0285 | -0.17285 | 42.1711 | 11.9 | 6.928 | 4.972 |  | 16-03-2026 17:10 | 40.637 | 41.828 | 1796.3 | 6.9713 | 7.0285 | -0.057181 | 42.1711 | 12.1 | 6.928 | 5.172 |  | 16-03-2026 17:10 | 38.418 | 39.106 | 1697.5 | 6.5177 | 6.6868 | -0.16909 | 40.1206 | 11.4 | 6.5911 | 4.8089 |  | 16-03-2026 17:10 | 71.6347 | 72.7548 | -1.1201 | 436.5288 | 125.4 | 71.7144 | 53.6856
16-03-2026 17:00 | 350 | 48.22 | 121.458 | 122.958 | 2373.1 | 20.493 | 20.8866 | -0.39362 | 125.3197 | 19.4 | 20.5879 | -1.1879 |  | 16-03-2026 17:00 | 123.008 | 124.402 | 2390.8 | 20.7337 | 20.8866 | -0.15296 | 125.3197 | 20.9 | 20.5879 | 0.31206 |  | 16-03-2026 17:00 | 122.236 | 124.74 | 2361.6 | 20.79 | 20.8866 | -0.096622 | 125.3197 | 20.5 | 20.5879 | -0.087944 |  | 16-03-2026 17:00 | 122.049 | 123.594 | 2371.8 | 20.599 | 20.8866 | -0.28762 | 125.3197 | 20.7 | 20.5879 | 0.11206 |  | 16-03-2026 17:00 | 91.282 | 92.356 | 1789.5 | 15.3927 | 15.4716 | -0.078905 | 92.8294 | 15.4 | 15.2503 | 0.14967 |  | 16-03-2026 17:00 | 89.25 | 90.371 | 1770.8 | 15.0618 | 15.4716 | -0.40974 | 92.8294 | 15.1 | 15.2503 | -0.15033 |  | 16-03-2026 17:00 | 89.499 | 90.614 | 1770.9 | 15.1023 | 15.4716 | -0.36924 | 92.8294 | 15.1 | 15.2503 | -0.15033 |  | 16-03-2026 17:00 | 89.022 | 91.486 | 1784.2 | 15.2477 | 15.4716 | -0.22391 | 92.8294 | 15.1 | 15.2503 | -0.15033 |  | 16-03-2026 17:00 | 84.093 | 85.192 | 1686.1 | 14.1987 | 14.7193 | -0.52062 | 88.3157 | 14.1 | 14.5088 | -0.4088 |  | 16-03-2026 17:00 | 157.6188 | 160.1521 | -2.5332 | 960.9124 | 156.3 | 157.8619 | -1.5619
16-03-2026 16:50 | 382 | 48.22 | 131.79 | 133.445 | 2353.7 | 22.2408 | 22.7963 | -0.55542 | 136.7775 | 54.8 | 22.4703 | 32.3297 |  | 16-03-2026 16:50 | 131.51 | 136.295 | 2369.9 | 22.7158 | 22.7963 | -0.080423 | 136.7775 | 25.5 | 22.4703 | 3.0297 |  | 16-03-2026 16:50 | 132.83 | 135.113 | 2341.1 | 22.5188 | 22.7963 | -0.27742 | 136.7775 | 25.2 | 22.4703 | 2.7297 |  | 16-03-2026 16:50 | 133.434 | 135.15 | 2351.1 | 22.525 | 22.7963 | -0.27126 | 136.7775 | 25 | 22.4703 | 2.5297 |  | 16-03-2026 16:50 | 99.728 | 100.99 | 1774.1 | 16.8317 | 16.8861 | -0.054449 | 101.3167 | 18.7 | 16.6446 | 2.0554 |  | 16-03-2026 16:50 | 97.455 | 98.659 | 1755.7 | 16.4432 | 16.8861 | -0.44295 | 101.3167 | 18.3 | 16.6446 | 1.6554 |  | 16-03-2026 16:50 | 97.388 | 98.611 | 1755.8 | 16.4352 | 16.8861 | -0.45095 | 101.3167 | 18.3 | 16.6446 | 1.6554 |  | 16-03-2026 16:50 | 97.216 | 99.892 | 1769.1 | 16.6487 | 16.8861 | -0.23745 | 101.3167 | 18 | 16.6446 | 1.3554 |  | 16-03-2026 16:50 | 92.069 | 93.234 | 1672 | 15.539 | 16.065 | -0.52605 | 96.3903 | 17.2 | 15.8353 | 1.3647 |  | 16-03-2026 16:50 | 171.8982 | 174.7945 | -2.8964 | 1048.7672 | 221 | 172.295 | 48.705
16-03-2026 16:40 | 471 | 48.22 | 166.313 | 168.469 | 2328.6 | 28.0782 | 28.1074 | -0.029259 | 168.6446 | 0 | 27.7055 | -27.7055 |  | 16-03-2026 16:40 | 168.413 | 170.824 | 2344.4 | 28.4707 | 28.1074 | 0.36324 | 168.6446 | 29.3 | 27.7055 | 1.5945 |  | 16-03-2026 16:40 | 164.054 | 167.329 | 2315.9 | 27.8882 | 28.1074 | -0.21926 | 168.6446 | 29.3 | 27.7055 | 1.5945 |  | 16-03-2026 16:40 | 165.003 | 167.193 | 2326.1 | 27.8655 | 28.1074 | -0.24193 | 168.6446 | 29.4 | 27.7055 | 1.6945 |  | 16-03-2026 16:40 | 122.877 | 124.47 | 1755.4 | 20.745 | 20.8203 | -0.075316 | 124.9219 | 22 | 20.5226 | 1.4774 |  | 16-03-2026 16:40 | 119.897 | 121.427 | 1737.4 | 20.2378 | 20.8203 | -0.58248 | 124.9219 | 21.5 | 20.5226 | 0.97741 |  | 16-03-2026 16:40 | 119.225 | 120.746 | 1737.5 | 20.1243 | 20.8203 | -0.69598 | 124.9219 | 21.8 | 20.5226 | 1.2774 |  | 16-03-2026 16:40 | 118.686 | 121.935 | 1751.1 | 20.3225 | 20.8203 | -0.49782 | 124.9219 | 21.9 | 20.5226 | 1.3774 |  | 16-03-2026 16:40 | 112.422 | 113.868 | 1654.8 | 18.978 | 19.808 | -0.82995 | 118.8477 | 20.7 | 19.5247 | 1.1753 |  | 16-03-2026 16:40 | 212.7102 | 215.5189 | -2.8088 | 1293.1135 | 195.9 | 212.437 | -16.537
16-03-2026 16:30 | 528 | 48.22 | 183.377 | 185.811 | 2298.9 | 30.9685 | 31.509 | -0.54046 | 189.0538 | 31.1 | 31.0584 | 0.041616 |  | 16-03-2026 16:30 | 0 | 0 | 2315.1 | 0 | 31.509 | -31.509 | 189.0538 | 32.3 | 31.0584 | 1.2416 |  | 16-03-2026 16:30 | 184.032 | 187.825 | 2286.6 | 31.3042 | 31.509 | -0.2048 | 189.0538 | 31.6 | 31.0584 | 0.54162 |  | 16-03-2026 16:30 | 184.623 | 187.131 | 2296.7 | 31.1885 | 31.509 | -0.32046 | 189.0538 | 31.6 | 31.0584 | 0.54162 |  | 16-03-2026 16:30 | 138.652 | 140.436 | 1733.4 | 23.406 | 23.34 | 0.066028 | 140.0398 | 24.1 | 23.0062 | 1.0938 |  | 16-03-2026 16:30 | 135.489 | 137.224 | 1715.9 | 22.8707 | 23.34 | -0.46931 | 140.0398 | 23.3 | 23.0062 | 0.29379 |  | 16-03-2026 16:30 | 135.796 | 137.543 | 1715.7 | 22.9238 | 23.34 | -0.41614 | 140.0398 | 23.1 | 23.0062 | 0.09379 |  | 16-03-2026 16:30 | 135.843 | 139.674 | 1729.2 | 23.279 | 23.34 | -0.060972 | 140.0398 | 23.1 | 23.0062 | 0.09379 |  | 16-03-2026 16:30 | 128.107 | 129.781 | 1634.1 | 21.6302 | 22.2051 | -0.57493 | 133.2306 | 22 | 21.8876 | 0.11244 |  | 16-03-2026 16:30 | 207.5708 | 241.6008 | -34.03 | 1449.605 | 242.2 | 238.1459 | 4.0541
16-03-2026 16:20 | 414 | 48.5 | 162.807 | 165.583 | 2267.8 | 27.5972 | 24.6795 | 2.9176 | 148.0772 | 32.5 | 24.3266 | 8.1734 |  | 16-03-2026 16:20 | 144.18 | 146.123 | 2282.8 | 24.3538 | 24.6795 | -0.3257 | 148.0772 | 32.4 | 24.3266 | 8.0734 |  | 16-03-2026 16:20 | 154.44 | 156.49 | 2255 | 26.0817 | 24.6795 | 1.4021 | 148.0772 | 32.1 | 24.3266 | 7.7734 |  | 16-03-2026 16:20 | 145.465 | 147.441 | 2265.1 | 24.5735 | 24.6795 | -0.10604 | 148.0772 | 32.1 | 24.3266 | 7.7734 |  | 16-03-2026 16:20 | 121.721 | 123.299 | 1709.3 | 20.5498 | 18.2811 | 2.2687 | 109.6868 | 23.8 | 18.0197 | 5.7803 |  | 16-03-2026 16:20 | 105.687 | 107.462 | 1692.6 | 17.9103 | 18.2811 | -0.37081 | 109.6868 | 23.4 | 18.0197 | 5.3803 |  | 16-03-2026 16:20 | 109.735 | 112.905 | 1692.6 | 18.8175 | 18.2811 | 0.53636 | 109.6868 | 23.5 | 18.0197 | 5.4803 |  | 16-03-2026 16:20 | 112.745 | 116.755 | 1706.1 | 19.4592 | 18.2811 | 1.178 | 109.6868 | 23.5 | 18.0197 | 5.4803 |  | 16-03-2026 16:20 | 101.257 | 102.591 | 1612.1 | 17.0985 | 17.3922 | -0.29374 | 104.3534 | 22.2 | 17.1435 | 5.0565 |  | 16-03-2026 16:20 | 196.4415 | 189.2349 | 7.2066 | 1135.4096 | 245.5 | 186.5289 | 58.9711
16-03-2026 16:10 | 618 | 48.5 | 214.727 | 217.732 | 2235.3 | 36.2887 | 36.8405 | -0.5518 | 221.0428 | 36.3 | 36.3136 | -0.01365 |  | 16-03-2026 16:10 | 221.887 | 225.083 | 2250.4 | 37.5138 | 36.8405 | 0.67337 | 221.0428 | 36.9 | 36.3136 | 0.58635 |  | 16-03-2026 16:10 | 213.667 | 218.468 | 2222.9 | 36.4113 | 36.8405 | -0.42913 | 221.0428 | 36.8 | 36.3136 | 0.48635 |  | 16-03-2026 16:10 | 215.581 | 218.642 | 2233 | 36.4403 | 36.8405 | -0.40013 | 221.0428 | 36.9 | 36.3136 | 0.58635 |  | 16-03-2026 16:10 | 160.82 | 162.955 | 1685.5 | 27.1592 | 27.2892 | -0.13007 | 163.7354 | 27.7 | 26.899 | 0.801 |  | 16-03-2026 16:10 | 157.792 | 160.029 | 1669.2 | 26.6715 | 27.2892 | -0.61774 | 163.7354 | 27.6 | 26.899 | 0.701 |  | 16-03-2026 16:10 | 157.772 | 159.882 | 1669.1 | 26.647 | 27.2892 | -0.64224 | 163.7354 | 27.6 | 26.899 | 0.701 |  | 16-03-2026 16:10 | 160.325 | 163.101 | 1682.6 | 27.1835 | 27.2892 | -0.10574 | 163.7354 | 27.7 | 26.899 | 0.801 |  | 16-03-2026 16:10 | 151.214 | 153.252 | 1589.9 | 25.542 | 25.9623 | -0.42033 | 155.774 | 26.1 | 25.5911 | 0.50893 |  | 16-03-2026 16:10 | 279.8573 | 282.4811 | -2.6238 | 1694.8869 | 283.6 | 278.4417 | 5.1583
16-03-2026 16:00 | 599 | 48.22 | 202.227 | 210.239 | 2199 | 35.0398 | 35.746 | -0.70613 | 214.4758 | 33.1 | 35.2348 | -2.1348 |  | 16-03-2026 16:00 | 211.504 | 214.507 | 2213.5 | 35.7512 | 35.746 | 0.0052043 | 214.4758 | 34.6 | 35.2348 | -0.6348 |  | 16-03-2026 16:00 | 209.985 | 215.006 | 2186.1 | 35.8343 | 35.746 | 0.088371 | 214.4758 | 33.2 | 35.2348 | -2.0348 |  | 16-03-2026 16:00 | 211.396 | 214.419 | 2196.1 | 35.7365 | 35.746 | -0.0094623 | 214.4758 | 34 | 35.2348 | -1.2348 |  | 16-03-2026 16:00 | 159.123 | 161.252 | 1657.8 | 26.8753 | 26.4785 | 0.39684 | 158.8709 | 25.4 | 26.0998 | -0.69985 |  | 16-03-2026 16:00 | 152.571 | 155.133 | 1641.6 | 25.8555 | 26.4785 | -0.62299 | 158.8709 | 24.5 | 26.0998 | -1.5998 |  | 16-03-2026 16:00 | 153.743 | 156.245 | 1641.5 | 26.0408 | 26.4785 | -0.43766 | 158.8709 | 24.6 | 26.0998 | -1.4998 |  | 16-03-2026 16:00 | 155.231 | 159.792 | 1654.9 | 26.632 | 26.4785 | 0.15351 | 158.8709 | 24.6 | 26.0998 | -1.4998 |  | 16-03-2026 16:00 | 143.197 | 144.77 | 1563.8 | 24.1283 | 25.191 | -1.0627 | 151.146 | 23 | 24.8308 | -1.8308 |  | 16-03-2026 16:00 | 271.8938 | 274.0888 | -2.195 | 1644.5329 | 257 | 270.1693 | -13.1693
16-03-2026 15:50 | 629 | 48.22 | 211.495 | 220.306 | 2165.9 | 36.7177 | 37.5362 | -0.81858 | 225.2175 | 36.4 | 36.9995 | -0.59948 |  | 16-03-2026 15:50 | 220.533 | 223.71 | 2178.9 | 37.285 | 37.5362 | -0.25124 | 225.2175 | 37.3 | 36.9995 | 0.30052 |  | 16-03-2026 15:50 | 215.342 | 220.281 | 2152.9 | 36.7135 | 37.5362 | -0.82274 | 225.2175 | 36.4 | 36.9995 | -0.59948 |  | 16-03-2026 15:50 | 227.455 | 230.802 | 2162.1 | 38.467 | 37.5362 | 0.93076 | 225.2175 | 36.1 | 36.9995 | -0.89948 |  | 16-03-2026 15:50 | 164.922 | 167.885 | 1632.4 | 27.9808 | 27.8046 | 0.17621 | 166.8278 | 27 | 27.407 | -0.40702 |  | 16-03-2026 15:50 | 164.326 | 166.592 | 1617.1 | 27.7653 | 27.8046 | -0.039292 | 166.8278 | 26.6 | 27.407 | -0.80702 |  | 16-03-2026 15:50 | 160.843 | 163.028 | 1616.9 | 27.1713 | 27.8046 | -0.63329 | 166.8278 | 26.6 | 27.407 | -0.80702 |  | 16-03-2026 15:50 | 161.14 | 165.475 | 1630.3 | 27.5792 | 27.8046 | -0.22546 | 166.8278 | 26.8 | 27.407 | -0.60702 |  | 16-03-2026 15:50 | 152.79 | 154.881 | 1540.8 | 25.8135 | 26.4527 | -0.63916 | 158.7159 | 25.5 | 26.0744 | -0.57438 |  | 16-03-2026 15:50 | 285.4933 | 287.8161 | -2.3228 | 1726.8968 | 278.7 | 283.7004 | -5.0004
16-03-2026 15:40 | 534 | 47.93 | 196.837 | 199.551 | 2129.5 | 33.2585 | 31.9022 | 1.3563 | 191.4133 | 35.4 | 31.446 | 3.954 |  | 16-03-2026 15:40 | 232.673 | 236.12 | 2141.6 | 39.3533 | 31.9022 | 7.4511 | 191.4133 | 34.2 | 31.446 | 2.754 |  | 16-03-2026 15:40 | 192.928 | 197.197 | 2116.5 | 32.8662 | 31.9022 | 0.96394 | 191.4133 | 35 | 31.446 | 3.554 |  | 16-03-2026 15:40 | 190.127 | 192.827 | 2126 | 32.1378 | 31.9022 | 0.23561 | 191.4133 | 35.3 | 31.446 | 3.854 |  | 16-03-2026 15:40 | 142.687 | 144.625 | 1605.4 | 24.1042 | 23.6313 | 0.47289 | 141.7877 | 26.4 | 23.2934 | 3.1066 |  | 16-03-2026 15:40 | 138.053 | 140.173 | 1590.5 | 23.3622 | 23.6313 | -0.26911 | 141.7877 | 26 | 23.2934 | 2.7066 |  | 16-03-2026 15:40 | 139.802 | 141.77 | 1590.3 | 23.6283 | 23.6313 | -0.002944 | 141.7877 | 25.9 | 23.2934 | 2.6066 |  | 16-03-2026 15:40 | 140.372 | 144.479 | 1603.5 | 24.0798 | 23.6313 | 0.44856 | 141.7877 | 26.3 | 23.2934 | 3.0066 |  | 16-03-2026 15:40 | 132.542 | 134.342 | 1515.3 | 22.3903 | 22.4822 | -0.0919 | 134.8934 | 24.7 | 22.1607 | 2.5393 |  | 16-03-2026 15:40 | 255.1807 | 244.6162 | 10.5644 | 1467.6974 | 269.2 | 241.1182 | 28.0818
16-03-2026 15:30 | 409 | 47.64 | 145.848 | 147.784 | 2094.1 | 24.6307 | 24.4614 | 0.16923 | 146.7686 | 27.6 | 24.1116 | 3.4884 |  | 16-03-2026 15:30 | 149.013 | 148.465 | 2107.4 | 24.7442 | 24.4614 | 0.28273 | 146.7686 | 27.6 | 24.1116 | 3.4884 |  | 16-03-2026 15:30 | 147.439 | 150.549 | 2081.5 | 25.0915 | 24.4614 | 0.63006 | 146.7686 | 27.1 | 24.1116 | 2.9884 |  | 16-03-2026 15:30 | 146.579 | 148.57 | 2090.7 | 24.7617 | 24.4614 | 0.30023 | 146.7686 | 27.2 | 24.1116 | 3.0884 |  | 16-03-2026 15:30 | 110.729 | 112.187 | 1579 | 18.6978 | 18.1196 | 0.57825 | 108.7175 | 20.2 | 17.8605 | 2.3395 |  | 16-03-2026 15:30 | 108.009 | 109.458 | 1564.5 | 18.243 | 18.1196 | 0.12341 | 108.7175 | 20 | 17.8605 | 2.1395 |  | 16-03-2026 15:30 | 109.892 | 111.638 | 1564.4 | 18.6063 | 18.1196 | 0.48675 | 108.7175 | 20.3 | 17.8605 | 2.4395 |  | 16-03-2026 15:30 | 108.14 | 111.021 | 1577.2 | 18.5035 | 18.1196 | 0.38391 | 108.7175 | 20.1 | 17.8605 | 2.2395 |  | 16-03-2026 15:30 | 101.552 | 102.9 | 1490.6 | 17.15 | 17.2385 | -0.088541 | 103.4312 | 19 | 16.992 | 2.008 |  | 16-03-2026 15:30 | 190.4287 | 187.5626 | 2.866 | 1125.3759 | 209.1 | 184.8805 | 24.2195
16-03-2026 15:20 | 540 | 48.5 | 212.515 | 215.576 | 2066.5 | 35.9293 | 32.1907 | 3.7386 | 193.1442 | 47 | 31.7304 | 15.2696 |  | 16-03-2026 15:20 | 229.133 | 232.622 | 2079.8 | 38.7703 | 32.1907 | 6.5796 | 193.1442 | 47.3 | 31.7304 | 15.5696 |  | 16-03-2026 15:20 | 186.498 | 190.786 | 2054.4 | 31.7977 | 32.1907 | -0.39303 | 193.1442 | 45.8 | 31.7304 | 14.0696 |  | 16-03-2026 15:20 | 184.895 | 187.577 | 2063.5 | 31.2628 | 32.1907 | -0.92787 | 193.1442 | 46.3 | 31.7304 | 14.5696 |  | 16-03-2026 15:20 | 137.769 | 139.668 | 1558.8 | 23.278 | 23.845 | -0.56696 | 143.0698 | 34.6 | 23.504 | 11.096 |  | 16-03-2026 15:20 | 134.043 | 135.905 | 1544.5 | 22.6508 | 23.845 | -1.1941 | 143.0698 | 34 | 23.504 | 10.496 |  | 16-03-2026 15:20 | 138.17 | 140.629 | 1544.1 | 23.4382 | 23.845 | -0.4068 | 143.0698 | 33.6 | 23.504 | 10.096 |  | 16-03-2026 15:20 | 137.368 | 140.172 | 1557.1 | 23.362 | 23.845 | -0.48296 | 143.0698 | 33.8 | 23.504 | 10.296 |  | 16-03-2026 15:20 | 128.87 | 130.673 | 1471.6 | 21.7788 | 22.6855 | -0.9067 | 136.1132 | 32.2 | 22.3611 | 9.8389 |  | 16-03-2026 15:20 | 252.268 | 246.8282 | 5.4398 | 1480.9691 | 354.6 | 243.2985 | 111.3015
16-03-2026 15:10 | 878 | 48.5 | 286.77 | 292.674 | 2019.5 | 48.779 | 52.3397 | -3.5607 | 314.0382 | 45.3 | 51.5912 | -6.2912 |  | 16-03-2026 15:10 | 301.712 | 306.68 | 2032.5 | 51.1133 | 52.3397 | -1.2264 | 314.0382 | 46 | 51.5912 | -5.5912 |  | 16-03-2026 15:10 | 296.449 | 305.053 | 2008.6 | 50.8422 | 52.3397 | -1.4975 | 314.0382 | 45.3 | 51.5912 | -6.2912 |  | 16-03-2026 15:10 | 299.029 | 303.953 | 2017.2 | 50.6588 | 52.3397 | -1.6809 | 314.0382 | 45.6 | 51.5912 | -5.9912 |  | 16-03-2026 15:10 | 223.82 | 227.547 | 1524.2 | 37.9245 | 38.7701 | -0.84564 | 232.6209 | 34.1 | 38.2157 | -4.1157 |  | 16-03-2026 15:10 | 222.135 | 226.27 | 1510.5 | 37.7117 | 38.7701 | -1.0585 | 232.6209 | 33.5 | 38.2157 | -4.7157 |  | 16-03-2026 15:10 | 220.867 | 224.812 | 1510.5 | 37.4687 | 38.7701 | -1.3015 | 232.6209 | 33.5 | 38.2157 | -4.7157 |  | 16-03-2026 15:10 | 222.93 | 229.366 | 1523.3 | 38.2277 | 38.7701 | -0.54248 | 232.6209 | 34.2 | 38.2157 | -4.0157 |  | 16-03-2026 15:10 | 210.188 | 213.324 | 1439.4 | 35.554 | 36.885 | -1.331 | 221.3099 | 31.9 | 36.3575 | -4.4575 |  | 16-03-2026 15:10 | 388.2798 | 401.3243 | -13.0445 | 2407.9461 | 349.4 | 395.5854 | -46.1854
16-03-2026 15:00 | 896 | 49.08 | 305.238 | 310.233 | 1974.2 | 51.7055 | 53.2946 | -1.5891 | 319.7674 | 48.4 | 52.5325 | -4.1325 | 0.9839 | 16-03-2026 15:00 | 312.399 | 317.64 | 1986.5 | 52.94 | 53.2946 | -0.35457 | 319.7674 | 50.8 | 52.5325 | -1.7325 | 0.9835 | 16-03-2026 15:00 | 300.67 | 308.829 | 1963.3 | 51.4715 | 53.2946 | -1.8231 | 319.7674 | 49.9 | 52.5325 | -2.6325 | 0.97358 | 16-03-2026 15:00 | 304.348 | 309.423 | 1971.6 | 51.5705 | 53.2946 | -1.7241 | 319.7674 | 50.7 | 52.5325 | -1.8325 | 0.9836 | 16-03-2026 15:00 | 226.544 | 229.994 | 1490.1 | 38.3323 | 39.4775 | -1.1451 | 236.8648 | 37.7 | 38.9129 | -1.2129 | 0.985 | 16-03-2026 15:00 | 222.993 | 227.398 | 1477 | 37.8997 | 39.4775 | -1.5778 | 236.8648 | 37.1 | 38.9129 | -1.8129 | 0.98063 | 16-03-2026 15:00 | 223.097 | 227.266 | 1477 | 37.8777 | 39.4775 | -1.5998 | 236.8648 | 37.1 | 38.9129 | -1.8129 | 0.98166 | 16-03-2026 15:00 | 224.655 | 231.354 | 1489.1 | 38.559 | 39.4775 | -0.91846 | 236.8648 | 36.7 | 38.9129 | -2.2129 | 0.97104 | 16-03-2026 15:00 | 212.355 | 215.545 | 1407.5 | 35.9242 | 37.5579 | -1.6337 | 225.3475 | 35.1 | 37.0208 | -1.9208 | 0.9852 | 16-03-2026 15:00 | 396.2803 | 408.646 | -12.3657 | 2451.8763 | 383.5 | 402.8024 | -19.3024
16-03-2026 14:50 | 800 | 49.08 | 271.17 | 275.551 | 1925.8 | 45.9252 | 47.5844 | -1.6593 | 285.5066 | 50.8 | 46.904 | 3.896 | 0.9841 | 16-03-2026 14:50 | 281.639 | 287.222 | 1935.7 | 47.8703 | 47.5844 | 0.28589 | 285.5066 | 50.9 | 46.904 | 3.996 | 0.98056 | 16-03-2026 14:50 | 270.332 | 278.019 | 1913.4 | 46.3365 | 47.5844 | -1.2479 | 285.5066 | 50.6 | 46.904 | 3.696 | 0.97235 | 16-03-2026 14:50 | 271.172 | 275.581 | 1920.9 | 45.9302 | 47.5844 | -1.6543 | 285.5066 | 50.3 | 46.904 | 3.396 | 0.984 | 16-03-2026 14:50 | 205.047 | 207.575 | 1452.4 | 34.5958 | 35.2477 | -0.6519 | 211.4864 | 38.7 | 34.7437 | 3.9563 | 0.98782 | 16-03-2026 14:50 | 200.608 | 204.607 | 1439.9 | 34.1012 | 35.2477 | -1.1466 | 211.4864 | 37.4 | 34.7437 | 2.6563 | 0.98046 | 16-03-2026 14:50 | 202.348 | 206.535 | 1439.9 | 34.4225 | 35.2477 | -0.82523 | 211.4864 | 37.6 | 34.7437 | 2.8563 | 0.97973 | 16-03-2026 14:50 | 204.032 | 210.071 | 1452.4 | 35.0118 | 35.2477 | -0.2359 | 211.4864 | 37.8 | 34.7437 | 3.0563 | 0.97125 | 16-03-2026 14:50 | 189.23 | 192.014 | 1372.4 | 32.0023 | 33.5339 | -1.5315 | 201.2031 | 35.7 | 33.0543 | 2.6457 | 0.9855 | 16-03-2026 14:50 | 356.1958 | 364.8625 | -8.6667 | 2189.1753 | 389.8 | 359.645 | 30.155
16-03-2026 14:40 | 935 | 49.08 | 312.21 | 317.448 | 1875 | 52.908 | 55.6143 | -2.7063 | 333.6859 | 53.6 | 54.819 | -1.219 | 0.9835 | 16-03-2026 14:40 | 317.755 | 323.185 | 1884.8 | 53.8642 | 55.6143 | -1.7501 | 333.6859 | 53.6 | 54.819 | -1.219 | 0.9832 | 16-03-2026 14:40 | 313.478 | 322.471 | 1862.8 | 53.7452 | 55.6143 | -1.8691 | 333.6859 | 52.5 | 54.819 | -2.319 | 0.97211 | 16-03-2026 14:40 | 315.399 | 320.715 | 1870.6 | 53.4525 | 55.6143 | -2.1618 | 333.6859 | 53.9 | 54.819 | -0.91903 | 0.98342 | 16-03-2026 14:40 | 236.539 | 241.646 | 1413.7 | 40.2743 | 41.1958 | -0.92145 | 247.1747 | 39.8 | 40.6067 | -0.80669 | 0.97887 | 16-03-2026 14:40 | 232.795 | 237.427 | 1402.5 | 39.5712 | 41.1958 | -1.6246 | 247.1747 | 39.6 | 40.6067 | -1.0067 | 0.98049 | 16-03-2026 14:40 | 235.334 | 240.12 | 1402.3 | 40.02 | 41.1958 | -1.1758 | 247.1747 | 39.6 | 40.6067 | -1.0067 | 0.98007 | 16-03-2026 14:40 | 236.639 | 243.695 | 1414.6 | 40.6158 | 41.1958 | -0.57995 | 247.1747 | 40 | 40.6067 | -0.60669 | 0.97105 | 16-03-2026 14:40 | 220.758 | 224.143 | 1336.7 | 37.3572 | 39.1927 | -1.8355 | 235.1561 | 37.3 | 38.6322 | -1.3322 | 0.9849 | 16-03-2026 14:40 | 411.8083 | 426.4331 | -14.6248 | 2558.5986 | 409.9 | 420.3351 | -10.4351
16-03-2026 14:30 | 972 | 49.36 | 323.329 | 328.753 | 1821.4 | 54.7922 | 57.7532 | -2.9611 | 346.5193 | 52.7 | 56.9273 | -4.2273 | 0.9835 | 16-03-2026 14:30 | 328.351 | 334.03 | 1831.2 | 55.6717 | 57.7532 | -2.0816 | 346.5193 | 56 | 56.9273 | -0.92735 | 0.983 | 16-03-2026 14:30 | 322.956 | 332.476 | 1810.3 | 55.4127 | 57.7532 | -2.3406 | 346.5193 | 53.6 | 56.9273 | -3.3273 | 0.97137 | 16-03-2026 14:30 | 325.93 | 331.567 | 1816.7 | 55.2612 | 57.7532 | -2.4921 | 346.5193 | 53.1 | 56.9273 | -3.8273 | 0.983 | 16-03-2026 14:30 | 244.563 | 248.388 | 1373.9 | 41.398 | 42.7802 | -1.3822 | 256.681 | 39.9 | 42.1684 | -2.2684 | 0.9846 | 16-03-2026 14:30 | 239.585 | 244.116 | 1362.9 | 40.686 | 42.7802 | -2.0942 | 256.681 | 39.7 | 42.1684 | -2.4684 | 0.98144 | 16-03-2026 14:30 | 240.641 | 245.442 | 1362.7 | 40.907 | 42.7802 | -1.8732 | 256.681 | 39.9 | 42.1684 | -2.2684 | 0.98044 | 16-03-2026 14:30 | 242.059 | 249.336 | 1374.6 | 41.556 | 42.7802 | -1.2242 | 256.681 | 40.1 | 42.1684 | -2.0684 | 0.97081 | 16-03-2026 14:30 | 227.754 | 231.269 | 1299.4 | 38.5448 | 40.7 | -2.1552 | 244.2002 | 37.7 | 40.118 | -2.418 | 0.9848 | 16-03-2026 14:30 | 424.2295 | 442.8336 | -18.6041 | 2657.0014 | 412.7 | 436.501 | -23.801
16-03-2026 14:20 | 973 | 49.36 | 323.159 | 328.591 | 1768.7 | 54.7652 | 57.8126 | -3.0475 | 346.8758 | 54.2 | 56.9859 | -2.7859 | 0.98347 | 16-03-2026 14:20 | 327.416 | 333.146 | 1775.2 | 55.5243 | 57.8126 | -2.2883 | 346.8758 | 54.8 | 56.9859 | -2.1859 | 0.9828 | 16-03-2026 14:20 | 321.412 | 330.649 | 1756.7 | 55.1082 | 57.8126 | -2.7045 | 346.8758 | 54.2 | 56.9859 | -2.7859 | 0.97206 | 16-03-2026 14:20 | 324.35 | 330.026 | 1763.6 | 55.0043 | 57.8126 | -2.8083 | 346.8758 | 55.2 | 56.9859 | -1.7859 | 0.9828 | 16-03-2026 14:20 | 243.666 | 247.502 | 1334 | 41.2503 | 42.8242 | -1.5738 | 256.9451 | 41.6 | 42.2118 | -0.61179 | 0.9845 | 16-03-2026 14:20 | 239.389 | 244.048 | 1323.2 | 40.6747 | 42.8242 | -2.1495 | 256.9451 | 40.3 | 42.2118 | -1.9118 | 0.98091 | 16-03-2026 14:20 | 240.694 | 245.1 | 1322.8 | 40.85 | 42.8242 | -1.9742 | 256.9451 | 40.5 | 42.2118 | -1.7118 | 0.98202 | 16-03-2026 14:20 | 242.281 | 249.372 | 1334.5 | 41.562 | 42.8242 | -1.2622 | 256.9451 | 40.8 | 42.2118 | -1.4118 | 0.97156 | 16-03-2026 14:20 | 227.8 | 231.34 | 1261.7 | 38.5567 | 40.7419 | -2.1852 | 244.4514 | 38.3 | 40.1593 | -1.8593 | 0.9847 | 16-03-2026 14:20 | 423.2957 | 443.2892 | -19.9935 | 2659.7349 | 419.9 | 436.9501 | -17.0501
16-03-2026 14:10 | 969 | 49.36 | 321.604 | 327.099 | 1714.5 | 54.5165 | 57.575 | -3.0585 | 345.4498 | 54.2 | 56.7516 | -2.5516 | 0.9832 | 16-03-2026 14:10 | 327.355 | 333.084 | 1720.4 | 55.514 | 57.575 | -2.061 | 345.4498 | 55.8 | 56.7516 | -0.95165 | 0.9828 | 16-03-2026 14:10 | 320.638 | 329.725 | 1702.5 | 54.9542 | 57.575 | -2.6208 | 345.4498 | 53.9 | 56.7516 | -2.8516 | 0.97244 | 16-03-2026 14:10 | 323.652 | 329.283 | 1708.4 | 54.8805 | 57.575 | -2.6945 | 345.4498 | 53.7 | 56.7516 | -3.0516 | 0.9829 | 16-03-2026 14:10 | 242.463 | 246.28 | 1292.4 | 41.0467 | 42.6481 | -1.6015 | 255.8888 | 40.2 | 42.0383 | -1.8383 | 0.9845 | 16-03-2026 14:10 | 238.378 | 242.764 | 1282.9 | 40.4607 | 42.6481 | -2.1875 | 255.8888 | 39.6 | 42.0383 | -2.4383 | 0.98193 | 16-03-2026 14:10 | 239.085 | 243.753 | 1282.3 | 40.6255 | 42.6481 | -2.0226 | 255.8888 | 40.1 | 42.0383 | -1.9383 | 0.98085 | 16-03-2026 14:10 | 241.376 | 248.199 | 1293.7 | 41.3665 | 42.6481 | -1.2816 | 255.8888 | 40.4 | 42.0383 | -1.6383 | 0.97251 | 16-03-2026 14:10 | 227.026 | 230.553 | 1223.4 | 38.4255 | 40.5744 | -2.1489 | 243.4465 | 38.2 | 39.9942 | -1.7942 | 0.9847 | 16-03-2026 14:10 | 421.79 | 441.4668 | -19.6768 | 2648.8008 | 416.1 | 435.1538 | -19.0538
16-03-2026 14:00 | 1005 | 49.36 | 331.112 | 336.838 | 1660.3 | 56.1397 | 59.714 | -3.5743 | 358.2839 | 57.1 | 58.8601 | -1.7601 | 0.983 | 16-03-2026 14:00 | 334.868 | 340.451 | 1664.6 | 56.7418 | 59.714 | -2.9721 | 358.2839 | 54.6 | 58.8601 | -4.2601 | 0.9836 | 16-03-2026 14:00 | 329.195 | 338.44 | 1648.6 | 56.4067 | 59.714 | -3.3073 | 358.2839 | 55.7 | 58.8601 | -3.1601 | 0.97268 | 16-03-2026 14:00 | 328.563 | 333.872 | 1654.7 | 55.6453 | 59.714 | -4.0686 | 358.2839 | 55.4 | 58.8601 | -3.4601 | 0.9841 | 16-03-2026 14:00 | 247.475 | 251.422 | 1252.2 | 41.9037 | 44.2326 | -2.3289 | 265.3955 | 42.1 | 43.6001 | -1.5001 | 0.9843 | 16-03-2026 14:00 | 245.541 | 250.327 | 1243.3 | 41.7212 | 44.2326 | -2.5114 | 265.3955 | 41.3 | 43.6001 | -2.3001 | 0.98088 | 16-03-2026 14:00 | 244.353 | 248.779 | 1242.2 | 41.4632 | 44.2326 | -2.7694 | 265.3955 | 40.9 | 43.6001 | -2.7001 | 0.98221 | 16-03-2026 14:00 | 246.757 | 253.753 | 1253.3 | 42.2922 | 44.2326 | -1.9404 | 265.3955 | 41.3 | 43.6001 | -2.3001 | 0.97243 | 16-03-2026 14:00 | 234.184 | 237.847 | 1185.2 | 39.6412 | 42.0818 | -2.4407 | 252.4909 | 38.8 | 41.48 | -2.68 | 0.9846 | 16-03-2026 14:00 | 431.9548 | 457.868 | -25.9132 | 2747.2082 | 427.2 | 451.3205 | -24.1205
16-03-2026 13:50 | 1006 | 49.65 | 332.617 | 338.369 | 1603.2 | 56.3948 | 59.7071 | -3.3122 | 358.2424 | 53.1 | 58.8533 | -5.7533 | 0.983 | 16-03-2026 13:50 | 328.82 | 334.167 | 1610 | 55.6945 | 59.7071 | -4.0126 | 358.2424 | 53.8 | 58.8533 | -5.0533 | 0.984 | 16-03-2026 13:50 | 331.693 | 341.394 | 1592.9 | 56.899 | 59.7071 | -2.8081 | 358.2424 | 55.3 | 58.8533 | -3.5533 | 0.97158 | 16-03-2026 13:50 | 324.163 | 329.3 | 1599.3 | 54.8833 | 59.7071 | -4.8237 | 358.2424 | 55.2 | 58.8533 | -3.6533 | 0.9844 | 16-03-2026 13:50 | 250.92 | 254.974 | 1210.1 | 42.4957 | 44.2275 | -1.7318 | 265.3648 | 42.3 | 43.595 | -1.295 | 0.9841 | 16-03-2026 13:50 | 247.248 | 252.303 | 1202 | 42.0505 | 44.2275 | -2.177 | 265.3648 | 41.6 | 43.595 | -1.995 | 0.97996 | 16-03-2026 13:50 | 247.533 | 252.75 | 1201.3 | 42.125 | 44.2275 | -2.1025 | 265.3648 | 41.7 | 43.595 | -1.895 | 0.97936 | 16-03-2026 13:50 | 249.746 | 256.777 | 1212 | 42.7962 | 44.2275 | -1.4313 | 265.3648 | 42 | 43.595 | -1.595 | 0.97262 | 16-03-2026 13:50 | 235.538 | 239.222 | 1146.4 | 39.8703 | 42.0769 | -2.2066 | 252.4617 | 39.7 | 41.4752 | -1.7752 | 0.9846 | 16-03-2026 13:50 | 433.2093 | 457.8151 | -24.6057 | 2746.8904 | 424.7 | 451.2683 | -26.5683
16-03-2026 13:40 | 1029 | 49.65 | 330.874 | 336.22 | 1550.1 | 56.0367 | 61.0721 | -5.0355 | 366.4329 | 57.1 | 60.1988 | -3.0988 | 0.9841 | 16-03-2026 13:40 | 332.558 | 341.496 | 1556.2 | 56.916 | 61.0721 | -4.1561 | 366.4329 | 55.9 | 60.1988 | -4.2988 | 0.97383 | 16-03-2026 13:40 | 336.492 | 346.386 | 1537.6 | 57.731 | 61.0721 | -3.3411 | 366.4329 | 54.4 | 60.1988 | -5.7988 | 0.97144 | 16-03-2026 13:40 | 326.516 | 331.724 | 1544.1 | 55.2873 | 61.0721 | -5.7848 | 366.4329 | 54.9 | 60.1988 | -5.2988 | 0.9843 | 16-03-2026 13:40 | 254.35 | 258.486 | 1167.8 | 43.081 | 45.2386 | -2.1576 | 271.4317 | 42.5 | 44.5917 | -2.0917 | 0.984 | 16-03-2026 13:40 | 250.676 | 255.497 | 1160.4 | 42.5828 | 45.2386 | -2.6558 | 271.4317 | 41.9 | 44.5917 | -2.6917 | 0.98113 | 16-03-2026 13:40 | 250.931 | 256.526 | 1159.6 | 42.7543 | 45.2386 | -2.4843 | 271.4317 | 42 | 44.5917 | -2.5917 | 0.97819 | 16-03-2026 13:40 | 252.784 | 259.968 | 1170 | 43.328 | 45.2386 | -1.9106 | 271.4317 | 42.2 | 44.5917 | -2.3917 | 0.97237 | 16-03-2026 13:40 | 238.713 | 242.545 | 1106.7 | 40.4242 | 43.0389 | -2.6148 | 258.2337 | 39.8 | 42.4235 | -2.6235 | 0.9842 | 16-03-2026 13:40 | 438.1413 | 468.282 | -30.1407 | 2809.6921 | 430.7 | 461.5856 | -30.8856
16-03-2026 13:30 | 1043 | 49.65 | 335.005 | 340.418 | 1493 | 56.7363 | 61.9031 | -5.1667 | 371.4183 | 56.3 | 61.0178 | -4.7178 | 0.9841 | 16-03-2026 13:30 | 331.902 | 337.162 | 1500.3 | 56.1937 | 61.9031 | -5.7094 | 371.4183 | 54.6 | 61.0178 | -6.4178 | 0.9844 | 16-03-2026 13:30 | 334.821 | 343.516 | 1483.2 | 57.2527 | 61.9031 | -4.6504 | 371.4183 | 55.4 | 61.0178 | -5.6178 | 0.97469 | 16-03-2026 13:30 | 330.014 | 335.278 | 1489.2 | 55.8797 | 61.9031 | -6.0234 | 371.4183 | 54 | 61.0178 | -7.0178 | 0.9843 | 16-03-2026 13:30 | 258.975 | 263.217 | 1125.3 | 43.8695 | 45.8541 | -1.9846 | 275.1247 | 42.8 | 45.1984 | -2.3984 | 0.98388 | 16-03-2026 13:30 | 254.527 | 259.93 | 1118.5 | 43.3217 | 45.8541 | -2.5324 | 275.1247 | 42.7 | 45.1984 | -2.4984 | 0.97921 | 16-03-2026 13:30 | 255.281 | 260.645 | 1117.6 | 43.4408 | 45.8541 | -2.4133 | 275.1247 | 42.9 | 45.1984 | -2.2984 | 0.97942 | 16-03-2026 13:30 | 256.992 | 264.651 | 1127.8 | 44.1085 | 45.8541 | -1.7456 | 275.1247 | 43.2 | 45.1984 | -1.9984 | 0.97106 | 16-03-2026 13:30 | 242.014 | 245.924 | 1066.9 | 40.9873 | 43.6245 | -2.6372 | 261.7471 | 40.7 | 43.0007 | -2.3007 | 0.9841 | 16-03-2026 13:30 | 441.7902 | 474.6532 | -32.863 | 2847.9192 | 432.6 | 467.8657 | -35.2657
16-03-2026 13:20 | 1057 | 49.65 | 338.837 | 339.014 | 1436.7 | 56.5023 | 62.734 | -6.2316 | 376.4038 | 55.2 | 61.8369 | -6.6369 | 0.99948 | 16-03-2026 13:20 | 332.902 | 338.212 | 1445.7 | 56.3687 | 62.734 | -6.3653 | 376.4038 | 55.3 | 61.8369 | -6.5369 | 0.9843 | 16-03-2026 13:20 | 334.787 | 344.936 | 1427.8 | 57.4893 | 62.734 | -5.2446 | 376.4038 | 55.2 | 61.8369 | -6.6369 | 0.97058 | 16-03-2026 13:20 | 330.567 | 335.874 | 1435.2 | 55.979 | 62.734 | -6.755 | 376.4038 | 54 | 61.8369 | -7.8369 | 0.9842 | 16-03-2026 13:20 | 260.775 | 265.042 | 1082.5 | 44.1737 | 46.4696 | -2.2959 | 278.8176 | 44.4 | 45.8051 | -1.4051 | 0.9839 | 16-03-2026 13:20 | 256.672 | 261.976 | 1075.8 | 43.6627 | 46.4696 | -2.8069 | 278.8176 | 43 | 45.8051 | -2.8051 | 0.97975 | 16-03-2026 13:20 | 257.735 | 263.273 | 1074.7 | 43.8788 | 46.4696 | -2.5908 | 278.8176 | 43.2 | 45.8051 | -2.6051 | 0.97896 | 16-03-2026 13:20 | 259.485 | 267.463 | 1084.6 | 44.5772 | 46.4696 | -1.8924 | 278.8176 | 43.6 | 45.8051 | -2.2051 | 0.97017 | 16-03-2026 13:20 | 244.384 | 248.358 | 1026.2 | 41.393 | 44.2101 | -2.8171 | 265.2605 | 40.9 | 43.5779 | -2.6779 | 0.984 | 16-03-2026 13:20 | 444.0247 | 481.0244 | -36.9997 | 2886.1463 | 434.8 | 474.1457 | -39.3457
16-03-2026 13:10 | 1058 | 49.65 | 335.228 | 340.61 | 1381.5 | 56.7683 | 62.7933 | -6.025 | 376.7599 | 58 | 61.8954 | -3.8954 | 0.9842 | 16-03-2026 13:10 | 334.334 | 339.701 | 1390.4 | 56.6168 | 62.7933 | -6.1765 | 376.7599 | 57.4 | 61.8954 | -4.4954 | 0.9842 | 16-03-2026 13:10 | 334.707 | 344.963 | 1372.6 | 57.4938 | 62.7933 | -5.2995 | 376.7599 | 55.9 | 61.8954 | -5.9954 | 0.97027 | 16-03-2026 13:10 | 329.145 | 334.361 | 1381.2 | 55.7268 | 62.7933 | -7.0665 | 376.7599 | 55.2 | 61.8954 | -6.6954 | 0.9844 | 16-03-2026 13:10 | 261.829 | 266.14 | 1038.1 | 44.3567 | 46.5136 | -2.1569 | 279.0814 | 43.2 | 45.8484 | -2.6484 | 0.9838 | 16-03-2026 13:10 | 256.985 | 261.991 | 1032.8 | 43.6652 | 46.5136 | -2.8484 | 279.0814 | 43 | 45.8484 | -2.8484 | 0.98089 | 16-03-2026 13:10 | 258.669 | 263.973 | 1031.5 | 43.9955 | 46.5136 | -2.5181 | 279.0814 | 43.1 | 45.8484 | -2.7484 | 0.97991 | 16-03-2026 13:10 | 260.775 | 268.751 | 1041 | 44.7918 | 46.5136 | -1.7217 | 279.0814 | 44.1 | 45.8484 | -1.7484 | 0.97032 | 16-03-2026 13:10 | 244.833 | 248.839 | 985.3 | 41.4732 | 44.2519 | -2.7787 | 265.5114 | 41.1 | 43.6191 | -2.5191 | 0.9839 | 16-03-2026 13:10 | 444.8882 | 481.4795 | -36.5913 | 2888.8768 | 441 | 474.5943 | -33.5943
16-03-2026 13:00 | 1066 | 49.36 | 345.185 | 350.94 | 1323.5 | 58.49 | 63.3384 | -4.8484 | 380.0305 | 56.2 | 62.4327 | -6.2327 | 0.9836 | 16-03-2026 13:00 | 341.991 | 347.622 | 1333 | 57.937 | 63.3384 | -5.4014 | 380.0305 | 54.8 | 62.4327 | -7.6327 | 0.9838 | 16-03-2026 13:00 | 340.594 | 350.798 | 1316.7 | 58.4663 | 63.3384 | -4.8721 | 380.0305 | 56.4 | 62.4327 | -6.0327 | 0.97091 | 16-03-2026 13:00 | 336.46 | 341.931 | 1326 | 56.9885 | 63.3384 | -6.3499 | 380.0305 | 55.9 | 62.4327 | -6.5327 | 0.984 | 16-03-2026 13:00 | 263.266 | 267.628 | 994.9 | 44.6047 | 46.9173 | -2.3127 | 281.504 | 44.3 | 46.2464 | -1.9464 | 0.9837 | 16-03-2026 13:00 | 259.171 | 264.323 | 989.8 | 44.0538 | 46.9173 | -2.8635 | 281.504 | 43 | 46.2464 | -3.2464 | 0.98051 | 16-03-2026 13:00 | 259.239 | 264.546 | 988.4 | 44.091 | 46.9173 | -2.8263 | 281.504 | 43.1 | 46.2464 | -3.1464 | 0.97994 | 16-03-2026 13:00 | 260.732 | 268.628 | 996.9 | 44.7713 | 46.9173 | -2.146 | 281.504 | 42.7 | 46.2464 | -3.5464 | 0.97061 | 16-03-2026 13:00 | 246.747 | 250.785 | 944.2 | 41.7975 | 44.636 | -2.8385 | 267.8162 | 40.9 | 43.9977 | -3.0977 | 0.9839 | 16-03-2026 13:00 | 451.2002 | 485.659 | -34.4589 | 2913.9542 | 437.3 | 478.7141 | -41.4141
16-03-2026 12:50 | 1057 | 48.79 | 339.151 | 344.596 | 1267.3 | 57.4327 | 62.9406 | -5.508 | 377.6438 | 56.8 | 62.0406 | -5.2406 | 0.9842 | 16-03-2026 12:50 | 337.322 | 342.361 | 1278.2 | 57.0602 | 62.9406 | -5.8805 | 377.6438 | 56.3 | 62.0406 | -5.7406 | 0.98528 | 16-03-2026 12:50 | 333.848 | 343.48 | 1260.3 | 57.2467 | 62.9406 | -5.694 | 377.6438 | 57.4 | 62.0406 | -4.6406 | 0.97196 | 16-03-2026 12:50 | 335.075 | 341.927 | 1270.1 | 56.9878 | 62.9406 | -5.9528 | 377.6438 | 56.7 | 62.0406 | -5.3406 | 0.97996 | 16-03-2026 12:50 | 263.432 | 267.715 | 950.6 | 44.6192 | 46.6227 | -2.0035 | 279.7361 | 43.4 | 45.956 | -2.556 | 0.984 | 16-03-2026 12:50 | 258.404 | 263.483 | 946.8 | 43.9138 | 46.6227 | -2.7089 | 279.7361 | 43.3 | 45.956 | -2.656 | 0.98072 | 16-03-2026 12:50 | 259.601 | 264.933 | 945.3 | 44.1555 | 46.6227 | -2.4672 | 279.7361 | 43.4 | 45.956 | -2.556 | 0.97987 | 16-03-2026 12:50 | 261.157 | 268.899 | 954.2 | 44.8165 | 46.6227 | -1.8062 | 279.7361 | 43.6 | 45.956 | -2.356 | 0.97121 | 16-03-2026 12:50 | 245.949 | 249.923 | 903.3 | 41.6538 | 44.3557 | -2.7019 | 266.1343 | 41.2 | 43.7214 | -2.5214 | 0.9841 | 16-03-2026 12:50 | 447.8862 | 482.609 | -34.7228 | 2895.6539 | 442.1 | 475.7077 | -33.6077
16-03-2026 12:40 | 1059 | 48.79 | 342.295 | 347.755 | 1210.5 | 57.9592 | 63.0597 | -5.1006 | 378.3583 | 56 | 62.158 | -6.158 | 0.9843 | 16-03-2026 12:40 | 334.235 | 347.114 | 1221.9 | 57.8523 | 63.0597 | -5.2074 | 378.3583 | 57.7 | 62.158 | -4.458 | 0.9629 | 16-03-2026 12:40 | 341.66 | 351.727 | 1202.9 | 58.6212 | 63.0597 | -4.4386 | 378.3583 | 56.3 | 62.158 | -5.858 | 0.97138 | 16-03-2026 12:40 | 342.414 | 348.052 | 1213.4 | 58.0087 | 63.0597 | -5.0511 | 378.3583 | 56.9 | 62.158 | -5.258 | 0.9838 | 16-03-2026 12:40 | 264.049 | 268.342 | 907.2 | 44.7237 | 46.7109 | -1.9872 | 280.2654 | 44.3 | 46.0429 | -1.7429 | 0.984 | 16-03-2026 12:40 | 259.952 | 264.872 | 903.5 | 44.1453 | 46.7109 | -2.5656 | 280.2654 | 43.1 | 46.0429 | -2.9429 | 0.98142 | 16-03-2026 12:40 | 261.193 | 266.859 | 901.9 | 44.4765 | 46.7109 | -2.2344 | 280.2654 | 43.3 | 46.0429 | -2.7429 | 0.97877 | 16-03-2026 12:40 | 262.702 | 270.673 | 910.6 | 45.1122 | 46.7109 | -1.5987 | 280.2654 | 43.5 | 46.0429 | -2.5429 | 0.97055 | 16-03-2026 12:40 | 247.47 | 251.468 | 862.1 | 41.9113 | 44.4396 | -2.5283 | 266.6378 | 41 | 43.8042 | -2.8042 | 0.9841 | 16-03-2026 12:40 | 452.8103 | 483.5221 | -30.7118 | 2901.1329 | 442.1 | 476.6078 | -34.5078
16-03-2026 12:30 | 1059 | 48.79 | 349.012 | 355.229 | 1154.5 | 59.2048 | 63.0597 | -3.8549 | 378.3583 | 58.3 | 62.158 | -3.858 | 0.9825 | 16-03-2026 12:30 | 342.724 | 344.955 | 1164.2 | 57.4925 | 63.0597 | -5.5672 | 378.3583 | 58.7 | 62.158 | -3.458 | 0.99353 | 16-03-2026 12:30 | 338.15 | 348.068 | 1146.6 | 58.0113 | 63.0597 | -5.0484 | 378.3583 | 56.4 | 62.158 | -5.758 | 0.97151 | 16-03-2026 12:30 | 344.33 | 350.036 | 1156.5 | 58.3393 | 63.0597 | -4.7204 | 378.3583 | 55.6 | 62.158 | -6.558 | 0.9837 | 16-03-2026 12:30 | 263.78 | 268.079 | 862.9 | 44.6798 | 46.7109 | -2.0311 | 280.2654 | 43.4 | 46.0429 | -2.6429 | 0.98396 | 16-03-2026 12:30 | 259.802 | 264.802 | 860.4 | 44.1337 | 46.7109 | -2.5772 | 280.2654 | 43.2 | 46.0429 | -2.8429 | 0.98112 | 16-03-2026 12:30 | 260.663 | 266.081 | 858.6 | 44.3468 | 46.7109 | -2.3641 | 280.2654 | 43.3 | 46.0429 | -2.7429 | 0.97964 | 16-03-2026 12:30 | 261.883 | 269.859 | 867.1 | 44.9765 | 46.7109 | -1.7344 | 280.2654 | 43.6 | 46.0429 | -2.4429 | 0.97044 | 16-03-2026 12:30 | 247.23 | 251.224 | 821.1 | 41.8707 | 44.4396 | -2.569 | 266.6378 | 41.1 | 43.8042 | -2.7042 | 0.9841 | 16-03-2026 12:30 | 453.0555 | 483.5221 | -30.4666 | 2901.1329 | 443.6 | 476.6078 | -33.0078
16-03-2026 12:20 | 1053 | 48.79 | 348.232 | 346.063 | 1096.2 | 57.6772 | 62.7024 | -5.0253 | 376.2147 | 59.2 | 61.8058 | -2.6058 | 1.0063 | 16-03-2026 12:20 | 349.334 | 355.195 | 1105.5 | 59.1992 | 62.7024 | -3.5033 | 376.2147 | 55.9 | 61.8058 | -5.9058 | 0.9835 | 16-03-2026 12:20 | 335.39 | 345.417 | 1090.2 | 57.5695 | 62.7024 | -5.1329 | 376.2147 | 57.6 | 61.8058 | -4.2058 | 0.97097 | 16-03-2026 12:20 | 335.042 | 340.118 | 1100.9 | 56.6863 | 62.7024 | -6.0161 | 376.2147 | 56.3 | 61.8058 | -5.5058 | 0.98508 | 16-03-2026 12:20 | 261.153 | 265.399 | 819.5 | 44.2332 | 46.4463 | -2.2131 | 278.6775 | 44 | 45.7821 | -1.7821 | 0.984 | 16-03-2026 12:20 | 257.445 | 262.293 | 817.2 | 43.7155 | 46.4463 | -2.7308 | 278.6775 | 42.9 | 45.7821 | -2.8821 | 0.98152 | 16-03-2026 12:20 | 257.814 | 263.151 | 815.3 | 43.8585 | 46.4463 | -2.5878 | 278.6775 | 43 | 45.7821 | -2.7821 | 0.97972 | 16-03-2026 12:20 | 259.713 | 267.411 | 823.5 | 44.5685 | 46.4463 | -1.8778 | 278.6775 | 43.3 | 45.7821 | -2.4821 | 0.97121 | 16-03-2026 12:20 | 245.211 | 249.173 | 780 | 41.5288 | 44.1879 | -2.659 | 265.1271 | 40.9 | 43.556 | -2.656 | 0.9841 | 16-03-2026 12:20 | 449.0367 | 480.7826 | -31.746 | 2884.6958 | 443.1 | 473.9074 | -30.8074
16-03-2026 12:10 | 1048 | 48.5 | 345.9 | 351.954 | 1037 | 58.659 | 62.4738 | -3.8148 | 374.8428 | 55.3 | 61.5804 | -6.2804 | 0.9828 | 16-03-2026 12:10 | 0 | 0 | 1049.6 | 0 | 62.4738 | -62.4738 | 374.8428 | 59.6 | 61.5804 | -1.9804 |  | 16-03-2026 12:10 | 345.227 | 355.298 | 1032.6 | 59.2163 | 62.4738 | -3.2575 | 374.8428 | 57.4 | 61.5804 | -4.1804 | 0.97165 | 16-03-2026 12:10 | 337.958 | 343.418 | 1044.6 | 57.2363 | 62.4738 | -5.2375 | 374.8428 | 57.4 | 61.5804 | -4.1804 | 0.9841 | 16-03-2026 12:10 | 261.03 | 265.22 | 775.5 | 44.2033 | 46.2769 | -2.0736 | 277.6613 | 43 | 45.6151 | -2.6151 | 0.9842 | 16-03-2026 12:10 | 257.114 | 261.989 | 774.3 | 43.6648 | 46.2769 | -2.6121 | 277.6613 | 42.3 | 45.6151 | -3.3151 | 0.98139 | 16-03-2026 12:10 | 257.816 | 263.253 | 772.3 | 43.8755 | 46.2769 | -2.4014 | 277.6613 | 42.5 | 45.6151 | -3.1151 | 0.97935 | 16-03-2026 12:10 | 259.732 | 267.24 | 780.2 | 44.54 | 46.2769 | -1.7369 | 277.6613 | 42.8 | 45.6151 | -2.8151 | 0.97191 | 16-03-2026 12:10 | 244.986 | 248.873 | 739.1 | 41.4788 | 44.0267 | -2.5479 | 264.1604 | 40.3 | 43.3971 | -3.0971 | 0.98438 | 16-03-2026 12:10 | 392.8742 | 479.0295 | -86.1553 | 2874.1771 | 440.6 | 472.1794 | -31.5794
16-03-2026 12:00 | 1037 | 48.5 | 342.393 | 348.338 | 981.7 | 58.0563 | 61.8181 | -3.7617 | 370.9084 | 55.9 | 60.9341 | -5.0341 | 0.98293 | 16-03-2026 12:00 | 345.513 | 351.417 | 990 | 58.5695 | 61.8181 | -3.2486 | 370.9084 | 55.4 | 60.9341 | -5.5341 | 0.9832 | 16-03-2026 12:00 | 341.237 | 351.735 | 975.2 | 58.6225 | 61.8181 | -3.1956 | 370.9084 | 56.5 | 60.9341 | -4.4341 | 0.97015 | 16-03-2026 12:00 | 337.883 | 343.482 | 987.2 | 57.247 | 61.8181 | -4.5711 | 370.9084 | 56.1 | 60.9341 | -4.8341 | 0.9837 | 16-03-2026 12:00 | 258.427 | 262.561 | 732.5 | 43.7602 | 45.7912 | -2.031 | 274.747 | 42.7 | 45.1363 | -2.4363 | 0.98426 | 16-03-2026 12:00 | 254.481 | 259.538 | 732 | 43.2563 | 45.7912 | -2.5348 | 274.747 | 42.2 | 45.1363 | -2.9363 | 0.98052 | 16-03-2026 12:00 | 255.64 | 260.709 | 729.8 | 43.4515 | 45.7912 | -2.3397 | 274.747 | 42.1 | 45.1363 | -3.0363 | 0.98056 | 16-03-2026 12:00 | 257.111 | 264.66 | 737.4 | 44.11 | 45.7912 | -1.6812 | 274.747 | 42.5 | 45.1363 | -2.6363 | 0.97148 | 16-03-2026 12:00 | 242.515 | 246.408 | 698.8 | 41.068 | 43.5646 | -2.4966 | 261.3877 | 40.1 | 42.9416 | -2.8416 | 0.9842 | 16-03-2026 12:00 | 448.1413 | 474.0015 | -25.8602 | 2844.0092 | 433.5 | 467.2233 | -33.7233
16-03-2026 11:50 | 1021 | 48.5 | 338.851 | 344.676 | 925.8 | 57.446 | 60.8643 | -3.4183 | 365.1856 | 57.2 | 59.9939 | -2.7939 | 0.9831 | 16-03-2026 11:50 | 340.776 | 346.423 | 934.6 | 57.7372 | 60.8643 | -3.1271 | 365.1856 | 55.5 | 59.9939 | -4.4939 | 0.9837 | 16-03-2026 11:50 | 337.598 | 347.594 | 918.7 | 57.9323 | 60.8643 | -2.9319 | 365.1856 | 56.1 | 59.9939 | -3.8939 | 0.97124 | 16-03-2026 11:50 | 334.497 | 339.971 | 931.1 | 56.6618 | 60.8643 | -4.2024 | 365.1856 | 56.4 | 59.9939 | -3.5939 | 0.9839 | 16-03-2026 11:50 | 254.818 | 258.909 | 689.8 | 43.1515 | 45.0846 | -1.9331 | 270.5079 | 42.3 | 44.4399 | -2.1399 | 0.9842 | 16-03-2026 11:50 | 251.461 | 256.418 | 689.8 | 42.7363 | 45.0846 | -2.3483 | 270.5079 | 41.8 | 44.4399 | -2.6399 | 0.98067 | 16-03-2026 11:50 | 251.668 | 256.769 | 687.7 | 42.7948 | 45.0846 | -2.2898 | 270.5079 | 41.9 | 44.4399 | -2.5399 | 0.98013 | 16-03-2026 11:50 | 253.453 | 261.14 | 694.9 | 43.5233 | 45.0846 | -1.5613 | 270.5079 | 42 | 44.4399 | -2.4399 | 0.97056 | 16-03-2026 11:50 | 239.452 | 243.271 | 658.7 | 40.5452 | 42.8925 | -2.3473 | 257.3547 | 39.8 | 42.2791 | -2.4791 | 0.9843 | 16-03-2026 11:50 | 442.5285 | 466.6881 | -24.1596 | 2800.1286 | 433 | 460.0145 | -27.0145
16-03-2026 11:40 | 1006 | 48.5 | 335.516 | 341.249 | 868.6 | 56.8748 | 59.9701 | -3.0952 | 359.8205 | 54.9 | 59.1125 | -4.2125 | 0.9832 | 16-03-2026 11:40 | 340.627 | 346.553 | 879.1 | 57.7588 | 59.9701 | -2.2112 | 359.8205 | 56.4 | 59.1125 | -2.7125 | 0.9829 | 16-03-2026 11:40 | 334.118 | 343.582 | 862.6 | 57.2637 | 59.9701 | -2.7064 | 359.8205 | 54.7 | 59.1125 | -4.4125 | 0.97245 | 16-03-2026 11:40 | 336.976 | 342.873 | 874.7 | 57.1455 | 59.9701 | -2.8246 | 359.8205 | 55.1 | 59.1125 | -4.0125 | 0.9828 | 16-03-2026 11:40 | 251.823 | 255.814 | 647.5 | 42.6357 | 44.4223 | -1.7866 | 266.5337 | 41.2 | 43.787 | -2.587 | 0.9844 | 16-03-2026 11:40 | 248.494 | 253.266 | 648 | 42.211 | 44.4223 | -2.2113 | 266.5337 | 40.7 | 43.787 | -3.087 | 0.98116 | 16-03-2026 11:40 | 248.48 | 253.23 | 645.8 | 42.205 | 44.4223 | -2.2173 | 266.5337 | 40.6 | 43.787 | -3.187 | 0.98124 | 16-03-2026 11:40 | 249.692 | 257.142 | 652.9 | 42.857 | 44.4223 | -1.5653 | 266.5337 | 41.5 | 43.787 | -2.287 | 0.97103 | 16-03-2026 11:40 | 236.348 | 240.069 | 618.9 | 40.0115 | 42.2623 | -2.2508 | 253.5738 | 39.3 | 41.6579 | -2.3579 | 0.9845 | 16-03-2026 11:40 | 438.963 | 459.8318 | -20.8688 | 2758.9906 | 424.4 | 453.2562 | -28.8562
16-03-2026 11:30 | 984 | 48.5 | 327.782 | 333.326 | 813.7 | 55.5543 | 58.6586 | -3.1043 | 351.9517 | 54.9 | 57.8198 | -2.9198 | 0.98337 | 16-03-2026 11:30 | 333.611 | 339.311 | 822.7 | 56.5518 | 58.6586 | -2.1068 | 351.9517 | 55.1 | 57.8198 | -2.7198 | 0.9832 | 16-03-2026 11:30 | 326.787 | 336.073 | 807.9 | 56.0122 | 58.6586 | -2.6464 | 351.9517 | 54 | 57.8198 | -3.8198 | 0.97237 | 16-03-2026 11:30 | 331.016 | 336.706 | 819.6 | 56.1177 | 58.6586 | -2.5409 | 351.9517 | 54.6 | 57.8198 | -3.2198 | 0.9831 | 16-03-2026 11:30 | 247.16 | 251.026 | 606.3 | 41.8377 | 43.4508 | -1.6132 | 260.7049 | 40.7 | 42.8295 | -2.1295 | 0.9846 | 16-03-2026 11:30 | 244.411 | 248.901 | 607.3 | 41.4835 | 43.4508 | -1.9673 | 260.7049 | 40.3 | 42.8295 | -2.5295 | 0.98196 | 16-03-2026 11:30 | 244.394 | 248.942 | 605.2 | 41.4903 | 43.4508 | -1.9605 | 260.7049 | 40.3 | 42.8295 | -2.5295 | 0.98173 | 16-03-2026 11:30 | 245.199 | 252.405 | 611.4 | 42.0675 | 43.4508 | -1.3833 | 260.7049 | 40.5 | 42.8295 | -2.3295 | 0.97145 | 16-03-2026 11:30 | 232.144 | 235.775 | 579.6 | 39.2958 | 41.3381 | -2.0422 | 248.0285 | 38.3 | 40.7469 | -2.4469 | 0.9846 | 16-03-2026 11:30 | 430.4108 | 449.7758 | -19.365 | 2698.6548 | 418.7 | 443.344 | -24.644
16-03-2026 11:20 | 962 | 48.5 | 321.156 | 326.544 | 758.8 | 54.424 | 57.3471 | -2.9231 | 344.0828 | 52.7 | 56.5271 | -3.8271 | 0.9835 | 16-03-2026 11:20 | 325.578 | 331.141 | 767.6 | 55.1902 | 57.3471 | -2.157 | 344.0828 | 54.3 | 56.5271 | -2.2271 | 0.9832 | 16-03-2026 11:20 | 320.211 | 329.38 | 753.9 | 54.8967 | 57.3471 | -2.4505 | 344.0828 | 52.6 | 56.5271 | -3.9271 | 0.97216 | 16-03-2026 11:20 | 323.682 | 329.246 | 765 | 54.8743 | 57.3471 | -2.4728 | 344.0828 | 53.3 | 56.5271 | -3.2271 | 0.9831 | 16-03-2026 11:20 | 240.97 | 244.747 | 565.6 | 40.7912 | 42.4794 | -1.6882 | 254.8762 | 40.1 | 41.8719 | -1.7719 | 0.98457 | 16-03-2026 11:20 | 238.583 | 243.05 | 567 | 40.5083 | 42.4794 | -1.971 | 254.8762 | 39.7 | 41.8719 | -2.1719 | 0.98162 | 16-03-2026 11:20 | 238.293 | 243.107 | 564.9 | 40.5178 | 42.4794 | -1.9615 | 254.8762 | 39.7 | 41.8719 | -2.1719 | 0.9802 | 16-03-2026 11:20 | 240.48 | 247.462 | 570.9 | 41.2437 | 42.4794 | -1.2357 | 254.8762 | 39.5 | 41.8719 | -2.3719 | 0.97179 | 16-03-2026 11:20 | 227.224 | 230.731 | 541.3 | 38.4552 | 40.4139 | -1.9587 | 242.4831 | 37.3 | 39.8359 | -2.5359 | 0.9848 | 16-03-2026 11:20 | 420.9013 | 439.7198 | -18.8185 | 2638.319 | 409.2 | 433.4318 | -24.2318
16-03-2026 11:10 | 943 | 48.5 | 314.569 | 319.879 | 706.1 | 53.3132 | 56.2145 | -2.9013 | 337.287 | 51.6 | 55.4106 | -3.8106 | 0.9834 | 16-03-2026 11:10 | 320.543 | 325.987 | 713.3 | 54.3312 | 56.2145 | -1.8833 | 337.287 | 53.3 | 55.4106 | -2.1106 | 0.9833 | 16-03-2026 11:10 | 313.653 | 321.953 | 701.3 | 53.6588 | 56.2145 | -2.5557 | 337.287 | 52.1 | 55.4106 | -3.3106 | 0.97422 | 16-03-2026 11:10 | 318.174 | 323.578 | 711.7 | 53.9297 | 56.2145 | -2.2848 | 337.287 | 52.7 | 55.4106 | -2.7106 | 0.9833 | 16-03-2026 11:10 | 236.981 | 240.676 | 525.5 | 40.1127 | 41.6404 | -1.5277 | 249.8422 | 38.8 | 41.0449 | -2.2449 | 0.98465 | 16-03-2026 11:10 | 235.229 | 239.259 | 527.3 | 39.8765 | 41.6404 | -1.7639 | 249.8422 | 38.6 | 41.0449 | -2.4449 | 0.98316 | 16-03-2026 11:10 | 234.897 | 239.528 | 525.2 | 39.9213 | 41.6404 | -1.719 | 249.8422 | 38.5 | 41.0449 | -2.5449 | 0.98067 | 16-03-2026 11:10 | 237.034 | 244.345 | 531.4 | 40.7242 | 41.6404 | -0.9162 | 249.8422 | 38.9 | 41.0449 | -2.1449 | 0.97008 | 16-03-2026 11:10 | 224.06 | 227.449 | 504 | 37.9082 | 39.6157 | -1.7075 | 237.6939 | 36.9 | 39.0492 | -2.1492 | 0.9851 | 16-03-2026 11:10 | 413.7757 | 431.0351 | -17.2595 | 2586.2109 | 401.4 | 424.8713 | -23.4713
16-03-2026 11:00 | 920 | 48.5 | 310.509 | 315.622 | 654.5 | 52.6037 | 54.8434 | -2.2397 | 329.0605 | 51.4 | 54.0592 | -2.6592 | 0.9838 | 16-03-2026 11:00 | 314.762 | 320.043 | 660 | 53.3405 | 54.8434 | -1.5029 | 329.0605 | 51.3 | 54.0592 | -2.7592 | 0.9835 | 16-03-2026 11:00 | 309.602 | 317.911 | 649.2 | 52.9852 | 54.8434 | -1.8582 | 329.0605 | 50.4 | 54.0592 | -3.6592 | 0.97386 | 16-03-2026 11:00 | 312.869 | 318.118 | 659 | 53.0197 | 54.8434 | -1.8237 | 329.0605 | 51.6 | 54.0592 | -2.4592 | 0.9835 | 16-03-2026 11:00 | 232.83 | 236.4 | 486.7 | 39.4 | 40.6248 | -1.2248 | 243.7485 | 38.3 | 40.0438 | -1.7438 | 0.9849 | 16-03-2026 11:00 | 231.809 | 236.105 | 488.7 | 39.3508 | 40.6248 | -1.2739 | 243.7485 | 38.1 | 40.0438 | -1.9438 | 0.9818 | 16-03-2026 11:00 | 231.021 | 235.299 | 486.7 | 39.2165 | 40.6248 | -1.4083 | 243.7485 | 38 | 40.0438 | -2.0438 | 0.98182 | 16-03-2026 11:00 | 234.389 | 241.13 | 492.5 | 40.1883 | 40.6248 | -0.43642 | 243.7485 | 38.5 | 40.0438 | -1.5438 | 0.97204 | 16-03-2026 11:00 | 221.827 | 225.114 | 467.1 | 37.519 | 38.6494 | -1.1304 | 231.8965 | 36.4 | 38.0967 | -1.6967 | 0.9854 | 16-03-2026 11:00 | 407.6237 | 420.5221 | -12.8984 | 2523.1325 | 394 | 414.5086 | -20.5086
16-03-2026 10:50 | 897 | 48.79 | 302.845 | 307.832 | 603.1 | 51.3053 | 53.4132 | -2.1079 | 320.4791 | 50.6 | 52.6494 | -2.0494 | 0.9838 | 16-03-2026 10:50 | 307.656 | 312.817 | 608.7 | 52.1362 | 53.4132 | -1.277 | 320.4791 | 50.8 | 52.6494 | -1.8494 | 0.9835 | 16-03-2026 10:50 | 301.823 | 309.771 | 598.8 | 51.6285 | 53.4132 | -1.7847 | 320.4791 | 49.9 | 52.6494 | -2.7494 | 0.97434 | 16-03-2026 10:50 | 305.068 | 310.123 | 607.4 | 51.6872 | 53.4132 | -1.726 | 320.4791 | 49.9 | 52.6494 | -2.7494 | 0.9837 | 16-03-2026 10:50 | 226.61 | 230.061 | 448.4 | 38.3435 | 39.5653 | -1.2218 | 237.392 | 37.1 | 38.9995 | -1.8995 | 0.985 | 16-03-2026 10:50 | 225.395 | 229.134 | 450.6 | 38.189 | 39.5653 | -1.3763 | 237.392 | 36.8 | 38.9995 | -2.1995 | 0.98368 | 16-03-2026 10:50 | 224.518 | 228.782 | 448.7 | 38.1303 | 39.5653 | -1.435 | 237.392 | 36.8 | 38.9995 | -2.1995 | 0.98136 | 16-03-2026 10:50 | 227.273 | 234.233 | 454 | 39.0388 | 39.5653 | -0.52649 | 237.392 | 37.2 | 38.9995 | -1.7995 | 0.97029 | 16-03-2026 10:50 | 215.014 | 218.222 | 430.7 | 36.3703 | 37.6415 | -1.2712 | 225.8491 | 35.6 | 37.1032 | -1.5032 | 0.9853 | 16-03-2026 10:50 | 396.8292 | 409.5556 | -12.7264 | 2457.3335 | 384.7 | 403.6989 | -18.9989
16-03-2026 10:40 | 868 | 48.79 | 292.959 | 297.692 | 552.5 | 49.6153 | 51.6863 | -2.071 | 310.1181 | 47.1 | 50.9472 | -3.8472 | 0.9841 | 16-03-2026 10:40 | 297.098 | 301.929 | 557.9 | 50.3215 | 51.6863 | -1.3648 | 310.1181 | 49.8 | 50.9472 | -1.1472 | 0.984 | 16-03-2026 10:40 | 291.535 | 299.309 | 548.9 | 49.8848 | 51.6863 | -1.8015 | 310.1181 | 47.6 | 50.9472 | -3.3472 | 0.97403 | 16-03-2026 10:40 | 295.115 | 299.982 | 557.5 | 49.997 | 51.6863 | -1.6893 | 310.1181 | 48 | 50.9472 | -2.9472 | 0.98378 | 16-03-2026 10:40 | 218.931 | 222.197 | 411.3 | 37.0328 | 38.2862 | -1.2533 | 229.7171 | 36.2 | 37.7387 | -1.5387 | 0.9853 | 16-03-2026 10:40 | 218.142 | 221.78 | 413.8 | 36.9633 | 38.2862 | -1.3228 | 229.7171 | 36 | 37.7387 | -1.7387 | 0.9836 | 16-03-2026 10:40 | 217.784 | 221.464 | 411.9 | 36.9107 | 38.2862 | -1.3755 | 229.7171 | 35.9 | 37.7387 | -1.8387 | 0.98338 | 16-03-2026 10:40 | 219.818 | 226.275 | 416.8 | 37.7125 | 38.2862 | -0.57368 | 229.7171 | 36.2 | 37.7387 | -1.5387 | 0.97146 | 16-03-2026 10:40 | 207.988 | 211.091 | 395.1 | 35.1818 | 36.4246 | -1.2427 | 218.5474 | 33.8 | 35.9037 | -2.1037 | 0.9853 | 16-03-2026 10:40 | 383.6198 | 396.3147 | -12.6948 | 2377.8879 | 370.6 | 390.6474 | -20.0474
16-03-2026 10:30 | 832 | 48.5 | 283.052 | 287.538 | 505.4 | 47.923 | 49.5975 | -1.6745 | 297.5851 | 46.3 | 48.8883 | -2.5883 | 0.9844 | 16-03-2026 10:30 | 285.301 | 289.94 | 508.1 | 48.3233 | 49.5975 | -1.2742 | 297.5851 | 45 | 48.8883 | -3.8883 | 0.984 | 16-03-2026 10:30 | 282.55 | 289.595 | 501.3 | 48.2658 | 49.5975 | -1.3317 | 297.5851 | 46.1 | 48.8883 | -2.7883 | 0.97567 | 16-03-2026 10:30 | 284.875 | 289.478 | 509.5 | 48.2463 | 49.5975 | -1.3512 | 297.5851 | 46.7 | 48.8883 | -2.1883 | 0.9841 | 16-03-2026 10:30 | 211.888 | 215.006 | 375.1 | 35.8343 | 36.7389 | -0.90457 | 220.4334 | 34.7 | 36.2135 | -1.5135 | 0.9855 | 16-03-2026 10:30 | 210.925 | 214.31 | 377.8 | 35.7183 | 36.7389 | -1.0206 | 220.4334 | 34.7 | 36.2135 | -1.5135 | 0.98421 | 16-03-2026 10:30 | 210.299 | 213.89 | 376 | 35.6483 | 36.7389 | -1.0906 | 220.4334 | 34.5 | 36.2135 | -1.7135 | 0.98321 | 16-03-2026 10:30 | 212.576 | 218.743 | 380.6 | 36.4572 | 36.7389 | -0.28174 | 220.4334 | 34.9 | 36.2135 | -1.3135 | 0.97181 | 16-03-2026 10:30 | 201.324 | 204.286 | 361.3 | 34.0477 | 34.9525 | -0.90485 | 209.7151 | 33.2 | 34.4527 | -1.2527 | 0.9855 | 16-03-2026 10:30 | 370.4643 | 380.2982 | -9.8339 | 2281.7894 | 356.1 | 374.86 | -18.76
16-03-2026 10:20 | 803 | 48.79 | 270.862 | 275.154 | 459.1 | 45.859 | 47.8158 | -1.9568 | 286.8949 | 43.8 | 47.1321 | -3.3321 | 0.9844 | 16-03-2026 10:20 | 270.723 | 275.013 | 463.1 | 45.8355 | 47.8158 | -1.9803 | 286.8949 | 45.7 | 47.1321 | -1.4321 | 0.9844 | 16-03-2026 10:20 | 272.433 | 279.257 | 455.2 | 46.5428 | 47.8158 | -1.273 | 286.8949 | 44.2 | 47.1321 | -2.9321 | 0.97556 | 16-03-2026 10:20 | 276.586 | 280.998 | 462.8 | 46.833 | 47.8158 | -0.98282 | 286.8949 | 45.4 | 47.1321 | -1.7321 | 0.9843 | 16-03-2026 10:20 | 204.752 | 207.744 | 340.4 | 34.624 | 35.4191 | -0.79513 | 212.5148 | 33.1 | 34.9126 | -1.8126 | 0.9856 | 16-03-2026 10:20 | 204.129 | 207.271 | 343.1 | 34.5452 | 35.4191 | -0.87396 | 212.5148 | 33 | 34.9126 | -1.9126 | 0.98484 | 16-03-2026 10:20 | 203.847 | 207.074 | 341.5 | 34.5123 | 35.4191 | -0.90679 | 212.5148 | 32.9 | 34.9126 | -2.0126 | 0.98442 | 16-03-2026 10:20 | 206.264 | 212.037 | 345.7 | 35.3395 | 35.4191 | -0.079628 | 212.5148 | 33.3 | 34.9126 | -1.6126 | 0.97277 | 16-03-2026 10:20 | 195.421 | 198.236 | 328.1 | 33.0393 | 33.6969 | -0.65758 | 202.1815 | 31.5 | 33.215 | -1.715 | 0.9858 | 16-03-2026 10:20 | 357.1307 | 366.6367 | -9.506 | 2199.8203 | 342.9 | 361.3938 | -18.4938
16-03-2026 10:10 | 764 | 48.79 | 258.504 | 262.494 | 415.3 | 43.749 | 45.4935 | -1.7445 | 272.9611 | 43.4 | 44.843 | -1.443 | 0.9848 | 16-03-2026 10:10 | 262.469 | 265.984 | 417.4 | 44.3307 | 45.4935 | -1.1628 | 272.9611 | 44.6 | 44.843 | -0.24295 | 0.98678 | 16-03-2026 10:10 | 256.645 | 263.197 | 411 | 43.8662 | 45.4935 | -1.6273 | 272.9611 | 42.7 | 44.843 | -2.143 | 0.97511 | 16-03-2026 10:10 | 263.015 | 267.156 | 417.4 | 44.526 | 45.4935 | -0.96751 | 272.9611 | 42.7 | 44.843 | -2.143 | 0.9845 | 16-03-2026 10:10 | 194.703 | 197.15 | 307.3 | 32.8583 | 33.6989 | -0.84056 | 202.1934 | 32 | 33.217 | -1.217 | 0.98759 | 16-03-2026 10:10 | 195.639 | 198.65 | 310.1 | 33.1083 | 33.6989 | -0.59056 | 202.1934 | 32 | 33.217 | -1.217 | 0.98484 | 16-03-2026 10:10 | 194.367 | 197.709 | 308.6 | 32.9515 | 33.6989 | -0.7474 | 202.1934 | 31.8 | 33.217 | -1.417 | 0.9831 | 16-03-2026 10:10 | 197.152 | 202.956 | 312.4 | 33.826 | 33.6989 | 0.1271 | 202.1934 | 32.1 | 33.217 | -1.117 | 0.9714 | 16-03-2026 10:10 | 187.529 | 190.25 | 296.6 | 31.7083 | 32.0603 | -0.35199 | 192.362 | 30.6 | 31.6019 | -1.0019 | 0.9857 | 16-03-2026 10:10 | 340.9243 | 348.83 | -7.9056 | 2092.9797 | 331.9 | 343.8417 | -11.9417
16-03-2026 10:00 | 732 | 49.08 | 251.823 | 255.658 | 371.9 | 42.6097 | 43.5398 | -0.9301 | 261.2386 | 41.7 | 42.9171 | -1.2171 | 0.985 | 16-03-2026 10:00 | 255.445 | 259.388 | 372.8 | 43.2313 | 43.5398 | -0.30843 | 261.2386 | 40.5 | 42.9171 | -2.4171 | 0.9848 | 16-03-2026 10:00 | 250.387 | 256.591 | 368.3 | 42.7652 | 43.5398 | -0.7746 | 261.2386 | 40.8 | 42.9171 | -2.1171 | 0.97582 | 16-03-2026 10:00 | 254.451 | 258.378 | 374.7 | 43.063 | 43.5398 | -0.47676 | 261.2386 | 41.4 | 42.9171 | -1.5171 | 0.9848 | 16-03-2026 10:00 | 187.717 | 190.403 | 275.3 | 31.7338 | 32.2517 | -0.51784 | 193.5101 | 30.2 | 31.7905 | -1.5905 | 0.98589 | 16-03-2026 10:00 | 188.332 | 191.233 | 278.1 | 31.8722 | 32.2517 | -0.37951 | 193.5101 | 30.3 | 31.7905 | -1.4905 | 0.98483 | 16-03-2026 10:00 | 186.904 | 189.657 | 276.8 | 31.6095 | 32.2517 | -0.64218 | 193.5101 | 30.6 | 31.7905 | -1.1905 | 0.98548 | 16-03-2026 10:00 | 188.939 | 194.61 | 280.3 | 32.435 | 32.2517 | 0.18332 | 193.5101 | 30.9 | 31.7905 | -0.89048 | 0.97086 | 16-03-2026 10:00 | 179.928 | 182.464 | 266 | 30.4107 | 30.6835 | -0.27281 | 184.1009 | 29.3 | 30.2447 | -0.9447 | 0.9861 | 16-03-2026 10:00 | 329.7303 | 333.8492 | -4.1189 | 2003.0954 | 315.7 | 329.0752 | -13.3752
16-03-2026 09:50 | 688 | 48.79 | 238.388 | 241.92 | 330.2 | 40.32 | 40.968 | -0.64798 | 245.8079 | 37.9 | 40.3821 | -2.4821 |  | 16-03-2026 09:50 | 241.963 | 245.623 | 332.3 | 40.9372 | 40.968 | -0.030811 | 245.8079 | 39.6 | 40.3821 | -0.78214 |  | 16-03-2026 09:50 | 237.958 | 243.516 | 327.5 | 40.586 | 40.968 | -0.38198 | 245.8079 | 38.9 | 40.3821 | -1.4821 |  | 16-03-2026 09:50 | 241.14 | 244.762 | 333.3 | 40.7937 | 40.968 | -0.17431 | 245.8079 | 39.3 | 40.3821 | -1.0821 |  | 16-03-2026 09:50 | 178.718 | 181.2 | 245.1 | 30.2 | 30.3466 | -0.14665 | 182.0799 | 29.1 | 29.9127 | -0.81269 |  | 16-03-2026 09:50 | 178.626 | 181.242 | 247.8 | 30.207 | 30.3466 | -0.13965 | 182.0799 | 29.2 | 29.9127 | -0.71269 |  | 16-03-2026 09:50 | 178.182 | 180.629 | 246.2 | 30.1048 | 30.3466 | -0.24182 | 182.0799 | 28.6 | 29.9127 | -1.3127 |  | 16-03-2026 09:50 | 180.072 | 185.21 | 249.4 | 30.8683 | 30.3466 | 0.52168 | 182.0799 | 28.9 | 29.9127 | -1.0127 |  | 16-03-2026 09:50 | 170.368 | 172.717 | 236.7 | 28.7862 | 28.8711 | -0.084912 | 173.2265 | 27.9 | 28.4582 | -0.55822 |  | 16-03-2026 09:50 | 312.8032 | 314.1296 | -1.3264 | 1884.7775 | 299.4 | 309.6375 | -10.2375
16-03-2026 09:40 | 650 | 48.5 | 227.809 | 231.03 | 292.3 | 38.505 | 38.7481 | -0.24307 | 232.4884 | 36.9 | 38.194 | -1.294 |  | 16-03-2026 09:40 | 230.801 | 234.173 | 292.7 | 39.0288 | 38.7481 | 0.28077 | 232.4884 | 36.8 | 38.194 | -1.394 |  | 16-03-2026 09:40 | 226.846 | 231.857 | 288.6 | 38.6428 | 38.7481 | -0.10523 | 232.4884 | 36.7 | 38.194 | -1.494 |  | 16-03-2026 09:40 | 229.837 | 233.195 | 294 | 38.8658 | 38.7481 | 0.11777 | 232.4884 | 37.2 | 38.194 | -0.99397 |  | 16-03-2026 09:40 | 170.065 | 172.392 | 216 | 28.732 | 28.7023 | 0.029729 | 172.2136 | 27.5 | 28.2918 | -0.79183 |  | 16-03-2026 09:40 | 170.315 | 172.611 | 218.6 | 28.7685 | 28.7023 | 0.066229 | 172.2136 | 27.5 | 28.2918 | -0.79183 |  | 16-03-2026 09:40 | 169.813 | 172.263 | 217.6 | 28.7105 | 28.7023 | 0.0082294 | 172.2136 | 27.4 | 28.2918 | -0.89183 |  | 16-03-2026 09:40 | 171.672 | 176.577 | 220.5 | 29.4295 | 28.7023 | 0.72723 | 172.2136 | 27.7 | 28.2918 | -0.59183 |  | 16-03-2026 09:40 | 162.839 | 165.051 | 208.8 | 27.5085 | 27.3067 | 0.20184 | 163.8399 | 26.4 | 26.9162 | -0.51617 |  | 16-03-2026 09:40 | 298.1915 | 297.108 | 1.0835 | 1782.648 | 284.1 | 292.8594 | -8.7594
16-03-2026 09:30 | 607 | 48.5 | 214.302 | 217.281 | 255.4 | 36.2135 | 36.1847 | 0.028768 | 217.1084 | 34.5 | 35.6673 | -1.1673 |  | 16-03-2026 09:30 | 215.196 | 218.229 | 255.9 | 36.3715 | 36.1847 | 0.18677 | 217.1084 | 35.4 | 35.6673 | -0.26729 |  | 16-03-2026 09:30 | 212.942 | 217.398 | 251.9 | 36.233 | 36.1847 | 0.048268 | 217.1084 | 34.2 | 35.6673 | -1.4673 |  | 16-03-2026 09:30 | 216.009 | 219.054 | 256.8 | 36.509 | 36.1847 | 0.32427 | 217.1084 | 34.9 | 35.6673 | -0.76729 |  | 16-03-2026 09:30 | 159.357 | 161.489 | 188.5 | 26.9148 | 26.8035 | 0.11133 | 160.821 | 25.7 | 26.4202 | -0.72021 |  | 16-03-2026 09:30 | 159.903 | 162.026 | 191.1 | 27.0043 | 26.8035 | 0.20083 | 160.821 | 25.8 | 26.4202 | -0.62021 |  | 16-03-2026 09:30 | 159.202 | 161.315 | 190.2 | 26.8858 | 26.8035 | 0.082328 | 160.821 | 26.1 | 26.4202 | -0.32021 |  | 16-03-2026 09:30 | 160.983 | 165.254 | 192.8 | 27.5423 | 26.8035 | 0.73883 | 160.821 | 26.4 | 26.4202 | -0.020215 |  | 16-03-2026 09:30 | 152.553 | 154.578 | 182.4 | 25.763 | 25.5002 | 0.26278 | 153.0013 | 24.5 | 25.1356 | -0.63556 |  | 16-03-2026 09:30 | 279.4373 | 277.4532 | 1.9842 | 1664.719 | 267.5 | 273.4856 | -5.9856
16-03-2026 09:20 | 567 | 48.5 | 200.949 | 203.608 | 220.9 | 33.9347 | 33.8002 | 0.13443 | 202.8014 | 32 | 33.3169 | -1.3169 |  | 16-03-2026 09:20 | 200.695 | 203.483 | 220.5 | 33.9138 | 33.8002 | 0.1136 | 202.8014 | 32.1 | 33.3169 | -1.2169 |  | 16-03-2026 09:20 | 199.642 | 203.478 | 217.7 | 33.913 | 33.8002 | 0.11276 | 202.8014 | 32.2 | 33.3169 | -1.1169 |  | 16-03-2026 09:20 | 202.456 | 205.227 | 221.9 | 34.2045 | 33.8002 | 0.40426 | 202.8014 | 32.6 | 33.3169 | -0.71689 |  | 16-03-2026 09:20 | 149.5 | 151.469 | 162.8 | 25.2448 | 25.0372 | 0.20762 | 150.2233 | 24 | 24.6792 | -0.67918 |  | 16-03-2026 09:20 | 150.095 | 152.057 | 165.3 | 25.3428 | 25.0372 | 0.30562 | 150.2233 | 24.2 | 24.6792 | -0.47918 |  | 16-03-2026 09:20 | 149.302 | 151.238 | 164.1 | 25.2063 | 25.0372 | 0.16912 | 150.2233 | 23.7 | 24.6792 | -0.97918 |  | 16-03-2026 09:20 | 150.853 | 154.863 | 166.4 | 25.8105 | 25.0372 | 0.77329 | 150.2233 | 23.9 | 24.6792 | -0.77918 |  | 16-03-2026 09:20 | 143.204 | 145.061 | 157.9 | 24.1768 | 23.8198 | 0.35703 | 142.9188 | 22.8 | 23.4792 | -0.67918 |  | 16-03-2026 09:20 | 261.7473 | 259.1696 | 2.5777 | 1555.0176 | 247.5 | 255.4635 | -7.9635
16-03-2026 09:10 | 524 | 48.22 | 185.801 | 188.229 | 188.9 | 31.3715 | 31.2703 | 0.10124 | 187.6215 | 30.6 | 30.8231 | -0.22309 |  | 16-03-2026 09:10 | 185.87 | 189.949 | 188.4 | 31.6582 | 31.2703 | 0.38791 | 187.6215 | 29.9 | 30.8231 | -0.92309 |  | 16-03-2026 09:10 | 183.284 | 186.613 | 185.5 | 31.1022 | 31.2703 | -0.16809 | 187.6215 | 29.4 | 30.8231 | -1.4231 |  | 16-03-2026 09:10 | 187.029 | 189.527 | 189.3 | 31.5878 | 31.2703 | 0.31758 | 187.6215 | 30.1 | 30.8231 | -0.72309 |  | 16-03-2026 09:10 | 137.992 | 139.753 | 138.8 | 23.2922 | 23.1632 | 0.12901 | 138.9789 | 22.1 | 22.8319 | -0.73192 |  | 16-03-2026 09:10 | 138.779 | 140.536 | 141.1 | 23.4227 | 23.1632 | 0.25951 | 138.9789 | 22.3 | 22.8319 | -0.53192 |  | 16-03-2026 09:10 | 138.19 | 139.939 | 140.4 | 23.3232 | 23.1632 | 0.16001 | 138.9789 | 22.2 | 22.8319 | -0.63192 |  | 16-03-2026 09:10 | 139.83 | 143.522 | 142.5 | 23.9203 | 23.1632 | 0.75718 | 138.9789 | 22.5 | 22.8319 | -0.33192 |  | 16-03-2026 09:10 | 132.807 | 134.502 | 135.1 | 22.417 | 22.0369 | 0.38013 | 132.2212 | 21.6 | 21.7217 | -0.12174 |  | 16-03-2026 09:10 | 242.095 | 239.7705 | 2.3245 | 1438.6231 | 230.7 | 236.3418 | -5.6418
16-03-2026 09:00 | 487 | 47.93 | 171.739 | 173.913 | 158.3 | 28.9855 | 29.0944 | -0.10885 | 174.5661 | 27.3 | 28.6783 | -1.3783 |  | 16-03-2026 09:00 | 172.454 | 174.708 | 158.5 | 29.118 | 29.0944 | 0.023649 | 174.5661 | 28.6 | 28.6783 | -0.078301 |  | 16-03-2026 09:00 | 170.199 | 173.541 | 156.1 | 28.9235 | 29.0944 | -0.17085 | 174.5661 | 27 | 28.6783 | -1.6783 |  | 16-03-2026 09:00 | 173.743 | 175.996 | 159.2 | 29.3327 | 29.0944 | 0.23832 | 174.5661 | 27.6 | 28.6783 | -1.0783 |  | 16-03-2026 09:00 | 127.729 | 129.32 | 116.7 | 21.5533 | 21.5514 | 0.0019624 | 129.3082 | 20.4 | 21.2432 | -0.84319 |  | 16-03-2026 09:00 | 128.761 | 130.338 | 118.8 | 21.723 | 21.5514 | 0.17163 | 129.3082 | 20.5 | 21.2432 | -0.74319 |  | 16-03-2026 09:00 | 128.053 | 129.635 | 118.2 | 21.6058 | 21.5514 | 0.054462 | 129.3082 | 20.4 | 21.2432 | -0.84319 |  | 16-03-2026 09:00 | 129.724 | 133.085 | 120 | 22.1808 | 21.5514 | 0.62946 | 129.3082 | 20.7 | 21.2432 | -0.54319 |  | 16-03-2026 09:00 | 122.94 | 124.416 | 113.5 | 20.736 | 20.5035 | 0.23254 | 123.0208 | 19.6 | 20.2103 | -0.61026 |  | 16-03-2026 09:00 | 224.1587 | 223.0863 | 1.0723 | 1338.5181 | 212.1 | 219.8962 | -7.7962
16-03-2026 08:50 | 445 | 47.64 | 156.567 | 158.485 | 131 | 26.4142 | 26.6145 | -0.20036 | 159.6872 | 24.7 | 26.2339 | -1.5339 |  | 16-03-2026 08:50 | 157.419 | 159.396 | 129.9 | 26.566 | 26.6145 | -0.048526 | 159.6872 | 24 | 26.2339 | -2.2339 |  | 16-03-2026 08:50 | 155.305 | 157.864 | 129.1 | 26.3107 | 26.6145 | -0.30386 | 159.6872 | 24.7 | 26.2339 | -1.5339 |  | 16-03-2026 08:50 | 157.343 | 159.144 | 131.6 | 26.524 | 26.6145 | -0.090526 | 159.6872 | 25.2 | 26.2339 | -1.0339 |  | 16-03-2026 08:50 | 116.355 | 117.78 | 96.3 | 19.63 | 19.7145 | -0.084463 | 118.2868 | 18.5 | 19.4325 | -0.93255 |  | 16-03-2026 08:50 | 117.542 | 118.958 | 98.3 | 19.8263 | 19.7145 | 0.11187 | 118.2868 | 18.8 | 19.4325 | -0.63255 |  | 16-03-2026 08:50 | 116.901 | 118.309 | 97.8 | 19.7182 | 19.7145 | 0.0037033 | 118.2868 | 18.6 | 19.4325 | -0.83255 |  | 16-03-2026 08:50 | 118.494 | 121.681 | 99.3 | 20.2802 | 19.7145 | 0.5657 | 118.2868 | 19.1 | 19.4325 | -0.33255 |  | 16-03-2026 08:50 | 112.287 | 113.639 | 93.9 | 18.9398 | 18.7559 | 0.18396 | 112.5352 | 17.9 | 18.4877 | -0.58766 |  | 16-03-2026 08:50 | 204.2093 | 204.0718 | 0.13751 | 1224.431 | 191.5 | 201.1536 | -9.6536
16-03-2026 08:40 | 402 | 47.35 | 142.004 | 143.7 | 106.3 | 23.95 | 24.0693 | -0.11929 | 144.4157 | 22.2 | 23.7251 | -1.5251 |  | 16-03-2026 08:40 | 142.572 | 144.304 | 105.9 | 24.0507 | 24.0693 | -0.018622 | 144.4157 | 22.5 | 23.7251 | -1.2251 |  | 16-03-2026 08:40 | 139.618 | 141.636 | 104.4 | 23.606 | 24.0693 | -0.46329 | 144.4157 | 21.9 | 23.7251 | -1.8251 |  | 16-03-2026 08:40 | 143.286 | 145.012 | 106.4 | 24.1687 | 24.0693 | 0.099378 | 144.4157 | 22.3 | 23.7251 | -1.4251 |  | 16-03-2026 08:40 | 105.21 | 106.445 | 77.8 | 17.7408 | 17.8291 | -0.088269 | 106.9746 | 16.4 | 17.5741 | -1.1741 |  | 16-03-2026 08:40 | 106.431 | 107.68 | 79.5 | 17.9467 | 17.8291 | 0.11756 | 106.9746 | 16.8 | 17.5741 | -0.77415 |  | 16-03-2026 08:40 | 105.906 | 107.149 | 79.2 | 17.8582 | 17.8291 | 0.029064 | 106.9746 | 16.8 | 17.5741 | -0.77415 |  | 16-03-2026 08:40 | 107.29 | 110.066 | 80.2 | 18.3443 | 17.8291 | 0.51523 | 106.9746 | 16.8 | 17.5741 | -0.77415 |  | 16-03-2026 08:40 | 101.643 | 102.846 | 76 | 17.141 | 16.9622 | 0.17882 | 101.7731 | 15.9 | 16.7196 | -0.81962 |  | 16-03-2026 08:40 | 184.8063 | 184.5557 | 0.25059 | 1107.3345 | 171.6 | 181.9166 | -10.3166
16-03-2026 08:30 | 358 | 43.62 | 126.119 | 127.56 | 84.1 | 21.26 | 21.7384 | -0.47842 | 130.4305 | 19.8 | 21.4276 | -1.6276 |  | 16-03-2026 08:30 | 124.961 | 126.428 | 83.4 | 21.0713 | 21.7384 | -0.66708 | 130.4305 | 19.3 | 21.4276 | -2.1276 |  | 16-03-2026 08:30 | 123.606 | 125.197 | 82.5 | 20.8662 | 21.7384 | -0.87225 | 130.4305 | 19.2 | 21.4276 | -2.2276 |  | 16-03-2026 08:30 | 127.189 | 128.598 | 84.1 | 21.433 | 21.7384 | -0.30542 | 130.4305 | 19.8 | 21.4276 | -1.6276 |  | 16-03-2026 08:30 | 92.921 | 94.213 | 61.4 | 15.7022 | 16.1025 | -0.40037 | 96.6152 | 14.5 | 15.8723 | -1.3723 |  | 16-03-2026 08:30 | 94.282 | 95.34 | 62.7 | 15.89 | 16.1025 | -0.21253 | 96.6152 | 14.7 | 15.8723 | -1.1723 |  | 16-03-2026 08:30 | 93.813 | 94.876 | 62.4 | 15.8127 | 16.1025 | -0.28987 | 96.6152 | 14.6 | 15.8723 | -1.2723 |  | 16-03-2026 08:30 | 95.138 | 97.666 | 63.4 | 16.2777 | 16.1025 | 0.17513 | 96.6152 | 14.8 | 15.8723 | -1.0723 |  | 16-03-2026 08:30 | 90.29 | 91.331 | 60.1 | 15.2218 | 15.3196 | -0.097732 | 91.9174 | 14.1 | 15.1005 | -1.0005 |  | 16-03-2026 08:30 | 163.5348 | 166.6834 | -3.1485 | 1000.1002 | 150.8 | 164.2998 | -13.4998
16-03-2026 08:20 | 312 | 34.73 | 108.755 | 109.953 | 64.3 | 18.3255 | 19.5758 | -1.2503 | 117.4547 | 16.6 | 19.2959 | -2.6959 |  | 16-03-2026 08:20 | 109.088 | 110.324 | 64.1 | 18.3873 | 19.5758 | -1.1885 | 117.4547 | 16.8 | 19.2959 | -2.4959 |  | 16-03-2026 08:20 | 107.259 | 108.497 | 63.3 | 18.0828 | 19.5758 | -1.493 | 117.4547 | 16.4 | 19.2959 | -2.8959 |  | 16-03-2026 08:20 | 109.066 | 110.301 | 64.3 | 18.3835 | 19.5758 | -1.1923 | 117.4547 | 16.6 | 19.2959 | -2.6959 |  | 16-03-2026 08:20 | 80.53 | 81.475 | 46.9 | 13.5792 | 14.5006 | -0.92142 | 87.0035 | 12.3 | 14.2932 | -1.9932 |  | 16-03-2026 08:20 | 81.746 | 82.672 | 48 | 13.7787 | 14.5006 | -0.72192 | 87.0035 | 12.4 | 14.2932 | -1.8932 |  | 16-03-2026 08:20 | 81.303 | 82.249 | 47.8 | 13.7082 | 14.5006 | -0.79242 | 87.0035 | 12.4 | 14.2932 | -1.8932 |  | 16-03-2026 08:20 | 82.603 | 84.864 | 48.6 | 14.144 | 14.5006 | -0.35658 | 87.0035 | 12.5 | 14.2932 | -1.7932 |  | 16-03-2026 08:20 | 78.395 | 79.331 | 46 | 13.2218 | 13.7955 | -0.57368 | 82.7731 | 11.9 | 13.5982 | -1.6982 |  | 16-03-2026 08:20 | 141.611 | 150.101 | -8.49 | 900.606 | 127.9 | 147.9546 | -20.0546
16-03-2026 08:10 | 265 | 26.12 | 91.26 | 92.238 | 47.7 | 15.373 | 17.1456 | -1.7726 | 102.8735 | 13.7 | 16.9004 | -3.2004 |  | 16-03-2026 08:10 | 91.252 | 92.221 | 47.3 | 15.3702 | 17.1456 | -1.7754 | 102.8735 | 13.6 | 16.9004 | -3.3004 |  | 16-03-2026 08:10 | 89.845 | 91.093 | 46.9 | 15.1822 | 17.1456 | -1.9634 | 102.8735 | 13.6 | 16.9004 | -3.3004 |  | 16-03-2026 08:10 | 91.899 | 92.912 | 47.7 | 15.4853 | 17.1456 | -1.6603 | 102.8735 | 13.9 | 16.9004 | -3.0004 |  | 16-03-2026 08:10 | 66.389 | 67.195 | 34.6 | 11.1992 | 12.7004 | -1.5013 | 76.2026 | 10.1 | 12.5188 | -2.4188 |  | 16-03-2026 08:10 | 68.499 | 69.303 | 35.6 | 11.5505 | 12.7004 | -1.1499 | 76.2026 | 10.4 | 12.5188 | -2.1188 |  | 16-03-2026 08:10 | 68.046 | 68.872 | 35.4 | 11.4787 | 12.7004 | -1.2218 | 76.2026 | 10.3 | 12.5188 | -2.2188 |  | 16-03-2026 08:10 | 69.16 | 71.072 | 36.1 | 11.8453 | 12.7004 | -0.8551 | 76.2026 | 10.6 | 12.5188 | -1.9188 |  | 16-03-2026 08:10 | 65.693 | 66.491 | 34.1 | 11.0818 | 12.0829 | -1.0011 | 72.4973 | 10 | 11.9101 | -1.9101 |  | 16-03-2026 08:10 | 118.5662 | 131.467 | -12.9008 | 788.8019 | 106.2 | 129.587 | -23.387
16-03-2026 08:00 | 218 | 26.12 | 73.562 | 75.201 | 34 | 12.5335 | 14.1047 | -1.5712 | 84.628 | 11.2 | 13.903 | -2.703 |  | 16-03-2026 08:00 | 74.122 | 74.977 | 33.7 | 12.4962 | 14.1047 | -1.6085 | 84.628 | 11.2 | 13.903 | -2.703 |  | 16-03-2026 08:00 | 72.909 | 73.735 | 33.3 | 12.2892 | 14.1047 | -1.8155 | 84.628 | 10.9 | 13.903 | -3.003 |  | 16-03-2026 08:00 | 74.452 | 75.303 | 33.8 | 12.5505 | 14.1047 | -1.5542 | 84.628 | 11.1 | 13.903 | -2.803 |  | 16-03-2026 08:00 | 54.04 | 54.741 | 24.5 | 9.1235 | 10.4479 | -1.3244 | 62.6874 | 8 | 10.2985 | -2.2985 |  | 16-03-2026 08:00 | 55.552 | 56.249 | 25.2 | 9.3748 | 10.4479 | -1.0731 | 62.6874 | 8.2 | 10.2985 | -2.0985 |  | 16-03-2026 08:00 | 55.2 | 55.928 | 25.1 | 9.3213 | 10.4479 | -1.1266 | 62.6874 | 8.2 | 10.2985 | -2.0985 |  | 16-03-2026 08:00 | 56.141 | 57.896 | 25.5 | 9.6493 | 10.4479 | -0.79857 | 62.6874 | 8.2 | 10.2985 | -2.0985 |  | 16-03-2026 08:00 | 53.382 | 54.091 | 24.1 | 9.0152 | 9.9399 | -0.92472 | 59.6393 | 7.9 | 9.7977 | -1.8977 |  | 16-03-2026 08:00 | 96.3535 | 108.1502 | -11.7967 | 648.9012 | 84.9 | 106.6036 | -21.7036
16-03-2026 07:50 | 174 | 21.52 | 0 | 58.699 | 22.8 | 9.7832 | 11.4398 | -1.6567 | 68.6389 | 8.2 | 11.2762 | -3.0762 |  | 16-03-2026 07:50 | 56.712 | 58.239 | 22.5 | 9.7065 | 11.4398 | -1.7333 | 68.6389 | 8.4 | 11.2762 | -2.8762 |  | 16-03-2026 07:50 | 57.047 | 57.746 | 22.4 | 9.6243 | 11.4398 | -1.8155 | 68.6389 | 8.2 | 11.2762 | -3.0762 |  | 16-03-2026 07:50 | 58.194 | 58.886 | 22.7 | 9.8143 | 11.4398 | -1.6255 | 68.6389 | 8.4 | 11.2762 | -2.8762 |  | 16-03-2026 07:50 | 42.422 | 43.024 | 16.5 | 7.1707 | 8.4739 | -1.3033 | 50.8437 | 6.1 | 8.3528 | -2.2528 |  | 16-03-2026 07:50 | 43.689 | 44.296 | 17 | 7.3827 | 8.4739 | -1.0913 | 50.8437 | 6.4 | 8.3528 | -1.9528 |  | 16-03-2026 07:50 | 43.497 | 44.128 | 16.9 | 7.3547 | 8.4739 | -1.1193 | 50.8437 | 6.3 | 8.3528 | -2.0528 |  | 16-03-2026 07:50 | 44.192 | 45.408 | 17.3 | 7.568 | 8.4739 | -0.90594 | 50.8437 | 6.4 | 8.3528 | -1.9528 |  | 16-03-2026 07:50 | 42.057 | 42.676 | 16.2 | 7.1127 | 8.0619 | -0.94924 | 48.3714 | 6.1 | 7.9466 | -1.8466 |  | 16-03-2026 07:50 | 75.517 | 87.717 | -12.2 | 526.3018 | 64.5 | 86.4626 | -21.9626
16-03-2026 07:40 | 132 | 17.51 | 43.642 | 44.244 | 14.6 | 7.374 | 8.7988 | -1.4248 | 52.7929 | 6.4 | 8.673 | -2.273 |  | 16-03-2026 07:40 | 41.791 | 42.771 | 14.1 | 7.1285 | 8.7988 | -1.6703 | 52.7929 | 6 | 8.673 | -2.673 |  | 16-03-2026 07:40 | 42.687 | 43.289 | 14.2 | 7.2148 | 8.7988 | -1.584 | 52.7929 | 6.1 | 8.673 | -2.573 |  | 16-03-2026 07:40 | 43.518 | 44.14 | 14.3 | 7.3567 | 8.7988 | -1.4422 | 52.7929 | 6.1 | 8.673 | -2.573 |  | 16-03-2026 07:40 | 31.662 | 32.212 | 10.4 | 5.3687 | 6.5176 | -1.149 | 39.1059 | 4.5 | 6.4244 | -1.9244 |  | 16-03-2026 07:40 | 32.595 | 33.095 | 10.6 | 5.5158 | 6.5176 | -1.0018 | 39.1059 | 4.6 | 6.4244 | -1.8244 |  | 16-03-2026 07:40 | 32.525 | 33.04 | 10.6 | 5.5067 | 6.5176 | -1.011 | 39.1059 | 4.5 | 6.4244 | -1.9244 |  | 16-03-2026 07:40 | 33.128 | 34.14 | 10.9 | 5.69 | 6.5176 | -0.82765 | 39.1059 | 4.7 | 6.4244 | -1.7244 |  | 16-03-2026 07:40 | 31.37 | 31.867 | 10.1 | 5.3112 | 6.2007 | -0.88957 | 37.2044 | 4.4 | 6.1121 | -1.7121 |  | 16-03-2026 07:40 | 56.4663 | 67.4666 | -11.0003 | 404.7997 | 47.3 | 66.5018 | -19.2018
16-03-2026 07:30 | 92 | 15.5 | 30.4 | 30.885 | 8.2 | 5.1475 | 6.1746 | -1.0271 | 37.0473 | 4 | 6.0863 | -2.0863 |  | 16-03-2026 07:30 | 28.196 | 30.427 | 8.1 | 5.0712 | 6.1746 | -1.1034 | 37.0473 | 4 | 6.0863 | -2.0863 |  | 16-03-2026 07:30 | 29.825 | 30.313 | 8.1 | 5.0522 | 6.1746 | -1.1224 | 37.0473 | 4 | 6.0863 | -2.0863 |  | 16-03-2026 07:30 | 30.117 | 30.641 | 8.2 | 5.1068 | 6.1746 | -1.0677 | 37.0473 | 4 | 6.0863 | -2.0863 |  | 16-03-2026 07:30 | 22.063 | 22.534 | 5.9 | 3.7557 | 4.5737 | -0.81808 | 27.4425 | 3 | 4.5083 | -1.5083 |  | 16-03-2026 07:30 | 22.755 | 23.203 | 6 | 3.8672 | 4.5737 | -0.70658 | 27.4425 | 3 | 4.5083 | -1.5083 |  | 16-03-2026 07:30 | 22.701 | 23.16 | 6.1 | 3.86 | 4.5737 | -0.71374 | 27.4425 | 3.1 | 4.5083 | -1.4083 |  | 16-03-2026 07:30 | 23.167 | 23.96 | 6.2 | 3.9933 | 4.5737 | -0.58041 | 27.4425 | 3.1 | 4.5083 | -1.4083 |  | 16-03-2026 07:30 | 21.54 | 21.989 | 5.7 | 3.6648 | 4.3513 | -0.68652 | 26.1081 | 2.9 | 4.2891 | -1.3891 |  | 16-03-2026 07:30 | 39.5187 | 47.3445 | -7.8259 | 284.0672 | 31.1 | 46.6675 | -15.5675
16-03-2026 07:20 | 49 | 14.35 | 19.374 | 19.796 | 4.2 | 3.2993 | 3.3014 | -0.002098 | 19.8086 | 2.5 | 3.2542 | -0.75422 |  | 16-03-2026 07:20 | 18.907 | 19.467 | 4.1 | 3.2445 | 3.3014 | -0.056931 | 19.8086 | 2.4 | 3.2542 | -0.85422 |  | 16-03-2026 07:20 | 19.021 | 19.443 | 4.1 | 3.2405 | 3.3014 | -0.060931 | 19.8086 | 2.4 | 3.2542 | -0.85422 |  | 16-03-2026 07:20 | 18.89 | 19.648 | 4.2 | 3.2747 | 3.3014 | -0.026765 | 19.8086 | 2.5 | 3.2542 | -0.75422 |  | 16-03-2026 07:20 | 13.749 | 14.513 | 2.9 | 2.4188 | 2.4455 | -0.026671 | 14.673 | 1.7 | 2.4105 | -0.71053 |  | 16-03-2026 07:20 | 14.163 | 14.528 | 3 | 2.4213 | 2.4455 | -0.024171 | 14.673 | 1.8 | 2.4105 | -0.61053 |  | 16-03-2026 07:20 | 14.209 | 14.588 | 3 | 2.4313 | 2.4455 | -0.014171 | 14.673 | 1.8 | 2.4105 | -0.61053 |  | 16-03-2026 07:20 | 14.475 | 15.196 | 3.1 | 2.5327 | 2.4455 | 0.087162 | 14.673 | 1.8 | 2.4105 | -0.61053 |  | 16-03-2026 07:20 | 13.435 | 13.794 | 2.8 | 2.299 | 2.3266 | -0.027595 | 13.9596 | 1.7 | 2.2933 | -0.59332 |  | 16-03-2026 07:20 | 25.1622 | 25.3143 | -0.15217 | 151.886 | 18.6 | 24.9523 | -6.3523
16-03-2026 07:10 | 28 | 13.49 | 10.065 | 10.415 | 1.7 | 1.7358 | 1.892 | -0.15617 | 11.352 | 1.2 | 1.865 | -0.66495 |  | 16-03-2026 07:10 | 10.395 | 10.983 | 1.7 | 1.8305 | 1.892 | -0.061507 | 11.352 | 1.2 | 1.865 | -0.66495 |  | 16-03-2026 07:10 | 10.491 | 10.847 | 1.7 | 1.8078 | 1.892 | -0.084173 | 11.352 | 1.2 | 1.865 | -0.66495 |  | 16-03-2026 07:10 | 10.553 | 11.409 | 1.7 | 1.9015 | 1.892 | 0.0094934 | 11.352 | 1.2 | 1.865 | -0.66495 |  | 16-03-2026 07:10 | 7.618 | 8.359 | 1.2 | 1.3932 | 1.4015 | -0.0083197 | 8.4089 | 0.9 | 1.3814 | -0.48145 |  | 16-03-2026 07:10 | 7.704 | 8.002 | 1.2 | 1.3337 | 1.4015 | -0.06782 | 8.4089 | 0.9 | 1.3814 | -0.48145 |  | 16-03-2026 07:10 | 7.663 | 7.962 | 1.2 | 1.327 | 1.4015 | -0.074486 | 8.4089 | 0.9 | 1.3814 | -0.48145 |  | 16-03-2026 07:10 | 7.911 | 8.59 | 1.3 | 1.4317 | 1.4015 | 0.03018 | 8.4089 | 1 | 1.3814 | -0.38145 |  | 16-03-2026 07:10 | 7.287 | 7.573 | 1.1 | 1.2622 | 1.3333 | -0.071174 | 8 | 0.8 | 1.3143 | -0.51427 |  | 16-03-2026 07:10 | 14.0233 | 14.5073 | -0.48398 | 87.0439 | 9.3 | 14.2999 | -4.9999
16-03-2026 07:00 | 13 | 13.49 | 4.896 | 5.117 | 0.5 | 0.85283 | 0.87843 | -0.025598 | 5.2706 | 0.5 | 0.86587 | -0.36587 |  | 16-03-2026 07:00 | 4.924 | 5.637 | 0.5 | 0.9395 | 0.87843 | 0.061068 | 5.2706 | 0.5 | 0.86587 | -0.36587 |  | 16-03-2026 07:00 | 4.77 | 4.988 | 0.5 | 0.83133 | 0.87843 | -0.047098 | 5.2706 | 0.5 | 0.86587 | -0.36587 |  | 16-03-2026 07:00 | 4.854 | 5.618 | 0.5 | 0.93633 | 0.87843 | 0.057902 | 5.2706 | 0.5 | 0.86587 | -0.36587 |  | 16-03-2026 07:00 | 3.396 | 4.168 | 0.3 | 0.69467 | 0.65069 | 0.043977 | 3.9041 | 0.3 | 0.64139 | -0.34139 |  | 16-03-2026 07:00 | 3.459 | 3.616 | 0.3 | 0.60267 | 0.65069 | -0.048023 | 3.9041 | 0.3 | 0.64139 | -0.34139 |  | 16-03-2026 07:00 | 3.449 | 3.615 | 0.3 | 0.6025 | 0.65069 | -0.04819 | 3.9041 | 0.3 | 0.64139 | -0.34139 |  | 16-03-2026 07:00 | 3.572 | 3.985 | 0.3 | 0.66417 | 0.65069 | 0.013477 | 3.9041 | 0.3 | 0.64139 | -0.34139 |  | 16-03-2026 07:00 | 3.294 | 3.453 | 0.3 | 0.5755 | 0.61905 | -0.043551 | 3.7143 | 0.3 | 0.6102 | -0.3102 |  | 16-03-2026 07:00 | 6.6995 | 6.7355 | -0.036038 | 40.4132 | 3.5 | 6.6392 | -3.1392
[110 empty] | Total: - | 18941.4833 | 19750.4208 | -808.9375 |  | 18822.5 | 19467.9898 | -645.4898
Sum:- | 43126 |  | 14496.01 |  | 93513.9 |  |  |  |  | 2442.2 | 2538.9654 | -96.7654 | 0.98494 |  | 14167.054 |  | 91683.4 |  |  |  |  | 2460.5 | 2538.9654 | -78.4654 | 0.98299 |  | 14461.134 |  | 92958.8 |  |  |  |  | 2430.3 | 2538.9654 | -108.6654 | 0.9726 |  | 14518.187 |  | 93503.8 |  |  |  |  | 2440.4 | 2538.9654 | -98.5654 | 0.9837 |  | 10958.358 |  | 70344.3 |  |  |  |  | 1840.4 | 1880.7151 | -40.3151 | 0.9845 |  | 10826.515 |  | 69830.8 |  |  |  |  | 1820.6 | 1880.7151 | -60.1151 | 0.98165 |  | 10837.192 |  | 69781.2 |  |  |  |  | 1820.7 | 1880.7151 | -60.0151 | 0.98088 |  | 10922.364 |  | 70380.2 |  |  |  |  | 1834.1 | 1880.7151 | -46.6151 | 0.9713 |  | 10305.216 |  | 66553 |  |  |  |  | 1733.3 | 1789.2675 | -55.9675 | 0.98473

## 17 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
17-03-2026 19:00 | 0 | 34.15 | 0.076 | 0.093 | 2022.8 | 0.0155 | 0 | 0.0155 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0 | 0.251 | 2037.4 | 0.041833 | 0 | 0.041833 | 0 | 0.1 | 0 | 0.1 |  | 17-03-2026 19:00 | 0.095 | 0.1 | 2006.1 | 0.016667 | 0 | 0.016667 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.093 | 0.13 | 2019.6 | 0.021667 | 0 | 0.021667 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.103 | 0.108 | 1512.3 | 0.018 | 0 | 0.018 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.09 | 0.095 | 1497.8 | 0.015833 | 0 | 0.015833 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.067 | 0.07 | 1501.9 | 0.011667 | 0 | 0.011667 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.103 | 0.108 | 1519.7 | 0.018 | 0 | 0.018 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.052 | 0.057 | 1432.8 | 0.0095 | 0 | 0.0095 | 0 | 0 | 0 | 0 |  | 17-03-2026 19:00 | 0.16867 | 0 | 0.16867 | 0 | 0.1 | 0 | 0.1 | 1 | 99.1%
17-03-2026 18:50 | 0 | 36.16 | 0.477 | 0.502 | 2022.8 | 0.083667 | 0 | 0.083667 | 0 | 0.3 | 0 | 0.3 |  | 17-03-2026 18:50 | 0.579 | 0.797 | 2037.3 | 0.13283 | 0 | 0.13283 | 0 | 0.3 | 0 | 0.3 |  | 17-03-2026 18:50 | 0.474 | 0.455 | 2006.1 | 0.075833 | 0 | 0.075833 | 0 | 0.3 | 0 | 0.3 |  | 17-03-2026 18:50 | 0.482 | 0.88 | 2019.6 | 0.14667 | 0 | 0.14667 | 0 | 0.4 | 0 | 0.4 |  | 17-03-2026 18:50 | 0.171 | 0.263 | 1512.3 | 0.043833 | 0 | 0.043833 | 0 | 0.2 | 0 | 0.2 |  | 17-03-2026 18:50 | 0.125 | 0.131 | 1497.8 | 0.021833 | 0 | 0.021833 | 0 | 0.2 | 0 | 0.2 |  | 17-03-2026 18:50 | 0.111 | 0.117 | 1501.8 | 0.0195 | 0 | 0.0195 | 0 | 0.2 | 0 | 0.2 |  | 17-03-2026 18:50 | 0.317 | 0.524 | 1519.7 | 0.087333 | 0 | 0.087333 | 0 | 0.3 | 0 | 0.3 |  | 17-03-2026 18:50 | 0.125 | 0.131 | 1432.8 | 0.021833 | 0 | 0.021833 | 0 | 0.2 | 0 | 0.2 |  | 17-03-2026 18:50 | 0.63333 | 0 | 0.63333 | 0 | 2.4 | 0 | 2.4 | 2 | 98.49%
17-03-2026 18:40 | 5 | 38.75 | 3.777 | 3.969 | 2022.5 | 0.6615 | 0.30914 | 0.35236 | 1.8549 | 1.2 | 0.30472 | 0.89528 |  | 17-03-2026 18:40 | 3.958 | 4.292 | 2037 | 0.71533 | 0.30914 | 0.40619 | 1.8549 | 1.2 | 0.30472 | 0.89528 |  | 17-03-2026 18:40 | 3.707 | 3.898 | 2005.8 | 0.64967 | 0.30914 | 0.34052 | 1.8549 | 1.2 | 0.30472 | 0.89528 |  | 17-03-2026 18:40 | 3.802 | 4.238 | 2019.2 | 0.70633 | 0.30914 | 0.39719 | 1.8549 | 1.1 | 0.30472 | 0.79528 |  | 17-03-2026 18:40 | 2.483 | 2.671 | 1512.1 | 0.44517 | 0.229 | 0.21617 | 1.374 | 0.8 | 0.22572 | 0.57428 |  | 17-03-2026 18:40 | 2.315 | 2.434 | 1497.6 | 0.40567 | 0.229 | 0.17667 | 1.374 | 0.8 | 0.22572 | 0.57428 |  | 17-03-2026 18:40 | 2.602 | 2.736 | 1501.6 | 0.456 | 0.229 | 0.227 | 1.374 | 0.8 | 0.22572 | 0.57428 |  | 17-03-2026 18:40 | 2.702 | 3.03 | 1519.4 | 0.505 | 0.229 | 0.276 | 1.374 | 0.8 | 0.22572 | 0.57428 |  | 17-03-2026 18:40 | 2.441 | 2.567 | 1432.6 | 0.42783 | 0.21786 | 0.20997 | 1.3072 | 0.7 | 0.21475 | 0.48525 |  | 17-03-2026 18:40 | 4.9725 | 2.3704 | 2.6021 | 14.2226 | 8.6 | 2.3365 | 6.2635 | 3 | 97.47%
17-03-2026 18:30 | 25 | 41.04 | 11.315 | 11.728 | 2021.3 | 1.9547 | 1.5327 | 0.42196 | 9.1963 | 2.2 | 1.5108 | 0.68921 |  | 17-03-2026 18:30 | 11.42 | 11.847 | 2035.8 | 1.9745 | 1.5327 | 0.44179 | 9.1963 | 2.3 | 1.5108 | 0.78921 |  | 17-03-2026 18:30 | 10.865 | 11.268 | 2004.6 | 1.878 | 1.5327 | 0.34529 | 9.1963 | 2.2 | 1.5108 | 0.68921 |  | 17-03-2026 18:30 | 11.026 | 11.435 | 2018.1 | 1.9058 | 1.5327 | 0.37312 | 9.1963 | 2.3 | 1.5108 | 0.78921 |  | 17-03-2026 18:30 | 7.94 | 8.278 | 1511.3 | 1.3797 | 1.1353 | 0.24433 | 6.812 | 1.7 | 1.1191 | 0.58089 |  | 17-03-2026 18:30 | 7.909 | 8.241 | 1496.8 | 1.3735 | 1.1353 | 0.23816 | 6.812 | 1.6 | 1.1191 | 0.48089 |  | 17-03-2026 18:30 | 7.856 | 8.189 | 1500.8 | 1.3648 | 1.1353 | 0.22949 | 6.812 | 1.7 | 1.1191 | 0.58089 |  | 17-03-2026 18:30 | 7.84 | 8.348 | 1518.6 | 1.3913 | 1.1353 | 0.25599 | 6.812 | 1.7 | 1.1191 | 0.58089 |  | 17-03-2026 18:30 | 7.358 | 7.677 | 1431.9 | 1.2795 | 1.0801 | 0.19936 | 6.4808 | 1.6 | 1.0647 | 0.53531 |  | 17-03-2026 18:30 | 14.5018 | 11.7523 | 2.7495 | 70.514 | 17.3 | 11.5843 | 5.7157 | 4 | 98.4%
17-03-2026 18:20 | 37 | 42.76 | 14.522 | 14.963 | 2019.1 | 2.4938 | 2.2539 | 0.23989 | 13.5237 | 3.1 | 2.2217 | 0.87829 |  | 17-03-2026 18:20 | 14.925 | 15.379 | 2033.5 | 2.5632 | 2.2539 | 0.30922 | 13.5237 | 3.2 | 2.2217 | 0.97829 |  | 17-03-2026 18:20 | 14.42 | 14.868 | 2002.4 | 2.478 | 2.2539 | 0.22406 | 13.5237 | 3.1 | 2.2217 | 0.87829 |  | 17-03-2026 18:20 | 14.515 | 14.972 | 2015.8 | 2.4953 | 2.2539 | 0.24139 | 13.5237 | 3.1 | 2.2217 | 0.87829 |  | 17-03-2026 18:20 | 10.69 | 11.093 | 1509.6 | 1.8488 | 1.6696 | 0.17925 | 10.0175 | 2.3 | 1.6457 | 0.65429 |  | 17-03-2026 18:20 | 10.57 | 10.941 | 1495.2 | 1.8235 | 1.6696 | 0.15391 | 10.0175 | 2.3 | 1.6457 | 0.65429 |  | 17-03-2026 18:20 | 10.595 | 10.971 | 1499.1 | 1.8285 | 1.6696 | 0.15891 | 10.0175 | 2.2 | 1.6457 | 0.55429 |  | 17-03-2026 18:20 | 10.558 | 11.057 | 1516.9 | 1.8428 | 1.6696 | 0.17325 | 10.0175 | 2.2 | 1.6457 | 0.55429 |  | 17-03-2026 18:20 | 9.892 | 10.276 | 1430.3 | 1.7127 | 1.5884 | 0.12426 | 9.5304 | 2.1 | 1.5657 | 0.53431 |  | 17-03-2026 18:20 | 19.0867 | 17.2825 | 1.8041 | 103.6951 | 23.6 | 17.0354 | 6.5646 | 5 | 98.48%
17-03-2026 18:10 | 64 | 44.77 | 26.425 | 27.018 | 2016 | 4.503 | 3.8695 | 0.63353 | 23.2168 | 5 | 3.8141 | 1.1859 |  | 17-03-2026 18:10 | 27.142 | 27.727 | 2030.3 | 4.6212 | 3.8695 | 0.7517 | 23.2168 | 5 | 3.8141 | 1.1859 |  | 17-03-2026 18:10 | 26.729 | 27.305 | 1999.3 | 4.5508 | 3.8695 | 0.68137 | 23.2168 | 4.9 | 3.8141 | 1.0859 |  | 17-03-2026 18:10 | 26.885 | 27.459 | 2012.7 | 4.5765 | 3.8695 | 0.70703 | 23.2168 | 4.9 | 3.8141 | 1.0859 |  | 17-03-2026 18:10 | 19.751 | 20.245 | 1507.3 | 3.3742 | 2.8663 | 0.5079 | 17.1976 | 3.6 | 2.8253 | 0.77472 |  | 17-03-2026 18:10 | 19.518 | 20.023 | 1492.9 | 3.3372 | 2.8663 | 0.4709 | 17.1976 | 3.6 | 2.8253 | 0.77472 |  | 17-03-2026 18:10 | 19.437 | 19.952 | 1496.9 | 3.3253 | 2.8663 | 0.45906 | 17.1976 | 3.6 | 2.8253 | 0.77472 |  | 17-03-2026 18:10 | 18.406 | 19.16 | 1514.7 | 3.1933 | 2.8663 | 0.32706 | 17.1976 | 3.5 | 2.8253 | 0.67472 |  | 17-03-2026 18:10 | 18.057 | 18.524 | 1428.2 | 3.0873 | 2.7269 | 0.36043 | 16.3614 | 3.4 | 2.6879 | 0.71209 |  | 17-03-2026 18:10 | 34.5688 | 29.6698 | 4.899 | 178.0191 | 37.5 | 29.2456 | 8.2544 | 6 | 98.32%
17-03-2026 18:00 | 69 | 46.49 | 27.382 | 27.969 | 2011 | 4.6615 | 4.1448 | 0.51671 | 24.8687 | 5.1 | 4.0855 | 1.0145 |  | 17-03-2026 18:00 | 27.693 | 28.293 | 2025.3 | 4.7155 | 4.1448 | 0.57071 | 24.8687 | 5.2 | 4.0855 | 1.1145 |  | 17-03-2026 18:00 | 27.73 | 28.325 | 1994.4 | 4.7208 | 4.1448 | 0.57605 | 24.8687 | 5 | 4.0855 | 0.91448 |  | 17-03-2026 18:00 | 27.753 | 28.354 | 2007.8 | 4.7257 | 4.1448 | 0.58088 | 24.8687 | 5.1 | 4.0855 | 1.0145 |  | 17-03-2026 18:00 | 20.808 | 21.282 | 1503.7 | 3.547 | 3.0702 | 0.47679 | 18.4213 | 3.9 | 3.0263 | 0.87369 |  | 17-03-2026 18:00 | 20.497 | 20.999 | 1489.3 | 3.4998 | 3.0702 | 0.42962 | 18.4213 | 3.8 | 3.0263 | 0.77369 |  | 17-03-2026 18:00 | 20.597 | 21.072 | 1493.3 | 3.512 | 3.0702 | 0.44179 | 18.4213 | 3.7 | 3.0263 | 0.67369 |  | 17-03-2026 18:00 | 19.947 | 20.738 | 1511.2 | 3.4563 | 3.0702 | 0.38612 | 18.4213 | 3.7 | 3.0263 | 0.67369 |  | 17-03-2026 18:00 | 19.094 | 19.58 | 1424.8 | 3.2633 | 2.9209 | 0.34241 | 17.5256 | 3.5 | 2.8792 | 0.62084 |  | 17-03-2026 18:00 | 36.102 | 31.7809 | 4.3211 | 190.6855 | 39 | 31.3265 | 7.6735 | 7 | 98.27%
17-03-2026 17:50 | 106 | 47.07 | 41.421 | 40.627 | 2005.9 | 6.7712 | 6.3534 | 0.41779 | 38.1203 | 10.4 | 6.2625 | 4.1375 |  | 17-03-2026 17:50 | 41.061 | 41.805 | 2020.1 | 6.9675 | 6.3534 | 0.61412 | 38.1203 | 10.5 | 6.2625 | 4.2375 |  | 17-03-2026 17:50 | 38.929 | 39.639 | 1989.4 | 6.6065 | 6.3534 | 0.25312 | 38.1203 | 10.6 | 6.2625 | 4.3375 |  | 17-03-2026 17:50 | 39.74 | 40.468 | 2002.7 | 6.7447 | 6.3534 | 0.39129 | 38.1203 | 10.5 | 6.2625 | 4.2375 |  | 17-03-2026 17:50 | 29.293 | 29.888 | 1499.8 | 4.9813 | 4.7062 | 0.27513 | 28.2372 | 7.7 | 4.6389 | 3.0611 |  | 17-03-2026 17:50 | 29.171 | 29.763 | 1485.5 | 4.9605 | 4.7062 | 0.2543 | 28.2372 | 7.6 | 4.6389 | 2.9611 |  | 17-03-2026 17:50 | 28.834 | 29.422 | 1489.6 | 4.9037 | 4.7062 | 0.19746 | 28.2372 | 7.7 | 4.6389 | 3.0611 |  | 17-03-2026 17:50 | 28.801 | 29.681 | 1507.5 | 4.9468 | 4.7062 | 0.24063 | 28.2372 | 7.6 | 4.6389 | 2.9611 |  | 17-03-2026 17:50 | 27.267 | 27.855 | 1421.3 | 4.6425 | 4.4774 | 0.16513 | 26.8642 | 7.2 | 4.4133 | 2.7867 |  | 17-03-2026 17:50 | 51.5247 | 48.7157 | 2.809 | 292.2941 | 79.8 | 48.0191 | 31.7809 | 8 | 97.22%
17-03-2026 17:40 | 221 | 47.35 | 77.586 | 78.363 | 1995.5 | 13.0605 | 13.2321 | -0.17162 | 79.3927 | 12.7 | 13.0429 | -0.3429 |  | 17-03-2026 17:40 | 78.166 | 79.196 | 2009.6 | 13.1993 | 13.2321 | -0.032788 | 79.3927 | 13.3 | 13.0429 | 0.2571 |  | 17-03-2026 17:40 | 77.424 | 78.548 | 1978.8 | 13.0913 | 13.2321 | -0.14079 | 79.3927 | 12.8 | 13.0429 | -0.2429 |  | 17-03-2026 17:40 | 77.373 | 78.392 | 1992.2 | 13.0653 | 13.2321 | -0.16679 | 79.3927 | 12.8 | 13.0429 | -0.2429 |  | 17-03-2026 17:40 | 57.183 | 58.024 | 1492.1 | 9.6707 | 9.8016 | -0.1309 | 58.8094 | 9.6 | 9.6614 | -0.061409 |  | 17-03-2026 17:40 | 56.953 | 57.779 | 1477.9 | 9.6298 | 9.8016 | -0.17174 | 58.8094 | 9.6 | 9.6614 | -0.061409 |  | 17-03-2026 17:40 | 56.995 | 57.85 | 1481.9 | 9.6417 | 9.8016 | -0.1599 | 58.8094 | 9.6 | 9.6614 | -0.061409 |  | 17-03-2026 17:40 | 56.67 | 58.29 | 1499.9 | 9.715 | 9.8016 | -0.086571 | 58.8094 | 9.5 | 9.6614 | -0.16141 |  | 17-03-2026 17:40 | 53.572 | 54.382 | 1414.1 | 9.0637 | 9.325 | -0.26131 | 55.9499 | 9 | 9.1916 | -0.19163 |  | 17-03-2026 17:40 | 100.1373 | 101.4598 | -1.3224 | 608.7585 | 98.9 | 100.0089 | -1.1089 | 9 | 98.5%
17-03-2026 17:30 | 209 | 47.64 | 74.256 | 75.226 | 1982.8 | 12.5377 | 12.4999 | 0.037811 | 74.9991 | 10.6 | 12.3211 | -1.7211 |  | 17-03-2026 17:30 | 75.492 | 76.51 | 1996.3 | 12.7517 | 12.4999 | 0.25181 | 74.9991 | 19.5 | 12.3211 | 7.1789 |  | 17-03-2026 17:30 | 74.444 | 75.432 | 1966 | 12.572 | 12.4999 | 0.072144 | 74.9991 | 10.5 | 12.3211 | -1.8211 |  | 17-03-2026 17:30 | 74.498 | 75.487 | 1979.4 | 12.5812 | 12.4999 | 0.081311 | 74.9991 | 10.4 | 12.3211 | -1.9211 |  | 17-03-2026 17:30 | 54.966 | 55.797 | 1482.5 | 9.2995 | 9.2592 | 0.040348 | 55.5549 | 7.9 | 9.1267 | -1.2267 |  | 17-03-2026 17:30 | 54.847 | 55.66 | 1468.3 | 9.2767 | 9.2592 | 0.017514 | 55.5549 | 7.8 | 9.1267 | -1.3267 |  | 17-03-2026 17:30 | 54.607 | 55.433 | 1472.3 | 9.2388 | 9.2592 | -0.020319 | 55.5549 | 7.8 | 9.1267 | -1.3267 |  | 17-03-2026 17:30 | 54.39 | 55.809 | 1490.4 | 9.3015 | 9.2592 | 0.042348 | 55.5549 | 7.8 | 9.1267 | -1.3267 |  | 17-03-2026 17:30 | 51.467 | 52.356 | 1405.1 | 8.726 | 8.8089 | -0.082937 | 52.8536 | 7.4 | 8.683 | -1.283 |  | 17-03-2026 17:30 | 96.285 | 95.845 | 0.44003 | 575.0698 | 89.7 | 94.4744 | -4.7744
17-03-2026 17:20 | 166 | 47.64 | 58.031 | 58.86 | 1972.2 | 9.81 | 9.9281 | -0.11812 | 59.5687 | 9.1 | 9.7861 | -0.68614 | [5 empty] | 0 | 9.9281 | -9.9281 | 59.5687 | 0 | 9.7861 | -9.7861 |  | 17-03-2026 17:20 | 59.667 | 60.563 | 1955.5 | 10.0938 | 9.9281 | 0.16572 | 59.5687 | 8.8 | 9.7861 | -0.98614 |  | 17-03-2026 17:20 | 60.291 | 61.159 | 1969 | 10.1932 | 9.9281 | 0.26505 | 59.5687 | 8.8 | 9.7861 | -0.98614 |  | 17-03-2026 17:20 | 45.421 | 46.192 | 1474.6 | 7.6987 | 7.3542 | 0.34451 | 44.125 | 6.5 | 7.249 | -0.74899 |  | 17-03-2026 17:20 | 44.806 | 45.558 | 1460.5 | 7.593 | 7.3542 | 0.23884 | 44.125 | 6.4 | 7.249 | -0.84899 |  | 17-03-2026 17:20 | 45.306 | 46.121 | 1464.5 | 7.6868 | 7.3542 | 0.33267 | 44.125 | 6.4 | 7.249 | -0.84899 |  | 17-03-2026 17:20 | 45.437 | 46.823 | 1482.6 | 7.8038 | 7.3542 | 0.44967 | 44.125 | 6.4 | 7.249 | -0.84899 |  | 17-03-2026 17:20 | 42.895 | 43.632 | 1397.7 | 7.272 | 6.9966 | 0.27543 | 41.9794 | 6.2 | 6.8965 | -0.69652 |  | 17-03-2026 17:20 | 68.1513 | 76.1257 | -7.9743 | 456.754 | 58.6 | 75.0371 | -16.4371
17-03-2026 17:10 | 188 | 47.64 | 67.043 | 67.988 | 1963.1 | 11.3313 | 11.2439 | 0.087444 | 67.4633 | 13.6 | 11.0831 | 2.5169 |  | 17-03-2026 17:10 | 67.881 | 68.926 | 1976.8 | 11.4877 | 11.2439 | 0.24378 | 67.4633 | 13.6 | 11.0831 | 2.5169 |  | 17-03-2026 17:10 | 66.759 | 67.721 | 1946.7 | 11.2868 | 11.2439 | 0.042944 | 67.4633 | 13.7 | 11.0831 | 2.6169 |  | 17-03-2026 17:10 | 67.412 | 68.376 | 1960.2 | 11.396 | 11.2439 | 0.15211 | 67.4633 | 13.6 | 11.0831 | 2.5169 |  | 17-03-2026 17:10 | 48.603 | 49.659 | 1468.1 | 8.2765 | 8.3288 | -0.052307 | 49.9728 | 10 | 8.2097 | 1.7903 |  | 17-03-2026 17:10 | 48.802 | 49.616 | 1454.1 | 8.2693 | 8.3288 | -0.059474 | 49.9728 | 9.9 | 8.2097 | 1.6903 |  | 17-03-2026 17:10 | 47.654 | 48.71 | 1458.1 | 8.1183 | 8.3288 | -0.21047 | 49.9728 | 9.9 | 8.2097 | 1.6903 |  | 17-03-2026 17:10 | 47.323 | 48.743 | 1476.2 | 8.1238 | 8.3288 | -0.20497 | 49.9728 | 9.9 | 8.2097 | 1.6903 |  | 17-03-2026 17:10 | 46.739 | 47.538 | 1391.5 | 7.923 | 7.9238 | -0.0008283 | 47.543 | 9.3 | 7.8105 | 1.4895 |  | 17-03-2026 17:10 | 86.2128 | 86.2146 | -0.0017807 | 517.2877 | 103.5 | 84.9817 | 18.5183
17-03-2026 17:00 | 328 | 47.93 | 118.361 | 119.847 | 1949.5 | 19.9745 | 19.5954 | 0.37913 | 117.5722 | 20.9 | 19.3152 | 1.5848 |  | 17-03-2026 17:00 | 117.23 | 118.738 | 1963.2 | 19.7897 | 19.5954 | 0.19429 | 117.5722 | 22.1 | 19.3152 | 2.7848 |  | 17-03-2026 17:00 | 115.505 | 117.352 | 1933 | 19.5587 | 19.5954 | -0.036707 | 117.5722 | 20.9 | 19.3152 | 1.5848 |  | 17-03-2026 17:00 | 114.574 | 116.048 | 1946.6 | 19.3413 | 19.5954 | -0.25404 | 117.5722 | 21 | 19.3152 | 1.6848 |  | 17-03-2026 17:00 | 83.668 | 84.787 | 1458.1 | 14.1312 | 14.5151 | -0.38393 | 87.0906 | 15.7 | 14.3075 | 1.3925 |  | 17-03-2026 17:00 | 83.293 | 84.382 | 1444.2 | 14.0637 | 14.5151 | -0.45143 | 87.0906 | 15.7 | 14.3075 | 1.3925 |  | 17-03-2026 17:00 | 81.199 | 82.277 | 1448.2 | 13.7128 | 14.5151 | -0.80226 | 87.0906 | 15.8 | 14.3075 | 1.4925 |  | 17-03-2026 17:00 | 80.097 | 81.786 | 1466.3 | 13.631 | 14.5151 | -0.88409 | 87.0906 | 15.7 | 14.3075 | 1.3925 |  | 17-03-2026 17:00 | 79.203 | 80.279 | 1382.2 | 13.3798 | 13.8093 | -0.42948 | 82.8559 | 14.8 | 13.6118 | 1.1882 |  | 17-03-2026 17:00 | 147.5827 | 150.2512 | -2.6685 | 901.507 | 162.6 | 148.1026 | 14.4974
17-03-2026 16:50 | 404 | 48.22 | 141.026 | 142.826 | 1928.6 | 23.8043 | 24.1091 | -0.3048 | 144.6548 | 55.3 | 23.7644 | 31.5356 |  | 17-03-2026 16:50 | 140.082 | 141.941 | 1941.1 | 23.6568 | 24.1091 | -0.4523 | 144.6548 | 24.5 | 23.7644 | 0.73563 |  | 17-03-2026 16:50 | 140.59 | 143.261 | 1912.1 | 23.8768 | 24.1091 | -0.2323 | 144.6548 | 25.2 | 23.7644 | 1.4356 |  | 17-03-2026 16:50 | 139.926 | 141.769 | 1925.6 | 23.6282 | 24.1091 | -0.48096 | 144.6548 | 25.2 | 23.7644 | 1.4356 |  | 17-03-2026 16:50 | 104.935 | 106.285 | 1442.4 | 17.7142 | 17.8586 | -0.14445 | 107.1517 | 18.9 | 17.6032 | 1.2968 |  | 17-03-2026 16:50 | 102.613 | 103.922 | 1428.5 | 17.3203 | 17.8586 | -0.53828 | 107.1517 | 18.3 | 17.6032 | 0.69676 |  | 17-03-2026 16:50 | 103.671 | 104.994 | 1432.4 | 17.499 | 17.8586 | -0.35961 | 107.1517 | 18.4 | 17.6032 | 0.79676 |  | 17-03-2026 16:50 | 103.32 | 106.264 | 1450.6 | 17.7107 | 17.8586 | -0.14795 | 107.1517 | 18.6 | 17.6032 | 0.99676 |  | 17-03-2026 16:50 | 97.601 | 98.785 | 1367.4 | 16.4642 | 16.9903 | -0.52609 | 101.9416 | 17.6 | 16.7473 | 0.8527 |  | 17-03-2026 16:50 | 181.6745 | 184.8612 | -3.1867 | 1109.1674 | 222 | 182.2177 | 39.7823
17-03-2026 16:40 | 402 | 48.79 | 143.649 | 145.541 | 1903 | 24.2568 | 23.9377 | 0.31915 | 143.6261 | 0 | 23.5954 | -23.5954 |  | 17-03-2026 16:40 | 141.655 | 143.564 | 1916.6 | 23.9273 | 23.9377 | -0.010351 | 143.6261 | 29.1 | 23.5954 | 5.5046 |  | 17-03-2026 16:40 | 139.327 | 141.768 | 1886.9 | 23.628 | 23.9377 | -0.30968 | 143.6261 | 28.7 | 23.5954 | 5.1046 |  | 17-03-2026 16:40 | 139.846 | 141.745 | 1900.4 | 23.6242 | 23.9377 | -0.31352 | 143.6261 | 28.7 | 23.5954 | 5.1046 |  | 17-03-2026 16:40 | 103.846 | 105.182 | 1423.5 | 17.5303 | 17.7316 | -0.20128 | 106.3897 | 21.7 | 17.4781 | 4.2219 |  | 17-03-2026 16:40 | 103.186 | 104.534 | 1410.2 | 17.4223 | 17.7316 | -0.30928 | 106.3897 | 21.4 | 17.4781 | 3.9219 |  | 17-03-2026 16:40 | 101.797 | 103.127 | 1414 | 17.1878 | 17.7316 | -0.54378 | 106.3897 | 21.5 | 17.4781 | 4.0219 |  | 17-03-2026 16:40 | 103.624 | 106.522 | 1432 | 17.7537 | 17.7316 | 0.022049 | 106.3897 | 21.4 | 17.4781 | 3.9219 |  | 17-03-2026 16:40 | 98.159 | 99.442 | 1349.8 | 16.5737 | 16.8694 | -0.29577 | 101.2166 | 20.2 | 16.6282 | 3.5718 |  | 17-03-2026 16:40 | 181.9042 | 183.5466 | -1.6425 | 1101.2799 | 192.7 | 180.9219 | 11.7781
17-03-2026 16:30 | 524 | 48.5 | 180.947 | 183.423 | 1873.3 | 30.5705 | 31.2369 | -0.6664 | 187.4214 | 27.1 | 30.7902 | -3.6902 |  | 17-03-2026 16:30 | 180.814 | 187.327 | 1887.5 | 31.2212 | 31.2369 | -0.015735 | 187.4214 | 28.5 | 30.7902 | -2.2902 |  | 17-03-2026 16:30 | 182.816 | 186.939 | 1858.2 | 31.1565 | 31.2369 | -0.080402 | 187.4214 | 28.2 | 30.7902 | -2.5902 |  | 17-03-2026 16:30 | 183.27 | 185.816 | 1871.7 | 30.9693 | 31.2369 | -0.26757 | 187.4214 | 28.4 | 30.7902 | -2.3902 |  | 17-03-2026 16:30 | 136.923 | 138.741 | 1401.8 | 23.1235 | 23.1384 | -0.014946 | 138.8307 | 21.5 | 22.8076 | -1.3076 |  | 17-03-2026 16:30 | 134.768 | 136.557 | 1388.8 | 22.7595 | 23.1384 | -0.37895 | 138.8307 | 21.1 | 22.8076 | -1.7076 |  | 17-03-2026 16:30 | 135.99 | 137.809 | 1392.5 | 22.9682 | 23.1384 | -0.17028 | 138.8307 | 21.2 | 22.8076 | -1.6076 |  | 17-03-2026 16:30 | 136.757 | 140.566 | 1410.6 | 23.4277 | 23.1384 | 0.28922 | 138.8307 | 22.5 | 22.8076 | -0.30757 |  | 17-03-2026 16:30 | 129.16 | 130.888 | 1329.6 | 21.8147 | 22.0134 | -0.1987 | 132.0802 | 20.3 | 21.6986 | -1.3986 |  | 17-03-2026 16:30 | 238.011 | 239.5148 | -1.5038 | 1437.0885 | 218.8 | 236.0897 | -17.2897
17-03-2026 16:20 | 555 | 48.5 | 0 | 0 | 1846.2 | 0 | 33.0849 | -33.0849 | 198.5093 | 23.8 | 32.6118 | -8.8118 |  | 17-03-2026 16:20 | 0 | 0 | 1859 | 0 | 33.0849 | -33.0849 | 198.5093 | 23.6 | 32.6118 | -9.0118 |  | 17-03-2026 16:20 | 0 | 0 | 1830 | 0 | 33.0849 | -33.0849 | 198.5093 | 22.4 | 32.6118 | -10.2118 |  | 17-03-2026 16:20 | 0 | 0 | 1843.3 | 0 | 33.0849 | -33.0849 | 198.5093 | 22.4 | 32.6118 | -10.2118 |  | 17-03-2026 16:20 | 0 | 0 | 1380.3 | 0 | 24.5073 | -24.5073 | 147.0439 | 16.6 | 24.1569 | -7.5569 |  | 17-03-2026 16:20 | 0 | 0 | 1367.7 | 0 | 24.5073 | -24.5073 | 147.0439 | 16.4 | 24.1569 | -7.7569 |  | 17-03-2026 16:20 | 0 | 0 | 1371.3 | 0 | 24.5073 | -24.5073 | 147.0439 | 16.4 | 24.1569 | -7.7569 |  | 17-03-2026 16:20 | 0 | 0 | 1388.1 | 0 | 24.5073 | -24.5073 | 147.0439 | 16.5 | 24.1569 | -7.6569 |  | 17-03-2026 16:20 | 0 | 0 | 1309.3 | 0 | 23.3157 | -23.3157 | 139.8941 | 15.5 | 22.9823 | -7.4823 |  | 17-03-2026 16:20 | 0 | 253.6845 | -253.6845 | 1522.1071 | 173.6 | 250.0568 | -76.4568
17-03-2026 16:10 | 536 | 48.22 | 183.983 | 186.444 | 1822.4 | 31.074 | 31.9864 | -0.91237 | 191.9182 | 24.5 | 31.529 | -7.029 |  | 17-03-2026 16:10 | 175.381 | 177.781 | 1835.4 | 29.6302 | 31.9864 | -2.3562 | 191.9182 | 25.9 | 31.529 | -5.629 |  | 17-03-2026 16:10 | 192.29 | 196.338 | 1807.6 | 32.723 | 31.9864 | 0.73663 | 191.9182 | 26 | 31.529 | -5.529 |  | 17-03-2026 16:10 | 191.39 | 194.029 | 1820.9 | 32.3382 | 31.9864 | 0.3518 | 191.9182 | 26.2 | 31.529 | -5.329 |  | 17-03-2026 16:10 | 143.51 | 145.4 | 1363.7 | 24.2333 | 23.6936 | 0.53973 | 142.1616 | 19.5 | 23.3548 | -3.8548 |  | 17-03-2026 16:10 | 140.374 | 142.209 | 1351.3 | 23.7015 | 23.6936 | 0.0078924 | 142.1616 | 19.4 | 23.3548 | -3.9548 |  | 17-03-2026 16:10 | 141 | 142.857 | 1354.9 | 23.8095 | 23.6936 | 0.11589 | 142.1616 | 19.3 | 23.3548 | -4.0548 |  | 17-03-2026 16:10 | 140.72 | 144.486 | 1371.6 | 24.081 | 23.6936 | 0.38739 | 142.1616 | 19.5 | 23.3548 | -3.8548 |  | 17-03-2026 16:10 | 132.929 | 134.68 | 1293.8 | 22.4467 | 22.5415 | -0.094866 | 135.2492 | 18.5 | 22.2192 | -3.7192 |  | 17-03-2026 16:10 | 244.0373 | 245.2614 | -1.2241 | 1471.5687 | 198.8 | 241.7542 | -42.9542
17-03-2026 16:00 | 419 | 47.93 | 154.087 | 156.101 | 1797.9 | 26.0168 | 25.0319 | 0.98494 | 150.1914 | 22.2 | 24.6739 | -2.4739 |  | 17-03-2026 16:00 | 152.387 | 154.41 | 1809.5 | 25.735 | 25.0319 | 0.7031 | 150.1914 | 22 | 24.6739 | -2.6739 |  | 17-03-2026 16:00 | 152.115 | 155.344 | 1781.6 | 25.8907 | 25.0319 | 0.85877 | 150.1914 | 21.7 | 24.6739 | -2.9739 |  | 17-03-2026 16:00 | 152.796 | 154.856 | 1794.7 | 25.8093 | 25.0319 | 0.77744 | 150.1914 | 22.1 | 24.6739 | -2.5739 |  | 17-03-2026 16:00 | 114.309 | 115.791 | 1344.2 | 19.2985 | 18.5421 | 0.75636 | 111.2529 | 16.5 | 18.277 | -1.777 |  | 17-03-2026 16:00 | 113.387 | 114.734 | 1331.9 | 19.1223 | 18.5421 | 0.58019 | 111.2529 | 16.3 | 18.277 | -1.977 |  | 17-03-2026 16:00 | 113.444 | 114.903 | 1335.6 | 19.1505 | 18.5421 | 0.60836 | 111.2529 | 16.4 | 18.277 | -1.877 |  | 17-03-2026 16:00 | 114.709 | 117.904 | 1352.1 | 19.6507 | 18.5421 | 1.1085 | 111.2529 | 16.5 | 18.277 | -1.777 |  | 17-03-2026 16:00 | 108.604 | 110.012 | 1275.3 | 18.3353 | 17.6406 | 0.69478 | 105.8433 | 15.6 | 17.3883 | -1.7883 |  | 17-03-2026 16:00 | 199.0092 | 191.9367 | 7.0725 | 1151.6203 | 169.3 | 189.192 | -19.892
17-03-2026 15:50 | 284 | 47.93 | 106.571 | 107.942 | 1775.7 | 17.9903 | 16.9667 | 1.0236 | 101.8004 | 18.4 | 16.7241 | 1.6759 |  | 17-03-2026 15:50 | 107.218 | 108.637 | 1787.5 | 18.1062 | 16.9667 | 1.1394 | 101.8004 | 17.9 | 16.7241 | 1.1759 |  | 17-03-2026 15:50 | 105.616 | 107.457 | 1759.9 | 17.9095 | 16.9667 | 0.94277 | 101.8004 | 17.9 | 16.7241 | 1.1759 |  | 17-03-2026 15:50 | 106.206 | 107.616 | 1772.6 | 17.936 | 16.9667 | 0.96927 | 101.8004 | 17.8 | 16.7241 | 1.0759 |  | 17-03-2026 15:50 | 78.885 | 79.965 | 1327.7 | 13.3275 | 12.5679 | 0.75955 | 75.4077 | 13.2 | 12.3882 | 0.81178 |  | 17-03-2026 15:50 | 78.199 | 79.269 | 1315.6 | 13.2115 | 12.5679 | 0.64355 | 75.4077 | 13.5 | 12.3882 | 1.1118 |  | 17-03-2026 15:50 | 78.258 | 79.329 | 1319.2 | 13.2215 | 12.5679 | 0.65355 | 75.4077 | 13.3 | 12.3882 | 0.91178 |  | 17-03-2026 15:50 | 78.94 | 81.012 | 1335.6 | 13.502 | 12.5679 | 0.93405 | 75.4077 | 13.4 | 12.3882 | 1.0118 |  | 17-03-2026 15:50 | 74.654 | 75.699 | 1259.7 | 12.6165 | 11.9568 | 0.65966 | 71.7411 | 12.7 | 11.7859 | 0.91414 |  | 17-03-2026 15:50 | 137.821 | 130.0955 | 7.7255 | 780.5732 | 138.1 | 128.2352 | 9.8648
17-03-2026 15:40 | 339 | 48.22 | 126.663 | 128.623 | 1757.3 | 21.4372 | 20.2302 | 1.207 | 121.3811 | 22.1 | 19.9409 | 2.1591 |  | 17-03-2026 15:40 | 129.763 | 131.525 | 1769.6 | 21.9208 | 20.2302 | 1.6906 | 121.3811 | 22.1 | 19.9409 | 2.1591 |  | 17-03-2026 15:40 | 121.391 | 123.907 | 1742 | 20.6512 | 20.2302 | 0.42098 | 121.3811 | 21.7 | 19.9409 | 1.7591 |  | 17-03-2026 15:40 | 122.404 | 124.054 | 1754.8 | 20.6757 | 20.2302 | 0.44548 | 121.3811 | 22.1 | 19.9409 | 2.1591 |  | 17-03-2026 15:40 | 89.88 | 91.092 | 1314.5 | 15.182 | 14.9853 | 0.19668 | 89.9119 | 16.4 | 14.771 | 1.629 |  | 17-03-2026 15:40 | 92.88 | 94.103 | 1302.1 | 15.6838 | 14.9853 | 0.69851 | 89.9119 | 15.8 | 14.771 | 1.029 |  | 17-03-2026 15:40 | 90.037 | 91.214 | 1305.9 | 15.2023 | 14.9853 | 0.21701 | 89.9119 | 15.9 | 14.771 | 1.129 |  | 17-03-2026 15:40 | 90.436 | 92.807 | 1322.2 | 15.4678 | 14.9853 | 0.48251 | 89.9119 | 16 | 14.771 | 1.229 |  | 17-03-2026 15:40 | 85.686 | 86.859 | 1247 | 14.4765 | 14.2567 | 0.21982 | 85.5401 | 15.1 | 14.0528 | 1.0472 |  | 17-03-2026 15:40 | 160.6973 | 155.1187 | 5.5786 | 930.7123 | 167.2 | 152.9005 | 14.2995
17-03-2026 15:30 | 458 | 48.79 | 179.073 | 181.652 | 1735.2 | 30.2753 | 27.2723 | 3.003 | 163.6337 | 38.2 | 26.8823 | 11.3177 |  | 17-03-2026 15:30 | 175.278 | 177.857 | 1747.5 | 29.6428 | 27.2723 | 2.3705 | 163.6337 | 40.5 | 26.8823 | 13.6177 |  | 17-03-2026 15:30 | 160.469 | 160.479 | 1720.3 | 26.7465 | 27.2723 | -0.52579 | 163.6337 | 38.2 | 26.8823 | 11.3177 |  | 17-03-2026 15:30 | 159.049 | 161.356 | 1732.7 | 26.8927 | 27.2723 | -0.37962 | 163.6337 | 38 | 26.8823 | 11.1177 |  | 17-03-2026 15:30 | 118.532 | 120.178 | 1298.1 | 20.0297 | 20.2017 | -0.17203 | 121.2102 | 28.4 | 19.9128 | 8.4872 |  | 17-03-2026 15:30 | 115.448 | 117.284 | 1286.3 | 19.5473 | 20.2017 | -0.65436 | 121.2102 | 28.3 | 19.9128 | 8.3872 |  | 17-03-2026 15:30 | 114.778 | 116.361 | 1290 | 19.3935 | 20.2017 | -0.80819 | 121.2102 | 28.4 | 19.9128 | 8.4872 |  | 17-03-2026 15:30 | 113.942 | 116.909 | 1306.2 | 19.4848 | 20.2017 | -0.71686 | 121.2102 | 28.5 | 19.9128 | 8.5872 |  | 17-03-2026 15:30 | 107.901 | 109.4 | 1231.9 | 18.2333 | 19.2194 | -0.98608 | 115.3165 | 27 | 18.9446 | 8.0554 |  | 17-03-2026 15:30 | 210.246 | 209.1153 | 1.1307 | 1254.692 | 295.5 | 206.125 | 89.375
17-03-2026 15:20 | 686 | 49.08 | 238.755 | 242.415 | 1697 | 40.4025 | 40.8037 | -0.40116 | 244.8219 | 42.2 | 40.2202 | 1.9798 |  | 17-03-2026 15:20 | 238.856 | 242.592 | 1707 | 40.432 | 40.8037 | -0.37166 | 244.8219 | 40.9 | 40.2202 | 0.67984 |  | 17-03-2026 15:20 | 237.463 | 243.64 | 1682.1 | 40.6067 | 40.8037 | -0.19699 | 244.8219 | 42.4 | 40.2202 | 2.1798 |  | 17-03-2026 15:20 | 236.358 | 240.055 | 1694.7 | 40.0092 | 40.8037 | -0.79449 | 244.8219 | 42.7 | 40.2202 | 2.4798 |  | 17-03-2026 15:20 | 174.496 | 177.028 | 1269.7 | 29.5047 | 30.2249 | -0.72026 | 181.3496 | 31.8 | 29.7927 | 2.0073 |  | 17-03-2026 15:20 | 171.516 | 174.108 | 1258 | 29.018 | 30.2249 | -1.2069 | 181.3496 | 31.1 | 29.7927 | 1.3073 |  | 17-03-2026 15:20 | 173.697 | 176.941 | 1261.6 | 29.4902 | 30.2249 | -0.73476 | 181.3496 | 31 | 29.7927 | 1.2073 |  | 17-03-2026 15:20 | 175.503 | 180.956 | 1277.7 | 30.1593 | 30.2249 | -0.065598 | 181.3496 | 31.3 | 29.7927 | 1.5073 |  | 17-03-2026 15:20 | 164.326 | 166.943 | 1204.9 | 27.8238 | 28.7553 | -0.93145 | 172.5317 | 29.5 | 28.3441 | 1.1559 |  | 17-03-2026 15:20 | 307.4463 | 312.8696 | -5.4233 | 1877.2178 | 322.9 | 308.3956 | 14.5044
17-03-2026 15:10 | 872 | 49.36 | 295.251 | 300.082 | 1654.8 | 50.0137 | 51.8115 | -1.7979 | 310.8692 | 49.9 | 51.0706 | -1.1706 |  | 17-03-2026 15:10 | 301 | 303.098 | 1666.1 | 50.5163 | 51.8115 | -1.2952 | 310.8692 | 50.6 | 51.0706 | -0.47063 |  | 17-03-2026 15:10 | 291.599 | 299.592 | 1639.7 | 49.932 | 51.8115 | -1.8795 | 310.8692 | 48.3 | 51.0706 | -2.7706 |  | 17-03-2026 15:10 | 295.364 | 300.319 | 1652 | 50.0532 | 51.8115 | -1.7584 | 310.8692 | 48.7 | 51.0706 | -2.3706 |  | 17-03-2026 15:10 | 220.094 | 223.423 | 1237.9 | 37.2372 | 38.3789 | -1.1417 | 230.2735 | 36.5 | 37.8301 | -1.3301 |  | 17-03-2026 15:10 | 217.898 | 221.685 | 1226.9 | 36.9475 | 38.3789 | -1.4314 | 230.2735 | 35.9 | 37.8301 | -1.9301 |  | 17-03-2026 15:10 | 218.02 | 222.489 | 1230.6 | 37.0815 | 38.3789 | -1.2974 | 230.2735 | 36.1 | 37.8301 | -1.7301 |  | 17-03-2026 15:10 | 220.151 | 226.584 | 1246.4 | 37.764 | 38.3789 | -0.61491 | 230.2735 | 36.3 | 37.8301 | -1.5301 |  | 17-03-2026 15:10 | 208.147 | 211.295 | 1175.4 | 35.2158 | 36.5128 | -1.2969 | 219.0767 | 34.4 | 35.9906 | -1.5906 |  | 17-03-2026 15:10 | 384.7612 | 397.2746 | -12.5134 | 2383.6473 | 376.7 | 391.5935 | -14.8935
17-03-2026 15:00 | 867 | 49.36 | 287.942 | 292.654 | 1604.9 | 48.7757 | 51.5144 | -2.7388 | 309.0867 | 88 | 50.7778 | 37.2222 | 0.9839 | 17-03-2026 15:00 | 293.598 | 298.493 | 1615.5 | 49.7488 | 51.5144 | -1.7656 | 309.0867 | 88.8 | 50.7778 | 38.0222 | 0.9836 | 17-03-2026 15:00 | 290.527 | 298.842 | 1591.4 | 49.807 | 51.5144 | -1.7074 | 309.0867 | 88 | 50.7778 | 37.2222 | 0.97218 | 17-03-2026 15:00 | 291.36 | 296.188 | 1603.3 | 49.3647 | 51.5144 | -2.1498 | 309.0867 | 88.4 | 50.7778 | 37.6222 | 0.9837 | 17-03-2026 15:00 | 221.101 | 224.468 | 1201.4 | 37.4113 | 38.1588 | -0.74752 | 228.9531 | 66.3 | 37.6132 | 28.6868 | 0.985 | 17-03-2026 15:00 | 215.93 | 220.216 | 1191 | 36.7027 | 38.1588 | -1.4562 | 228.9531 | 65.3 | 37.6132 | 27.6868 | 0.98054 | 17-03-2026 15:00 | 220.725 | 225.336 | 1194.5 | 37.556 | 38.1588 | -0.60285 | 228.9531 | 65.9 | 37.6132 | 28.2868 | 0.97954 | 17-03-2026 15:00 | 222.888 | 229.901 | 1210.1 | 38.3168 | 38.1588 | 0.15798 | 228.9531 | 0 | 37.6132 | -37.6132 | 0.9695 | 17-03-2026 15:00 | 208.575 | 212.221 | 1141 | 35.3702 | 36.3034 | -0.93325 | 217.8205 | 62.4 | 35.7843 | 26.6157 | 0.98282 | 17-03-2026 15:00 | 383.0532 | 394.9966 | -11.9434 | 2369.9796 | 613.1 | 389.3482 | 223.7518
17-03-2026 14:50 | 896 | 48.79 |  |  |  | 0 | 53.3536 | -53.3536 | 320.1219 | 0 | 52.5907 | -52.5907 | [5 empty] | 0 | 53.3536 | -53.3536 | 320.1219 | 0 | 52.5907 | -52.5907 | [5 empty] | 0 | 53.3536 | -53.3536 | 320.1219 | 0 | 52.5907 | -52.5907 | [5 empty] | 0 | 53.3536 | -53.3536 | 320.1219 | 0 | 52.5907 | -52.5907 | [5 empty] | 0 | 39.5212 | -39.5212 | 237.1273 | 0 | 38.9561 | -38.9561 | [5 empty] | 0 | 39.5212 | -39.5212 | 237.1273 | 0 | 38.9561 | -38.9561 | [5 empty] | 0 | 39.5212 | -39.5212 | 237.1273 | 0 | 38.9561 | -38.9561 | [5 empty] | 0 | 39.5212 | -39.5212 | 237.1273 | 0 | 38.9561 | -38.9561 | [5 empty] | 0 | 37.5995 | -37.5995 | 225.5973 | 0 | 37.0619 | -37.0619 |  | 17-03-2026 14:50 | 0 | 409.099 | -409.099 | 2454.594 | 0 | 403.2489 | -403.2489
17-03-2026 14:40 | 670 | 49.08 | 278.09 | 242.505 | 1516.9 | 40.4175 | 39.852 | 0.56553 | 239.1118 | 49.4 | 39.2821 | 10.1179 | 1.1467 | 17-03-2026 14:40 | 233.667 | 237.346 | 1526.7 | 39.5577 | 39.852 | -0.2943 | 239.1118 | 48.5 | 39.2821 | 9.2179 | 0.9845 | 17-03-2026 14:40 | 222.348 | 226.249 | 1503.4 | 37.7082 | 39.852 | -2.1438 | 239.1118 | 47.5 | 39.2821 | 8.2179 | 0.98276 | 17-03-2026 14:40 | 226.114 | 229.674 | 1514.9 | 38.279 | 39.852 | -1.573 | 239.1118 | 48.7 | 39.2821 | 9.4179 | 0.9845 | 17-03-2026 14:40 | 165.122 | 167.518 | 1135.1 | 27.9197 | 29.52 | -1.6003 | 177.1199 | 36.3 | 29.0978 | 7.2022 | 0.9857 | 17-03-2026 14:40 | 163.574 | 165.947 | 1125.7 | 27.6578 | 29.52 | -1.8621 | 177.1199 | 35.8 | 29.0978 | 6.7022 | 0.9857 | 17-03-2026 14:40 | 166.729 | 169.148 | 1128.6 | 28.1913 | 29.52 | -1.3286 | 177.1199 | 35.3 | 29.0978 | 6.2022 | 0.9857 | 17-03-2026 14:40 | 166.59 | 170.892 | 1144 | 28.482 | 29.52 | -1.038 | 177.1199 | 35.6 | 29.0978 | 6.5022 | 0.97483 | 17-03-2026 14:40 | 159.558 | 161.906 | 1078.6 | 26.9843 | 28.0846 | -1.1003 | 168.5076 | 33.7 | 27.683 | 6.017 | 0.9855 | 17-03-2026 14:40 | 295.1975 | 305.5724 | -10.3749 | 1833.4343 | 370.8 | 301.2027 | 69.5973
17-03-2026 14:30 | 889 | 49.36 | 295.041 | 299.96 | 1467.5 | 49.9933 | 52.8216 | -2.8283 | 316.9297 | 49.4 | 52.0663 | -2.6663 | 0.9836 | 17-03-2026 14:30 | 297.065 | 308.303 | 1478.2 | 51.3838 | 52.8216 | -1.4378 | 316.9297 | 52.1 | 52.0663 | 0.033731 | 0.96355 | 17-03-2026 14:30 | 296.513 | 304.977 | 1455.9 | 50.8295 | 52.8216 | -1.9921 | 316.9297 | 49.7 | 52.0663 | -2.3663 | 0.97225 | 17-03-2026 14:30 | 297.541 | 302.241 | 1466.2 | 50.3735 | 52.8216 | -2.4481 | 316.9297 | 50 | 52.0663 | -2.0663 | 0.98445 | 17-03-2026 14:30 | 224.275 | 227.701 | 1098.8 | 37.9502 | 39.1271 | -1.177 | 234.7627 | 37.5 | 38.5676 | -1.0676 | 0.98495 | 17-03-2026 14:30 | 220.754 | 224.778 | 1089.9 | 37.463 | 39.1271 | -1.6641 | 234.7627 | 37 | 38.5676 | -1.5676 | 0.9821 | 17-03-2026 14:30 | 221.038 | 225.083 | 1093.3 | 37.5138 | 39.1271 | -1.6133 | 234.7627 | 37.1 | 38.5676 | -1.4676 | 0.98203 | 17-03-2026 14:30 | 221.873 | 228.469 | 1108.4 | 38.0782 | 39.1271 | -1.049 | 234.7627 | 37.3 | 38.5676 | -1.2676 | 0.97113 | 17-03-2026 14:30 | 210.163 | 213.363 | 1044.9 | 35.5605 | 37.2246 | -1.6641 | 223.3477 | 35.3 | 36.6923 | -1.3923 | 0.985 | 17-03-2026 14:30 | 389.1458 | 405.0196 | -15.8738 | 2430.1175 | 385.4 | 399.2278 | -13.8278
17-03-2026 14:20 | 921 | 49.36 | 316.022 | 315.937 | 1418.1 | 52.6562 | 54.723 | -2.0668 | 328.3378 | 51.6 | 53.9404 | -2.3404 | 1.0003 | 17-03-2026 14:20 | 319.64 | 325.168 | 1426.1 | 54.1947 | 54.723 | -0.52829 | 328.3378 | 50.9 | 53.9404 | -3.0404 | 0.983 | 17-03-2026 14:20 | 308.542 | 316.862 | 1406.2 | 52.8103 | 54.723 | -1.9126 | 328.3378 | 51.3 | 53.9404 | -2.6404 | 0.97374 | 17-03-2026 14:20 | 309.685 | 315.009 | 1416.2 | 52.5015 | 54.723 | -2.2215 | 328.3378 | 51.1 | 53.9404 | -2.8404 | 0.9831 | 17-03-2026 14:20 | 233.439 | 237.066 | 1061.3 | 39.511 | 40.5355 | -1.0245 | 243.2132 | 38.3 | 39.9559 | -1.6559 | 0.9847 | 17-03-2026 14:20 | 228.969 | 233.244 | 1052.9 | 38.874 | 40.5355 | -1.6615 | 243.2132 | 37.7 | 39.9559 | -2.2559 | 0.98167 | 17-03-2026 14:20 | 229.861 | 234.215 | 1056.2 | 39.0358 | 40.5355 | -1.4997 | 243.2132 | 37.8 | 39.9559 | -2.1559 | 0.98141 | 17-03-2026 14:20 | 230.927 | 237.473 | 1071.1 | 39.5788 | 40.5355 | -0.95669 | 243.2132 | 38.7 | 39.9559 | -1.2559 | 0.97243 | 17-03-2026 14:20 | 218.535 | 221.885 | 1009.6 | 36.9808 | 38.5645 | -1.5837 | 231.3872 | 36.7 | 38.0131 | -1.3131 | 0.9849 | 17-03-2026 14:20 | 406.1432 | 419.5985 | -13.4553 | 2517.5908 | 394.1 | 413.5982 | -19.4982
17-03-2026 14:10 | 911 | 49.36 | 305.764 | 310.862 | 1366.5 | 51.8103 | 54.1288 | -2.3185 | 324.7727 | 52.4 | 53.3547 | -0.95475 | 0.9836 | 17-03-2026 14:10 | 309.614 | 314.481 | 1375.2 | 52.4135 | 54.1288 | -1.7153 | 324.7727 | 53.7 | 53.3547 | 0.34525 | 0.98452 | 17-03-2026 14:10 | 303.955 | 312.422 | 1354.9 | 52.0703 | 54.1288 | -2.0585 | 324.7727 | 52.3 | 53.3547 | -1.0547 | 0.9729 | 17-03-2026 14:10 | 305.723 | 310.979 | 1365.1 | 51.8298 | 54.1288 | -2.299 | 324.7727 | 52.6 | 53.3547 | -0.75475 | 0.9831 | 17-03-2026 14:10 | 229.277 | 232.863 | 1023 | 38.8105 | 40.0954 | -1.2849 | 240.5724 | 39.5 | 39.522 | -0.022036 | 0.9846 | 17-03-2026 14:10 | 225.742 | 229.844 | 1015.2 | 38.3073 | 40.0954 | -1.7881 | 240.5724 | 38.9 | 39.522 | -0.62204 | 0.98215 | 17-03-2026 14:10 | 225.662 | 229.731 | 1018.4 | 38.2885 | 40.0954 | -1.8069 | 240.5724 | 39.1 | 39.522 | -0.42204 | 0.98229 | 17-03-2026 14:10 | 227.96 | 234.417 | 1032.4 | 39.0695 | 40.0954 | -1.0259 | 240.5724 | 38.8 | 39.522 | -0.72204 | 0.97246 | 17-03-2026 14:10 | 216.746 | 220.069 | 972.9 | 36.6782 | 38.1458 | -1.4676 | 228.8748 | 36.6 | 37.6003 | -1.0003 | 0.9849 | 17-03-2026 14:10 | 399.278 | 415.0426 | -15.7646 | 2490.2554 | 403.9 | 409.1075 | -5.2075
17-03-2026 14:00 | 838 | 49.36 | 276.216 | 279.489 | 1314.1 | 46.5815 | 49.7914 | -3.2099 | 298.7481 | 107.8 | 49.0793 | 58.7207 | 0.98829 | 17-03-2026 14:00 | 272.633 | 277.151 | 1321.5 | 46.1918 | 49.7914 | -3.5995 | 298.7481 | 107.7 | 49.0793 | 58.6207 | 0.9837 | 17-03-2026 14:00 | 279.279 | 287.021 | 1302.6 | 47.8368 | 49.7914 | -1.9545 | 298.7481 | 106.1 | 49.0793 | 57.0207 | 0.97303 | 17-03-2026 14:00 | 283.337 | 288.061 | 1312.5 | 48.0102 | 49.7914 | -1.7812 | 298.7481 | 106.9 | 49.0793 | 57.8207 | 0.9836 | 17-03-2026 14:00 | 214.069 | 217.307 | 983.5 | 36.2178 | 36.8825 | -0.66465 | 221.2949 | 80.1 | 36.3551 | 43.7449 | 0.9851 | 17-03-2026 14:00 | 210.997 | 215.318 | 976.3 | 35.8863 | 36.8825 | -0.99615 | 221.2949 | 79 | 36.3551 | 42.6449 | 0.97993 | 17-03-2026 14:00 | 214.977 | 219.824 | 979.3 | 36.6373 | 36.8825 | -0.24515 | 221.2949 | 79.2 | 36.3551 | 42.8449 | 0.97795 | 17-03-2026 14:00 | 218.19 | 225.268 | 993.6 | 37.5447 | 36.8825 | 0.66218 | 221.2949 | 79.8 | 36.3551 | 43.4449 | 0.96858 | 17-03-2026 14:00 | 205.331 | 208.416 | 936.3 | 34.736 | 35.0891 | -0.35312 | 210.5347 | 75.4 | 34.5873 | 40.8127 | 0.9852 | 17-03-2026 14:00 | 369.6425 | 381.7845 | -12.142 | 2290.707 | 822 | 376.325 | 445.675
17-03-2026 13:50 | 957 | 49.08 |  |  |  | 0 | 56.9229 | -56.9229 | 341.5373 | 0 | 56.1089 | -56.1089 | [5 empty] | 0 | 56.9229 | -56.9229 | 341.5373 | 0 | 56.1089 | -56.1089 | [5 empty] | 0 | 56.9229 | -56.9229 | 341.5373 | 0 | 56.1089 | -56.1089 | [5 empty] | 0 | 56.9229 | -56.9229 | 341.5373 | 0 | 56.1089 | -56.1089 | [5 empty] | 0 | 42.1651 | -42.1651 | 252.9906 | 0 | 41.5621 | -41.5621 | [5 empty] | 0 | 42.1651 | -42.1651 | 252.9906 | 0 | 41.5621 | -41.5621 | [5 empty] | 0 | 42.1651 | -42.1651 | 252.9906 | 0 | 41.5621 | -41.5621 | [5 empty] | 0 | 42.1651 | -42.1651 | 252.9906 | 0 | 41.5621 | -41.5621 | [5 empty] | 0 | 40.1149 | -40.1149 | 240.6892 | 0 | 39.5412 | -39.5412 |  | 17-03-2026 13:50 | 0 | 436.4668 | -436.4668 | 2618.8009 | 0 | 430.2253 | -430.2253
17-03-2026 13:40 | 1006 | 49.08 | 340.022 | 345.938 | 1206.3 | 57.6563 | 59.8374 | -2.1811 | 359.0246 | 53.7 | 58.9818 | -5.2818 | 0.9829 | 17-03-2026 13:40 | 340.562 | 346.593 | 1213.8 | 57.7655 | 59.8374 | -2.0719 | 359.0246 | 58.7 | 58.9818 | -0.28176 | 0.9826 | 17-03-2026 13:40 | 335.788 | 345.552 | 1196.5 | 57.592 | 59.8374 | -2.2454 | 359.0246 | 55.6 | 58.9818 | -3.3818 | 0.97174 | 17-03-2026 13:40 | 336.32 | 342.206 | 1205.6 | 57.0343 | 59.8374 | -2.8031 | 359.0246 | 55.9 | 58.9818 | -3.0818 | 0.9828 | 17-03-2026 13:40 | 253.785 | 257.807 | 903.4 | 42.9678 | 44.324 | -1.3562 | 265.9441 | 42 | 43.6902 | -1.6902 | 0.9844 | 17-03-2026 13:40 | 249.113 | 253.849 | 897.3 | 42.3082 | 44.324 | -2.0159 | 265.9441 | 41.4 | 43.6902 | -2.2902 | 0.98134 | 17-03-2026 13:40 | 249.659 | 254.41 | 900.1 | 42.4017 | 44.324 | -1.9224 | 265.9441 | 41.6 | 43.6902 | -2.0902 | 0.98133 | 17-03-2026 13:40 | 250.885 | 258.1 | 913.8 | 43.0167 | 44.324 | -1.3074 | 265.9441 | 41.9 | 43.6902 | -1.7902 | 0.97205 | 17-03-2026 13:40 | 237.262 | 241.046 | 860.9 | 40.1743 | 42.1688 | -1.9945 | 253.0129 | 39.4 | 41.5658 | -2.1658 | 0.9843 | 17-03-2026 13:40 | 440.9168 | 458.8146 | -17.8978 | 2752.8879 | 430.2 | 452.2536 | -22.0536
17-03-2026 13:30 | 901 | 49.08 | 303.531 | 308.623 | 1152.6 | 51.4372 | 53.592 | -2.1548 | 321.5519 | 51.6 | 52.8256 | -1.2256 | 0.9835 | 17-03-2026 13:30 | 338.905 | 331.554 | 1155.1 | 55.259 | 53.592 | 1.667 | 321.5519 | 48.8 | 52.8256 | -4.0256 | 1.0222 | 17-03-2026 13:30 | 302.868 | 310.345 | 1140.9 | 51.7242 | 53.592 | -1.8678 | 321.5519 | 49.9 | 52.8256 | -2.9256 | 0.97591 | 17-03-2026 13:30 | 309.615 | 314.873 | 1149.7 | 52.4788 | 53.592 | -1.1131 | 321.5519 | 51.3 | 52.8256 | -1.5256 | 0.9833 | 17-03-2026 13:30 | 226.642 | 230.14 | 861.4 | 38.3567 | 39.6978 | -1.3411 | 238.1866 | 38.4 | 39.1301 | -0.73008 | 0.9848 | 17-03-2026 13:30 | 226.797 | 230.274 | 855.9 | 38.379 | 39.6978 | -1.3188 | 238.1866 | 37.9 | 39.1301 | -1.2301 | 0.9849 | 17-03-2026 13:30 | 222.746 | 226.583 | 858.5 | 37.7638 | 39.6978 | -1.9339 | 238.1866 | 38 | 39.1301 | -1.1301 | 0.98307 | 17-03-2026 13:30 | 224.743 | 229.981 | 871.9 | 38.3302 | 39.6978 | -1.3676 | 238.1866 | 38.3 | 39.1301 | -0.83008 | 0.97722 | 17-03-2026 13:30 | 213.511 | 216.762 | 821.5 | 36.127 | 37.7675 | -1.6405 | 226.605 | 36.2 | 37.2274 | -1.0274 | 0.985 | 17-03-2026 13:30 | 399.8558 | 410.9264 | -11.0706 | 2465.5586 | 390.4 | 405.0502 | -14.6502
17-03-2026 13:20 | 958 | 48.79 | 343.985 | 332.061 | 1101 | 55.3435 | 57.0455 | -1.702 | 342.2732 | 58.2 | 56.2298 | 1.9702 | 1.0359 | 17-03-2026 13:20 | 327.908 | 333.793 | 1106.3 | 55.6322 | 57.0455 | -1.4134 | 342.2732 | 58.6 | 56.2298 | 2.3702 | 0.98237 | 17-03-2026 13:20 | 317.499 | 326.889 | 1091 | 54.4815 | 57.0455 | -2.564 | 342.2732 | 57.9 | 56.2298 | 1.6702 | 0.97127 | 17-03-2026 13:20 | 312.722 | 318.13 | 1098.4 | 53.0217 | 57.0455 | -4.0239 | 342.2732 | 57.1 | 56.2298 | 0.87022 | 0.983 | 17-03-2026 13:20 | 239.038 | 242.801 | 823 | 40.4668 | 42.2559 | -1.7891 | 253.5357 | 43.3 | 41.6517 | 1.6483 | 0.9845 | 17-03-2026 13:20 | 231.775 | 236.997 | 818 | 39.4995 | 42.2559 | -2.7564 | 253.5357 | 43.1 | 41.6517 | 1.4483 | 0.97797 | 17-03-2026 13:20 | 236.982 | 241.983 | 820.5 | 40.3305 | 42.2559 | -1.9254 | 253.5357 | 44 | 41.6517 | 2.3483 | 0.97933 | 17-03-2026 13:20 | 236.918 | 244.117 | 833.6 | 40.6862 | 42.2559 | -1.5698 | 253.5357 | 43.4 | 41.6517 | 1.7483 | 0.97051 | 17-03-2026 13:20 | 222.287 | 226.053 | 785.3 | 37.6755 | 40.2013 | -2.5258 | 241.2078 | 41.1 | 39.6264 | 1.4736 | 0.98334 | 17-03-2026 13:20 | 417.1373 | 437.4072 | -20.2699 | 2624.4431 | 446.7 | 431.1523 | 15.5477
17-03-2026 13:10 | 1052 | 49.08 | 352.597 | 357.021 | 1042.8 | 59.5035 | 62.5735 | -3.07 | 375.4412 | 57.7 | 61.6787 | -3.9787 | 0.98761 | 17-03-2026 13:10 | 352.731 | 358.873 | 1047.7 | 59.8122 | 62.5735 | -2.7614 | 375.4412 | 59.4 | 61.6787 | -2.2787 | 0.98289 | 17-03-2026 13:10 | 347.018 | 357.4 | 1033.1 | 59.5667 | 62.5735 | -3.0069 | 375.4412 | 59.3 | 61.6787 | -2.3787 | 0.97095 | 17-03-2026 13:10 | 350.323 | 356.599 | 1041.3 | 59.4332 | 62.5735 | -3.1404 | 375.4412 | 59.2 | 61.6787 | -2.4787 | 0.9824 | 17-03-2026 13:10 | 262.063 | 266.859 | 779.7 | 44.4765 | 46.3508 | -1.8743 | 278.1046 | 46.2 | 45.688 | 0.51205 | 0.98203 | 17-03-2026 13:10 | 260.018 | 264.62 | 774.9 | 44.1033 | 46.3508 | -2.2474 | 278.1046 | 45.1 | 45.688 | -0.58795 | 0.98261 | 17-03-2026 13:10 | 261.483 | 266.643 | 776.5 | 44.4405 | 46.3508 | -1.9103 | 278.1046 | 44.5 | 45.688 | -1.188 | 0.98065 | 17-03-2026 13:10 | 260.44 | 267.849 | 790.2 | 44.6415 | 46.3508 | -1.7093 | 278.1046 | 45.6 | 45.688 | -0.087953 | 0.97234 | 17-03-2026 13:10 | 246.838 | 250.801 | 744.2 | 41.8002 | 44.097 | -2.2968 | 264.5821 | 43 | 43.4664 | -0.46643 | 0.9842 | 17-03-2026 13:10 | 457.7775 | 479.7942 | -22.0167 | 2878.7655 | 460 | 472.9332 | -12.9332
17-03-2026 13:00 | 1139 | 49.08 | 352.601 | 357.971 | 985.1 | 59.6618 | 67.7483 | -8.0865 | 406.4901 | 57.8 | 66.7795 | -8.9795 |  | 17-03-2026 13:00 | 352.732 | 358.249 | 988.3 | 59.7082 | 67.7483 | -8.0402 | 406.4901 | 56.5 | 66.7795 | -10.2795 | 0.9846 | 17-03-2026 13:00 | 352.66 | 362.179 | 973.8 | 60.3632 | 67.7483 | -7.3852 | 406.4901 | 56.9 | 66.7795 | -9.8795 | 0.97372 | 17-03-2026 13:00 | 352.615 | 358.217 | 982.1 | 59.7028 | 67.7483 | -8.0455 | 406.4901 | 57.1 | 66.7795 | -9.6795 | 0.98436 | 17-03-2026 13:00 | 283.324 | 287.989 | 733.5 | 47.9982 | 50.184 | -2.1858 | 301.1038 | 45.3 | 49.4663 | -4.1663 | 0.9838 | 17-03-2026 13:00 | 280.018 | 285.351 | 729.8 | 47.5585 | 50.184 | -2.6255 | 301.1038 | 44.8 | 49.4663 | -4.6663 | 0.98131 | 17-03-2026 13:00 | 280.866 | 286.747 | 732 | 47.7912 | 50.184 | -2.3928 | 301.1038 | 45.2 | 49.4663 | -4.2663 | 0.97949 | 17-03-2026 13:00 | 282.323 | 291.14 | 744.6 | 48.5233 | 50.184 | -1.6606 | 301.1038 | 47.3 | 49.4663 | -2.1663 | 0.96972 | 17-03-2026 13:00 | 266.736 | 271.101 | 701.2 | 45.1835 | 47.7438 | -2.5603 | 286.4629 | 43.1 | 47.0611 | -3.9611 | 0.9839 | 17-03-2026 13:00 | 476.4907 | 519.473 | -42.9824 | 3116.8383 | 454 | 512.0446 | -58.0446
17-03-2026 12:50 | 792 | 49.08 |  |  |  | 0 | 47.1086 | -47.1086 | 282.6516 | 0 | 46.4349 | -46.4349 | [5 empty] | 0 | 47.1086 | -47.1086 | 282.6516 | 0 | 46.4349 | -46.4349 | [5 empty] | 0 | 47.1086 | -47.1086 | 282.6516 | 0 | 46.4349 | -46.4349 | [5 empty] | 0 | 47.1086 | -47.1086 | 282.6516 | 0 | 46.4349 | -46.4349 | [5 empty] | 0 | 34.8953 | -34.8953 | 209.3715 | 0 | 34.3963 | -34.3963 | [5 empty] | 0 | 34.8953 | -34.8953 | 209.3715 | 0 | 34.3963 | -34.3963 | [5 empty] | 0 | 34.8953 | -34.8953 | 209.3715 | 0 | 34.3963 | -34.3963 | [5 empty] | 0 | 34.8953 | -34.8953 | 209.3715 | 0 | 34.3963 | -34.3963 | [5 empty] | 0 | 33.1985 | -33.1985 | 199.1911 | 0 | 32.7238 | -32.7238 |  | 17-03-2026 12:50 | 0 | 361.2139 | -361.2139 | 2167.2835 | 0 | 356.0486 | -356.0486
17-03-2026 12:40 | 692 | 49.36 | 0 | 0 | 927.3 | 0 | 41.1165 | -41.1165 | 246.6989 | 0 | 40.5285 | -40.5285 |  | 17-03-2026 12:40 | 0 | 0 | 931.8 | 0 | 41.1165 | -41.1165 | 246.6989 | 0 | 40.5285 | -40.5285 |  | 17-03-2026 12:40 | 0 | 0 | 916.9 | 0 | 41.1165 | -41.1165 | 246.6989 | 0 | 40.5285 | -40.5285 |  | 17-03-2026 12:40 | 0 | 0 | 925 | 0 | 41.1165 | -41.1165 | 246.6989 | 0 | 40.5285 | -40.5285 |  | 17-03-2026 12:40 | 0 | 0 | 688.2 | 0 | 30.4567 | -30.4567 | 182.74 | 0 | 30.0211 | -30.0211 |  | 17-03-2026 12:40 | 0 | 0 | 685 | 0 | 30.4567 | -30.4567 | 182.74 | 0 | 30.0211 | -30.0211 |  | 17-03-2026 12:40 | 0 | 0 | 686.8 | 0 | 30.4567 | -30.4567 | 182.74 | 0 | 30.0211 | -30.0211 |  | 17-03-2026 12:40 | 0 | 0 | 697.3 | 0 | 30.4567 | -30.4567 | 182.74 | 0 | 30.0211 | -30.0211 |  | 17-03-2026 12:40 | 0 | 0 | 658.1 | 0 | 28.9757 | -28.9757 | 173.8544 | 0 | 28.5614 | -28.5614 |  | 17-03-2026 12:40 | 0 | 315.2683 | -315.2683 | 1891.61 | 0 | 310.76 | -310.76
17-03-2026 12:30 | 880 | 49.36 | 0 | 0 | 927.3 | 0 | 52.2869 | -52.2869 | 313.7212 | 0 | 51.5392 | -51.5392 |  | 17-03-2026 12:30 | 0 | 0 | 931.8 | 0 | 52.2869 | -52.2869 | 313.7212 | 0 | 51.5392 | -51.5392 |  | 17-03-2026 12:30 | 0 | 0 | 916.9 | 0 | 52.2869 | -52.2869 | 313.7212 | 0 | 51.5392 | -51.5392 |  | 17-03-2026 12:30 | 0 | 0 | 925 | 0 | 52.2869 | -52.2869 | 313.7212 | 0 | 51.5392 | -51.5392 |  | 17-03-2026 12:30 | 0 | 0 | 688.2 | 0 | 38.731 | -38.731 | 232.3861 | 0 | 38.1772 | -38.1772 |  | 17-03-2026 12:30 | 0 | 0 | 685 | 0 | 38.731 | -38.731 | 232.3861 | 0 | 38.1772 | -38.1772 |  | 17-03-2026 12:30 | 0 | 0 | 686.8 | 0 | 38.731 | -38.731 | 232.3861 | 0 | 38.1772 | -38.1772 |  | 17-03-2026 12:30 | 0 | 0 | 697.3 | 0 | 38.731 | -38.731 | 232.3861 | 0 | 38.1772 | -38.1772 |  | 17-03-2026 12:30 | 0 | 0 | 658.1 | 0 | 36.8478 | -36.8478 | 221.0866 | 0 | 36.3208 | -36.3208 |  | 17-03-2026 12:30 | 0 | 400.9193 | -400.9193 | 2405.5157 | 0 | 395.1861 | -395.1861
17-03-2026 12:20 | 1081 | 49.36 | 0 | 0 | 927.3 | 0 | 64.2297 | -64.2297 | 385.378 | 22.6 | 63.3112 | -40.7112 |  | 17-03-2026 12:20 | 0 | 0 | 931.8 | 0 | 64.2297 | -64.2297 | 385.378 | 22.1 | 63.3112 | -41.2112 |  | 17-03-2026 12:20 | 0 | 0 | 916.9 | 0 | 64.2297 | -64.2297 | 385.378 | 22 | 63.3112 | -41.3112 |  | 17-03-2026 12:20 | 0 | 0 | 925 | 0 | 64.2297 | -64.2297 | 385.378 | 21.8 | 63.3112 | -41.5112 |  | 17-03-2026 12:20 | 0 | 0 | 688.2 | 0 | 47.5775 | -47.5775 | 285.4652 | 16.7 | 46.8972 | -30.1972 |  | 17-03-2026 12:20 | 0 | 0 | 685 | 0 | 47.5775 | -47.5775 | 285.4652 | 16.5 | 46.8972 | -30.3972 |  | 17-03-2026 12:20 | 0 | 0 | 686.8 | 0 | 47.5775 | -47.5775 | 285.4652 | 16.5 | 46.8972 | -30.3972 |  | 17-03-2026 12:20 | 0 | 0 | 697.3 | 0 | 47.5775 | -47.5775 | 285.4652 | 17 | 46.8972 | -29.8972 |  | 17-03-2026 12:20 | 0 | 0 | 658.1 | 0 | 45.2641 | -45.2641 | 271.5847 | 15.9 | 44.6168 | -28.7168 |  | 17-03-2026 12:20 | 0 | 492.4929 | -492.4929 | 2954.9573 | 171.1 | 485.4502 | -314.3502
17-03-2026 12:10 | 713 | 47.93 | 236.604 | 251.87 | 904.7 | 41.9783 | 42.596 | -0.61771 | 255.5762 | 39 | 41.9869 | -2.9869 | 0.93939 | 17-03-2026 12:10 | 253.681 | 257.544 | 909.7 | 42.924 | 42.596 | 0.32796 | 255.5762 | 40.7 | 41.9869 | -1.2869 | 0.985 | 17-03-2026 12:10 | 249.52 | 256.109 | 894.9 | 42.6848 | 42.596 | 0.088792 | 255.5762 | 39 | 41.9869 | -2.9869 | 0.97427 | 17-03-2026 12:10 | 251.033 | 254.804 | 903.2 | 42.4673 | 42.596 | -0.12871 | 255.5762 | 39.4 | 41.9869 | -2.5869 | 0.9852 | 17-03-2026 12:10 | 188.11 | 190.704 | 671.5 | 31.784 | 31.5526 | 0.23138 | 189.3157 | 29.2 | 31.1014 | -1.9014 | 0.9864 | 17-03-2026 12:10 | 183.134 | 185.678 | 668.5 | 30.9463 | 31.5526 | -0.60629 | 189.3157 | 28.9 | 31.1014 | -2.2014 | 0.9863 | 17-03-2026 12:10 | 186.655 | 188.254 | 670.3 | 31.3757 | 31.5526 | -0.17696 | 189.3157 | 28.8 | 31.1014 | -2.3014 | 0.99151 | 17-03-2026 12:10 | 190.108 | 194.231 | 680.3 | 32.3718 | 31.5526 | 0.81921 | 189.3157 | 29.2 | 31.1014 | -1.9014 | 0.97877 | 17-03-2026 12:10 | 181.407 | 183.927 | 642.2 | 30.6545 | 30.0184 | 0.63609 | 180.1105 | 27.8 | 29.5891 | -1.7891 | 0.9863 | 17-03-2026 12:10 | 327.1868 | 326.6131 | 0.57376 | 1959.6784 | 302 | 321.9425 | -19.9425
17-03-2026 12:00 | 1061 | 48.79 | 352.812 | 358.476 | 865.7 | 59.746 | 63.1788 | -3.4328 | 379.0729 | 97.9 | 62.2754 | 35.6246 | 0.9842 | 17-03-2026 12:00 | 352.782 | 358.478 | 869 | 59.7463 | 63.1788 | -3.4325 | 379.0729 | 96.7 | 62.2754 | 34.4246 | 0.98411 | 17-03-2026 12:00 | 352.275 | 362.358 | 855.9 | 60.393 | 63.1788 | -2.7858 | 379.0729 | 96.6 | 62.2754 | 34.3246 | 0.97217 | 17-03-2026 12:00 | 352.427 | 358.158 | 863.8 | 59.693 | 63.1788 | -3.4858 | 379.0729 | 96.7 | 62.2754 | 34.4246 | 0.984 | 17-03-2026 12:00 | 266.747 | 270.974 | 642.3 | 45.1623 | 46.7991 | -1.6368 | 280.7947 | 73.3 | 46.1299 | 27.1701 | 0.9844 | 17-03-2026 12:00 | 265.132 | 269.485 | 639.6 | 44.9142 | 46.7991 | -1.885 | 280.7947 | 72.3 | 46.1299 | 26.1701 | 0.98385 | 17-03-2026 12:00 | 264.418 | 269.693 | 641.5 | 44.9488 | 46.7991 | -1.8503 | 280.7947 | 72.8 | 46.1299 | 26.6701 | 0.98044 | 17-03-2026 12:00 | 268.679 | 276.87 | 651.1 | 46.145 | 46.7991 | -0.65412 | 280.7947 | 72.5 | 46.1299 | 26.3701 | 0.97042 | 17-03-2026 12:00 | 254.31 | 258.34 | 614.4 | 43.0567 | 44.5236 | -1.4669 | 267.1414 | 68.5 | 43.8869 | 24.6131 | 0.9844 | 17-03-2026 12:00 | 463.8053 | 484.4353 | -20.63 | 2906.6119 | 747.3 | 477.5079 | 269.7921
17-03-2026 11:50 | 988 | 48.5 |  |  |  | 0 | 58.8971 | -58.8971 | 353.3824 | 0 | 58.0548 | -58.0548 | [5 empty] | 0 | 58.8971 | -58.8971 | 353.3824 | 0 | 58.0548 | -58.0548 | [5 empty] | 0 | 58.8971 | -58.8971 | 353.3824 | 0 | 58.0548 | -58.0548 | [5 empty] | 0 | 58.8971 | -58.8971 | 353.3824 | 0 | 58.0548 | -58.0548 | [5 empty] | 0 | 43.6275 | -43.6275 | 261.7647 | 0 | 43.0036 | -43.0036 | [5 empty] | 0 | 43.6275 | -43.6275 | 261.7647 | 0 | 43.0036 | -43.0036 | [5 empty] | 0 | 43.6275 | -43.6275 | 261.7647 | 0 | 43.0036 | -43.0036 | [5 empty] | 0 | 43.6275 | -43.6275 | 261.7647 | 0 | 43.0036 | -43.0036 | [5 empty] | 0 | 41.5061 | -41.5061 | 249.0367 | 0 | 40.9126 | -40.9126 |  | 17-03-2026 11:50 | 0 | 451.6042 | -451.6042 | 2709.625 | 0 | 445.1462 | -445.1462
17-03-2026 11:40 | 462 | 48.5 | 161.769 | 164.016 | 767.8 | 27.336 | 27.5409 | -0.20493 | 165.2456 | 42.3 | 27.1471 | 15.1529 | 0.9863 | 17-03-2026 11:40 | 163.048 | 165.38 | 772.3 | 27.5633 | 27.5409 | 0.022401 | 165.2456 | 44.5 | 27.1471 | 17.3529 | 0.9859 | 17-03-2026 11:40 | 160.944 | 164.89 | 759.3 | 27.4817 | 27.5409 | -0.059266 | 165.2456 | 42.9 | 27.1471 | 15.7529 | 0.97607 | 17-03-2026 11:40 | 161.734 | 164.014 | 767.1 | 27.3357 | 27.5409 | -0.20527 | 165.2456 | 43.4 | 27.1471 | 16.2529 | 0.9861 | 17-03-2026 11:40 | 120.723 | 122.387 | 569 | 20.3978 | 20.4007 | -0.0028574 | 122.4041 | 32.2 | 20.109 | 12.091 | 0.9864 | 17-03-2026 11:40 | 120.191 | 121.932 | 567.3 | 20.322 | 20.4007 | -0.078691 | 122.4041 | 32.1 | 20.109 | 11.991 | 0.98572 | 17-03-2026 11:40 | 119.194 | 120.813 | 568.7 | 20.1355 | 20.4007 | -0.26519 | 122.4041 | 31.7 | 20.109 | 11.591 | 0.9866 | 17-03-2026 11:40 | 120.878 | 124.465 | 578.6 | 20.7442 | 20.4007 | 0.34348 | 122.4041 | 32.2 | 20.109 | 12.091 | 0.97118 | 17-03-2026 11:40 | 114.246 | 115.809 | 545.9 | 19.3015 | 19.4087 | -0.10723 | 116.4524 | 30.5 | 19.1312 | 11.3688 | 0.9865 | 17-03-2026 11:40 | 210.6177 | 211.1752 | -0.55756 | 1267.0513 | 331.8 | 208.1554 | 123.6446
17-03-2026 11:30 | 821 | 48.5 | 270.776 | 275.067 | 725.5 | 45.8445 | 48.9418 | -3.0973 | 293.6507 | 52.9 | 48.2419 | 4.6581 | 0.9844 | 17-03-2026 11:30 | 278.168 | 282.749 | 727.8 | 47.1248 | 48.9418 | -1.817 | 293.6507 | 51.9 | 48.2419 | 3.6581 | 0.9838 | 17-03-2026 11:30 | 276.63 | 283.366 | 716.4 | 47.2277 | 48.9418 | -1.7141 | 293.6507 | 50.8 | 48.2419 | 2.5581 | 0.97623 | 17-03-2026 11:30 | 282.048 | 286.663 | 723.7 | 47.7772 | 48.9418 | -1.1646 | 293.6507 | 51.4 | 48.2419 | 3.1581 | 0.9839 | 17-03-2026 11:30 | 207.339 | 210.411 | 536.8 | 35.0685 | 36.2532 | -1.1847 | 217.5191 | 38.2 | 35.7348 | 2.4652 | 0.9854 | 17-03-2026 11:30 | 209.798 | 213.198 | 535.2 | 35.533 | 36.2532 | -0.72018 | 217.5191 | 38 | 35.7348 | 2.2652 | 0.98405 | 17-03-2026 11:30 | 206.267 | 209.466 | 537 | 34.911 | 36.2532 | -1.3422 | 217.5191 | 38 | 35.7348 | 2.2652 | 0.98473 | 17-03-2026 11:30 | 211.599 | 217.309 | 546.4 | 36.2182 | 36.2532 | -0.035009 | 217.5191 | 39.2 | 35.7348 | 3.4652 | 0.97372 | 17-03-2026 11:30 | 201.456 | 204.441 | 515.4 | 34.0735 | 34.4904 | -0.41691 | 206.9424 | 37 | 33.9972 | 3.0028 | 0.9854 | 17-03-2026 11:30 | 363.7783 | 375.2703 | -11.4919 | 2251.6215 | 397.4 | 369.9039 | 27.4961
17-03-2026 11:20 | 980 | 48.5 | 339.243 | 345.472 | 672.6 | 57.5787 | 58.4202 | -0.84149 | 350.521 | 34.8 | 57.5848 | -22.7848 | 0.98197 | 17-03-2026 11:20 | 340.75 | 346.713 | 675.9 | 57.7855 | 58.4202 | -0.63466 | 350.521 | 35.1 | 57.5848 | -22.4848 | 0.9828 | 17-03-2026 11:20 | 327.32 | 336.302 | 665.6 | 56.0503 | 58.4202 | -2.3698 | 350.521 | 35.3 | 57.5848 | -22.2848 | 0.97329 | 17-03-2026 11:20 | 329.891 | 335.63 | 672.3 | 55.9383 | 58.4202 | -2.4818 | 350.521 | 35.7 | 57.5848 | -21.8848 | 0.9829 | 17-03-2026 11:20 | 245.918 | 249.79 | 498.6 | 41.6317 | 43.2742 | -1.6425 | 259.6452 | 27.9 | 42.6554 | -14.7554 | 0.9845 | 17-03-2026 11:20 | 243.042 | 247.241 | 497.2 | 41.2068 | 43.2742 | -2.0674 | 259.6452 | 27.7 | 42.6554 | -14.9554 | 0.98302 | 17-03-2026 11:20 | 244.392 | 249.26 | 499 | 41.5433 | 43.2742 | -1.7309 | 259.6452 | 27.9 | 42.6554 | -14.7554 | 0.98047 | 17-03-2026 11:20 | 246.65 | 254.042 | 507.2 | 42.3403 | 43.2742 | -0.93386 | 259.6452 | 29.7 | 42.6554 | -12.9554 | 0.9709 | 17-03-2026 11:20 | 233.603 | 237.281 | 478.4 | 39.5468 | 41.17 | -1.6232 | 247.0202 | 26.3 | 40.5813 | -14.2813 | 0.9845 | 17-03-2026 11:20 | 433.6218 | 447.9474 | -14.3256 | 2687.6847 | 280.4 | 441.5418 | -161.1418
17-03-2026 11:10 | 684 | 48.5 | 0 | 0 | 637.8 | 0 | 40.7749 | -40.7749 | 244.6493 | 46.1 | 40.1918 | 5.9082 |  | 17-03-2026 11:10 | 0 | 0 | 640.8 | 0 | 40.7749 | -40.7749 | 244.6493 | 44.7 | 40.1918 | 4.5082 |  | 17-03-2026 11:10 | 0 | 0 | 630.3 | 0 | 40.7749 | -40.7749 | 244.6493 | 43 | 40.1918 | 2.8082 |  | 17-03-2026 11:10 | 0 | 0 | 636.6 | 0 | 40.7749 | -40.7749 | 244.6493 | 43.4 | 40.1918 | 3.2082 |  | 17-03-2026 11:10 | 0 | 0 | 470.7 | 0 | 30.2036 | -30.2036 | 181.2217 | 32.1 | 29.7717 | 2.3283 |  | 17-03-2026 11:10 | 0 | 0 | 469.5 | 0 | 30.2036 | -30.2036 | 181.2217 | 32 | 29.7717 | 2.2283 |  | 17-03-2026 11:10 | 0 | 0 | 471.1 | 0 | 30.2036 | -30.2036 | 181.2217 | 31.7 | 29.7717 | 1.9283 |  | 17-03-2026 11:10 | 0 | 0 | 477.5 | 0 | 30.2036 | -30.2036 | 181.2217 | 32.1 | 29.7717 | 2.3283 |  | 17-03-2026 11:10 | 0 | 0 | 452.1 | 0 | 28.735 | -28.735 | 172.41 | 30.3 | 28.3241 | 1.9759 |  | 17-03-2026 11:10 | 0 | 312.649 | -312.649 | 1875.8942 | 335.4 | 308.1782 | 27.2218
17-03-2026 11:00 | 1030 | 48.79 | 346.597 | 357.145 | 591.7 | 59.5242 | 61.3329 | -1.8087 | 367.9972 | 99.1 | 60.4558 | 38.6442 | 0.97047 | 17-03-2026 11:00 | 352.686 | 358.494 | 596.1 | 59.749 | 61.3329 | -1.5839 | 367.9972 | 101.4 | 60.4558 | 40.9442 | 0.9838 | 17-03-2026 11:00 | 346.95 | 356.092 | 587.3 | 59.3487 | 61.3329 | -1.9842 | 367.9972 | 99.9 | 60.4558 | 39.4442 | 0.97433 | 17-03-2026 11:00 | 351.193 | 357.521 | 593.2 | 59.5868 | 61.3329 | -1.746 | 367.9972 | 101.3 | 60.4558 | 40.8442 | 0.9823 | 17-03-2026 11:00 | 257.123 | 262.343 | 438.6 | 43.7238 | 45.4318 | -1.7079 | 272.5905 | 75.5 | 44.7821 | 30.7179 | 0.9801 | 17-03-2026 11:00 | 257.446 | 261.579 | 437.5 | 43.5965 | 45.4318 | -1.8353 | 272.5905 | 75.2 | 44.7821 | 30.4179 | 0.9842 | 17-03-2026 11:00 | 252.924 | 257.344 | 439.4 | 42.8907 | 45.4318 | -2.5411 | 272.5905 | 75.3 | 44.7821 | 30.5179 | 0.98282 | 17-03-2026 11:00 | 255.483 | 262.649 | 445.4 | 43.7748 | 45.4318 | -1.6569 | 272.5905 | 76.1 | 44.7821 | 31.3179 | 0.97272 | 17-03-2026 11:00 | 243.816 | 247.705 | 421.8 | 41.2842 | 43.2227 | -1.9385 | 259.3361 | 72 | 42.6046 | 29.3954 | 0.9843 | 17-03-2026 11:00 | 453.4787 | 470.2812 | -16.8025 | 2821.6873 | 775.8 | 463.5562 | 312.2438
17-03-2026 10:50 | 892 | 48.79 |  |  |  | 0 | 53.1155 | -53.1155 | 318.6928 | 0 | 52.3559 | -52.3559 | [5 empty] | 0 | 53.1155 | -53.1155 | 318.6928 | 0 | 52.3559 | -52.3559 | [5 empty] | 0 | 53.1155 | -53.1155 | 318.6928 | 0 | 52.3559 | -52.3559 | [5 empty] | 0 | 53.1155 | -53.1155 | 318.6928 | 0 | 52.3559 | -52.3559 | [5 empty] | 0 | 39.3448 | -39.3448 | 236.0687 | 0 | 38.7822 | -38.7822 | [5 empty] | 0 | 39.3448 | -39.3448 | 236.0687 | 0 | 38.7822 | -38.7822 | [5 empty] | 0 | 39.3448 | -39.3448 | 236.0687 | 0 | 38.7822 | -38.7822 | [5 empty] | 0 | 39.3448 | -39.3448 | 236.0687 | 0 | 38.7822 | -38.7822 | [5 empty] | 0 | 37.4317 | -37.4317 | 224.5901 | 0 | 36.8964 | -36.8964 |  | 17-03-2026 10:50 | 0 | 407.2727 | -407.2727 | 2443.636 | 0 | 401.4487 | -401.4487
17-03-2026 10:40 | 941 | 48.5 | 329.33 | 334.651 | 492.6 | 55.7752 | 56.0953 | -0.32011 | 336.5717 | 42.8 | 55.2931 | -12.4931 | 0.9841 | 17-03-2026 10:40 | 299.018 | 303.757 | 494.7 | 50.6262 | 56.0953 | -5.4691 | 336.5717 | 41.9 | 55.2931 | -13.3931 | 0.9844 | 17-03-2026 10:40 | 324.684 | 332.585 | 487.4 | 55.4308 | 56.0953 | -0.66444 | 336.5717 | 41.8 | 55.2931 | -13.4931 | 0.97624 | 17-03-2026 10:40 | 327.895 | 333.362 | 491.9 | 55.5603 | 56.0953 | -0.53494 | 336.5717 | 41.7 | 55.2931 | -13.5931 | 0.9836 | 17-03-2026 10:40 | 242.234 | 245.848 | 363.1 | 40.9747 | 41.5521 | -0.57739 | 249.3123 | 30.9 | 40.9579 | -10.0579 | 0.9853 | 17-03-2026 10:40 | 242.049 | 245.663 | 362.3 | 40.9438 | 41.5521 | -0.60822 | 249.3123 | 30.9 | 40.9579 | -10.0579 | 0.98529 | 17-03-2026 10:40 | 240.849 | 245.224 | 364.1 | 40.8707 | 41.5521 | -0.68139 | 249.3123 | 30.9 | 40.9579 | -10.0579 | 0.98216 | 17-03-2026 10:40 | 242.244 | 249.565 | 369.3 | 41.5942 | 41.5521 | 0.04211 | 249.3123 | 31.9 | 40.9579 | -9.0579 | 0.97066 | 17-03-2026 10:40 | 229.169 | 232.635 | 349.8 | 38.7725 | 39.5316 | -0.75914 | 237.1898 | 30.3 | 38.9663 | -8.6663 | 0.9851 | 17-03-2026 10:40 | 420.5483 | 430.121 | -9.5726 | 2580.7258 | 323.1 | 423.9702 | -100.8702
17-03-2026 10:30 | 846 | 48.5 | 275.551 | 279.804 | 449.8 | 46.634 | 50.4321 | -3.7981 | 302.5926 | 45.6 | 49.7109 | -4.1109 | 0.9848 | 17-03-2026 10:30 | 288.986 | 293.861 | 452.8 | 48.9768 | 50.4321 | -1.4553 | 302.5926 | 47.6 | 49.7109 | -2.1109 | 0.98341 | 17-03-2026 10:30 | 294.063 | 301.838 | 445.6 | 50.3063 | 50.4321 | -0.12576 | 302.5926 | 46.7 | 49.7109 | -3.0109 | 0.97424 | 17-03-2026 10:30 | 298.607 | 303.432 | 450.2 | 50.572 | 50.4321 | 0.1399 | 302.5926 | 47.3 | 49.7109 | -2.4109 | 0.9841 | 17-03-2026 10:30 | 221.828 | 225.046 | 332.2 | 37.5077 | 37.3571 | 0.15056 | 224.1427 | 35.8 | 36.8229 | -1.0229 | 0.9857 | 17-03-2026 10:30 | 223.191 | 226.628 | 331.4 | 37.7713 | 37.3571 | 0.41422 | 224.1427 | 35.7 | 36.8229 | -1.1229 | 0.98483 | 17-03-2026 10:30 | 221.289 | 225.424 | 333.2 | 37.5707 | 37.3571 | 0.21356 | 224.1427 | 35.7 | 36.8229 | -1.1229 | 0.98166 | 17-03-2026 10:30 | 225.533 | 232.362 | 337.4 | 38.727 | 37.3571 | 1.3699 | 224.1427 | 35.7 | 36.8229 | -1.1229 | 0.97061 | 17-03-2026 10:30 | 212.426 | 215.508 | 319.5 | 35.918 | 35.5407 | 0.37734 | 213.244 | 33.7 | 35.0324 | -1.3324 | 0.9857 | 17-03-2026 10:30 | 383.9838 | 386.6975 | -2.7137 | 2320.1849 | 363.8 | 381.1677 | -17.3677
17-03-2026 10:20 | 751 | 48.5 | 269.93 | 273.957 | 404.2 | 45.6595 | 44.7689 | 0.89058 | 268.6135 | 37.2 | 44.1287 | -6.9287 | 0.9853 | 17-03-2026 10:20 | 269.413 | 273.46 | 405.2 | 45.5767 | 44.7689 | 0.80775 | 268.6135 | 37.1 | 44.1287 | -7.0287 | 0.9852 | 17-03-2026 10:20 | 268.809 | 275.343 | 398.9 | 45.8905 | 44.7689 | 1.1216 | 268.6135 | 36.6 | 44.1287 | -7.5287 | 0.97627 | 17-03-2026 10:20 | 268.902 | 272.942 | 402.9 | 45.4903 | 44.7689 | 0.72141 | 268.6135 | 37.3 | 44.1287 | -6.8287 | 0.9852 | 17-03-2026 10:20 | 198.721 | 201.44 | 296.4 | 33.5733 | 33.1622 | 0.41117 | 198.973 | 27.2 | 32.6879 | -5.4879 | 0.9865 | 17-03-2026 10:20 | 200.873 | 204.676 | 295.7 | 34.1127 | 33.1622 | 0.9505 | 198.973 | 27.2 | 32.6879 | -5.4879 | 0.98142 | 17-03-2026 10:20 | 199.723 | 203.022 | 297.5 | 33.837 | 33.1622 | 0.67484 | 198.973 | 27.3 | 32.6879 | -5.3879 | 0.98375 | 17-03-2026 10:20 | 204.859 | 210.511 | 301.7 | 35.0852 | 33.1622 | 1.923 | 198.973 | 27.5 | 32.6879 | -5.1879 | 0.97315 | 17-03-2026 10:20 | 193.676 | 196.366 | 285.8 | 32.7277 | 31.5497 | 1.178 | 189.2981 | 26.1 | 31.0985 | -4.9985 | 0.9863 | 17-03-2026 10:20 | 351.9528 | 343.274 | 8.6788 | 2059.6441 | 283.5 | 338.3652 | -54.8652
17-03-2026 10:10 | 441 | 48.5 | 157.562 | 159.67 | 367 | 26.6117 | 26.2891 | 0.32259 | 157.7344 | 34.7 | 25.9131 | 8.7869 | 0.9868 | 17-03-2026 10:10 | 157.977 | 160.123 | 368.1 | 26.6872 | 26.2891 | 0.39809 | 157.7344 | 32.7 | 25.9131 | 6.7869 | 0.9866 | 17-03-2026 10:10 | 153.472 | 156.467 | 362.3 | 26.0778 | 26.2891 | -0.21124 | 157.7344 | 32 | 25.9131 | 6.0869 | 0.98086 | 17-03-2026 10:10 | 158.104 | 160.268 | 365.6 | 26.7113 | 26.2891 | 0.42226 | 157.7344 | 32.1 | 25.9131 | 6.1869 | 0.9865 | 17-03-2026 10:10 | 115.797 | 117.473 | 269.2 | 19.5788 | 19.4734 | 0.10545 | 116.8403 | 23.6 | 19.1949 | 4.4051 | 0.98573 | 17-03-2026 10:10 | 116.178 | 117.962 | 268.5 | 19.6603 | 19.4734 | 0.18695 | 116.8403 | 23.7 | 19.1949 | 4.5051 | 0.98488 | 17-03-2026 10:10 | 115.088 | 116.802 | 270.2 | 19.467 | 19.4734 | -0.0063867 | 116.8403 | 24 | 19.1949 | 4.8051 | 0.98533 | 17-03-2026 10:10 | 116.119 | 119.419 | 274.2 | 19.9032 | 19.4734 | 0.42978 | 116.8403 | 24.4 | 19.1949 | 5.2051 | 0.97237 | 17-03-2026 10:10 | 110.405 | 111.882 | 259.7 | 18.647 | 18.5265 | 0.12048 | 111.1591 | 23.1 | 18.2616 | 4.8384 | 0.9868 | 17-03-2026 10:10 | 203.3443 | 201.5764 | 1.768 | 1209.4581 | 250.3 | 198.6938 | 51.6062
17-03-2026 10:00 | 675 | 48.79 | 232.21 | 245.483 | 332.3 | 40.9138 | 40.1939 | 0.71996 | 241.1632 | 78.6 | 39.6191 | 38.9809 | 0.94593 | 17-03-2026 10:00 | 242.743 | 246.546 | 335.4 | 41.091 | 40.1939 | 0.89713 | 241.1632 | 81.7 | 39.6191 | 42.0809 | 0.98457 | 17-03-2026 10:00 | 238.437 | 243.55 | 330.3 | 40.5917 | 40.1939 | 0.39779 | 241.1632 | 80.2 | 39.6191 | 40.5809 | 0.97901 | 17-03-2026 10:00 | 239.017 | 242.509 | 333.5 | 40.4182 | 40.1939 | 0.22429 | 241.1632 | 81.1 | 39.6191 | 41.4809 | 0.9856 | 17-03-2026 10:00 | 176.79 | 179.191 | 245.6 | 29.8652 | 29.7732 | 0.091927 | 178.6394 | 60 | 29.3475 | 30.6525 | 0.9866 | 17-03-2026 10:00 | 177.22 | 179.768 | 244.8 | 29.9613 | 29.7732 | 0.18809 | 178.6394 | 60.1 | 29.3475 | 30.7525 | 0.98583 | 17-03-2026 10:00 | 177.172 | 179.578 | 246.2 | 29.9297 | 29.7732 | 0.15643 | 178.6394 | 59.6 | 29.3475 | 30.2525 | 0.9866 | 17-03-2026 10:00 | 180.193 | 185.016 | 249.8 | 30.836 | 29.7732 | 1.0628 | 178.6394 | 60.2 | 29.3475 | 30.8525 | 0.97393 | 17-03-2026 10:00 | 171.367 | 173.712 | 236.6 | 28.952 | 28.3255 | 0.62645 | 169.9533 | 57.7 | 27.9205 | 29.7795 | 0.9865 | 17-03-2026 10:00 | 312.5588 | 308.194 | 4.3648 | 1849.164 | 619.2 | 303.7868 | 315.4132
17-03-2026 09:50 | 764 | 48.5 |  |  |  | 0 | 45.5439 | -45.5439 | 273.2633 | 0 | 44.8926 | -44.8926 | [5 empty] | 0 | 45.5439 | -45.5439 | 273.2633 | 0 | 44.8926 | -44.8926 | [5 empty] | 0 | 45.5439 | -45.5439 | 273.2633 | 0 | 44.8926 | -44.8926 | [5 empty] | 0 | 45.5439 | -45.5439 | 273.2633 | 0 | 44.8926 | -44.8926 | [5 empty] | 0 | 33.7362 | -33.7362 | 202.4172 | 0 | 33.2538 | -33.2538 | [5 empty] | 0 | 33.7362 | -33.7362 | 202.4172 | 0 | 33.2538 | -33.2538 | [5 empty] | 0 | 33.7362 | -33.7362 | 202.4172 | 0 | 33.2538 | -33.2538 | [5 empty] | 0 | 33.7362 | -33.7362 | 202.4172 | 0 | 33.2538 | -33.2538 | [5 empty] | 0 | 32.0958 | -32.0958 | 192.5749 | 0 | 31.6369 | -31.6369 |  | 17-03-2026 09:50 | 0 | 349.2162 | -349.2162 | 2095.297 | 0 | 344.2224 | -344.2224
17-03-2026 09:40 | 719 | 46.21 | 262.799 | 268.142 | 253.7 | 44.6903 | 43.2356 | 1.4547 | 259.4139 | 23.7 | 42.6174 | -18.9174 |  | 17-03-2026 09:40 | 265.169 | 268.907 | 253.7 | 44.8178 | 43.2356 | 1.5822 | 259.4139 | 24.1 | 42.6174 | -18.5174 |  | 17-03-2026 09:40 | 260.582 | 266.329 | 250.1 | 44.3882 | 43.2356 | 1.1525 | 259.4139 | 23.9 | 42.6174 | -18.7174 |  | 17-03-2026 09:40 | 263.237 | 266.948 | 252.4 | 44.4913 | 43.2356 | 1.2557 | 259.4139 | 24 | 42.6174 | -18.6174 |  | 17-03-2026 09:40 | 194.624 | 197.128 | 185.6 | 32.8547 | 32.0264 | 0.82826 | 192.1584 | 17.9 | 31.5684 | -13.6684 |  | 17-03-2026 09:40 | 195.03 | 197.539 | 184.7 | 32.9232 | 32.0264 | 0.89676 | 192.1584 | 18 | 31.5684 | -13.5684 |  | 17-03-2026 09:40 | 194.653 | 197.137 | 186.6 | 32.8562 | 32.0264 | 0.82976 | 192.1584 | 18 | 31.5684 | -13.5684 |  | 17-03-2026 09:40 | 196.597 | 202.054 | 189.6 | 33.6757 | 32.0264 | 1.6493 | 192.1584 | 18.4 | 31.5684 | -13.1684 |  | 17-03-2026 09:40 | 187.08 | 189.486 | 178.9 | 31.581 | 30.4692 | 1.1118 | 182.8149 | 16.8 | 30.0334 | -13.2334 |  | 17-03-2026 09:40 | 342.2783 | 331.5173 | 10.761 | 1989.104 | 184.8 | 326.7766 | -141.9766
17-03-2026 09:30 | 202 | 46.78 | 75.887 | 74.089 | 230 | 12.3482 | 12.1207 | 0.22747 | 72.7242 | 20.9 | 11.9474 | 8.9526 |  | 17-03-2026 09:30 | 73.903 | 74.914 | 229.6 | 12.4857 | 12.1207 | 0.36497 | 72.7242 | 20.8 | 11.9474 | 8.8526 |  | 17-03-2026 09:30 | 72.471 | 73.476 | 226.2 | 12.246 | 12.1207 | 0.12531 | 72.7242 | 20.3 | 11.9474 | 8.3526 |  | 17-03-2026 09:30 | 73.543 | 74.549 | 228.4 | 12.4248 | 12.1207 | 0.30414 | 72.7242 | 20.7 | 11.9474 | 8.7526 |  | 17-03-2026 09:30 | 53.9 | 54.743 | 167.7 | 9.1238 | 8.9783 | 0.14554 | 53.8698 | 15.1 | 8.8499 | 6.2501 |  | 17-03-2026 09:30 | 54.293 | 55.12 | 166.7 | 9.1867 | 8.9783 | 0.20837 | 53.8698 | 15.2 | 8.8499 | 6.3501 |  | 17-03-2026 09:30 | 54.168 | 55.004 | 168.6 | 9.1673 | 8.9783 | 0.18904 | 53.8698 | 15.5 | 8.8499 | 6.6501 |  | 17-03-2026 09:30 | 54.976 | 56.752 | 171.2 | 9.4587 | 8.9783 | 0.48037 | 53.8698 | 15.7 | 8.8499 | 6.8501 |  | 17-03-2026 09:30 | 52.166 | 52.993 | 162.1 | 8.8322 | 8.5417 | 0.29043 | 51.2504 | 15 | 8.4196 | 6.5804 |  | 17-03-2026 09:30 | 95.2733 | 92.9377 | 2.3357 | 557.6261 | 159.2 | 91.6087 | 67.5913
17-03-2026 09:20 | 475 | 48.5 | 174.32 | 176.544 | 209.1 | 29.424 | 28.3159 | 1.1081 | 169.8954 | 64.2 | 27.911 | 36.289 |  | 17-03-2026 09:20 | 170.432 | 176.827 | 208.8 | 29.4712 | 28.3159 | 1.1553 | 169.8954 | 64.3 | 27.911 | 36.389 |  | 17-03-2026 09:20 | 172.765 | 175.701 | 205.9 | 29.2835 | 28.3159 | 0.96761 | 169.8954 | 63 | 27.911 | 35.089 |  | 17-03-2026 09:20 | 174.385 | 176.646 | 207.7 | 29.441 | 28.3159 | 1.1251 | 169.8954 | 63.9 | 27.911 | 35.989 |  | 17-03-2026 09:20 | 129.123 | 130.654 | 152.6 | 21.7757 | 20.9747 | 0.80093 | 125.8484 | 47.2 | 20.6748 | 26.5252 |  | 17-03-2026 09:20 | 130.039 | 131.632 | 151.5 | 21.9387 | 20.9747 | 0.96393 | 125.8484 | 47.2 | 20.6748 | 26.5252 |  | 17-03-2026 09:20 | 128.241 | 129.812 | 153.1 | 21.6353 | 20.9747 | 0.6606 | 125.8484 | 46.9 | 20.6748 | 26.2252 |  | 17-03-2026 09:20 | 130.339 | 133.801 | 155.5 | 22.3002 | 20.9747 | 1.3254 | 125.8484 | 47.6 | 20.6748 | 26.9252 |  | 17-03-2026 09:20 | 122.973 | 124.492 | 147.1 | 20.7487 | 19.9549 | 0.7938 | 119.7292 | 45.1 | 19.6695 | 25.4305 |  | 17-03-2026 09:20 | 226.0182 | 217.1174 | 8.9008 | 1302.7043 | 489.4 | 214.0126 | 275.3874
17-03-2026 09:10 | 567 | 48.5 |  |  |  | 0 | 33.8002 | -33.8002 | 202.8014 | 0 | 33.3169 | -33.3169 | [5 empty] | 0 | 33.8002 | -33.8002 | 202.8014 | 0 | 33.3169 | -33.3169 | [5 empty] | 0 | 33.8002 | -33.8002 | 202.8014 | 0 | 33.3169 | -33.3169 | [5 empty] | 0 | 33.8002 | -33.8002 | 202.8014 | 0 | 33.3169 | -33.3169 | [5 empty] | 0 | 25.0372 | -25.0372 | 150.2233 | 0 | 24.6792 | -24.6792 | [5 empty] | 0 | 25.0372 | -25.0372 | 150.2233 | 0 | 24.6792 | -24.6792 | [5 empty] | 0 | 25.0372 | -25.0372 | 150.2233 | 0 | 24.6792 | -24.6792 | [5 empty] | 0 | 25.0372 | -25.0372 | 150.2233 | 0 | 24.6792 | -24.6792 | [5 empty] | 0 | 23.8198 | -23.8198 | 142.9188 | 0 | 23.4792 | -23.4792 |  | 17-03-2026 09:10 | 0 | 259.1696 | -259.1696 | 1555.0176 | 0 | 255.4635 | -255.4635
17-03-2026 09:00 | 473 | 42.76 | 176.837 | 178.985 | 144.9 | 29.8308 | 28.8139 | 1.0169 | 172.8834 | 21.2 | 28.4019 | -7.2019 |  | 17-03-2026 09:00 | 176.606 | 178.823 | 144.5 | 29.8038 | 28.8139 | 0.98993 | 172.8834 | 21.1 | 28.4019 | -7.3019 |  | 17-03-2026 09:00 | 176.384 | 180.022 | 142.9 | 30.0037 | 28.8139 | 1.1898 | 172.8834 | 21.2 | 28.4019 | -7.2019 |  | 17-03-2026 09:00 | 174.456 | 176.629 | 143.8 | 29.4382 | 28.8139 | 0.62426 | 172.8834 | 20.9 | 28.4019 | -7.5019 |  | 17-03-2026 09:00 | 129.19 | 130.719 | 105.4 | 21.7865 | 21.3436 | 0.44286 | 128.0618 | 15.5 | 21.0384 | -5.5384 |  | 17-03-2026 09:00 | 127.907 | 129.408 | 104.3 | 21.568 | 21.3436 | 0.22436 | 128.0618 | 15.4 | 21.0384 | -5.6384 |  | 17-03-2026 09:00 | 129.935 | 131.473 | 106.2 | 21.9122 | 21.3436 | 0.56853 | 128.0618 | 15.4 | 21.0384 | -5.6384 |  | 17-03-2026 09:00 | 131.821 | 135.727 | 107.9 | 22.6212 | 21.3436 | 1.2775 | 128.0618 | 15.7 | 21.0384 | -5.3384 |  | 17-03-2026 09:00 | 124.233 | 125.716 | 102 | 20.9527 | 20.3058 | 0.64684 | 121.835 | 15.1 | 20.0155 | -4.9155 |  | 17-03-2026 09:00 | 227.917 | 220.936 | 6.981 | 1325.616 | 161.5 | 217.7766 | -56.2766
17-03-2026 08:50 | 425 | 43.05 | 162.806 | 164.75 | 123.7 | 27.4583 | 25.8619 | 1.5965 | 155.1711 | 28 | 25.492 | 2.508 |  | 17-03-2026 08:50 | 156.872 | 158.793 | 123.4 | 26.4655 | 25.8619 | 0.60364 | 155.1711 | 28.2 | 25.492 | 2.708 |  | 17-03-2026 08:50 | 153.986 | 156.356 | 121.7 | 26.0593 | 25.8619 | 0.19748 | 155.1711 | 27.6 | 25.492 | 2.108 |  | 17-03-2026 08:50 | 155.436 | 157.34 | 122.9 | 26.2233 | 25.8619 | 0.36148 | 155.1711 | 28.4 | 25.492 | 2.908 |  | 17-03-2026 08:50 | 115.872 | 115.881 | 89.9 | 19.3135 | 19.1569 | 0.15657 | 114.9416 | 20.8 | 18.883 | 1.917 |  | 17-03-2026 08:50 | 114.972 | 116.409 | 88.9 | 19.4015 | 19.1569 | 0.24457 | 114.9416 | 21.1 | 18.883 | 2.217 |  | 17-03-2026 08:50 | 112.87 | 114.195 | 90.8 | 19.0325 | 19.1569 | -0.12443 | 114.9416 | 20.9 | 18.883 | 2.017 |  | 17-03-2026 08:50 | 115.762 | 118.828 | 92.2 | 19.8047 | 19.1569 | 0.64774 | 114.9416 | 21.4 | 18.883 | 2.517 |  | 17-03-2026 08:50 | 111.92 | 113.245 | 86.9 | 18.8742 | 18.2254 | 0.64872 | 109.3527 | 19.8 | 17.9648 | 1.8352 |  | 17-03-2026 08:50 | 202.6328 | 198.3006 | 4.3322 | 1189.8035 | 216.2 | 195.4649 | 20.7351
17-03-2026 08:40 | 409 | 35.59 | 152.414 | 154.14 | 95.7 | 25.69 | 25.5819 | 0.10811 | 153.4913 | 14.4 | 25.2161 | -10.8161 |  | 17-03-2026 08:40 | 129.315 | 153.959 | 95.2 | 25.6598 | 25.5819 | 0.077948 | 153.4913 | 14.4 | 25.2161 | -10.8161 |  | 17-03-2026 08:40 | 152.022 | 154.92 | 94.1 | 25.82 | 25.5819 | 0.23811 | 153.4913 | 14.3 | 25.2161 | -10.9161 |  | 17-03-2026 08:40 | 148.534 | 150.232 | 94.5 | 25.0387 | 25.5819 | -0.54322 | 153.4913 | 14.1 | 25.2161 | -11.1161 |  | 17-03-2026 08:40 | 110.807 | 112.051 | 69.1 | 18.6752 | 18.9495 | -0.27438 | 113.6973 | 10.5 | 18.6786 | -8.1786 |  | 17-03-2026 08:40 | 111.385 | 112.612 | 67.8 | 18.7687 | 18.9495 | -0.18088 | 113.6973 | 10.5 | 18.6786 | -8.1786 |  | 17-03-2026 08:40 | 112.397 | 113.647 | 69.9 | 18.9412 | 18.9495 | -0.0083783 | 113.6973 | 10.6 | 18.6786 | -8.0786 |  | 17-03-2026 08:40 | 114.528 | 117.853 | 70.8 | 19.6422 | 18.9495 | 0.69262 | 113.6973 | 10.7 | 18.6786 | -7.9786 |  | 17-03-2026 08:40 | 109.041 | 109.901 | 67.1 | 18.3168 | 18.0281 | 0.28869 | 108.1689 | 10.2 | 17.7703 | -7.5703 |  | 17-03-2026 08:40 | 196.5525 | 196.1539 | 0.39863 | 1176.9232 | 109.7 | 193.3489 | -83.6489
17-03-2026 08:30 | 140 | 35.01 | 50.888 | 51.637 | 81.3 | 8.6062 | 8.7751 | -0.16893 | 52.6506 | 11.1 | 8.6496 | 2.4504 |  | 17-03-2026 08:30 | 50.775 | 51.555 | 80.8 | 8.5925 | 8.7751 | -0.1826 | 52.6506 | 11 | 8.6496 | 2.3504 |  | 17-03-2026 08:30 | 50.097 | 50.865 | 79.8 | 8.4775 | 8.7751 | -0.2976 | 52.6506 | 10.8 | 8.6496 | 2.1504 |  | 17-03-2026 08:30 | 50.17 | 50.944 | 80.4 | 8.4907 | 8.7751 | -0.28443 | 52.6506 | 10.8 | 8.6496 | 2.1504 |  | 17-03-2026 08:30 | 36.888 | 37.514 | 58.6 | 6.2523 | 6.5001 | -0.24774 | 39.0004 | 7.9 | 6.4071 | 1.4929 |  | 17-03-2026 08:30 | 37.044 | 37.658 | 57.3 | 6.2763 | 6.5001 | -0.22374 | 39.0004 | 8 | 6.4071 | 1.5929 |  | 17-03-2026 08:30 | 36.889 | 37.519 | 59.3 | 6.2532 | 6.5001 | -0.2469 | 39.0004 | 7.9 | 6.4071 | 1.4929 |  | 17-03-2026 08:30 | 37.46 | 38.405 | 60.1 | 6.4008 | 6.5001 | -0.099238 | 39.0004 | 8 | 6.4071 | 1.5929 |  | 17-03-2026 08:30 | 35.12 | 35.731 | 56.9 | 5.9552 | 6.184 | -0.22885 | 37.1041 | 7.6 | 6.0956 | 1.5044 |  | 17-03-2026 08:30 | 65.3047 | 67.2847 | -1.98 | 403.7081 | 83.1 | 66.3225 | 16.7775
17-03-2026 08:20 | 245 | 34.73 | 92.946 | 93.98 | 70.2 | 15.6633 | 15.372 | 0.29132 | 92.2321 | 17.2 | 15.1522 | 2.0478 |  | 17-03-2026 08:20 | 89.212 | 90.241 | 69.8 | 15.0402 | 15.372 | -0.33185 | 92.2321 | 17.4 | 15.1522 | 2.2478 |  | 17-03-2026 08:20 | 87.518 | 88.56 | 69 | 14.76 | 15.372 | -0.61201 | 92.2321 | 16.9 | 15.1522 | 1.7478 |  | 17-03-2026 08:20 | 88.64 | 89.662 | 69.6 | 14.9437 | 15.372 | -0.42835 | 92.2321 | 17.1 | 15.1522 | 1.9478 |  | 17-03-2026 08:20 | 64.666 | 65.491 | 50.7 | 10.9152 | 11.3867 | -0.47151 | 68.3201 | 12.4 | 11.2238 | 1.1762 |  | 17-03-2026 08:20 | 65.588 | 66.405 | 49.3 | 11.0675 | 11.3867 | -0.31918 | 68.3201 | 12.5 | 11.2238 | 1.2762 |  | 17-03-2026 08:20 | 65.081 | 65.891 | 51.4 | 10.9818 | 11.3867 | -0.40484 | 68.3201 | 12.7 | 11.2238 | 1.4762 |  | 17-03-2026 08:20 | 65.907 | 67.475 | 52.1 | 11.2458 | 11.3867 | -0.14084 | 68.3201 | 12.9 | 11.2238 | 1.6762 |  | 17-03-2026 08:20 | 62.856 | 63.658 | 49.3 | 10.6097 | 10.833 | -0.22335 | 64.9981 | 12.3 | 10.6781 | 1.6219 |  | 17-03-2026 08:20 | 115.2272 | 117.8678 | -2.6406 | 707.2066 | 131.4 | 116.1823 | 15.2177
17-03-2026 08:10 | 291 | 32.14 | 105.744 | 108.118 | 53 | 18.0197 | 18.4295 | -0.40987 | 110.5772 | 14.8 | 18.166 | -3.366 |  | 17-03-2026 08:10 | 104.077 | 105.224 | 52.4 | 17.5373 | 18.4295 | -0.8922 | 110.5772 | 14.5 | 18.166 | -3.666 |  | 17-03-2026 08:10 | 104.992 | 106.257 | 52.1 | 17.7095 | 18.4295 | -0.72003 | 110.5772 | 14.5 | 18.166 | -3.666 |  | 17-03-2026 08:10 | 105.688 | 106.853 | 52.5 | 17.8088 | 18.4295 | -0.6207 | 110.5772 | 14.6 | 18.166 | -3.566 |  | 17-03-2026 08:10 | 77.731 | 78.627 | 38.3 | 13.1045 | 13.6515 | -0.54701 | 81.909 | 10.7 | 13.4563 | -2.7563 |  | 17-03-2026 08:10 | 73.961 | 74.821 | 36.8 | 12.4702 | 13.6515 | -1.1813 | 81.909 | 10.1 | 13.4563 | -3.3563 |  | 17-03-2026 08:10 | 77.844 | 78.742 | 38.7 | 13.1237 | 13.6515 | -0.52784 | 81.909 | 10.7 | 13.4563 | -2.7563 |  | 17-03-2026 08:10 | 78.18 | 80.278 | 39.2 | 13.3797 | 13.6515 | -0.27184 | 81.909 | 10.8 | 13.4563 | -2.6563 |  | 17-03-2026 08:10 | 74.677 | 75.553 | 37 | 12.5922 | 12.9877 | -0.39555 | 77.9263 | 10.3 | 12.802 | -2.502 |  | 17-03-2026 08:10 | 135.7455 | 141.3119 | -5.5664 | 847.8712 | 111 | 139.2911 | -28.2911
17-03-2026 08:00 | 162 | 27.84 | 57.003 | 57.754 | 38.2 | 9.6257 | 10.4181 | -0.79244 | 62.5086 | 9.2 | 10.2691 | -1.0691 |  | 17-03-2026 08:00 | 56.77 | 57.541 | 37.9 | 9.5902 | 10.4181 | -0.82794 | 62.5086 | 9.4 | 10.2691 | -0.86913 |  | 17-03-2026 08:00 | 58.024 | 58.794 | 37.6 | 9.799 | 10.4181 | -0.61911 | 62.5086 | 9.2 | 10.2691 | -1.0691 |  | 17-03-2026 08:00 | 58.341 | 59.127 | 37.9 | 9.8545 | 10.4181 | -0.56361 | 62.5086 | 9.4 | 10.2691 | -0.86913 |  | 17-03-2026 08:00 | 42.994 | 43.653 | 27.6 | 7.2755 | 7.7171 | -0.44162 | 46.3027 | 6.9 | 7.6068 | -0.70676 |  | 17-03-2026 08:00 | 41.119 | 41.749 | 26.7 | 6.9582 | 7.7171 | -0.75895 | 46.3027 | 6.6 | 7.6068 | -1.0068 |  | 17-03-2026 08:00 | 43.442 | 44.108 | 28 | 7.3513 | 7.7171 | -0.36578 | 46.3027 | 6.9 | 7.6068 | -0.70676 |  | 17-03-2026 08:00 | 43.486 | 44.556 | 28.4 | 7.426 | 7.7171 | -0.29112 | 46.3027 | 7 | 7.6068 | -0.60676 |  | 17-03-2026 08:00 | 41.101 | 41.686 | 26.7 | 6.9477 | 7.3419 | -0.39421 | 44.0513 | 6.6 | 7.2369 | -0.63689 |  | 17-03-2026 08:00 | 74.828 | 79.8828 | -5.0548 | 479.2966 | 71.2 | 78.7404 | -7.5404
17-03-2026 07:50 | 147 | 26.12 | 51.477 | 52.166 | 29 | 8.6943 | 9.5109 | -0.81662 | 57.0657 | 8.9 | 9.3749 | -0.47494 |  | 17-03-2026 07:50 | 51.07 | 51.779 | 28.5 | 8.6298 | 9.5109 | -0.88112 | 57.0657 | 8.7 | 9.3749 | -0.67494 |  | 17-03-2026 07:50 | 50.558 | 51.25 | 28.4 | 8.5417 | 9.5109 | -0.96928 | 57.0657 | 8.8 | 9.3749 | -0.57494 |  | 17-03-2026 07:50 | 51.093 | 51.803 | 28.5 | 8.6338 | 9.5109 | -0.87712 | 57.0657 | 9 | 9.3749 | -0.37494 |  | 17-03-2026 07:50 | 37.165 | 37.746 | 20.7 | 6.291 | 7.0451 | -0.75415 | 42.2709 | 6.4 | 6.9444 | -0.5444 |  | 17-03-2026 07:50 | 35.974 | 36.533 | 20.1 | 6.0888 | 7.0451 | -0.95631 | 42.2709 | 6.3 | 6.9444 | -0.6444 |  | 17-03-2026 07:50 | 37.681 | 38.263 | 21.1 | 6.3772 | 7.0451 | -0.66798 | 42.2709 | 6.6 | 6.9444 | -0.3444 |  | 17-03-2026 07:50 | 38.282 | 39.455 | 21.4 | 6.5758 | 7.0451 | -0.46931 | 42.2709 | 6.6 | 6.9444 | -0.3444 |  | 17-03-2026 07:50 | 36.277 | 36.882 | 20.1 | 6.147 | 6.7026 | -0.55558 | 40.2155 | 6.2 | 6.6067 | -0.40674 |  | 17-03-2026 07:50 | 65.9795 | 72.927 | -6.9475 | 437.5618 | 67.5 | 71.8841 | -4.3841
17-03-2026 07:40 | 163 | 23.53 | 56.735 | 57.403 | 20.1 | 9.5672 | 10.6421 | -1.075 | 63.8528 | 8.6 | 10.4899 | -1.8899 |  | 17-03-2026 07:40 | 56.072 | 56.782 | 19.8 | 9.4637 | 10.6421 | -1.1785 | 63.8528 | 8.7 | 10.4899 | -1.7899 |  | 17-03-2026 07:40 | 55.517 | 56.22 | 19.6 | 9.37 | 10.6421 | -1.2721 | 63.8528 | 8.3 | 10.4899 | -2.1899 |  | 17-03-2026 07:40 | 56.172 | 56.93 | 19.5 | 9.4883 | 10.6421 | -1.1538 | 63.8528 | 8.3 | 10.4899 | -2.1899 |  | 17-03-2026 07:40 | 40.78 | 41.384 | 14.3 | 6.8973 | 7.8831 | -0.98573 | 47.2984 | 6.2 | 7.7703 | -1.5703 |  | 17-03-2026 07:40 | 39.656 | 40.231 | 13.8 | 6.7052 | 7.8831 | -1.1779 | 47.2984 | 5.9 | 7.7703 | -1.8703 |  | 17-03-2026 07:40 | 41.562 | 42.169 | 14.5 | 7.0282 | 7.8831 | -0.85489 | 47.2984 | 6.2 | 7.7703 | -1.5703 |  | 17-03-2026 07:40 | 42.199 | 43.43 | 14.8 | 7.2383 | 7.8831 | -0.64473 | 47.2984 | 6.4 | 7.7703 | -1.3703 |  | 17-03-2026 07:40 | 40.022 | 40.619 | 13.9 | 6.7698 | 7.4998 | -0.72992 | 44.9985 | 6 | 7.3925 | -1.3925 |  | 17-03-2026 07:40 | 72.528 | 81.6005 | -9.0725 | 489.6031 | 64.6 | 80.4336 | -15.8336
17-03-2026 07:30 | 125 | 20.38 | 43.723 | 44.33 | 11.5 | 7.3883 | 8.2507 | -0.86233 | 49.504 | 6 | 8.1327 | -2.1327 |  | 17-03-2026 07:30 | 41.869 | 43.121 | 11.1 | 7.1868 | 8.2507 | -1.0638 | 49.504 | 5.6 | 8.1327 | -2.5327 |  | 17-03-2026 07:30 | 42.874 | 43.472 | 11.3 | 7.2453 | 8.2507 | -1.0053 | 49.504 | 5.9 | 8.1327 | -2.2327 |  | 17-03-2026 07:30 | 43.011 | 43.639 | 11.2 | 7.2732 | 8.2507 | -0.97749 | 49.504 | 5.8 | 8.1327 | -2.3327 |  | 17-03-2026 07:30 | 31.373 | 31.879 | 8.1 | 5.3132 | 6.1116 | -0.79843 | 36.6696 | 4.2 | 6.0242 | -1.8242 |  | 17-03-2026 07:30 | 30.403 | 30.885 | 7.9 | 5.1475 | 6.1116 | -0.9641 | 36.6696 | 4.1 | 6.0242 | -1.9242 |  | 17-03-2026 07:30 | 31.937 | 32.453 | 8.3 | 5.4088 | 6.1116 | -0.70277 | 36.6696 | 4.3 | 6.0242 | -1.7242 |  | 17-03-2026 07:30 | 32.39 | 33.47 | 8.4 | 5.5783 | 6.1116 | -0.53327 | 36.6696 | 4.3 | 6.0242 | -1.7242 |  | 17-03-2026 07:30 | 30.542 | 31.035 | 7.9 | 5.1725 | 5.8144 | -0.64193 | 34.8866 | 4.2 | 5.7313 | -1.5313 |  | 17-03-2026 07:30 | 55.714 | 63.2635 | -7.5495 | 379.5808 | 44.4 | 62.3588 | -17.9588
17-03-2026 07:20 | 68 | 17.51 | 27.527 | 27.953 | 5.5 | 4.6588 | 4.5327 | 0.12611 | 27.1964 | 3.4 | 4.4679 | -1.0679 |  | 17-03-2026 07:20 | 26.297 | 27.547 | 5.5 | 4.5912 | 4.5327 | 0.05844 | 27.1964 | 3.3 | 4.4679 | -1.1679 |  | 17-03-2026 07:20 | 26.954 | 27.44 | 5.4 | 4.5733 | 4.5327 | 0.040607 | 27.1964 | 3.3 | 4.4679 | -1.1679 |  | 17-03-2026 07:20 | 26.817 | 27.474 | 5.4 | 4.579 | 4.5327 | 0.046273 | 27.1964 | 3.3 | 4.4679 | -1.1679 |  | 17-03-2026 07:20 | 19.68 | 20.222 | 3.9 | 3.3703 | 3.3576 | 0.012758 | 20.1455 | 2.4 | 3.3096 | -0.90956 |  | 17-03-2026 07:20 | 19.039 | 19.457 | 3.8 | 3.2428 | 3.3576 | -0.11474 | 20.1455 | 2.4 | 3.3096 | -0.90956 |  | 17-03-2026 07:20 | 20.066 | 20.507 | 4 | 3.4178 | 3.3576 | 0.060258 | 20.1455 | 2.5 | 3.3096 | -0.80956 |  | 17-03-2026 07:20 | 20.386 | 21.218 | 4.1 | 3.5363 | 3.3576 | 0.17876 | 20.1455 | 2.6 | 3.3096 | -0.70956 |  | 17-03-2026 07:20 | 18.896 | 19.317 | 3.7 | 3.2195 | 3.1943 | 0.025183 | 19.1659 | 2.3 | 3.1486 | -0.84864 |  | 17-03-2026 07:20 | 35.1892 | 34.7555 | 0.43364 | 208.5332 | 25.5 | 34.2585 | -8.7585
17-03-2026 07:10 | 35 | 16.07 | 13.95 | 14.325 | 2.1 | 2.3875 | 2.3445 | 0.043021 | 14.0669 | 1.5 | 2.311 | -0.81095 |  | 17-03-2026 07:10 | 13.883 | 14.298 | 2.2 | 2.383 | 2.3445 | 0.038521 | 14.0669 | 1.6 | 2.311 | -0.71095 |  | 17-03-2026 07:10 | 13.887 | 14.272 | 2.1 | 2.3787 | 2.3445 | 0.034187 | 14.0669 | 1.5 | 2.311 | -0.81095 |  | 17-03-2026 07:10 | 13.82 | 14.348 | 2.1 | 2.3913 | 2.3445 | 0.046854 | 14.0669 | 1.5 | 2.311 | -0.81095 |  | 17-03-2026 07:10 | 10.045 | 10.749 | 1.5 | 1.7915 | 1.7367 | 0.054849 | 10.4199 | 1.1 | 1.7118 | -0.61182 |  | 17-03-2026 07:10 | 9.508 | 9.844 | 1.4 | 1.6407 | 1.7367 | -0.095985 | 10.4199 | 1.1 | 1.7118 | -0.61182 |  | 17-03-2026 07:10 | 10.124 | 10.466 | 1.5 | 1.7443 | 1.7367 | 0.0076821 | 10.4199 | 1.1 | 1.7118 | -0.61182 |  | 17-03-2026 07:10 | 10.345 | 11.009 | 1.5 | 1.8348 | 1.7367 | 0.098182 | 10.4199 | 1.1 | 1.7118 | -0.61182 |  | 17-03-2026 07:10 | 9.591 | 9.928 | 1.4 | 1.6547 | 1.6522 | 0.0024581 | 9.9133 | 1.1 | 1.6286 | -0.52858 |  | 17-03-2026 07:10 | 18.2065 | 17.9767 | 0.22977 | 107.8604 | 11.6 | 17.7197 | -6.1197
17-03-2026 07:00 | 14 | 16.07 | 5.7 | 5.946 | 0.6 | 0.991 | 0.93779 | 0.053208 | 5.6268 | 0.6 | 0.92438 | -0.32438 |  | 17-03-2026 07:00 | 5.642 | 6.304 | 0.6 | 1.0507 | 0.93779 | 0.11287 | 5.6268 | 0.6 | 0.92438 | -0.32438 |  | 17-03-2026 07:00 | 5.629 | 5.873 | 0.6 | 0.97883 | 0.93779 | 0.041042 | 5.6268 | 0.6 | 0.92438 | -0.32438 |  | 17-03-2026 07:00 | 5.66 | 6.426 | 0.6 | 1.071 | 0.93779 | 0.13321 | 5.6268 | 0.6 | 0.92438 | -0.32438 |  | 17-03-2026 07:00 | 4.001 | 4.636 | 0.4 | 0.77267 | 0.69466 | 0.078006 | 4.168 | 0.4 | 0.68473 | -0.28473 |  | 17-03-2026 07:00 | 3.815 | 3.994 | 0.3 | 0.66567 | 0.69466 | -0.028994 | 4.168 | 0.3 | 0.68473 | -0.38473 |  | 17-03-2026 07:00 | 4.056 | 4.246 | 0.4 | 0.70767 | 0.69466 | 0.013006 | 4.168 | 0.4 | 0.68473 | -0.28473 |  | 17-03-2026 07:00 | 4.14 | 4.369 | 0.4 | 0.72817 | 0.69466 | 0.033506 | 4.168 | 0.4 | 0.68473 | -0.28473 |  | 17-03-2026 07:00 | 3.839 | 4.015 | 0.3 | 0.66917 | 0.66088 | 0.0082832 | 3.9653 | 0.3 | 0.65143 | -0.35143 |  | 17-03-2026 07:00 | 7.6348 | 7.1907 | 0.44414 | 43.1442 | 4.2 | 7.0879 | -2.8879
[110 empty] | Total: - | 13202.0803 | 17905.1577 | -4703.0774 |  | 15484.2 | 17649.114 | -2164.914
Sum:- | 39056 |  | 10205.628 |  | 71333.9 |  |  |  |  | 2022.8 | 2301.7523 | -278.9523 | 0.99095 |  | 10114.252 |  | 69790.8 |  |  |  |  | 2037.4 | 2301.7523 | -264.3523 | 0.98487 |  | 10074.785 |  | 70689.9 |  |  |  |  | 2006.1 | 2301.7523 | -295.6523 | 0.9747 |  | 10130.262 |  | 71218 |  |  |  |  | 2019.6 | 2301.7523 | -282.1523 | 0.98399 |  | 7558.794 |  | 53244.7 |  |  |  |  | 1512.3 | 1705.0017 | -192.7017 | 0.98485 |  | 7490.839 |  | 52805.9 |  |  |  |  | 1497.8 | 1705.0017 | -207.2017 | 0.98316 |  | 7506.197 |  | 52976.9 |  |  |  |  | 1501.8 | 1705.0017 | -203.2017 | 0.98267 |  | 7573.573 |  | 53678.3 |  |  |  |  | 1453.6 | 1705.0017 | -251.4017 | 0.97224 |  | 7177.086 |  | 50623 |  |  |  |  | 1432.8 | 1622.0979 | -189.2979 | 0.98504

## 18 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
18-03-2026 19:00 | 0 | 34.73 | 0.104 | 0.109 | 1940.8 | 0.018167 | 0 | 0.018167 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 19:00 | 0.075 | 0.25 | 1943.2 | 0.041667 | 0 | 0.041667 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 19:00 | 0.085 | 0.089 | 1920.8 | 0.014833 | 0 | 0.014833 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.096 | 0.139 | 1935.6 | 0.023167 | 0 | 0.023167 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.098 | 0.103 | 1455.5 | 0.017167 | 0 | 0.017167 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.076 | 0.08 | 1443.9 | 0.013333 | 0 | 0.013333 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.069 | 0.073 | 1446.3 | 0.012167 | 0 | 0.012167 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.093 | 0.098 | 1452.4 | 0.016333 | 0 | 0.016333 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.097 | 0.102 | 1370.9 | 0.017 | 0 | 0.017 | 0 | 0 | 0 | 0 |  | 18-03-2026 19:00 | 0.17383 | 0 | 0.17383 | 0 | 0.2 | 0 | 0.2 | 1 | 98.11%
18-03-2026 18:50 | 0 | 36.16 | 0.119 | 0.125 | 1940.7 | 0.020833 | 0 | 0.020833 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.235 | 0.702 | 1943.1 | 0.117 | 0 | 0.117 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.121 | 0.127 | 1920.8 | 0.021167 | 0 | 0.021167 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.149 | 0.654 | 1935.6 | 0.109 | 0 | 0.109 | 0 | 0.2 | 0 | 0.2 |  | 18-03-2026 18:50 | 0.055 | 0.089 | 1455.5 | 0.014833 | 0 | 0.014833 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.003 | 0.094 | 1443.9 | 0.015667 | 0 | 0.015667 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.094 | 0.099 | 1446.3 | 0.0165 | 0 | 0.0165 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.03 | 0.345 | 1452.4 | 0.0575 | 0 | 0.0575 | 0 | 0.1 | 0 | 0.1 |  | 18-03-2026 18:50 | 0.074 | 0.078 | 1370.9 | 0.013 | 0 | 0.013 | 0 | 0 | 0 | 0 |  | 18-03-2026 18:50 | 0.3855 | 0 | 0.3855 | 0 | 0.9 | 0 | 0.9 | 2 | 101.6%
18-03-2026 18:40 | 3 | 37.31 | 1.552 | 1.632 | 1940.6 | 0.272 | 0.18647 | 0.085531 | 1.1188 | 0.8 | 0.1838 | 0.6162 |  | 18-03-2026 18:40 | 1.944 | 2.438 | 1943 | 0.40633 | 0.18647 | 0.21986 | 1.1188 | 0.9 | 0.1838 | 0.7162 |  | 18-03-2026 18:40 | 1.553 | 1.633 | 1920.7 | 0.27217 | 0.18647 | 0.085698 | 1.1188 | 0.9 | 0.1838 | 0.7162 |  | 18-03-2026 18:40 | 1.735 | 2.23 | 1935.4 | 0.37167 | 0.18647 | 0.1852 | 1.1188 | 0.8 | 0.1838 | 0.6162 |  | 18-03-2026 18:40 | 1.15 | 1.292 | 1455.4 | 0.21533 | 0.13813 | 0.077208 | 0.82875 | 0.6 | 0.13615 | 0.46385 |  | 18-03-2026 18:40 | 1.094 | 1.15 | 1443.8 | 0.19167 | 0.13813 | 0.053541 | 0.82875 | 0.6 | 0.13615 | 0.46385 |  | 18-03-2026 18:40 | 1.085 | 1.141 | 1446.2 | 0.19017 | 0.13813 | 0.052041 | 0.82875 | 0.6 | 0.13615 | 0.46385 |  | 18-03-2026 18:40 | 1.195 | 1.396 | 1452.3 | 0.23267 | 0.13813 | 0.094541 | 0.82875 | 0.6 | 0.13615 | 0.46385 |  | 18-03-2026 18:40 | 1.001 | 1.052 | 1370.9 | 0.17533 | 0.13141 | 0.043924 | 0.78845 | 0.6 | 0.12953 | 0.47047 |  | 18-03-2026 18:40 | 2.3273 | 1.4298 | 0.89755 | 8.5787 | 6.4 | 1.4093 | 4.9907 | 3 | 97.48%
18-03-2026 18:30 | 26 | 38.46 | 10.167 | 10.554 | 1939.8 | 1.759 | 1.6093 | 0.14973 | 9.6556 | 2.4 | 1.5863 | 0.81374 |  | 18-03-2026 18:30 | 10.735 | 10.815 | 1942.1 | 1.8025 | 1.6093 | 0.19323 | 9.6556 | 2.5 | 1.5863 | 0.91374 |  | 18-03-2026 18:30 | 9.611 | 10.005 | 1919.8 | 1.6675 | 1.6093 | 0.058232 | 9.6556 | 2.4 | 1.5863 | 0.81374 |  | 18-03-2026 18:30 | 9.727 | 10.212 | 1934.6 | 1.702 | 1.6093 | 0.092732 | 9.6556 | 2.5 | 1.5863 | 0.91374 |  | 18-03-2026 18:30 | 6.977 | 7.362 | 1454.8 | 1.227 | 1.1921 | 0.03495 | 7.1523 | 1.8 | 1.175 | 0.625 |  | 18-03-2026 18:30 | 6.908 | 7.212 | 1443.2 | 1.202 | 1.1921 | 0.0099496 | 7.1523 | 1.7 | 1.175 | 0.525 |  | 18-03-2026 18:30 | 6.991 | 7.301 | 1445.6 | 1.2168 | 1.1921 | 0.024783 | 7.1523 | 1.7 | 1.175 | 0.525 |  | 18-03-2026 18:30 | 7.014 | 7.36 | 1451.7 | 1.2267 | 1.1921 | 0.034616 | 7.1523 | 1.7 | 1.175 | 0.525 |  | 18-03-2026 18:30 | 6.596 | 6.89 | 1370.3 | 1.1483 | 1.1341 | 0.014245 | 6.8045 | 1.6 | 1.1179 | 0.48213 |  | 18-03-2026 18:30 | 12.9518 | 12.3394 | 0.61247 | 74.0362 | 18.3 | 12.1629 | 6.1371 | 4 | 98.47%
18-03-2026 18:20 | 49 | 38.75 | 18.08 | 18.486 | 1937.4 | 3.081 | 3.0296 | 0.051379 | 18.1777 | 3.1 | 2.9863 | 0.1137 |  | 18-03-2026 18:20 | 18.414 | 18.761 | 1939.6 | 3.1268 | 3.0296 | 0.097213 | 18.1777 | 3.1 | 2.9863 | 0.1137 |  | 18-03-2026 18:20 | 17.811 | 18.279 | 1917.4 | 3.0465 | 3.0296 | 0.016879 | 18.1777 | 3.1 | 2.9863 | 0.1137 |  | 18-03-2026 18:20 | 17.803 | 18.274 | 1932.1 | 3.0457 | 3.0296 | 0.016046 | 18.1777 | 3.1 | 2.9863 | 0.1137 |  | 18-03-2026 18:20 | 13.077 | 13.502 | 1453 | 2.2503 | 2.2442 | 0.0061698 | 13.465 | 2.3 | 2.2121 | 0.087928 |  | 18-03-2026 18:20 | 12.86 | 13.276 | 1441.5 | 2.2127 | 2.2442 | -0.031497 | 13.465 | 2.3 | 2.2121 | 0.087928 |  | 18-03-2026 18:20 | 12.896 | 13.317 | 1443.9 | 2.2195 | 2.2442 | -0.024664 | 13.465 | 2.3 | 2.2121 | 0.087928 |  | 18-03-2026 18:20 | 12.837 | 13.371 | 1450 | 2.2285 | 2.2442 | -0.015664 | 13.465 | 2.2 | 2.2121 | -0.012072 |  | 18-03-2026 18:20 | 12.114 | 12.539 | 1368.7 | 2.0898 | 2.135 | -0.04521 | 12.8103 | 2.2 | 2.1045 | 0.095487 |  | 18-03-2026 18:20 | 23.3008 | 23.2302 | 0.070652 | 139.3811 | 23.7 | 22.898 | 0.80201 | 5 | 98.45%
18-03-2026 18:10 | 49 | 39.03 | 18.281 | 18.75 | 1934.3 | 3.125 | 3.0265 | 0.098498 | 18.159 | 2.8 | 2.9832 | -0.18322 |  | 18-03-2026 18:10 | 18.45 | 19.299 | 1936.5 | 3.2165 | 3.0265 | 0.19 | 18.159 | 2.8 | 2.9832 | -0.18322 |  | 18-03-2026 18:10 | 18.45 | 18.923 | 1914.3 | 3.1538 | 3.0265 | 0.12733 | 18.159 | 2.8 | 2.9832 | -0.18322 |  | 18-03-2026 18:10 | 18.413 | 18.891 | 1929 | 3.1485 | 3.0265 | 0.122 | 18.159 | 2.7 | 2.9832 | -0.28322 |  | 18-03-2026 18:10 | 13.424 | 13.848 | 1450.7 | 2.308 | 2.2419 | 0.066147 | 13.4511 | 2 | 2.2098 | -0.20979 |  | 18-03-2026 18:10 | 13.201 | 13.627 | 1439.2 | 2.2712 | 2.2419 | 0.029314 | 13.4511 | 2 | 2.2098 | -0.20979 |  | 18-03-2026 18:10 | 13.258 | 13.681 | 1441.6 | 2.2802 | 2.2419 | 0.038314 | 13.4511 | 2 | 2.2098 | -0.20979 |  | 18-03-2026 18:10 | 12.791 | 13.615 | 1447.8 | 2.2692 | 2.2419 | 0.027314 | 13.4511 | 2 | 2.2098 | -0.20979 |  | 18-03-2026 18:10 | 12.358 | 12.772 | 1366.5 | 2.1287 | 2.1328 | -0.0041789 | 12.7971 | 1.8 | 2.1023 | -0.30235 |  | 18-03-2026 18:10 | 23.901 | 23.2063 | 0.69474 | 139.2376 | 20.9 | 22.8744 | -1.9744 | 6 | 98.36%
18-03-2026 18:00 | 50 | 40.18 | 18.561 | 19.041 | 1931.5 | 3.1735 | 3.0752 | 0.098305 | 18.4512 | 5.1 | 3.0312 | 2.0688 |  | 18-03-2026 18:00 | 18.63 | 19.149 | 1933.7 | 3.1915 | 3.0752 | 0.11631 | 18.4512 | 5.1 | 3.0312 | 2.0688 |  | 18-03-2026 18:00 | 18.347 | 18.825 | 1911.5 | 3.1375 | 3.0752 | 0.062305 | 18.4512 | 5 | 3.0312 | 1.9688 |  | 18-03-2026 18:00 | 18.211 | 18.691 | 1926.3 | 3.1152 | 3.0752 | 0.039972 | 18.4512 | 5.2 | 3.0312 | 2.1688 |  | 18-03-2026 18:00 | 13.436 | 13.859 | 1448.7 | 2.3098 | 2.2779 | 0.031911 | 13.6675 | 3.8 | 2.2453 | 1.5547 |  | 18-03-2026 18:00 | 13.209 | 13.627 | 1437.2 | 2.2712 | 2.2779 | -0.0067554 | 13.6675 | 3.7 | 2.2453 | 1.4547 |  | 18-03-2026 18:00 | 13.235 | 13.665 | 1439.6 | 2.2775 | 2.2779 | -0.00042209 | 13.6675 | 3.7 | 2.2453 | 1.4547 |  | 18-03-2026 18:00 | 13.149 | 13.755 | 1445.8 | 2.2925 | 2.2779 | 0.014578 | 13.6675 | 3.7 | 2.2453 | 1.4547 |  | 18-03-2026 18:00 | 12.444 | 12.854 | 1364.7 | 2.1423 | 2.1672 | -0.024827 | 13.003 | 3.5 | 2.1362 | 1.3638 |  | 18-03-2026 18:00 | 23.911 | 23.5796 | 0.33137 | 141.4778 | 38.8 | 23.2424 | 15.5576 | 7 | 98.21%
18-03-2026 17:50 | 117 | 42.19 | 41.307 | 42.008 | 1926.4 | 7.0013 | 7.1425 | -0.14116 | 42.855 | 7.8 | 7.0404 | 0.75965 |  | 18-03-2026 17:50 | 41.993 | 42.715 | 1928.6 | 7.1192 | 7.1425 | -0.023325 | 42.855 | 8.1 | 7.0404 | 1.0596 |  | 18-03-2026 17:50 | 41.158 | 41.853 | 1906.5 | 6.9755 | 7.1425 | -0.16699 | 42.855 | 7.9 | 7.0404 | 0.85965 |  | 18-03-2026 17:50 | 41.55 | 42.256 | 1921.1 | 7.0427 | 7.1425 | -0.099825 | 42.855 | 7.7 | 7.0404 | 0.65965 |  | 18-03-2026 17:50 | 30.927 | 31.497 | 1444.9 | 5.2495 | 5.2907 | -0.041235 | 31.7444 | 5.8 | 5.2151 | 0.58492 |  | 18-03-2026 17:50 | 30.26 | 30.812 | 1433.5 | 5.1353 | 5.2907 | -0.1554 | 31.7444 | 5.7 | 5.2151 | 0.48492 |  | 18-03-2026 17:50 | 30.168 | 30.727 | 1435.9 | 5.1212 | 5.2907 | -0.16957 | 31.7444 | 5.7 | 5.2151 | 0.48492 |  | 18-03-2026 17:50 | 29.958 | 30.529 | 1442.1 | 5.0882 | 5.2907 | -0.20257 | 31.7444 | 5.6 | 5.2151 | 0.38492 |  | 18-03-2026 17:50 | 28.342 | 28.909 | 1361.2 | 4.8182 | 5.0335 | -0.21531 | 30.2009 | 5.4 | 4.9615 | 0.4385 |  | 18-03-2026 17:50 | 53.551 | 54.7664 | -1.2154 | 328.5983 | 59.7 | 53.9832 | 5.7168 | 8 | 97.06%
18-03-2026 17:40 | 151 | 43.62 | 52.479 | 53.298 | 1918.6 | 8.883 | 9.169 | -0.286 | 55.014 | 10 | 9.0379 | 0.96212 |  | 18-03-2026 17:40 | 53.469 | 54.289 | 1920.5 | 9.0482 | 9.169 | -0.12083 | 55.014 | 10 | 9.0379 | 0.96212 |  | 18-03-2026 17:40 | 52.59 | 53.391 | 1898.6 | 8.8985 | 9.169 | -0.2705 | 55.014 | 9.8 | 9.0379 | 0.76212 |  | 18-03-2026 17:40 | 52.236 | 53.045 | 1913.4 | 8.8408 | 9.169 | -0.32816 | 55.014 | 9.9 | 9.0379 | 0.86212 |  | 18-03-2026 17:40 | 39.136 | 39.813 | 1439.1 | 6.6355 | 6.7919 | -0.15635 | 40.7511 | 7.3 | 6.6947 | 0.60527 |  | 18-03-2026 17:40 | 38.416 | 39.068 | 1427.8 | 6.5113 | 6.7919 | -0.28052 | 40.7511 | 7.2 | 6.6947 | 0.50527 |  | 18-03-2026 17:40 | 38.277 | 38.935 | 1430.2 | 6.4892 | 6.7919 | -0.30268 | 40.7511 | 7.2 | 6.6947 | 0.50527 |  | 18-03-2026 17:40 | 38.145 | 39.488 | 1436.5 | 6.5813 | 6.7919 | -0.21052 | 40.7511 | 7.2 | 6.6947 | 0.50527 |  | 18-03-2026 17:40 | 36.099 | 36.735 | 1355.8 | 6.1225 | 6.4616 | -0.3391 | 38.7696 | 6.8 | 6.3692 | 0.4308 |  | 18-03-2026 17:40 | 68.0103 | 70.305 | -2.2947 | 421.83 | 75.4 | 69.2996 | 6.1004 | 9 | 98.48%
18-03-2026 17:30 | 183 | 45.06 | 64.069 | 64.926 | 1908.6 | 10.821 | 11.0522 | -0.23119 | 66.3131 | 11.7 | 10.8941 | 0.80586 |  | 18-03-2026 17:30 | 64.822 | 65.709 | 1910.5 | 10.9515 | 11.0522 | -0.10069 | 66.3131 | 11.7 | 10.8941 | 0.80586 |  | 18-03-2026 17:30 | 63.383 | 64.228 | 1888.8 | 10.7047 | 11.0522 | -0.34752 | 66.3131 | 11.7 | 10.8941 | 0.80586 |  | 18-03-2026 17:30 | 63.937 | 64.805 | 1903.5 | 10.8008 | 11.0522 | -0.25135 | 66.3131 | 11.7 | 10.8941 | 0.80586 |  | 18-03-2026 17:30 | 47.613 | 48.372 | 1431.8 | 8.062 | 8.1868 | -0.12481 | 49.1208 | 8.7 | 8.0697 | 0.63027 |  | 18-03-2026 17:30 | 46.958 | 47.702 | 1420.6 | 7.9503 | 8.1868 | -0.23647 | 49.1208 | 8.7 | 8.0697 | 0.63027 |  | 18-03-2026 17:30 | 46.811 | 47.562 | 1423 | 7.927 | 8.1868 | -0.25981 | 49.1208 | 8.6 | 8.0697 | 0.53027 |  | 18-03-2026 17:30 | 46.704 | 48.295 | 1429.3 | 8.0492 | 8.1868 | -0.13764 | 49.1208 | 8.6 | 8.0697 | 0.53027 |  | 18-03-2026 17:30 | 44.242 | 44.966 | 1349 | 7.4943 | 7.7887 | -0.2944 | 46.7324 | 8.1 | 7.6774 | 0.42265 |  | 18-03-2026 17:30 | 82.7608 | 84.7447 | -1.9839 | 508.4682 | 89.5 | 83.5329 | 5.9671
18-03-2026 17:20 | 235 | 46.49 | 83.172 | 84.199 | 1896.9 | 14.0332 | 14.1163 | -0.083134 | 84.6978 | 12.1 | 13.9144 | -1.8144 |  | 18-03-2026 17:20 | 83.851 | 84.912 | 1898.8 | 14.152 | 14.1163 | 0.035699 | 84.6978 | 12 | 13.9144 | -1.9144 |  | 18-03-2026 17:20 | 82.763 | 84.146 | 1877.1 | 14.0243 | 14.1163 | -0.091968 | 84.6978 | 11.9 | 13.9144 | -2.0144 |  | 18-03-2026 17:20 | 82.933 | 83.974 | 1891.8 | 13.9957 | 14.1163 | -0.12063 | 84.6978 | 11.8 | 13.9144 | -2.1144 |  | 18-03-2026 17:20 | 61.628 | 62.471 | 1423.1 | 10.4118 | 10.4565 | -0.044686 | 62.7391 | 9 | 10.307 | -1.307 |  | 18-03-2026 17:20 | 60.992 | 61.814 | 1411.9 | 10.3023 | 10.4565 | -0.15419 | 62.7391 | 8.7 | 10.307 | -1.607 |  | 18-03-2026 17:20 | 60.821 | 61.647 | 1414.4 | 10.2745 | 10.4565 | -0.18202 | 62.7391 | 8.7 | 10.307 | -1.607 |  | 18-03-2026 17:20 | 60.683 | 62.556 | 1420.7 | 10.426 | 10.4565 | -0.030519 | 62.7391 | 8.7 | 10.307 | -1.607 |  | 18-03-2026 17:20 | 57.402 | 58.235 | 1340.9 | 9.7058 | 9.9481 | -0.24225 | 59.6885 | 8.2 | 9.8058 | -1.6058 |  | 18-03-2026 17:20 | 107.3257 | 108.2394 | -0.9137 | 649.4362 | 91.1 | 106.6915 | -15.5915
18-03-2026 17:10 | 101 | 47.35 | 34.98 | 35.632 | 1884.8 | 5.9387 | 6.0473 | -0.10859 | 36.2836 | 11.7 | 5.9608 | 5.7392 |  | 18-03-2026 17:10 | 35.618 | 36.401 | 1886.8 | 6.0668 | 6.0473 | 0.019574 | 36.2836 | 11.7 | 5.9608 | 5.7392 |  | 18-03-2026 17:10 | 36.488 | 37.18 | 1865.2 | 6.1967 | 6.0473 | 0.14941 | 36.2836 | 11.5 | 5.9608 | 5.5392 |  | 18-03-2026 17:10 | 36.678 | 37.377 | 1880 | 6.2295 | 6.0473 | 0.18224 | 36.2836 | 11.7 | 5.9608 | 5.7392 |  | 18-03-2026 17:10 | 27.207 | 27.799 | 1414.1 | 4.6332 | 4.4795 | 0.15372 | 26.8767 | 8.4 | 4.4154 | 3.9846 |  | 18-03-2026 17:10 | 26.943 | 27.524 | 1403.2 | 4.5873 | 4.4795 | 0.10788 | 26.8767 | 8.4 | 4.4154 | 3.9846 |  | 18-03-2026 17:10 | 27.321 | 27.91 | 1405.7 | 4.6517 | 4.4795 | 0.17222 | 26.8767 | 8.3 | 4.4154 | 3.8846 |  | 18-03-2026 17:10 | 27.863 | 28.843 | 1412 | 4.8072 | 4.4795 | 0.32772 | 26.8767 | 8.3 | 4.4154 | 3.8846 |  | 18-03-2026 17:10 | 25.926 | 26.504 | 1332.7 | 4.4173 | 4.2616 | 0.15569 | 25.5699 | 8.1 | 4.2007 | 3.8993 |  | 18-03-2026 17:10 | 47.5283 | 46.3685 | 1.1598 | 278.2109 | 88.1 | 45.7054 | 42.3946
18-03-2026 17:00 | 384 | 47.35 | 138.334 | 139.059 | 1873.1 | 23.1765 | 22.9916 | 0.18494 | 137.9494 | 15.4 | 22.6628 | -7.2628 |  | 18-03-2026 17:00 | 138.603 | 139.285 | 1875.1 | 23.2142 | 22.9916 | 0.22261 | 137.9494 | 15.6 | 22.6628 | -7.0628 |  | 18-03-2026 17:00 | 136.217 | 138.72 | 1853.7 | 23.12 | 22.9916 | 0.12844 | 137.9494 | 15.4 | 22.6628 | -7.2628 |  | 18-03-2026 17:00 | 136.043 | 137.751 | 1868.3 | 22.9585 | 22.9916 | -0.033059 | 137.9494 | 15.4 | 22.6628 | -7.2628 |  | 18-03-2026 17:00 | 101.79 | 103.058 | 1405.7 | 17.1763 | 17.0308 | 0.14555 | 102.1847 | 11.6 | 16.7872 | -5.1872 |  | 18-03-2026 17:00 | 99.967 | 101.191 | 1394.8 | 16.8652 | 17.0308 | -0.16562 | 102.1847 | 11.3 | 16.7872 | -5.4872 |  | 18-03-2026 17:00 | 100.048 | 101.273 | 1397.4 | 16.8788 | 17.0308 | -0.15195 | 102.1847 | 11.4 | 16.7872 | -5.3872 |  | 18-03-2026 17:00 | 99.855 | 102.398 | 1403.7 | 17.0663 | 17.0308 | 0.035549 | 102.1847 | 11.4 | 16.7872 | -5.3872 |  | 18-03-2026 17:00 | 94.415 | 95.581 | 1324.6 | 15.9302 | 16.2027 | -0.27252 | 97.2161 | 10.5 | 15.971 | -5.471 |  | 18-03-2026 17:00 | 176.386 | 176.2921 | 0.093943 | 1057.7523 | 118 | 173.7711 | -55.7711
18-03-2026 16:50 | 248 | 47.35 | 90.039 | 91.16 | 1857.7 | 15.1933 | 14.8487 | 0.34462 | 89.0923 | 30.1 | 14.6364 | 15.4636 |  | 18-03-2026 16:50 | 90.089 | 91.239 | 1859.5 | 15.2065 | 14.8487 | 0.35778 | 89.0923 | 30 | 14.6364 | 15.3636 |  | 18-03-2026 16:50 | 88.666 | 90.019 | 1838.3 | 15.0032 | 14.8487 | 0.15445 | 89.0923 | 17.5 | 14.6364 | 2.8636 |  | 18-03-2026 16:50 | 89.291 | 90.458 | 1852.9 | 15.0763 | 14.8487 | 0.22762 | 89.0923 | 17.5 | 14.6364 | 2.8636 |  | 18-03-2026 16:50 | 66.032 | 66.942 | 1394.1 | 11.157 | 10.999 | 0.15795 | 65.9943 | 12.9 | 10.8418 | 2.0582 |  | 18-03-2026 16:50 | 65.487 | 66.41 | 1383.5 | 11.0683 | 10.999 | 0.069285 | 65.9943 | 12.8 | 10.8418 | 1.9582 |  | 18-03-2026 16:50 | 65.087 | 65.998 | 1386 | 10.9997 | 10.999 | 0.00061834 | 65.9943 | 12.9 | 10.8418 | 2.0582 |  | 18-03-2026 16:50 | 65.124 | 66.84 | 1392.3 | 11.14 | 10.999 | 0.14095 | 65.9943 | 12.7 | 10.8418 | 1.8582 |  | 18-03-2026 16:50 | 61.628 | 62.516 | 1314.1 | 10.4193 | 10.4642 | -0.044899 | 62.7854 | 12.2 | 10.3146 | 1.8854 |  | 18-03-2026 16:50 | 115.2637 | 113.8553 | 1.4084 | 683.1317 | 158.6 | 112.2272 | 46.3728
18-03-2026 16:40 | 224 | 47.35 | 91.171 | 92.288 | 1840.2 | 15.3813 | 13.4117 | 1.9696 | 80.4705 | 0 | 13.22 | -13.22 | [5 empty] | 0 | 13.4117 | -13.4117 | 80.4705 | 0 | 13.22 | -13.22 |  | 18-03-2026 16:40 | 81.96 | 83.286 | 1820.8 | 13.881 | 13.4117 | 0.46926 | 80.4705 | 12.1 | 13.22 | -1.12 |  | 18-03-2026 16:40 | 81.778 | 82.88 | 1835.4 | 13.8133 | 13.4117 | 0.40159 | 80.4705 | 12.2 | 13.22 | -1.02 |  | 18-03-2026 16:40 | 61.332 | 62.209 | 1381.2 | 10.3682 | 9.9346 | 0.43354 | 59.6077 | 9.1 | 9.7926 | -0.69256 |  | 18-03-2026 16:40 | 60.341 | 61.204 | 1370.7 | 10.2007 | 9.9346 | 0.26604 | 59.6077 | 9 | 9.7926 | -0.79256 |  | 18-03-2026 16:40 | 60.161 | 61.021 | 1373.1 | 10.1702 | 9.9346 | 0.23554 | 59.6077 | 8.8 | 9.7926 | -0.99256 |  | 18-03-2026 16:40 | 60.561 | 62.398 | 1379.6 | 10.3997 | 9.9346 | 0.46504 | 59.6077 | 8.9 | 9.7926 | -0.89256 |  | 18-03-2026 16:40 | 56.586 | 57.465 | 1301.9 | 9.5775 | 9.4516 | 0.12594 | 56.7094 | 8.4 | 9.3164 | -0.91641 |  | 18-03-2026 16:40 | 93.7918 | 102.837 | -9.0452 | 617.0222 | 68.5 | 101.3665 | -32.8665
18-03-2026 16:30 | 206 | 47.35 | 75.65 | 76.677 | 1827.6 | 12.7795 | 12.334 | 0.44549 | 74.0041 | 12.8 | 12.1576 | 0.64236 |  | 18-03-2026 16:30 | 75.564 | 76.877 | 1829.5 | 12.8128 | 12.334 | 0.47882 | 74.0041 | 13.6 | 12.1576 | 1.4424 |  | 18-03-2026 16:30 | 74.997 | 76.202 | 1808.7 | 12.7003 | 12.334 | 0.36632 | 74.0041 | 12.9 | 12.1576 | 0.74236 |  | 18-03-2026 16:30 | 75.187 | 76.239 | 1823.2 | 12.7065 | 12.334 | 0.37249 | 74.0041 | 13 | 12.1576 | 0.84236 |  | 18-03-2026 16:30 | 55.958 | 56.839 | 1372.1 | 9.4732 | 9.1363 | 0.33686 | 54.8178 | 9.7 | 9.0057 | 0.69434 |  | 18-03-2026 16:30 | 55.313 | 56.178 | 1361.7 | 9.363 | 9.1363 | 0.22669 | 54.8178 | 9.6 | 9.0057 | 0.59434 |  | 18-03-2026 16:30 | 55.266 | 56.141 | 1364.3 | 9.3568 | 9.1363 | 0.22053 | 54.8178 | 9.7 | 9.0057 | 0.69434 |  | 18-03-2026 16:30 | 55.164 | 56.789 | 1370.7 | 9.4648 | 9.1363 | 0.32853 | 54.8178 | 9.8 | 9.0057 | 0.79434 |  | 18-03-2026 16:30 | 52.197 | 53.057 | 1293.5 | 8.8428 | 8.6921 | 0.15077 | 52.1524 | 9.1 | 8.5678 | 0.53223 |  | 18-03-2026 16:30 | 97.4998 | 94.5733 | 2.9265 | 567.4401 | 100.2 | 93.2209 | 6.9791
18-03-2026 16:20 | 228 | 47.35 | 85.622 | 86.767 | 1814.8 | 14.4612 | 13.6512 | 0.80993 | 81.9074 | 19.5 | 13.456 | 6.044 |  | 18-03-2026 16:20 | 84.651 | 85.836 | 1815.9 | 14.306 | 13.6512 | 0.65476 | 81.9074 | 19.5 | 13.456 | 6.044 |  | 18-03-2026 16:20 | 81.197 | 82.516 | 1795.8 | 13.7527 | 13.6512 | 0.10143 | 81.9074 | 19.6 | 13.456 | 6.144 |  | 18-03-2026 16:20 | 82.27 | 83.413 | 1810.2 | 13.9022 | 13.6512 | 0.25093 | 81.9074 | 19.7 | 13.456 | 6.244 |  | 18-03-2026 16:20 | 60.878 | 61.78 | 1362.4 | 10.2967 | 10.112 | 0.18464 | 60.6722 | 14.6 | 9.9674 | 4.6326 |  | 18-03-2026 16:20 | 60.348 | 61.283 | 1352.1 | 10.2138 | 10.112 | 0.10181 | 60.6722 | 14.4 | 9.9674 | 4.4326 |  | 18-03-2026 16:20 | 60.404 | 61.293 | 1354.6 | 10.2155 | 10.112 | 0.10347 | 60.6722 | 14.2 | 9.9674 | 4.2326 |  | 18-03-2026 16:20 | 60.375 | 62.056 | 1360.9 | 10.3427 | 10.112 | 0.23064 | 60.6722 | 14.1 | 9.9674 | 4.1326 |  | 18-03-2026 16:20 | 57.1 | 57.993 | 1284.4 | 9.6655 | 9.6203 | 0.045157 | 57.7221 | 13.3 | 9.4828 | 3.8172 |  | 18-03-2026 16:20 | 107.1562 | 104.6734 | 2.4828 | 628.0405 | 148.9 | 103.1766 | 45.7234
18-03-2026 16:10 | 347 | 47.93 | 125.716 | 127.446 | 1795.3 | 21.241 | 20.7305 | 0.51053 | 124.3828 | 26.2 | 20.434 | 5.766 |  | 18-03-2026 16:10 | 135.205 | 137.027 | 1796.4 | 22.8378 | 20.7305 | 2.1074 | 124.3828 | 26.3 | 20.434 | 5.866 |  | 18-03-2026 16:10 | 123.934 | 126.448 | 1776.2 | 21.0747 | 20.7305 | 0.3442 | 124.3828 | 25.9 | 20.434 | 5.466 |  | 18-03-2026 16:10 | 123.828 | 125.472 | 1790.5 | 20.912 | 20.7305 | 0.18153 | 124.3828 | 25.9 | 20.434 | 5.466 |  | 18-03-2026 16:10 | 93.044 | 94.26 | 1347.8 | 15.71 | 15.3559 | 0.3541 | 92.1354 | 19.7 | 15.1363 | 4.5637 |  | 18-03-2026 16:10 | 91.491 | 92.677 | 1337.7 | 15.4462 | 15.3559 | 0.090262 | 92.1354 | 19.3 | 15.1363 | 4.1637 |  | 18-03-2026 16:10 | 91.882 | 93.083 | 1340.4 | 15.5138 | 15.3559 | 0.15793 | 92.1354 | 19.5 | 15.1363 | 4.3637 |  | 18-03-2026 16:10 | 91.672 | 94.165 | 1346.8 | 15.6942 | 15.3559 | 0.33826 | 92.1354 | 19.6 | 15.1363 | 4.4637 |  | 18-03-2026 16:10 | 86.322 | 87.494 | 1271.1 | 14.5823 | 14.6092 | -0.026908 | 87.6554 | 18.4 | 14.4003 | 3.9997 |  | 18-03-2026 16:10 | 163.012 | 158.9547 | 4.0573 | 953.7285 | 200.8 | 156.6817 | 44.1183
18-03-2026 16:00 | 462 | 47.64 | 166.914 | 169.095 | 1769.1 | 28.1825 | 27.6313 | 0.55124 | 165.7876 | 22.1 | 27.2361 | -5.1361 |  | 18-03-2026 16:00 | 160.08 | 208.539 | 1770.1 | 34.7565 | 27.6313 | 7.1252 | 165.7876 | 21.3 | 27.2361 | -5.9361 |  | 18-03-2026 16:00 | 175.928 | 178.961 | 1750.3 | 29.8268 | 27.6313 | 2.1956 | 165.7876 | 21.7 | 27.2361 | -5.5361 |  | 18-03-2026 16:00 | 183.413 | 185.904 | 1764.6 | 30.984 | 27.6313 | 3.3527 | 165.7876 | 21.9 | 27.2361 | -5.3361 |  | 18-03-2026 16:00 | 141.963 | 143.804 | 1328.1 | 23.9673 | 20.4676 | 3.4997 | 122.8056 | 16.5 | 20.1749 | -3.6749 |  | 18-03-2026 16:00 | 140.034 | 141.821 | 1318.4 | 23.6368 | 20.4676 | 3.1692 | 122.8056 | 16.2 | 20.1749 | -3.9749 |  | 18-03-2026 16:00 | 143.598 | 145.445 | 1320.9 | 24.2408 | 20.4676 | 3.7732 | 122.8056 | 16.4 | 20.1749 | -3.7749 |  | 18-03-2026 16:00 | 149.86 | 155.19 | 1327.2 | 25.865 | 20.4676 | 5.3974 | 122.8056 | 16.3 | 20.1749 | -3.8749 |  | 18-03-2026 16:00 | 161.743 | 163.873 | 1252.7 | 27.3122 | 19.4724 | 7.8398 | 116.8343 | 15.3 | 19.1939 | -3.8939 |  | 18-03-2026 16:00 | 248.772 | 211.8678 | 36.9042 | 1271.207 | 167.7 | 208.8381 | -41.1381
18-03-2026 15:50 | 304 | 47.64 | 111.474 | 112.908 | 1747 | 18.818 | 18.1816 | 0.63639 | 109.0897 | 19.7 | 17.9216 | 1.7784 |  | 18-03-2026 15:50 | 111.792 | 113.264 | 1748.8 | 18.8773 | 18.1816 | 0.69572 | 109.0897 | 19.9 | 17.9216 | 1.9784 |  | 18-03-2026 15:50 | 110.136 | 112.103 | 1728.6 | 18.6838 | 18.1816 | 0.50222 | 109.0897 | 19.6 | 17.9216 | 1.6784 |  | 18-03-2026 15:50 | 111.024 | 112.493 | 1742.7 | 18.7488 | 18.1816 | 0.56722 | 109.0897 | 19.6 | 17.9216 | 1.6784 |  | 18-03-2026 15:50 | 82.713 | 83.819 | 1311.6 | 13.9698 | 13.4679 | 0.50198 | 80.8071 | 14.8 | 13.2753 | 1.5247 |  | 18-03-2026 15:50 | 81.931 | 83.01 | 1302.2 | 13.835 | 13.4679 | 0.36714 | 80.8071 | 14.7 | 13.2753 | 1.4247 |  | 18-03-2026 15:50 | 81.792 | 82.87 | 1304.5 | 13.8117 | 13.4679 | 0.34381 | 80.8071 | 14.6 | 13.2753 | 1.3247 |  | 18-03-2026 15:50 | 81.851 | 83.876 | 1310.9 | 13.9793 | 13.4679 | 0.51148 | 80.8071 | 14.6 | 13.2753 | 1.3247 |  | 18-03-2026 15:50 | 77.345 | 78.411 | 1237.4 | 13.0685 | 12.813 | 0.2555 | 76.878 | 13.9 | 12.6298 | 1.2702 |  | 18-03-2026 15:50 | 143.7923 | 139.4109 | 4.3815 | 836.4652 | 151.4 | 137.4173 | 13.9827
18-03-2026 15:40 | 372 | 47.35 | 136.497 | 138.253 | 1727.3 | 23.0422 | 22.2731 | 0.76909 | 133.6384 | 24.4 | 21.9546 | 2.4454 |  | 18-03-2026 15:40 | 137.025 | 138.858 | 1728.9 | 23.143 | 22.2731 | 0.86993 | 133.6384 | 24.1 | 21.9546 | 2.1454 |  | 18-03-2026 15:40 | 134.233 | 136.611 | 1709 | 22.7685 | 22.2731 | 0.49543 | 133.6384 | 23.7 | 21.9546 | 1.7454 |  | 18-03-2026 15:40 | 135.175 | 137.054 | 1723.1 | 22.8423 | 22.2731 | 0.56926 | 133.6384 | 23.8 | 21.9546 | 1.8454 |  | 18-03-2026 15:40 | 101.552 | 102.869 | 1296.8 | 17.1448 | 16.4986 | 0.64626 | 98.9914 | 17.9 | 16.2626 | 1.6374 |  | 18-03-2026 15:40 | 100.414 | 101.797 | 1287.5 | 16.9662 | 16.4986 | 0.46759 | 98.9914 | 17.6 | 16.2626 | 1.3374 |  | 18-03-2026 15:40 | 100.305 | 101.585 | 1289.9 | 16.9308 | 16.4986 | 0.43226 | 98.9914 | 17.6 | 16.2626 | 1.3374 |  | 18-03-2026 15:40 | 100.29 | 102.756 | 1296.3 | 17.126 | 16.4986 | 0.62743 | 98.9914 | 17.6 | 16.2626 | 1.3374 |  | 18-03-2026 15:40 | 94.662 | 95.975 | 1223.5 | 15.9958 | 15.6963 | 0.29949 | 94.1781 | 16.5 | 15.4719 | 1.0281 |  | 18-03-2026 15:40 | 175.9597 | 170.7829 | 5.1767 | 1024.6976 | 183.2 | 168.3407 | 14.8593
18-03-2026 15:30 | 364 | 47.64 | 131.955 | 133.666 | 1702.9 | 22.2777 | 21.7701 | 0.50758 | 130.6205 | 23.9 | 21.4588 | 2.4412 |  | 18-03-2026 15:30 | 132.675 | 134.368 | 1704.8 | 22.3947 | 21.7701 | 0.62458 | 130.6205 | 24.8 | 21.4588 | 3.3412 |  | 18-03-2026 15:30 | 131.063 | 133.539 | 1685.3 | 22.2565 | 21.7701 | 0.48642 | 130.6205 | 24 | 21.4588 | 2.5412 |  | 18-03-2026 15:30 | 132.237 | 133.979 | 1699.3 | 22.3298 | 21.7701 | 0.55975 | 130.6205 | 24.3 | 21.4588 | 2.8412 |  | 18-03-2026 15:30 | 98.699 | 99.958 | 1278.9 | 16.6597 | 16.126 | 0.53368 | 96.7559 | 17.6 | 15.8954 | 1.7046 |  | 18-03-2026 15:30 | 97.883 | 99.132 | 1269.9 | 16.522 | 16.126 | 0.39601 | 96.7559 | 17.6 | 15.8954 | 1.7046 |  | 18-03-2026 15:30 | 97.846 | 99.085 | 1272.3 | 16.5142 | 16.126 | 0.38818 | 96.7559 | 17.5 | 15.8954 | 1.6046 |  | 18-03-2026 15:30 | 97.838 | 100.44 | 1278.7 | 16.74 | 16.126 | 0.61401 | 96.7559 | 17.7 | 15.8954 | 1.8046 |  | 18-03-2026 15:30 | 92.598 | 93.789 | 1207 | 15.6315 | 15.3419 | 0.28962 | 92.0513 | 16.9 | 15.1225 | 1.7775 |  | 18-03-2026 15:30 | 171.326 | 166.9262 | 4.3998 | 1001.557 | 184.3 | 164.5391 | 19.7609
18-03-2026 15:20 | 501 | 47.35 | 166.209 | 168.398 | 1679 | 28.0663 | 29.9968 | -1.9305 | 179.9808 | 23.2 | 29.5678 | -6.3678 |  | 18-03-2026 15:20 | 160.203 | 164.872 | 1680 | 27.4787 | 29.9968 | -2.5181 | 179.9808 | 22.7 | 29.5678 | -6.8678 |  | 18-03-2026 15:20 | 175.18 | 182.908 | 1661.3 | 30.4847 | 29.9968 | 0.48787 | 179.9808 | 22.7 | 29.5678 | -6.8678 |  | 18-03-2026 15:20 | 167.673 | 169.973 | 1675 | 28.3288 | 29.9968 | -1.668 | 179.9808 | 22.9 | 29.5678 | -6.6678 |  | 18-03-2026 15:20 | 125.985 | 127.875 | 1261.3 | 21.3125 | 22.2199 | -0.90735 | 133.3191 | 17.1 | 21.9021 | -4.8021 |  | 18-03-2026 15:20 | 123.209 | 125.231 | 1252.3 | 20.8718 | 22.2199 | -1.348 | 133.3191 | 16.9 | 21.9021 | -5.0021 |  | 18-03-2026 15:20 | 121.991 | 123.781 | 1254.8 | 20.6302 | 22.2199 | -1.5897 | 133.3191 | 16.8 | 21.9021 | -5.1021 |  | 18-03-2026 15:20 | 121.66 | 124.703 | 1261 | 20.7838 | 22.2199 | -1.436 | 133.3191 | 16.6 | 21.9021 | -5.3021 |  | 18-03-2026 15:20 | 114.566 | 116.051 | 1190.1 | 19.3418 | 21.1394 | -1.7976 | 126.8366 | 15.9 | 20.8371 | -4.9371 |  | 18-03-2026 15:20 | 217.2987 | 230.006 | -12.7074 | 1380.0363 | 174.8 | 226.717 | -51.917
18-03-2026 15:10 | 286 | 47.35 | 106.49 | 107.849 | 1655.8 | 17.9748 | 17.1239 | 0.85091 | 102.7435 | 17.7 | 16.879 | 0.82095 |  | 18-03-2026 15:10 | 106.794 | 108.124 | 1657.3 | 18.0207 | 17.1239 | 0.89675 | 102.7435 | 18.1 | 16.879 | 1.221 |  | 18-03-2026 15:10 | 105.214 | 107.206 | 1638.6 | 17.8677 | 17.1239 | 0.74375 | 102.7435 | 17.6 | 16.879 | 0.72095 |  | 18-03-2026 15:10 | 106.168 | 107.545 | 1652.1 | 17.9242 | 17.1239 | 0.80025 | 102.7435 | 17.7 | 16.879 | 0.82095 |  | 18-03-2026 15:10 | 78.922 | 79.986 | 1244.2 | 13.331 | 12.6844 | 0.64661 | 76.1063 | 13.1 | 12.503 | 0.597 |  | 18-03-2026 15:10 | 78.434 | 79.491 | 1235.4 | 13.2485 | 12.6844 | 0.56411 | 76.1063 | 13.1 | 12.503 | 0.597 |  | 18-03-2026 15:10 | 78.181 | 79.243 | 1238 | 13.2072 | 12.6844 | 0.52278 | 76.1063 | 13.1 | 12.503 | 0.597 |  | 18-03-2026 15:10 | 78.233 | 80.31 | 1244.4 | 13.385 | 12.6844 | 0.70061 | 76.1063 | 13.1 | 12.503 | 0.597 |  | 18-03-2026 15:10 | 74.003 | 75.031 | 1174.2 | 12.5052 | 12.0676 | 0.43754 | 72.4057 | 12.2 | 11.8951 | 0.30494 |  | 18-03-2026 15:10 | 137.4642 | 131.3009 | 6.1633 | 787.8051 | 135.7 | 129.4233 | 6.2767
18-03-2026 15:00 | 291 | 47.35 | 108.141 | 109.532 | 1638.1 | 18.2553 | 17.4233 | 0.83204 | 104.5397 | 20.1 | 17.1741 | 2.9259 | 0.9873 | 18-03-2026 15:00 | 108.466 | 109.895 | 1639.2 | 18.3158 | 17.4233 | 0.89254 | 104.5397 | 20.2 | 17.1741 | 3.0259 | 0.987 | 18-03-2026 15:00 | 106.41 | 108.194 | 1621 | 18.0323 | 17.4233 | 0.60904 | 104.5397 | 19.8 | 17.1741 | 2.6259 | 0.98351 | 18-03-2026 15:00 | 107.474 | 108.879 | 1634.4 | 18.1465 | 17.4233 | 0.72321 | 104.5397 | 20.1 | 17.1741 | 2.9259 | 0.9871 | 18-03-2026 15:00 | 79.658 | 80.74 | 1231.1 | 13.4567 | 12.9061 | 0.55053 | 77.4368 | 14.9 | 12.7216 | 2.1784 | 0.9866 | 18-03-2026 15:00 | 79.223 | 80.309 | 1222.3 | 13.3848 | 12.9061 | 0.47869 | 77.4368 | 14.8 | 12.7216 | 2.0784 | 0.98648 | 18-03-2026 15:00 | 78.857 | 79.928 | 1224.9 | 13.3213 | 12.9061 | 0.41519 | 77.4368 | 15 | 12.7216 | 2.2784 | 0.9866 | 18-03-2026 15:00 | 78.973 | 80.941 | 1231.3 | 13.4902 | 12.9061 | 0.58403 | 77.4368 | 15 | 12.7216 | 2.2784 | 0.97569 | 18-03-2026 15:00 | 74.914 | 75.813 | 1162 | 12.6355 | 12.2786 | 0.3569 | 73.6716 | 14.2 | 12.103 | 2.097 | 0.98814 | 18-03-2026 15:00 | 139.0385 | 133.5963 | 5.4422 | 801.5779 | 154.1 | 131.6859 | 22.4141
18-03-2026 14:50 | 380 | 47.64 | 139.404 | 141.134 | 1618 | 23.5223 | 22.727 | 0.79532 | 136.3621 | 24.1 | 22.402 | 1.698 | 0.98774 | 18-03-2026 14:50 | 139.668 | 141.511 | 1619 | 23.5852 | 22.727 | 0.85816 | 136.3621 | 23.6 | 22.402 | 1.198 | 0.98698 | 18-03-2026 14:50 | 137.408 | 139.921 | 1601.2 | 23.3202 | 22.727 | 0.59316 | 136.3621 | 23.5 | 22.402 | 1.098 | 0.98204 | 18-03-2026 14:50 | 138.798 | 140.669 | 1614.3 | 23.4448 | 22.727 | 0.71782 | 136.3621 | 23.8 | 22.402 | 1.398 | 0.9867 | 18-03-2026 14:50 | 103.304 | 104.633 | 1216.2 | 17.4388 | 16.8348 | 0.60401 | 101.0089 | 17.7 | 16.5941 | 1.1059 | 0.9873 | 18-03-2026 14:50 | 102.516 | 103.856 | 1207.5 | 17.3093 | 16.8348 | 0.47451 | 101.0089 | 17.8 | 16.5941 | 1.2059 | 0.9871 | 18-03-2026 14:50 | 102.348 | 103.665 | 1209.9 | 17.2775 | 16.8348 | 0.44268 | 101.0089 | 17.3 | 16.5941 | 0.70592 | 0.9873 | 18-03-2026 14:50 | 102.548 | 105.373 | 1216.3 | 17.5622 | 16.8348 | 0.72734 | 101.0089 | 17.4 | 16.5941 | 0.80592 | 0.97319 | 18-03-2026 14:50 | 97.024 | 98.272 | 1147.8 | 16.3787 | 16.0162 | 0.36242 | 96.0975 | 17.1 | 15.7872 | 1.3128 | 0.9873 | 18-03-2026 14:50 | 179.839 | 174.2636 | 5.5754 | 1045.5815 | 182.3 | 171.7716 | 10.5284
18-03-2026 14:40 | 393 | 47.64 | 144.225 | 145.152 | 1593.9 | 24.192 | 23.5045 | 0.68749 | 141.0271 | 27.9 | 23.1684 | 4.7316 | 0.99361 | 18-03-2026 14:40 | 170.591 | 147.134 | 1595.4 | 24.5223 | 23.5045 | 1.0178 | 141.0271 | 28.1 | 23.1684 | 4.9316 | 1.1594 | 18-03-2026 14:40 | 140.684 | 143.265 | 1577.7 | 23.8775 | 23.5045 | 0.37299 | 141.0271 | 27.7 | 23.1684 | 4.5316 | 0.98198 | 18-03-2026 14:40 | 144.296 | 146.256 | 1590.5 | 24.376 | 23.5045 | 0.87149 | 141.0271 | 27.8 | 23.1684 | 4.6316 | 0.9866 | 18-03-2026 14:40 | 105.64 | 106.999 | 1198.5 | 17.8332 | 17.4108 | 0.42242 | 104.4645 | 20.7 | 17.1618 | 3.5382 | 0.9873 | 18-03-2026 14:40 | 106.628 | 108.011 | 1189.7 | 18.0018 | 17.4108 | 0.59108 | 104.4645 | 20.4 | 17.1618 | 3.2382 | 0.9872 | 18-03-2026 14:40 | 104.889 | 106.249 | 1192.6 | 17.7082 | 17.4108 | 0.29742 | 104.4645 | 20.3 | 17.1618 | 3.1382 | 0.9872 | 18-03-2026 14:40 | 105.436 | 108.076 | 1198.9 | 18.0127 | 17.4108 | 0.60192 | 104.4645 | 20.4 | 17.1618 | 3.2382 | 0.97557 | 18-03-2026 14:40 | 100.727 | 102.054 | 1130.7 | 17.009 | 16.5642 | 0.44483 | 99.385 | 19 | 16.3273 | 2.6727 | 0.987 | 18-03-2026 14:40 | 185.5327 | 180.2252 | 5.3074 | 1081.3514 | 212.3 | 177.648 | 34.652
18-03-2026 14:30 | 359 | 47.64 | 133.796 | 135.545 | 1566 | 22.5908 | 21.471 | 1.1198 | 128.8263 | 21.8 | 21.164 | 0.63599 | 0.9871 | 18-03-2026 14:30 | 131.767 | 133.47 | 1567.3 | 22.245 | 21.471 | 0.77396 | 128.8263 | 21.6 | 21.164 | 0.43599 | 0.98724 | 18-03-2026 14:30 | 132.099 | 134.909 | 1550 | 22.4848 | 21.471 | 1.0138 | 128.8263 | 21.2 | 21.164 | 0.035992 | 0.97917 | 18-03-2026 14:30 | 132.993 | 134.786 | 1562.7 | 22.4643 | 21.471 | 0.99329 | 128.8263 | 21.4 | 21.164 | 0.23599 | 0.9867 | 18-03-2026 14:30 | 99.469 | 100.759 | 1177.8 | 16.7932 | 15.9045 | 0.88869 | 95.4269 | 15.9 | 15.677 | 0.22296 | 0.9872 | 18-03-2026 14:30 | 98.46 | 99.737 | 1169.3 | 16.6228 | 15.9045 | 0.71836 | 95.4269 | 15.8 | 15.677 | 0.12296 | 0.9872 | 18-03-2026 14:30 | 98.55 | 99.838 | 1172.3 | 16.6397 | 15.9045 | 0.73519 | 95.4269 | 16 | 15.677 | 0.32296 | 0.9871 | 18-03-2026 14:30 | 98.948 | 101.724 | 1178.5 | 16.954 | 15.9045 | 1.0495 | 95.4269 | 16 | 15.677 | 0.32296 | 0.97271 | 18-03-2026 14:30 | 92.844 | 94.048 | 1111.7 | 15.6747 | 15.1311 | 0.54353 | 90.7868 | 15 | 14.9148 | 0.085235 | 0.9872 | 18-03-2026 14:30 | 172.4693 | 164.6332 | 7.8361 | 987.7994 | 164.7 | 162.279 | 2.421
18-03-2026 14:20 | 370 | 47.93 | 134.358 | 136.169 | 1544.2 | 22.6948 | 22.1045 | 0.5903 | 132.6272 | 27.2 | 21.7884 | 5.4116 | 0.9867 | 18-03-2026 14:20 | 135.065 | 136.899 | 1545.7 | 22.8165 | 22.1045 | 0.71196 | 132.6272 | 27.3 | 21.7884 | 5.5116 | 0.9866 | 18-03-2026 14:20 | 132.393 | 134.867 | 1528.8 | 22.4778 | 22.1045 | 0.3733 | 132.6272 | 26.8 | 21.7884 | 5.0116 | 0.98166 | 18-03-2026 14:20 | 134.355 | 136.18 | 1541.3 | 22.6967 | 22.1045 | 0.59213 | 132.6272 | 27.3 | 21.7884 | 5.5116 | 0.9866 | 18-03-2026 14:20 | 99.543 | 100.854 | 1161.9 | 16.809 | 16.3737 | 0.43527 | 98.2424 | 20.3 | 16.1396 | 4.1604 | 0.987 | 18-03-2026 14:20 | 99.193 | 100.51 | 1153.5 | 16.7517 | 16.3737 | 0.37794 | 98.2424 | 20.6 | 16.1396 | 4.4604 | 0.9869 | 18-03-2026 14:20 | 98.912 | 100.215 | 1156.3 | 16.7025 | 16.3737 | 0.32877 | 98.2424 | 20.5 | 16.1396 | 4.3604 | 0.987 | 18-03-2026 14:20 | 99.352 | 102.159 | 1162.5 | 17.0265 | 16.3737 | 0.65277 | 98.2424 | 20.7 | 16.1396 | 4.5604 | 0.97252 | 18-03-2026 14:20 | 94.096 | 95.335 | 1096.7 | 15.8892 | 15.5776 | 0.31159 | 93.4655 | 19.4 | 15.3548 | 4.0452 | 0.987 | 18-03-2026 14:20 | 173.8647 | 169.4907 | 4.374 | 1016.9439 | 210.1 | 167.0669 | 43.0331
18-03-2026 14:10 | 570 | 48.22 | 249.974 | 283.486 | 1517 | 47.2477 | 34.0154 | 13.2323 | 204.0921 | 34.4 | 33.5289 | 0.87106 | 0.88179 | 18-03-2026 14:10 | 259.284 | 208.971 | 1518.4 | 34.8285 | 34.0154 | 0.81314 | 204.0921 | 35.6 | 33.5289 | 2.0711 | 1.2408 | 18-03-2026 14:10 | 202.762 | 206.756 | 1502 | 34.4593 | 34.0154 | 0.44398 | 204.0921 | 34.4 | 33.5289 | 0.87106 | 0.98068 | 18-03-2026 14:10 | 212.513 | 215.596 | 1514 | 35.9327 | 34.0154 | 1.9173 | 204.0921 | 34.3 | 33.5289 | 0.77106 | 0.9857 | 18-03-2026 14:10 | 161.342 | 163.55 | 1141.6 | 27.2583 | 25.1966 | 2.0618 | 151.1794 | 26.2 | 24.8362 | 1.3638 | 0.9865 | 18-03-2026 14:10 | 201.446 | 204.286 | 1132.9 | 34.0477 | 25.1966 | 8.8511 | 151.1794 | 25.4 | 24.8362 | 0.56375 | 0.9861 | 18-03-2026 14:10 | 197.292 | 200.032 | 1135.8 | 33.3387 | 25.1966 | 8.1421 | 151.1794 | 25.7 | 24.8362 | 0.86375 | 0.9863 | 18-03-2026 14:10 | 216.358 | 220.071 | 1141.8 | 36.6785 | 25.1966 | 11.4819 | 151.1794 | 25.6 | 24.8362 | 0.76375 | 0.98313 | 18-03-2026 14:10 | 201.757 | 207.347 | 1077.3 | 34.5578 | 23.9714 | 10.5864 | 143.8284 | 24 | 23.6286 | 0.37138 | 0.97304 | 18-03-2026 14:10 | 318.3492 | 260.8191 | 57.5301 | 1564.9144 | 265.6 | 257.0894 | 8.5106
18-03-2026 14:00 | 478 | 48.22 | 168.266 | 170.621 | 1482.6 | 28.4368 | 28.5252 | -0.088325 | 171.151 | 39.3 | 28.1172 | 11.1828 | 0.9862 | 18-03-2026 14:00 | 188.463 | 173.14 | 1482.8 | 28.8567 | 28.5252 | 0.33151 | 171.151 | 39.7 | 28.1172 | 11.5828 | 1.0885 | 18-03-2026 14:00 | 166.051 | 169.774 | 1467.6 | 28.2957 | 28.5252 | -0.22949 | 171.151 | 38.8 | 28.1172 | 10.6828 | 0.97807 | 18-03-2026 14:00 | 168.476 | 170.885 | 1479.7 | 28.4808 | 28.5252 | -0.044325 | 171.151 | 39.7 | 28.1172 | 11.5828 | 0.9859 | 18-03-2026 14:00 | 125.218 | 126.919 | 1115.4 | 21.1532 | 21.1297 | 0.02342 | 126.7785 | 29.1 | 20.8276 | 8.2724 | 0.9866 | 18-03-2026 14:00 | 124.547 | 126.264 | 1107.5 | 21.044 | 21.1297 | -0.085747 | 126.7785 | 29 | 20.8276 | 8.1724 | 0.9864 | 18-03-2026 14:00 | 123.833 | 125.515 | 1110.1 | 20.9192 | 21.1297 | -0.21058 | 126.7785 | 28.4 | 20.8276 | 7.5724 | 0.9866 | 18-03-2026 14:00 | 124.448 | 127.696 | 1116.2 | 21.2827 | 21.1297 | 0.15292 | 126.7785 | 28.7 | 20.8276 | 7.8724 | 0.97456 | 18-03-2026 14:00 | 117.95 | 119.588 | 1053.3 | 19.9313 | 20.1023 | -0.171 | 120.614 | 27.3 | 19.8149 | 7.4851 | 0.9863 | 18-03-2026 14:00 | 218.4003 | 218.722 | -0.32163 | 1312.3318 | 300 | 215.5942 | 84.4058
18-03-2026 13:50 | 557 | 48.22 | 207.328 | 204.922 | 1443.3 | 34.1537 | 33.2396 | 0.9141 | 199.4374 | 34.4 | 32.7642 | 1.6358 | 1.0117 | 18-03-2026 13:50 | 202.745 | 229.77 | 1443.1 | 38.295 | 33.2396 | 5.0554 | 199.4374 | 33.8 | 32.7642 | 1.0358 | 0.88238 | 18-03-2026 13:50 | 194 | 198.764 | 1428.8 | 33.1273 | 33.2396 | -0.11223 | 199.4374 | 33.2 | 32.7642 | 0.43576 | 0.97603 | 18-03-2026 13:50 | 197.464 | 200.308 | 1440 | 33.3847 | 33.2396 | 0.1451 | 199.4374 | 33.6 | 32.7642 | 0.83576 | 0.9858 | 18-03-2026 13:50 | 145.336 | 147.34 | 1086.3 | 24.5567 | 24.6219 | -0.065235 | 147.7314 | 24.8 | 24.2698 | 0.53019 | 0.9864 | 18-03-2026 13:50 | 144.696 | 146.676 | 1078.5 | 24.446 | 24.6219 | -0.1759 | 147.7314 | 24.7 | 24.2698 | 0.43019 | 0.9865 | 18-03-2026 13:50 | 143.17 | 145.437 | 1081.7 | 24.2395 | 24.6219 | -0.3824 | 147.7314 | 24.9 | 24.2698 | 0.63019 | 0.98441 | 18-03-2026 13:50 | 143.565 | 147.573 | 1087.5 | 24.5955 | 24.6219 | -0.026402 | 147.7314 | 24.6 | 24.2698 | 0.33019 | 0.97284 | 18-03-2026 13:50 | 136.366 | 138.246 | 1026 | 23.041 | 23.4247 | -0.38369 | 140.5481 | 23.7 | 23.0897 | 0.61028 | 0.9864 | 18-03-2026 13:50 | 259.8393 | 254.8706 | 4.9688 | 1529.2234 | 257.7 | 251.2259 | 6.4741
18-03-2026 13:40 | 646 | 48.5 | 259.209 | 263.183 | 1408.9 | 43.8638 | 38.5096 | 5.3542 | 231.0577 | 45.2 | 37.9589 | 7.2411 | 0.9849 | 18-03-2026 13:40 | 308.57 | 295.251 | 1409.3 | 49.2085 | 38.5096 | 10.6989 | 231.0577 | 47.4 | 37.9589 | 9.4411 | 1.0451 | 18-03-2026 13:40 | 214.984 | 220.485 | 1395.6 | 36.7475 | 38.5096 | -1.7621 | 231.0577 | 46.3 | 37.9589 | 8.3411 | 0.97505 | 18-03-2026 13:40 | 223.476 | 228.652 | 1406.4 | 38.1087 | 38.5096 | -0.40095 | 231.0577 | 47.5 | 37.9589 | 9.5411 | 0.97736 | 18-03-2026 13:40 | 161.686 | 164.048 | 1061.5 | 27.3413 | 28.5256 | -1.1843 | 171.1538 | 36 | 28.1177 | 7.8823 | 0.9856 | 18-03-2026 13:40 | 161.9 | 164.265 | 1053.8 | 27.3775 | 28.5256 | -1.1481 | 171.1538 | 36 | 28.1177 | 7.8823 | 0.9856 | 18-03-2026 13:40 | 160.837 | 163.196 | 1056.8 | 27.1993 | 28.5256 | -1.3263 | 171.1538 | 35.3 | 28.1177 | 7.1823 | 0.98554 | 18-03-2026 13:40 | 160.934 | 165.564 | 1062.9 | 27.594 | 28.5256 | -0.93164 | 171.1538 | 35.9 | 28.1177 | 7.7823 | 0.97203 | 18-03-2026 13:40 | 158.798 | 161.085 | 1002.3 | 26.8475 | 27.1386 | -0.29111 | 162.8317 | 33.8 | 26.7505 | 7.0495 | 0.9858 | 18-03-2026 13:40 | 304.2882 | 295.2796 | 9.0085 | 1771.6779 | 363.4 | 291.0571 | 72.3429
18-03-2026 13:30 | 934 | 48.5 | 310.634 | 315.942 | 1363.7 | 52.657 | 55.678 | -3.021 | 334.0679 | 54.8 | 54.8818 | -0.081794 | 0.9832 | 18-03-2026 13:30 | 338.577 | 344.037 | 1361.9 | 57.3395 | 55.678 | 1.6615 | 334.0679 | 52.5 | 54.8818 | -2.3818 | 0.98413 | 18-03-2026 13:30 | 291.441 | 303.778 | 1349.3 | 50.6297 | 55.678 | -5.0483 | 334.0679 | 53.2 | 54.8818 | -1.6818 | 0.95939 | 18-03-2026 13:30 | 334.857 | 340.129 | 1358.9 | 56.6882 | 55.678 | 1.0102 | 334.0679 | 52.7 | 54.8818 | -2.1818 | 0.9845 | 18-03-2026 13:30 | 211.041 | 219.847 | 1025.5 | 36.6412 | 41.243 | -4.6018 | 247.4577 | 40.4 | 40.6532 | -0.25318 | 0.95994 | 18-03-2026 13:30 | 243.668 | 249.073 | 1017.8 | 41.5122 | 41.243 | 0.26921 | 247.4577 | 39.6 | 40.6532 | -1.0532 | 0.9783 | 18-03-2026 13:30 | 200.503 | 203.515 | 1021.5 | 33.9192 | 41.243 | -7.3238 | 247.4577 | 39.5 | 40.6532 | -1.1532 | 0.9852 | 18-03-2026 13:30 | 206.854 | 212.658 | 1027 | 35.443 | 41.243 | -5.8 | 247.4577 | 39.4 | 40.6532 | -1.2532 | 0.97271 | 18-03-2026 13:30 | 206.639 | 210.065 | 968.5 | 35.0108 | 39.2376 | -4.2267 | 235.4254 | 37.5 | 38.6765 | -1.1765 | 0.98369 | 18-03-2026 13:30 | 399.8407 | 426.9213 | -27.0807 | 2561.528 | 409.6 | 420.8164 | -11.2164
18-03-2026 13:20 | 518 | 48.22 | 181.855 | 184.456 | 1308.9 | 30.7427 | 30.9122 | -0.16953 | 185.4732 | 36.3 | 30.4702 | 5.8298 | 0.9859 | 18-03-2026 13:20 | 181.748 | 184.403 | 1309.4 | 30.7338 | 30.9122 | -0.17837 | 185.4732 | 38.4 | 30.4702 | 7.9298 | 0.9856 | 18-03-2026 13:20 | 181.491 | 185.96 | 1296.1 | 30.9933 | 30.9122 | 0.081132 | 185.4732 | 37.2 | 30.4702 | 6.7298 | 0.97597 | 18-03-2026 13:20 | 179.898 | 182.526 | 1306.2 | 30.421 | 30.9122 | -0.4912 | 185.4732 | 38.1 | 30.4702 | 7.6298 | 0.9856 | 18-03-2026 13:20 | 136.833 | 138.72 | 985.1 | 23.12 | 22.8979 | 0.22207 | 137.3876 | 28.8 | 22.5705 | 6.2295 | 0.9864 | 18-03-2026 13:20 | 133.001 | 134.912 | 978.2 | 22.4853 | 22.8979 | -0.41259 | 137.3876 | 29.1 | 22.5705 | 6.5295 | 0.98584 | 18-03-2026 13:20 | 134.592 | 136.717 | 982 | 22.7862 | 22.8979 | -0.11176 | 137.3876 | 28.4 | 22.5705 | 5.8295 | 0.98446 | 18-03-2026 13:20 | 133.228 | 136.996 | 987.6 | 22.8327 | 22.8979 | -0.06526 | 137.3876 | 28.5 | 22.5705 | 5.9295 | 0.9725 | 18-03-2026 13:20 | 124.725 | 126.483 | 931 | 21.0805 | 21.7845 | -0.70404 | 130.7072 | 27.2 | 21.473 | 5.727 | 0.9861 | 18-03-2026 13:20 | 235.1955 | 237.0251 | -1.8296 | 1422.1503 | 292 | 233.6356 | 58.3644
18-03-2026 13:10 | 1183 | 48.22 | 345.173 | 350.287 | 1272.6 | 58.3812 | 70.5968 | -12.2156 | 423.5807 | 57.7 | 69.5872 | -11.8872 | 0.9854 | 18-03-2026 13:10 | 333.327 | 338.334 | 1271 | 56.389 | 70.5968 | -14.2078 | 423.5807 | 112.9 | 69.5872 | 43.3128 | 0.9852 | 18-03-2026 13:10 | 347.542 | 358.076 | 1258.9 | 59.6793 | 70.5968 | -10.9175 | 423.5807 | 56.9 | 69.5872 | -12.6872 | 0.97058 | 18-03-2026 13:10 | 333.104 | 338.074 | 1268.1 | 56.3457 | 70.5968 | -14.2511 | 423.5807 | 56.1 | 69.5872 | -13.4872 | 0.9853 | 18-03-2026 13:10 | 291.695 | 296.679 | 956.3 | 49.4465 | 52.2939 | -2.8474 | 313.7635 | 45.9 | 51.5461 | -5.6461 | 0.9832 | 18-03-2026 13:10 | 287.004 | 293.06 | 949.1 | 48.8433 | 52.2939 | -3.4506 | 313.7635 | 45.3 | 51.5461 | -6.2461 | 0.97934 | 18-03-2026 13:10 | 287.71 | 294.221 | 953.6 | 49.0368 | 52.2939 | -3.2571 | 313.7635 | 45.9 | 51.5461 | -5.6461 | 0.97787 | 18-03-2026 13:10 | 288.281 | 297.046 | 959.1 | 49.5077 | 52.2939 | -2.7862 | 313.7635 | 45.9 | 51.5461 | -5.6461 | 0.97049 | 18-03-2026 13:10 | 272.438 | 277.065 | 903.8 | 46.1775 | 49.7512 | -3.5737 | 298.5071 | 43.4 | 49.0397 | -5.6397 | 0.9833 | 18-03-2026 13:10 | 473.807 | 541.314 | -67.507 | 3247.8838 | 510 | 533.5732 | -23.5732
18-03-2026 13:00 | 1054 | 48.5 | 340.402 | 345.691 | 1214.9 | 57.6152 | 62.8315 | -5.2163 | 376.9889 | 56.9 | 61.933 | -5.033 | 0.9847 |  |  |  |  | 0 | 62.8315 | -62.8315 | 376.9889 | 0 | 61.933 | -61.933 |  | 18-03-2026 13:00 | 345.027 | 355.372 | 1202 | 59.2287 | 62.8315 | -3.6028 | 376.9889 | 56.7 | 61.933 | -5.233 | 0.97089 | 18-03-2026 13:00 | 333.409 | 338.446 | 1212 | 56.4077 | 62.8315 | -6.4238 | 376.9889 | 56.4 | 61.933 | -5.533 | 0.98512 | 18-03-2026 13:00 | 265.011 | 269.293 | 910.4 | 44.8822 | 46.5418 | -1.6597 | 279.251 | 42.9 | 45.8763 | -2.9763 | 0.9841 | 18-03-2026 13:00 | 261.409 | 266.572 | 903.8 | 44.4287 | 46.5418 | -2.1132 | 279.251 | 42.8 | 45.8763 | -3.0763 | 0.98063 | 18-03-2026 13:00 | 261.408 | 267.234 | 907.7 | 44.539 | 46.5418 | -2.0028 | 279.251 | 42.2 | 45.8763 | -3.6763 | 0.9782 | 18-03-2026 13:00 | 262.271 | 270.103 | 913.2 | 45.0172 | 46.5418 | -1.5247 | 279.251 | 42.4 | 45.8763 | -3.4763 | 0.971 | 18-03-2026 13:00 | 247.708 | 251.685 | 860.4 | 41.9475 | 44.2788 | -2.3313 | 265.6728 | 40.1 | 43.6456 | -3.5456 | 0.9842 | 18-03-2026 13:00 | 394.066 | 481.772 | -87.706 | 2890.6323 | 380.4 | 474.8827 | -94.4827
18-03-2026 12:50 | 849 | 47.93 | 292.813 | 296.371 | 1158 | 49.3952 | 50.721 | -1.3258 | 304.3257 | 42.3 | 49.9956 | -7.6956 | 0.98799 | 18-03-2026 12:50 | 302.339 | 307.255 | 1158.1 | 51.2092 | 50.721 | 0.48821 | 304.3257 | 42.4 | 49.9956 | -7.5956 | 0.984 | 18-03-2026 12:50 | 306.285 | 315.017 | 1145.3 | 52.5028 | 50.721 | 1.7819 | 304.3257 | 42.4 | 49.9956 | -7.5956 | 0.97228 | 18-03-2026 12:50 | 307.324 | 312.416 | 1155.6 | 52.0693 | 50.721 | 1.3484 | 304.3257 | 43 | 49.9956 | -6.9956 | 0.9837 | 18-03-2026 12:50 | 228.567 | 232.001 | 867.5 | 38.6668 | 37.5711 | 1.0958 | 225.4265 | 32.2 | 37.0338 | -4.8338 | 0.9852 | 18-03-2026 12:50 | 230.76 | 234.948 | 861 | 39.158 | 37.5711 | 1.5869 | 225.4265 | 31.6 | 37.0338 | -5.4338 | 0.98217 | 18-03-2026 12:50 | 228.926 | 232.971 | 865.5 | 38.8285 | 37.5711 | 1.2574 | 225.4265 | 32.1 | 37.0338 | -4.9338 | 0.98264 | 18-03-2026 12:50 | 230.723 | 238.681 | 870.8 | 39.7802 | 37.5711 | 2.2091 | 225.4265 | 32.3 | 37.0338 | -4.7338 | 0.96666 | 18-03-2026 12:50 | 214.784 | 219.646 | 820.3 | 36.6077 | 35.7442 | 0.86344 | 214.4654 | 30.6 | 35.2331 | -4.6331 | 0.97786 | 18-03-2026 12:50 | 398.2177 | 388.9123 | 9.3053 | 2333.474 | 328.9 | 383.3509 | -54.4509
18-03-2026 12:40 | 1019 | 48.5 | 338.213 | 344.444 | 1115.7 | 57.4073 | 60.745 | -3.3377 | 364.4703 | 56 | 59.8764 | -3.8764 | 0.98191 | 18-03-2026 12:40 | 329.637 | 340.431 | 1115.7 | 56.7385 | 60.745 | -4.0065 | 364.4703 | 56.5 | 59.8764 | -3.3764 | 0.96829 | 18-03-2026 12:40 | 334.725 | 344.858 | 1102.9 | 57.4763 | 60.745 | -3.2687 | 364.4703 | 56.2 | 59.8764 | -3.6764 | 0.97062 | 18-03-2026 12:40 | 336.293 | 342.039 | 1112.6 | 57.0065 | 60.745 | -3.7385 | 364.4703 | 56.3 | 59.8764 | -3.5764 | 0.9832 | 18-03-2026 12:40 | 252.808 | 256.919 | 835.3 | 42.8198 | 44.9963 | -2.1765 | 269.978 | 42.6 | 44.3529 | -1.7529 | 0.984 | 18-03-2026 12:40 | 250.274 | 255.378 | 829.4 | 42.563 | 44.9963 | -2.4333 | 269.978 | 42.2 | 44.3529 | -2.1529 | 0.98001 | 18-03-2026 12:40 | 249.454 | 254.504 | 833.4 | 42.4173 | 44.9963 | -2.579 | 269.978 | 41.4 | 44.3529 | -2.9529 | 0.98016 | 18-03-2026 12:40 | 250.722 | 258.27 | 838.5 | 43.045 | 44.9963 | -1.9513 | 269.978 | 41.6 | 44.3529 | -2.7529 | 0.97077 | 18-03-2026 12:40 | 237.678 | 241.543 | 789.7 | 40.2572 | 42.8084 | -2.5513 | 256.8506 | 39.3 | 42.1963 | -2.8963 | 0.984 | 18-03-2026 12:40 | 439.731 | 465.7739 | -26.0429 | 2794.6435 | 432.1 | 459.1134 | -27.0134
18-03-2026 12:30 | 1012 | 48.5 | 337.945 | 343.929 | 1059.7 | 57.3215 | 60.3278 | -3.0063 | 361.9665 | 56.8 | 59.4651 | -2.6651 | 0.9826 | 18-03-2026 12:30 | 333.677 | 339.137 | 1059.2 | 56.5228 | 60.3278 | -3.8049 | 361.9665 | 56.5 | 59.4651 | -2.9651 | 0.9839 | 18-03-2026 12:30 | 333.672 | 343.703 | 1046.7 | 57.2838 | 60.3278 | -3.0439 | 361.9665 | 55.2 | 59.4651 | -4.2651 | 0.97081 | 18-03-2026 12:30 | 332.693 | 338.24 | 1056.3 | 56.3733 | 60.3278 | -3.9544 | 361.9665 | 55.7 | 59.4651 | -3.7651 | 0.9836 | 18-03-2026 12:30 | 253.189 | 257.306 | 792.7 | 42.8843 | 44.6872 | -1.8029 | 268.1234 | 41.7 | 44.0482 | -2.3482 | 0.984 | 18-03-2026 12:30 | 250.006 | 254.93 | 787.2 | 42.4883 | 44.6872 | -2.1989 | 268.1234 | 41.3 | 44.0482 | -2.7482 | 0.98068 | 18-03-2026 12:30 | 250.505 | 255.677 | 792 | 42.6128 | 44.6872 | -2.0744 | 268.1234 | 41.2 | 44.0482 | -2.8482 | 0.97977 | 18-03-2026 12:30 | 251.437 | 258.905 | 796.9 | 43.1508 | 44.6872 | -1.5364 | 268.1234 | 42.1 | 44.0482 | -1.9482 | 0.97116 | 18-03-2026 12:30 | 237.131 | 240.938 | 750.4 | 40.1563 | 42.5144 | -2.358 | 255.0862 | 39.3 | 41.9064 | -2.6064 | 0.9842 | 18-03-2026 12:30 | 438.7942 | 462.5743 | -23.7801 | 2775.4458 | 429.8 | 455.9595 | -26.1595
18-03-2026 12:20 | 1011 | 48.5 | 339.125 | 345.095 | 1002.9 | 57.5158 | 60.2681 | -2.7523 | 361.6089 | 56.7 | 59.4063 | -2.7063 | 0.9827 | 18-03-2026 12:20 | 341.405 | 347.486 | 1002.7 | 57.9143 | 60.2681 | -2.3538 | 361.6089 | 58.7 | 59.4063 | -0.70631 | 0.9825 | 18-03-2026 12:20 | 333.573 | 343.335 | 991.5 | 57.2225 | 60.2681 | -3.0456 | 361.6089 | 55.2 | 59.4063 | -4.2063 | 0.97157 | 18-03-2026 12:20 | 338.102 | 344.069 | 1000.6 | 57.3448 | 60.2681 | -2.9233 | 361.6089 | 55.8 | 59.4063 | -3.6063 | 0.98266 | 18-03-2026 12:20 | 252.081 | 256.154 | 751 | 42.6923 | 44.6431 | -1.9507 | 267.8584 | 41.7 | 44.0047 | -2.3047 | 0.9841 | 18-03-2026 12:20 | 249.652 | 254.534 | 745.9 | 42.4223 | 44.6431 | -2.2207 | 267.8584 | 41.3 | 44.0047 | -2.7047 | 0.98082 | 18-03-2026 12:20 | 249.042 | 254.188 | 750.8 | 42.3647 | 44.6431 | -2.2784 | 267.8584 | 41.2 | 44.0047 | -2.8047 | 0.97976 | 18-03-2026 12:20 | 249.703 | 257.165 | 754.8 | 42.8608 | 44.6431 | -1.7822 | 267.8584 | 41.3 | 44.0047 | -2.7047 | 0.97098 | 18-03-2026 12:20 | 236.811 | 240.662 | 711.1 | 40.1103 | 42.4724 | -2.362 | 254.8341 | 39.6 | 41.865 | -2.265 | 0.984 | 18-03-2026 12:20 | 440.448 | 462.1172 | -21.6692 | 2772.7033 | 431.5 | 455.5089 | -24.0089
18-03-2026 12:10 | 1007 | 48.79 | 334.375 | 341.546 | 946.2 | 56.9243 | 59.9633 | -3.039 | 359.7798 | 54.6 | 59.1058 | -4.5058 | 0.979 | 18-03-2026 12:10 | 338.166 | 344.224 | 944 | 57.3707 | 59.9633 | -2.5926 | 359.7798 | 56.4 | 59.1058 | -2.7058 | 0.9824 | 18-03-2026 12:10 | 330.986 | 340.737 | 936.3 | 56.7895 | 59.9633 | -3.1738 | 359.7798 | 54.5 | 59.1058 | -4.6058 | 0.97138 | 18-03-2026 12:10 | 334.699 | 340.73 | 944.8 | 56.7883 | 59.9633 | -3.175 | 359.7798 | 55.2 | 59.1058 | -3.9058 | 0.9823 | 18-03-2026 12:10 | 250.321 | 254.365 | 709.3 | 42.3942 | 44.4173 | -2.0231 | 266.5036 | 41.3 | 43.7821 | -2.4821 | 0.9841 | 18-03-2026 12:10 | 247.608 | 252.276 | 704.6 | 42.046 | 44.4173 | -2.3713 | 266.5036 | 40.9 | 43.7821 | -2.8821 | 0.9815 | 18-03-2026 12:10 | 247.538 | 252.748 | 709.6 | 42.1247 | 44.4173 | -2.2926 | 266.5036 | 41.5 | 43.7821 | -2.2821 | 0.97939 | 18-03-2026 12:10 | 248.559 | 255.951 | 713.5 | 42.6585 | 44.4173 | -1.7588 | 266.5036 | 41.1 | 43.7821 | -2.6821 | 0.97112 | 18-03-2026 12:10 | 235.073 | 238.823 | 671.5 | 39.8038 | 42.2575 | -2.4537 | 253.5451 | 38.9 | 41.6532 | -2.7532 | 0.9843 | 18-03-2026 12:10 | 436.9 | 459.7798 | -22.8798 | 2758.6787 | 424.4 | 453.2049 | -28.8049
18-03-2026 12:00 | 983 | 48.79 | 327.87 | 333.676 | 891.6 | 55.6127 | 58.5342 | -2.9215 | 351.2051 | 55.5 | 57.6971 | -2.1971 | 0.9826 | 18-03-2026 12:00 | 330.19 | 336.774 | 887.6 | 56.129 | 58.5342 | -2.4052 | 351.2051 | 51.2 | 57.6971 | -6.4971 | 0.98045 | 18-03-2026 12:00 | 323.62 | 332.78 | 881.8 | 55.4633 | 58.5342 | -3.0709 | 351.2051 | 53.9 | 57.6971 | -3.7971 | 0.97247 | 18-03-2026 12:00 | 328.303 | 334.151 | 889.6 | 55.6918 | 58.5342 | -2.8424 | 351.2051 | 54.7 | 57.6971 | -2.9971 | 0.9825 | 18-03-2026 12:00 | 245.05 | 249.06 | 668 | 41.51 | 43.3587 | -1.8487 | 260.1519 | 40.8 | 42.7386 | -1.9386 | 0.9839 | 18-03-2026 12:00 | 242.693 | 247.495 | 663.7 | 41.2492 | 43.3587 | -2.1095 | 260.1519 | 41 | 42.7386 | -1.7386 | 0.9806 | 18-03-2026 12:00 | 242.865 | 247.619 | 668.1 | 41.2698 | 43.3587 | -2.0888 | 260.1519 | 40.5 | 42.7386 | -2.2386 | 0.9808 | 18-03-2026 12:00 | 244.43 | 251.66 | 672.4 | 41.9433 | 43.3587 | -1.4153 | 260.1519 | 40.8 | 42.7386 | -1.9386 | 0.97127 | 18-03-2026 12:00 | 230.694 | 234.374 | 632.6 | 39.0623 | 41.2504 | -2.1881 | 247.5024 | 39.1 | 40.6605 | -1.5605 | 0.9843 | 18-03-2026 12:00 | 427.9315 | 448.8218 | -20.8903 | 2692.9307 | 417.5 | 442.4036 | -24.9036
18-03-2026 11:50 | 991 | 48.79 | 331.814 | 337.621 | 836.1 | 56.2702 | 59.0106 | -2.7404 | 354.0634 | 54.8 | 58.1667 | -3.3667 | 0.9828 | 18-03-2026 11:50 | 334.974 | 340.871 | 836.4 | 56.8118 | 59.0106 | -2.1987 | 354.0634 | 56.6 | 58.1667 | -1.5667 | 0.9827 | 18-03-2026 11:50 | 326.918 | 336.413 | 827.9 | 56.0688 | 59.0106 | -2.9417 | 354.0634 | 54.6 | 58.1667 | -3.5667 | 0.97178 | 18-03-2026 11:50 | 331.471 | 337.341 | 834.9 | 56.2235 | 59.0106 | -2.7871 | 354.0634 | 55.2 | 58.1667 | -2.9667 | 0.9826 | 18-03-2026 11:50 | 247.563 | 251.563 | 627.2 | 41.9272 | 43.7115 | -1.7844 | 262.2692 | 41.2 | 43.0865 | -1.8865 | 0.9841 | 18-03-2026 11:50 | 245.644 | 250.385 | 622.7 | 41.7308 | 43.7115 | -1.9807 | 262.2692 | 40.4 | 43.0865 | -2.6865 | 0.98107 | 18-03-2026 11:50 | 245.901 | 251.151 | 627.6 | 41.8585 | 43.7115 | -1.853 | 262.2692 | 40.5 | 43.0865 | -2.5865 | 0.9791 | 18-03-2026 11:50 | 247.316 | 254.499 | 631.6 | 42.4165 | 43.7115 | -1.295 | 262.2692 | 41.2 | 43.0865 | -1.8865 | 0.97178 | 18-03-2026 11:50 | 233.452 | 237.152 | 593.5 | 39.5253 | 41.5861 | -2.0608 | 249.5166 | 38.4 | 40.9914 | -2.5914 | 0.9844 | 18-03-2026 11:50 | 432.8327 | 452.4745 | -19.6418 | 2714.8467 | 422.9 | 446.0041 | -23.1041
18-03-2026 11:40 | 977 | 48.79 | 327.873 | 335.149 | 781.3 | 55.8582 | 58.1769 | -2.3187 | 349.0615 | 54.9 | 57.345 | -2.445 | 0.97829 | 18-03-2026 11:40 | 330.088 | 335.899 | 779.8 | 55.9832 | 58.1769 | -2.1937 | 349.0615 | 54.5 | 57.345 | -2.845 | 0.9827 | 18-03-2026 11:40 | 323.085 | 332.284 | 773.3 | 55.3807 | 58.1769 | -2.7962 | 349.0615 | 53.3 | 57.345 | -4.045 | 0.97232 | 18-03-2026 11:40 | 326.864 | 332.618 | 779.7 | 55.4363 | 58.1769 | -2.7406 | 349.0615 | 54.1 | 57.345 | -3.245 | 0.9827 | 18-03-2026 11:40 | 243.896 | 247.862 | 586 | 41.3103 | 43.094 | -1.7837 | 258.564 | 40.5 | 42.4778 | -1.9778 | 0.984 | 18-03-2026 11:40 | 242.12 | 246.945 | 582.3 | 41.1575 | 43.094 | -1.9365 | 258.564 | 40.1 | 42.4778 | -2.3778 | 0.98046 | 18-03-2026 11:40 | 242.29 | 247.054 | 587.1 | 41.1757 | 43.094 | -1.9183 | 258.564 | 40.1 | 42.4778 | -2.3778 | 0.98072 | 18-03-2026 11:40 | 243.329 | 250.254 | 590.4 | 41.709 | 43.094 | -1.385 | 258.564 | 40.3 | 42.4778 | -2.1778 | 0.97233 | 18-03-2026 11:40 | 230.382 | 234.033 | 555.1 | 39.0055 | 40.9986 | -1.9931 | 245.9917 | 38.1 | 40.4123 | -2.3123 | 0.9844 | 18-03-2026 11:40 | 427.0163 | 446.0823 | -19.0659 | 2676.4937 | 415.9 | 439.7033 | -23.8033
18-03-2026 11:30 | 969 | 48.79 | 324.921 | 331.342 | 726.4 | 55.2237 | 57.7005 | -2.4769 | 346.2032 | 53.5 | 56.8754 | -3.3754 | 0.98062 | 18-03-2026 11:30 | 327.683 | 333.418 | 725.3 | 55.5697 | 57.7005 | -2.1309 | 346.2032 | 53.7 | 56.8754 | -3.1754 | 0.9828 | 18-03-2026 11:30 | 321.355 | 330.702 | 720 | 55.117 | 57.7005 | -2.5835 | 346.2032 | 53.2 | 56.8754 | -3.6754 | 0.97174 | 18-03-2026 11:30 | 325.38 | 331.108 | 725.6 | 55.1847 | 57.7005 | -2.5159 | 346.2032 | 54.7 | 56.8754 | -2.1754 | 0.9827 | 18-03-2026 11:30 | 243.199 | 247.078 | 545.5 | 41.1797 | 42.7411 | -1.5615 | 256.4468 | 41.4 | 42.1299 | -0.72994 | 0.9843 | 18-03-2026 11:30 | 241.302 | 245.694 | 542.2 | 40.949 | 42.7411 | -1.7921 | 256.4468 | 40.6 | 42.1299 | -1.5299 | 0.98212 | 18-03-2026 11:30 | 241.583 | 246.694 | 547 | 41.1157 | 42.7411 | -1.6255 | 256.4468 | 40.7 | 42.1299 | -1.4299 | 0.97928 | 18-03-2026 11:30 | 243.195 | 250.415 | 550.1 | 41.7358 | 42.7411 | -1.0053 | 256.4468 | 40.5 | 42.1299 | -1.6299 | 0.97117 | 18-03-2026 11:30 | 229.716 | 233.309 | 517 | 38.8848 | 40.6629 | -1.7781 | 243.9774 | 38.2 | 40.0814 | -1.8814 | 0.9846 | 18-03-2026 11:30 | 424.96 | 442.4296 | -17.4696 | 2654.5777 | 416.5 | 436.1029 | -19.6029
18-03-2026 11:20 | 956 | 49.36 | 324.808 | 330.392 | 672.9 | 55.0653 | 56.8026 | -1.7372 | 340.8153 | 54 | 55.9903 | -1.9903 | 0.9831 | 18-03-2026 11:20 | 325.978 | 331.683 | 671.6 | 55.2805 | 56.8026 | -1.5221 | 340.8153 | 54.5 | 55.9903 | -1.4903 | 0.9828 | 18-03-2026 11:20 | 320.309 | 329.571 | 666.8 | 54.9285 | 56.8026 | -1.8741 | 340.8153 | 53.4 | 55.9903 | -2.5903 | 0.9719 | 18-03-2026 11:20 | 322.217 | 327.789 | 670.9 | 54.6315 | 56.8026 | -2.1711 | 340.8153 | 53.3 | 55.9903 | -2.6903 | 0.983 | 18-03-2026 11:20 | 241.294 | 245.093 | 504.1 | 40.8488 | 42.076 | -1.2271 | 252.4558 | 39.1 | 41.4743 | -2.3743 | 0.9845 | 18-03-2026 11:20 | 239.053 | 243.415 | 501.6 | 40.5692 | 42.076 | -1.5068 | 252.4558 | 39.5 | 41.4743 | -1.9743 | 0.98208 | 18-03-2026 11:20 | 240.772 | 245.456 | 506.3 | 40.9093 | 42.076 | -1.1666 | 252.4558 | 40.1 | 41.4743 | -1.3743 | 0.98092 | 18-03-2026 11:20 | 241.621 | 248.675 | 509.6 | 41.4458 | 42.076 | -0.63013 | 252.4558 | 39.6 | 41.4743 | -1.8743 | 0.97163 | 18-03-2026 11:20 | 227.406 | 230.97 | 478.8 | 38.495 | 40.0301 | -1.5351 | 240.1804 | 37.6 | 39.4576 | -1.8576 | 0.98457 | 18-03-2026 11:20 | 422.174 | 435.5441 | -13.3701 | 2613.2647 | 411.1 | 429.3158 | -18.2158
18-03-2026 11:10 | 960 | 49.08 | 329.569 | 335.098 | 618.9 | 55.8497 | 57.1013 | -1.2517 | 342.608 | 53.5 | 56.2848 | -2.7848 | 0.9835 | 18-03-2026 11:10 | 0 | 335.995 | 617.1 | 55.9992 | 57.1013 | -1.1022 | 342.608 | 53.1 | 56.2848 | -3.1848 |  | 18-03-2026 11:10 | 323.732 | 332.48 | 613.4 | 55.4133 | 57.1013 | -1.688 | 342.608 | 52.4 | 56.2848 | -3.8848 | 0.97369 | 18-03-2026 11:10 | 328.296 | 333.906 | 617.6 | 55.651 | 57.1013 | -1.4503 | 342.608 | 52.4 | 56.2848 | -3.8848 | 0.9832 | 18-03-2026 11:10 | 245.029 | 248.811 | 465 | 41.4685 | 42.2973 | -0.82878 | 253.7837 | 39.9 | 41.6924 | -1.7924 | 0.9848 | 18-03-2026 11:10 | 244.077 | 248.211 | 462.1 | 41.3685 | 42.2973 | -0.92878 | 253.7837 | 39 | 41.6924 | -2.6924 | 0.98334 | 18-03-2026 11:10 | 244.259 | 248.84 | 466.2 | 41.4733 | 42.2973 | -0.82395 | 253.7837 | 39.2 | 41.6924 | -2.4924 | 0.98159 | 18-03-2026 11:10 | 245.962 | 253.246 | 470 | 42.2077 | 42.2973 | -0.089613 | 253.7837 | 40.1 | 41.6924 | -1.5924 | 0.97124 | 18-03-2026 11:10 | 231.833 | 235.866 | 441.2 | 39.311 | 40.2406 | -0.92962 | 241.4437 | 37.4 | 39.6652 | -2.2652 | 0.9829 | 18-03-2026 11:10 | 428.7422 | 437.8351 | -9.0929 | 2627.0103 | 407 | 431.574 | -24.574
18-03-2026 11:00 | 310 | 48.5 | 101.961 | 107.706 | 565.4 | 17.951 | 18.4798 | -0.52885 | 110.8791 | 34 | 18.2156 | 15.7844 | 0.94666 | 18-03-2026 11:00 | 106.32 | 107.764 | 564 | 17.9607 | 18.4798 | -0.51918 | 110.8791 | 35.5 | 18.2156 | 17.2844 | 0.9866 | 18-03-2026 11:00 | 117.036 | 120.941 | 561 | 20.1568 | 18.4798 | 1.677 | 110.8791 | 35.8 | 18.2156 | 17.5844 | 0.96771 | 18-03-2026 11:00 | 108.737 | 109.829 | 565.2 | 18.3048 | 18.4798 | -0.17501 | 110.8791 | 36.5 | 18.2156 | 18.2844 | 0.99006 | 18-03-2026 11:00 | 120.666 | 122.694 | 425.1 | 20.449 | 13.6888 | 6.7602 | 82.1327 | 27.5 | 13.493 | 14.007 | 0.98347 | 18-03-2026 11:00 | 81.498 | 82.647 | 423.1 | 13.7745 | 13.6888 | 0.085725 | 82.1327 | 27.6 | 13.493 | 14.107 | 0.9861 | 18-03-2026 11:00 | 125.401 | 130.981 | 427 | 21.8302 | 13.6888 | 8.1414 | 82.1327 | 27.5 | 13.493 | 14.007 | 0.9574 | 18-03-2026 11:00 | 95.936 | 101.665 | 429.9 | 16.9442 | 13.6888 | 3.2554 | 82.1327 | 27.7 | 13.493 | 14.207 | 0.94365 | 18-03-2026 11:00 | 74.808 | 75.909 | 403.8 | 12.6515 | 13.0232 | -0.37167 | 78.139 | 26.3 | 12.8369 | 13.4631 | 0.9855 | 18-03-2026 11:00 | 160.0227 | 141.6977 | 18.325 | 850.186 | 278.4 | 139.6714 | 138.7286
18-03-2026 10:50 | 877 | 48.5 | 342.007 | 347.568 | 531.4 | 57.928 | 52.2801 | 5.6479 | 313.6805 | 39.3 | 51.5325 | -12.2325 | 0.984 | 18-03-2026 10:50 | 336.113 | 341.613 | 528.5 | 56.9355 | 52.2801 | 4.6554 | 313.6805 | 39.1 | 51.5325 | -12.4325 | 0.9839 | 18-03-2026 10:50 | 234.955 | 238.388 | 525.2 | 39.7313 | 52.2801 | -12.5487 | 313.6805 | 38.2 | 51.5325 | -13.3325 | 0.9856 | 18-03-2026 10:50 | 338.031 | 343.632 | 528.7 | 57.272 | 52.2801 | 4.9919 | 313.6805 | 39 | 51.5325 | -12.5325 | 0.9837 | 18-03-2026 10:50 | 183.138 | 185.701 | 397.6 | 30.9502 | 38.726 | -7.7758 | 232.3559 | 29.6 | 38.1722 | -8.5722 | 0.9862 | 18-03-2026 10:50 | 240.876 | 244.42 | 395.5 | 40.7367 | 38.726 | 2.0107 | 232.3559 | 29.3 | 38.1722 | -8.8722 | 0.9855 | 18-03-2026 10:50 | 188.542 | 191.161 | 399.5 | 31.8602 | 38.726 | -6.8658 | 232.3559 | 29.7 | 38.1722 | -8.4722 | 0.9863 | 18-03-2026 10:50 | 206.928 | 211.285 | 402.2 | 35.2142 | 38.726 | -3.5118 | 232.3559 | 30 | 38.1722 | -8.1722 | 0.97938 | 18-03-2026 10:50 | 227.762 | 231.09 | 377.5 | 38.515 | 36.843 | 1.672 | 221.0579 | 28.1 | 36.3161 | -8.2161 | 0.9856 | 18-03-2026 10:50 | 389.143 | 400.8673 | -11.7243 | 2405.2035 | 302.3 | 395.1349 | -92.8349
18-03-2026 10:40 | 842 | 48.22 | 308.222 | 312.979 | 492.1 | 52.1632 | 50.2472 | 1.9159 | 301.4835 | 23 | 49.5287 | -26.5287 | 0.9848 | 18-03-2026 10:40 | 298.838 | 303.481 | 489.4 | 50.5802 | 50.2472 | 0.33292 | 301.4835 | 23.3 | 49.5287 | -26.2287 | 0.9847 | 18-03-2026 10:40 | 280.39 | 284.573 | 487 | 47.4288 | 50.2472 | -2.8184 | 301.4835 | 23.1 | 49.5287 | -26.4287 | 0.9853 | 18-03-2026 10:40 | 292.916 | 297.346 | 489.7 | 49.5577 | 50.2472 | -0.68958 | 301.4835 | 22.8 | 49.5287 | -26.7287 | 0.9851 | 18-03-2026 10:40 | 229.617 | 232.83 | 368 | 38.805 | 37.2202 | 1.5848 | 223.3211 | 17.3 | 36.6879 | -19.3879 | 0.9862 | 18-03-2026 10:40 | 216.552 | 220.043 | 366.2 | 36.6738 | 37.2202 | -0.54635 | 223.3211 | 16.9 | 36.6879 | -19.7879 | 0.98413 | 18-03-2026 10:40 | 225.65 | 229.311 | 369.8 | 38.2185 | 37.2202 | 0.99832 | 223.3211 | 17.3 | 36.6879 | -19.3879 | 0.98403 | 18-03-2026 10:40 | 221.417 | 228.73 | 372.2 | 38.1217 | 37.2202 | 0.90148 | 223.3211 | 17.3 | 36.6879 | -19.3879 | 0.96803 | 18-03-2026 10:40 | 201.343 | 204.16 | 349.4 | 34.0267 | 35.4104 | -1.3837 | 212.4624 | 16.1 | 34.904 | -18.804 | 0.9862 | 18-03-2026 10:40 | 385.5755 | 385.2801 | 0.29539 | 2311.6806 | 177.1 | 379.7706 | -202.6706
18-03-2026 10:30 | 490 | 49.08 | 298.588 | 303.258 | 469.1 | 50.543 | 29.1455 | 21.3975 | 174.8728 | 45.7 | 28.7287 | 16.9713 | 0.9846 | 18-03-2026 10:30 | 283.773 | 198.979 | 466.1 | 33.1632 | 29.1455 | 4.0177 | 174.8728 | 44.8 | 28.7287 | 16.0713 | 1.4261 | 18-03-2026 10:30 | 173.167 | 177.699 | 463.9 | 29.6165 | 29.1455 | 0.47103 | 174.8728 | 44.9 | 28.7287 | 16.1713 | 0.9745 | 18-03-2026 10:30 | 178.676 | 181.268 | 466.9 | 30.2113 | 29.1455 | 1.0659 | 174.8728 | 44.8 | 28.7287 | 16.0713 | 0.9857 | 18-03-2026 10:30 | 135.567 | 137.571 | 350.7 | 22.9285 | 21.5892 | 1.3393 | 129.5354 | 34.6 | 21.2805 | 13.3195 | 0.98543 | 18-03-2026 10:30 | 132.569 | 134.383 | 349.3 | 22.3972 | 21.5892 | 0.80793 | 129.5354 | 34 | 21.2805 | 12.7195 | 0.9865 | 18-03-2026 10:30 | 130.657 | 132.533 | 352.5 | 22.0888 | 21.5892 | 0.4996 | 129.5354 | 35 | 21.2805 | 13.7195 | 0.98585 | 18-03-2026 10:30 | 126.509 | 129.771 | 354.9 | 21.6285 | 21.5892 | 0.039263 | 129.5354 | 36.1 | 21.2805 | 14.8195 | 0.97486 | 18-03-2026 10:30 | 123.468 | 125.17 | 333.3 | 20.8617 | 20.5395 | 0.32218 | 123.2369 | 33.5 | 20.2458 | 13.2542 | 0.9864 | 18-03-2026 10:30 | 253.4387 | 223.4783 | 29.9604 | 1340.8698 | 353.4 | 220.2826 | 133.1174
18-03-2026 10:20 | 558 | 48.79 | 226.439 | 228.395 | 423.4 | 38.0658 | 33.2269 | 4.8389 | 199.3616 | 39.1 | 32.7518 | 6.3482 | 0.99144 | 18-03-2026 10:20 | 319.641 | 324.739 | 421.3 | 54.1232 | 33.2269 | 20.8962 | 199.3616 | 39.4 | 32.7518 | 6.6482 | 0.9843 | 18-03-2026 10:20 | 201.947 | 205.31 | 419 | 34.2183 | 33.2269 | 0.9914 | 199.3616 | 38.7 | 32.7518 | 5.9482 | 0.98362 | 18-03-2026 10:20 | 192.797 | 195.554 | 422.1 | 32.5923 | 33.2269 | -0.6346 | 199.3616 | 39.8 | 32.7518 | 7.0482 | 0.9859 | 18-03-2026 10:20 | 156.587 | 158.714 | 316.1 | 26.4523 | 24.6125 | 1.8398 | 147.6753 | 29.5 | 24.2606 | 5.2394 | 0.9866 | 18-03-2026 10:20 | 155.026 | 158.202 | 315.3 | 26.367 | 24.6125 | 1.7545 | 147.6753 | 29.5 | 24.2606 | 5.2394 | 0.97992 | 18-03-2026 10:20 | 177.56 | 179.99 | 317.5 | 29.9983 | 24.6125 | 5.3858 | 147.6753 | 29.5 | 24.2606 | 5.2394 | 0.9865 | 18-03-2026 10:20 | 161.375 | 167.222 | 318.8 | 27.8703 | 24.6125 | 3.2578 | 147.6753 | 29.4 | 24.2606 | 5.1394 | 0.96503 | 18-03-2026 10:20 | 150.966 | 152.97 | 299.8 | 25.495 | 23.4158 | 2.0792 | 140.4947 | 27.7 | 23.0809 | 4.6191 | 0.9869 | 18-03-2026 10:20 | 295.1827 | 254.7737 | 40.409 | 1528.6422 | 302.6 | 251.1304 | 51.4696
18-03-2026 10:10 | 585 | 48.79 | 191.592 | 194.234 | 384.3 | 32.3723 | 34.8347 | -2.4624 | 209.0081 | 36.3 | 34.3366 | 1.9634 | 0.9864 | 18-03-2026 10:10 | 187.198 | 192.783 | 381.9 | 32.1305 | 34.8347 | -2.7042 | 209.0081 | 37.6 | 34.3366 | 3.2634 | 0.97103 | 18-03-2026 10:10 | 175.773 | 182.334 | 380.3 | 30.389 | 34.8347 | -4.4457 | 209.0081 | 37.5 | 34.3366 | 3.1634 | 0.96402 | 18-03-2026 10:10 | 163.571 | 165.86 | 382.3 | 27.6433 | 34.8347 | -7.1914 | 209.0081 | 37.1 | 34.3366 | 2.7634 | 0.9862 | 18-03-2026 10:10 | 134.638 | 136.384 | 286.6 | 22.7307 | 25.8035 | -3.0728 | 154.8208 | 28.4 | 25.4345 | 2.9655 | 0.9872 | 18-03-2026 10:10 | 119.318 | 121.356 | 285.8 | 20.226 | 25.8035 | -5.5775 | 154.8208 | 28 | 25.4345 | 2.5655 | 0.98321 | 18-03-2026 10:10 | 141.448 | 144.857 | 288 | 24.1428 | 25.8035 | -1.6606 | 154.8208 | 28.5 | 25.4345 | 3.0655 | 0.97647 | 18-03-2026 10:10 | 125.448 | 131.921 | 289.4 | 21.9868 | 25.8035 | -3.8166 | 154.8208 | 28.4 | 25.4345 | 2.9655 | 0.95093 | 18-03-2026 10:10 | 109.341 | 110.792 | 272.1 | 18.4653 | 24.5488 | -6.0835 | 147.2929 | 26.6 | 24.1978 | 2.4022 | 0.9869 | 18-03-2026 10:10 | 230.0868 | 267.1015 | -37.0146 | 1602.6088 | 288.4 | 263.2819 | 25.1181
18-03-2026 10:00 | 557 | 48.5 | 214.964 | 218.359 | 348 | 36.3932 | 33.2041 | 3.1891 | 199.2247 | 36.4 | 32.7293 | 3.6707 | 0.98445 | 18-03-2026 10:00 | 216.222 | 219.27 | 344.3 | 36.545 | 33.2041 | 3.3409 | 199.2247 | 36.7 | 32.7293 | 3.9707 | 0.9861 | 18-03-2026 10:00 | 176.379 | 181.149 | 342.8 | 30.1915 | 33.2041 | -3.0126 | 199.2247 | 37.1 | 32.7293 | 4.3707 | 0.97367 | 18-03-2026 10:00 | 170.639 | 172.957 | 345.2 | 28.8262 | 33.2041 | -4.3779 | 199.2247 | 36.7 | 32.7293 | 3.9707 | 0.9866 | 18-03-2026 10:00 | 112.991 | 114.993 | 258.2 | 19.1655 | 24.5956 | -5.4301 | 147.5738 | 27.7 | 24.2439 | 3.4561 | 0.98259 | 18-03-2026 10:00 | 108.157 | 109.593 | 257.8 | 18.2655 | 24.5956 | -6.3301 | 147.5738 | 27.6 | 24.2439 | 3.3561 | 0.9869 | 18-03-2026 10:00 | 108.332 | 110.482 | 259.5 | 18.4137 | 24.5956 | -6.182 | 147.5738 | 27.7 | 24.2439 | 3.4561 | 0.98054 | 18-03-2026 10:00 | 106.145 | 109.676 | 261 | 18.2793 | 24.5956 | -6.3163 | 147.5738 | 27.7 | 24.2439 | 3.4561 | 0.96781 | 18-03-2026 10:00 | 99.541 | 100.873 | 245.5 | 16.8122 | 23.3997 | -6.5875 | 140.3982 | 26.3 | 23.0651 | 3.2349 | 0.9868 | 18-03-2026 10:00 | 222.892 | 254.5987 | -31.7067 | 1527.5922 | 283.9 | 250.9579 | 32.9421
18-03-2026 09:50 | 764 | 48.79 | 269.563 | 276.42 | 311.6 | 46.07 | 45.4935 | 0.57649 | 272.9611 | 42.3 | 44.843 | -2.543 |  | 18-03-2026 09:50 | 268.244 | 274.472 | 307.6 | 45.7453 | 45.4935 | 0.25182 | 272.9611 | 40.4 | 44.843 | -4.443 |  | 18-03-2026 09:50 | 266.776 | 273.099 | 305.7 | 45.5165 | 45.4935 | 0.02299 | 272.9611 | 40.4 | 44.843 | -4.443 |  | 18-03-2026 09:50 | 269.093 | 273.219 | 308.5 | 45.5365 | 45.4935 | 0.04299 | 272.9611 | 41.3 | 44.843 | -3.543 |  | 18-03-2026 09:50 | 201.707 | 204.509 | 230.5 | 34.0848 | 33.6989 | 0.38594 | 202.1934 | 30.9 | 33.217 | -2.317 |  | 18-03-2026 09:50 | 200.481 | 203.527 | 230.2 | 33.9212 | 33.6989 | 0.22227 | 202.1934 | 30.7 | 33.217 | -2.517 |  | 18-03-2026 09:50 | 201.028 | 204.423 | 231.8 | 34.0705 | 33.6989 | 0.3716 | 202.1934 | 30.8 | 33.217 | -2.417 |  | 18-03-2026 09:50 | 201.935 | 207.411 | 233.3 | 34.5685 | 33.6989 | 0.8696 | 202.1934 | 31 | 33.217 | -2.217 |  | 18-03-2026 09:50 | 190.206 | 192.868 | 219.2 | 32.1447 | 32.0603 | 0.084341 | 192.362 | 29.2 | 31.6019 | -2.4019 |  | 18-03-2026 09:50 | 351.658 | 348.83 | 2.828 | 2092.9797 | 317 | 343.8417 | -26.8417
18-03-2026 09:40 | 645 | 48.5 | 230.411 | 233.938 | 269.3 | 38.9897 | 38.45 | 0.53966 | 230.7 | 36.1 | 37.9002 | -1.8002 |  | 18-03-2026 09:40 | 230.551 | 233.896 | 267.2 | 38.9827 | 38.45 | 0.53266 | 230.7 | 37.9 | 37.9002 | -0.00016819 |  | 18-03-2026 09:40 | 226.582 | 231.647 | 265.3 | 38.6078 | 38.45 | 0.15783 | 230.7 | 35.8 | 37.9002 | -2.1002 |  | 18-03-2026 09:40 | 229.425 | 232.73 | 267.2 | 38.7883 | 38.45 | 0.33833 | 230.7 | 36.3 | 37.9002 | -1.6002 |  | 18-03-2026 09:40 | 170.766 | 173.068 | 199.6 | 28.8447 | 28.4815 | 0.36318 | 170.8889 | 27.4 | 28.0742 | -0.6742 |  | 18-03-2026 09:40 | 170.679 | 172.98 | 199.5 | 28.83 | 28.4815 | 0.34852 | 170.8889 | 27.4 | 28.0742 | -0.6742 |  | 18-03-2026 09:40 | 170.563 | 173.029 | 201 | 28.8382 | 28.4815 | 0.35668 | 170.8889 | 27.4 | 28.0742 | -0.6742 |  | 18-03-2026 09:40 | 171.603 | 176.251 | 202.3 | 29.3752 | 28.4815 | 0.89368 | 170.8889 | 27.6 | 28.0742 | -0.4742 |  | 18-03-2026 09:40 | 162.054 | 164.238 | 190 | 27.373 | 27.0966 | 0.2764 | 162.5796 | 26 | 26.7091 | -0.70912 |  | 18-03-2026 09:40 | 298.6295 | 294.8226 | 3.8069 | 1768.9353 | 281.9 | 290.6066 | -8.7066
18-03-2026 09:30 | 595 | 48.79 | 214.851 | 217.747 | 233.2 | 36.2912 | 35.4302 | 0.86101 | 212.5809 | 33.5 | 34.9235 | -1.4235 |  | 18-03-2026 09:30 | 212.35 | 215.278 | 229.3 | 35.8797 | 35.4302 | 0.44951 | 212.5809 | 32.7 | 34.9235 | -2.2235 |  | 18-03-2026 09:30 | 210.939 | 215.353 | 229.5 | 35.8922 | 35.4302 | 0.46201 | 212.5809 | 33 | 34.9235 | -1.9235 |  | 18-03-2026 09:30 | 213.672 | 216.618 | 230.9 | 36.103 | 35.4302 | 0.67285 | 212.5809 | 33.7 | 34.9235 | -1.2235 |  | 18-03-2026 09:30 | 158.466 | 160.537 | 172.2 | 26.7562 | 26.2446 | 0.51161 | 157.4674 | 24.8 | 25.8693 | -1.0693 |  | 18-03-2026 09:30 | 158.638 | 160.695 | 172.1 | 26.7825 | 26.2446 | 0.53794 | 157.4674 | 24.7 | 25.8693 | -1.1693 |  | 18-03-2026 09:30 | 158.071 | 160.274 | 173.6 | 26.7123 | 26.2446 | 0.46777 | 157.4674 | 24.8 | 25.8693 | -1.0693 |  | 18-03-2026 09:30 | 159.383 | 163.599 | 174.7 | 27.2665 | 26.2446 | 1.0219 | 157.4674 | 24.9 | 25.8693 | -0.96926 |  | 18-03-2026 09:30 | 150.75 | 152.705 | 164 | 25.4508 | 24.9684 | 0.48239 | 149.8107 | 23.5 | 24.6114 | -1.1114 |  | 18-03-2026 09:30 | 277.1343 | 271.6673 | 5.467 | 1630.0038 | 255.6 | 267.7825 | -12.1825
18-03-2026 09:20 | 471 | 47.93 | 177.242 | 179.486 | 199.7 | 29.9143 | 28.1385 | 1.7759 | 168.8309 | 28 | 27.7361 | 0.2639 |  | 18-03-2026 09:20 | 173.32 | 175.585 | 196.6 | 29.2642 | 28.1385 | 1.1257 | 168.8309 | 26.9 | 27.7361 | -0.8361 |  | 18-03-2026 09:20 | 174.27 | 177.229 | 196.5 | 29.5382 | 28.1385 | 1.3997 | 168.8309 | 27.6 | 27.7361 | -0.1361 |  | 18-03-2026 09:20 | 172.192 | 174.425 | 197.2 | 29.0708 | 28.1385 | 0.93235 | 168.8309 | 26.5 | 27.7361 | -1.2361 |  | 18-03-2026 09:20 | 132.978 | 134.634 | 147.4 | 22.439 | 20.8433 | 1.5957 | 125.0599 | 20.9 | 20.5453 | 0.35474 |  | 18-03-2026 09:20 | 130.842 | 132.471 | 147.4 | 22.0785 | 20.8433 | 1.2352 | 125.0599 | 20.2 | 20.5453 | -0.34526 |  | 18-03-2026 09:20 | 133.784 | 135.561 | 148.8 | 22.5935 | 20.8433 | 1.7502 | 125.0599 | 21 | 20.5453 | 0.45474 |  | 18-03-2026 09:20 | 134.715 | 138.217 | 149.8 | 23.0362 | 20.8433 | 2.1928 | 125.0599 | 20.9 | 20.5453 | 0.35474 |  | 18-03-2026 09:20 | 125.846 | 127.439 | 140.5 | 21.2398 | 19.8298 | 1.41 | 118.979 | 19.2 | 19.5463 | -0.34627 |  | 18-03-2026 09:20 | 229.1745 | 215.757 | 13.4175 | 1294.5421 | 211.2 | 212.6717 | -1.4717
18-03-2026 09:10 | 340 | 47.35 | 137.141 | 137.07 | 171.7 | 22.845 | 20.3571 | 2.4879 | 122.1427 | 25.6 | 20.066 | 5.534 |  | 18-03-2026 09:10 | 140.509 | 141.474 | 169.7 | 23.579 | 20.3571 | 3.2219 | 122.1427 | 24.6 | 20.066 | 4.534 |  | 18-03-2026 09:10 | 128.044 | 129.906 | 168.9 | 21.651 | 20.3571 | 1.2939 | 122.1427 | 25.5 | 20.066 | 5.434 |  | 18-03-2026 09:10 | 125.623 | 127.2 | 170.7 | 21.2 | 20.3571 | 0.84289 | 122.1427 | 24.8 | 20.066 | 4.734 |  | 18-03-2026 09:10 | 100.542 | 101.794 | 126.5 | 16.9657 | 15.0793 | 1.8863 | 90.476 | 19.5 | 14.8637 | 4.6363 |  | 18-03-2026 09:10 | 96.06 | 97.237 | 127.2 | 16.2062 | 15.0793 | 1.1268 | 90.476 | 18.8 | 14.8637 | 3.9363 |  | 18-03-2026 09:10 | 100.471 | 101.702 | 127.8 | 16.9503 | 15.0793 | 1.871 | 90.476 | 19.5 | 14.8637 | 4.6363 |  | 18-03-2026 09:10 | 100.186 | 102.654 | 128.9 | 17.109 | 15.0793 | 2.0297 | 90.476 | 19.5 | 14.8637 | 4.6363 |  | 18-03-2026 09:10 | 90.147 | 91.142 | 121.3 | 15.1903 | 14.3461 | 0.84421 | 86.0767 | 17.8 | 14.141 | 3.659 |  | 18-03-2026 09:10 | 171.6965 | 156.0919 | 15.6046 | 936.5516 | 195.6 | 153.8598 | 41.7402
18-03-2026 09:00 | 457 | 45.92 | 166.175 | 168.261 | 146.1 | 28.0435 | 27.5109 | 0.53258 | 165.0655 | 26.3 | 27.1175 | -0.81751 |  | 18-03-2026 09:00 | 163.856 | 165.93 | 145.1 | 27.655 | 27.5109 | 0.14408 | 165.0655 | 25.3 | 27.1175 | -1.8175 |  | 18-03-2026 09:00 | 162.607 | 165.583 | 143.4 | 27.5972 | 27.5109 | 0.086246 | 165.0655 | 25.4 | 27.1175 | -1.7175 |  | 18-03-2026 09:00 | 165.156 | 167.23 | 145.9 | 27.8717 | 27.5109 | 0.36075 | 165.0655 | 25.5 | 27.1175 | -1.6175 |  | 18-03-2026 09:00 | 122.343 | 123.796 | 107 | 20.6327 | 20.3785 | 0.25421 | 122.2708 | 19.1 | 20.087 | -0.98705 |  | 18-03-2026 09:00 | 123.086 | 124.594 | 108.4 | 20.7657 | 20.3785 | 0.38721 | 122.2708 | 19.3 | 20.087 | -0.78705 |  | 18-03-2026 09:00 | 122.941 | 124.447 | 108.3 | 20.7412 | 20.3785 | 0.36271 | 122.2708 | 19.2 | 20.087 | -0.88705 |  | 18-03-2026 09:00 | 123.936 | 127.1 | 109.4 | 21.1833 | 20.3785 | 0.80487 | 122.2708 | 19.4 | 20.087 | -0.68705 |  | 18-03-2026 09:00 | 117.213 | 118.673 | 103.5 | 19.7788 | 19.3876 | 0.39125 | 116.3255 | 18.4 | 19.1103 | -0.71034 |  | 18-03-2026 09:00 | 214.269 | 210.9451 | 3.3239 | 1265.6706 | 197.9 | 207.9286 | -10.0286
18-03-2026 08:50 | 382 | 43.62 | 138.152 | 139.816 | 119.8 | 23.3027 | 23.1957 | 0.10692 | 139.1745 | 21.5 | 22.864 | -1.364 |  | 18-03-2026 08:50 | 135.75 | 139.36 | 119.8 | 23.2267 | 23.1957 | 0.030924 | 139.1745 | 22.9 | 22.864 | 0.035957 |  | 18-03-2026 08:50 | 136.503 | 138.783 | 118 | 23.1305 | 23.1957 | -0.065242 | 139.1745 | 21.5 | 22.864 | -1.364 |  | 18-03-2026 08:50 | 136.971 | 139.404 | 120.4 | 23.234 | 23.1957 | 0.038258 | 139.1745 | 22.2 | 22.864 | -0.66404 |  | 18-03-2026 08:50 | 101.848 | 103.075 | 87.9 | 17.1792 | 17.182 | -0.0028647 | 103.0922 | 16.1 | 16.9363 | -0.83633 |  | 18-03-2026 08:50 | 102.015 | 103.212 | 89.1 | 17.202 | 17.182 | 0.019969 | 103.0922 | 16.2 | 16.9363 | -0.73633 |  | 18-03-2026 08:50 | 102.591 | 103.712 | 89.1 | 17.2853 | 17.182 | 0.1033 | 103.0922 | 16.3 | 16.9363 | -0.63633 |  | 18-03-2026 08:50 | 103.071 | 105.965 | 90 | 17.6608 | 17.182 | 0.4788 | 103.0922 | 16.3 | 16.9363 | -0.63633 |  | 18-03-2026 08:50 | 97.034 | 98.193 | 85.1 | 16.3655 | 16.3466 | 0.018925 | 98.0794 | 15.4 | 16.1128 | -0.71282 |  | 18-03-2026 08:50 | 178.5867 | 177.8577 | 0.729 | 1067.146 | 168.4 | 175.3143 | -6.9143
18-03-2026 08:40 | 364 | 43.05 | 130.646 | 132.206 | 98.3 | 22.0343 | 22.1499 | -0.11558 | 132.8995 | 20.7 | 21.8332 | -1.1332 |  | 18-03-2026 08:40 | 128.771 | 131.443 | 96.9 | 21.9072 | 22.1499 | -0.24275 | 132.8995 | 19.7 | 21.8332 | -2.1332 |  | 18-03-2026 08:40 | 128.222 | 130.206 | 96.5 | 21.701 | 22.1499 | -0.44892 | 132.8995 | 20.2 | 21.8332 | -1.6332 |  | 18-03-2026 08:40 | 130.62 | 132.206 | 98.2 | 22.0343 | 22.1499 | -0.11558 | 132.8995 | 20.3 | 21.8332 | -1.5332 |  | 18-03-2026 08:40 | 96.103 | 97.241 | 71.8 | 16.2068 | 16.4073 | -0.20051 | 98.4441 | 14.9 | 16.1727 | -1.2727 |  | 18-03-2026 08:40 | 97.193 | 98.334 | 72.9 | 16.389 | 16.4073 | -0.018347 | 98.4441 | 15.4 | 16.1727 | -0.77272 |  | 18-03-2026 08:40 | 96.717 | 97.862 | 72.8 | 16.3103 | 16.4073 | -0.097014 | 98.4441 | 15.2 | 16.1727 | -0.97272 |  | 18-03-2026 08:40 | 97.383 | 99.861 | 73.7 | 16.6435 | 16.4073 | 0.23615 | 98.4441 | 15.4 | 16.1727 | -0.77272 |  | 18-03-2026 08:40 | 92.34 | 93.424 | 69.7 | 15.5707 | 15.6096 | -0.038892 | 93.6574 | 14.6 | 15.3863 | -0.78634 |  | 18-03-2026 08:40 | 168.7972 | 169.8386 | -1.0415 | 1019.0317 | 156.4 | 167.4099 | -11.0099
18-03-2026 08:30 | 325 | 41.61 | 115.871 | 117.219 | 77.6 | 19.5365 | 19.8831 | -0.34661 | 119.2987 | 18.1 | 19.5988 | -1.4988 |  | 18-03-2026 08:30 | 114.85 | 116.276 | 77.2 | 19.3793 | 19.8831 | -0.50378 | 119.2987 | 17.6 | 19.5988 | -1.9988 |  | 18-03-2026 08:30 | 113.683 | 115.455 | 76.3 | 19.2425 | 19.8831 | -0.64061 | 119.2987 | 17.6 | 19.5988 | -1.9988 |  | 18-03-2026 08:30 | 116.252 | 117.629 | 77.9 | 19.6048 | 19.8831 | -0.27828 | 119.2987 | 18 | 19.5988 | -1.5988 |  | 18-03-2026 08:30 | 85.089 | 86.105 | 56.9 | 14.3508 | 14.7282 | -0.3774 | 88.3694 | 13.2 | 14.5176 | -1.3176 |  | 18-03-2026 08:30 | 86.487 | 87.502 | 57.5 | 14.5837 | 14.7282 | -0.14456 | 88.3694 | 13.2 | 14.5176 | -1.3176 |  | 18-03-2026 08:30 | 85.857 | 86.9 | 57.6 | 14.4833 | 14.7282 | -0.2449 | 88.3694 | 13.3 | 14.5176 | -1.2176 |  | 18-03-2026 08:30 | 86.638 | 89.084 | 58.3 | 14.8473 | 14.7282 | 0.1191 | 88.3694 | 13.4 | 14.5176 | -1.1176 |  | 18-03-2026 08:30 | 82.183 | 83.19 | 55.1 | 13.865 | 14.0121 | -0.14709 | 84.0725 | 12.7 | 13.8117 | -1.1117 |  | 18-03-2026 08:30 | 149.8933 | 152.4574 | -2.5641 | 914.7446 | 137.1 | 150.2773 | -13.1773
18-03-2026 08:20 | 282 | 39.89 | 98.952 | 100.073 | 59.5 | 16.6788 | 17.3627 | -0.68386 | 104.1761 | 14.8 | 17.1144 | -2.3144 |  | 18-03-2026 08:20 | 98.66 | 100.215 | 59.6 | 16.7025 | 17.3627 | -0.66019 | 104.1761 | 15.3 | 17.1144 | -1.8144 |  | 18-03-2026 08:20 | 97.312 | 98.627 | 58.7 | 16.4378 | 17.3627 | -0.92486 | 104.1761 | 14.8 | 17.1144 | -2.3144 |  | 18-03-2026 08:20 | 99.705 | 100.857 | 59.9 | 16.8095 | 17.3627 | -0.55319 | 104.1761 | 15.4 | 17.1144 | -1.7144 |  | 18-03-2026 08:20 | 73.005 | 73.922 | 43.7 | 12.3203 | 12.8613 | -0.54092 | 77.1675 | 11.3 | 12.6773 | -1.3773 |  | 18-03-2026 08:20 | 74.393 | 75.306 | 44.3 | 12.551 | 12.8613 | -0.31025 | 77.1675 | 11.5 | 12.6773 | -1.1773 |  | 18-03-2026 08:20 | 73.684 | 74.592 | 44.3 | 12.432 | 12.8613 | -0.42925 | 77.1675 | 11.2 | 12.6773 | -1.4773 |  | 18-03-2026 08:20 | 74.487 | 76.647 | 44.9 | 12.7745 | 12.8613 | -0.086752 | 77.1675 | 11.4 | 12.6773 | -1.2773 |  | 18-03-2026 08:20 | 70.503 | 71.395 | 42.4 | 11.8992 | 12.2359 | -0.33672 | 73.4153 | 10.8 | 12.0609 | -1.2609 |  | 18-03-2026 08:20 | 128.6057 | 133.1317 | -4.526 | 798.79 | 116.5 | 131.2279 | -14.7279
18-03-2026 08:10 | 239 | 33 | 81.453 | 83.856 | 44.7 | 13.976 | 15.0896 | -1.1136 | 90.5373 | 12.8 | 14.8738 | -2.0738 |  | 18-03-2026 08:10 | 82.775 | 83.78 | 44.3 | 13.9633 | 15.0896 | -1.1262 | 90.5373 | 12.5 | 14.8738 | -2.3738 |  | 18-03-2026 08:10 | 81.514 | 82.487 | 43.9 | 13.7478 | 15.0896 | -1.3417 | 90.5373 | 12.5 | 14.8738 | -2.3738 |  | 18-03-2026 08:10 | 83.229 | 84.231 | 44.5 | 14.0385 | 15.0896 | -1.0511 | 90.5373 | 12.5 | 14.8738 | -2.3738 |  | 18-03-2026 08:10 | 60.844 | 61.611 | 32.4 | 10.2685 | 11.1774 | -0.90895 | 67.0647 | 9.1 | 11.0176 | -1.9176 |  | 18-03-2026 08:10 | 62.217 | 63.011 | 32.8 | 10.5018 | 11.1774 | -0.67561 | 67.0647 | 9.4 | 11.0176 | -1.6176 |  | 18-03-2026 08:10 | 61.781 | 62.56 | 33.1 | 10.4267 | 11.1774 | -0.75078 | 67.0647 | 9.5 | 11.0176 | -1.5176 |  | 18-03-2026 08:10 | 62.489 | 64.42 | 33.5 | 10.7367 | 11.1774 | -0.44078 | 67.0647 | 9.6 | 11.0176 | -1.4176 |  | 18-03-2026 08:10 | 59.267 | 60.072 | 31.6 | 10.012 | 10.634 | -0.62196 | 63.8037 | 9.1 | 10.4819 | -1.3819 |  | 18-03-2026 08:10 | 107.6713 | 115.702 | -8.0306 | 694.2118 | 97 | 114.0474 | -17.0474
18-03-2026 08:00 | 199 | 30.42 | 67.525 | 68.366 | 31.9 | 11.3943 | 12.6808 | -1.2865 | 76.085 | 10.2 | 12.4995 | -2.2995 |  | 18-03-2026 08:00 | 65.871 | 68.626 | 31.8 | 11.4377 | 12.6808 | -1.2432 | 76.085 | 10.1 | 12.4995 | -2.3995 |  | 18-03-2026 08:00 | 66.847 | 67.693 | 31.4 | 11.2822 | 12.6808 | -1.3987 | 76.085 | 10 | 12.4995 | -2.4995 |  | 18-03-2026 08:00 | 68.329 | 69.194 | 32 | 11.5323 | 12.6808 | -1.1485 | 76.085 | 10.2 | 12.4995 | -2.2995 |  | 18-03-2026 08:00 | 49.948 | 50.678 | 23.3 | 8.4463 | 9.3932 | -0.94687 | 56.3592 | 7.5 | 9.2589 | -1.7589 |  | 18-03-2026 08:00 | 51.144 | 51.87 | 23.4 | 8.645 | 9.3932 | -0.74821 | 56.3592 | 7.7 | 9.2589 | -1.5589 |  | 18-03-2026 08:00 | 50.756 | 51.492 | 23.6 | 8.582 | 9.3932 | -0.81121 | 56.3592 | 7.6 | 9.2589 | -1.6589 |  | 18-03-2026 08:00 | 51.376 | 52.952 | 23.9 | 8.8253 | 9.3932 | -0.56787 | 56.3592 | 7.6 | 9.2589 | -1.6589 |  | 18-03-2026 08:00 | 48.688 | 49.404 | 22.5 | 8.234 | 8.9365 | -0.70247 | 53.6188 | 7.2 | 8.8087 | -1.6087 |  | 18-03-2026 08:00 | 88.3792 | 97.2326 | -8.8534 | 583.3957 | 78.1 | 95.8422 | -17.7422
18-03-2026 07:50 | 161 | 29.27 | 53.452 | 54.189 | 21.7 | 9.0315 | 10.3015 | -1.27 | 61.8087 | 7.7 | 10.1541 | -2.4541 |  | 18-03-2026 07:50 | 53.795 | 54.57 | 21.7 | 9.095 | 10.3015 | -1.2065 | 61.8087 | 8 | 10.1541 | -2.1541 |  | 18-03-2026 07:50 | 52.942 | 53.683 | 21.4 | 8.9472 | 10.3015 | -1.3543 | 61.8087 | 7.8 | 10.1541 | -2.3541 |  | 18-03-2026 07:50 | 54.112 | 54.88 | 21.8 | 9.1467 | 10.3015 | -1.1548 | 61.8087 | 8 | 10.1541 | -2.1541 |  | 18-03-2026 07:50 | 39.489 | 40.131 | 15.8 | 6.6885 | 7.6307 | -0.94221 | 45.7843 | 5.8 | 7.5216 | -1.7216 |  | 18-03-2026 07:50 | 40.375 | 41.007 | 15.7 | 6.8345 | 7.6307 | -0.79621 | 45.7843 | 5.9 | 7.5216 | -1.6216 |  | 18-03-2026 07:50 | 40.183 | 40.824 | 16 | 6.804 | 7.6307 | -0.82671 | 45.7843 | 5.8 | 7.5216 | -1.7216 |  | 18-03-2026 07:50 | 40.653 | 41.785 | 16.3 | 6.9642 | 7.6307 | -0.66654 | 45.7843 | 6 | 7.5216 | -1.5216 |  | 18-03-2026 07:50 | 38.443 | 39.06 | 15.3 | 6.51 | 7.2597 | -0.74967 | 43.558 | 5.7 | 7.1559 | -1.4559 |  | 18-03-2026 07:50 | 70.0215 | 78.9883 | -8.9668 | 473.93 | 60.7 | 77.8588 | -17.1588
18-03-2026 07:40 | 123 | 28.13 | 40.896 | 41.531 | 14 | 6.9218 | 7.9019 | -0.9801 | 47.4116 | 5.9 | 7.7889 | -1.8889 |  | 18-03-2026 07:40 | 39.594 | 40.63 | 13.7 | 6.7717 | 7.9019 | -1.1303 | 47.4116 | 5.6 | 7.7889 | -2.1889 |  | 18-03-2026 07:40 | 39.786 | 40.425 | 13.6 | 6.7375 | 7.9019 | -1.1644 | 47.4116 | 5.6 | 7.7889 | -2.1889 |  | 18-03-2026 07:40 | 40.558 | 41.209 | 13.8 | 6.8682 | 7.9019 | -1.0338 | 47.4116 | 5.7 | 7.7889 | -2.0889 |  | 18-03-2026 07:40 | 29.557 | 30.099 | 10 | 5.0165 | 5.8533 | -0.83678 | 35.1197 | 4.2 | 5.7696 | -1.5696 |  | 18-03-2026 07:40 | 30.348 | 30.873 | 9.8 | 5.1455 | 5.8533 | -0.70778 | 35.1197 | 4.2 | 5.7696 | -1.5696 |  | 18-03-2026 07:40 | 30.204 | 30.733 | 10.2 | 5.1222 | 5.8533 | -0.73112 | 35.1197 | 4.3 | 5.7696 | -1.4696 |  | 18-03-2026 07:40 | 30.431 | 31.462 | 10.3 | 5.2437 | 5.8533 | -0.60962 | 35.1197 | 4.3 | 5.7696 | -1.4696 |  | 18-03-2026 07:40 | 28.801 | 29.329 | 9.6 | 4.8882 | 5.5687 | -0.68051 | 33.4121 | 4 | 5.489 | -1.489 |  | 18-03-2026 07:40 | 52.7152 | 60.5896 | -7.8744 | 363.5373 | 43.8 | 59.7231 | -15.9231
18-03-2026 07:30 | 88 | 26.69 | 28.847 | 29.376 | 8.1 | 4.896 | 5.6822 | -0.78623 | 34.0934 | 3.9 | 5.601 | -1.701 |  | 18-03-2026 07:30 | 28.537 | 29.084 | 8.1 | 4.8473 | 5.6822 | -0.83489 | 34.0934 | 3.9 | 5.601 | -1.701 |  | 18-03-2026 07:30 | 28.397 | 28.922 | 8 | 4.8203 | 5.6822 | -0.86189 | 34.0934 | 3.9 | 5.601 | -1.701 |  | 18-03-2026 07:30 | 28.703 | 29.247 | 8.1 | 4.8745 | 5.6822 | -0.80773 | 34.0934 | 3.9 | 5.601 | -1.701 |  | 18-03-2026 07:30 | 20.894 | 21.471 | 5.8 | 3.5785 | 4.2091 | -0.63056 | 25.2543 | 2.9 | 4.1489 | -1.2489 |  | 18-03-2026 07:30 | 20.346 | 20.808 | 5.6 | 3.468 | 4.2091 | -0.74106 | 25.2543 | 2.8 | 4.1489 | -1.3489 |  | 18-03-2026 07:30 | 21.34 | 21.825 | 5.9 | 3.6375 | 4.2091 | -0.57156 | 25.2543 | 2.9 | 4.1489 | -1.2489 |  | 18-03-2026 07:30 | 21.741 | 22.505 | 6 | 3.7508 | 4.2091 | -0.45822 | 25.2543 | 3 | 4.1489 | -1.1489 |  | 18-03-2026 07:30 | 20.263 | 20.727 | 5.6 | 3.4545 | 4.0044 | -0.5499 | 24.0264 | 2.8 | 3.9471 | -1.1471 |  | 18-03-2026 07:30 | 37.3275 | 43.5695 | -6.242 | 261.4171 | 30 | 42.9465 | -12.9465
18-03-2026 07:20 | 50 | 24.68 | 18.621 | 19.065 | 4.2 | 3.1775 | 3.2514 | -0.073885 | 19.5083 | 2.4 | 3.2049 | -0.80489 |  | 18-03-2026 07:20 | 17.687 | 18.541 | 4.2 | 3.0902 | 3.2514 | -0.16122 | 19.5083 | 2.4 | 3.2049 | -0.80489 |  | 18-03-2026 07:20 | 18.527 | 18.977 | 4.1 | 3.1628 | 3.2514 | -0.088552 | 19.5083 | 2.4 | 3.2049 | -0.80489 |  | 18-03-2026 07:20 | 18.662 | 19.24 | 4.2 | 3.2067 | 3.2514 | -0.044718 | 19.5083 | 2.5 | 3.2049 | -0.70489 |  | 18-03-2026 07:20 | 13.46 | 13.89 | 2.9 | 2.315 | 2.4084 | -0.093433 | 14.4506 | 1.7 | 2.374 | -0.67399 |  | 18-03-2026 07:20 | 13.042 | 13.437 | 2.8 | 2.2395 | 2.4084 | -0.16893 | 14.4506 | 1.6 | 2.374 | -0.77399 |  | 18-03-2026 07:20 | 13.68 | 14.063 | 3 | 2.3438 | 2.4084 | -0.0646 | 14.4506 | 1.8 | 2.374 | -0.57399 |  | 18-03-2026 07:20 | 13.978 | 14.65 | 3 | 2.4417 | 2.4084 | 0.033233 | 14.4506 | 1.7 | 2.374 | -0.67399 |  | 18-03-2026 07:20 | 13 | 13.394 | 2.8 | 2.2323 | 2.2913 | -0.058993 | 13.748 | 1.7 | 2.2586 | -0.55856 |  | 18-03-2026 07:20 | 24.2095 | 24.9306 | -0.7211 | 149.5836 | 18.2 | 24.5741 | -6.3741
18-03-2026 07:10 | 29 | 24.11 | 10.768 | 11.144 | 1.8 | 1.8573 | 1.8896 | -0.032228 | 11.3374 | 1.3 | 1.8625 | -0.56254 |  | 18-03-2026 07:10 | 10.614 | 11.447 | 1.8 | 1.9078 | 1.8896 | 0.018272 | 11.3374 | 1.3 | 1.8625 | -0.56254 |  | 18-03-2026 07:10 | 10.524 | 10.9 | 1.7 | 1.8167 | 1.8896 | -0.072895 | 11.3374 | 1.2 | 1.8625 | -0.66254 |  | 18-03-2026 07:10 | 10.609 | 11.3 | 1.7 | 1.8833 | 1.8896 | -0.006228 | 11.3374 | 1.2 | 1.8625 | -0.66254 |  | 18-03-2026 07:10 | 7.68 | 8.29 | 1.2 | 1.3817 | 1.3997 | -0.018008 | 8.3981 | 0.9 | 1.3797 | -0.47966 |  | 18-03-2026 07:10 | 7.363 | 7.658 | 1.2 | 1.2763 | 1.3997 | -0.12334 | 8.3981 | 0.9 | 1.3797 | -0.47966 |  | 18-03-2026 07:10 | 7.812 | 8.131 | 1.2 | 1.3552 | 1.3997 | -0.044508 | 8.3981 | 0.9 | 1.3797 | -0.47966 |  | 18-03-2026 07:10 | 7.938 | 8.535 | 1.3 | 1.4225 | 1.3997 | 0.022825 | 8.3981 | 1 | 1.3797 | -0.37966 |  | 18-03-2026 07:10 | 7.349 | 7.654 | 1.1 | 1.2757 | 1.3316 | -0.055951 | 7.9897 | 0.8 | 1.3126 | -0.51258 |  | 18-03-2026 07:10 | 14.1765 | 14.4886 | -0.31206 | 86.9314 | 9.5 | 14.2814 | -4.7814
|  |  | 4.898 | 5.127 | 0.5 | 0.8545 | 0 | 0.8545 | 0 | 0.5 | 0 | 0.5 |  | 18-03-2026 07:00 | 5.038 | 5.823 | 0.5 | 0.9705 | 0 | 0.9705 | 0 | 0.5 | 0 | 0.5 |  | 18-03-2026 07:00 | 4.798 | 5.052 | 0.5 | 0.842 | 0 | 0.842 | 0 | 0.5 | 0 | 0.5 |  | 18-03-2026 07:00 | 4.921 | 5.61 | 0.5 | 0.935 | 0 | 0.935 | 0 | 0.5 | 0 | 0.5 |  | 18-03-2026 07:00 | 3.445 | 4.089 | 0.3 | 0.6815 | 0 | 0.6815 | 0 | 0.3 | 0 | 0.3 |  | 18-03-2026 07:00 | 3.28 | 3.446 | 0.3 | 0.57433 | 0 | 0.57433 | 0 | 0.3 | 0 | 0.3 |  | 18-03-2026 07:00 | 3.488 | 3.665 | 0.3 | 0.61083 | 0 | 0.61083 | 0 | 0.3 | 0 | 0.3 |  | 18-03-2026 07:00 | 3.56 | 4 | 0.3 | 0.66667 | 0 | 0.66667 | 0 | 0.3 | 0 | 0.3 |  | 18-03-2026 07:00 | 3.289 | 3.455 | 0.3 | 0.57583 | 0 | 0.57583 | 0 | 0.3 | 0 | 0.3 |  | 0 | 6.7112 | 0 | 6.7112 | 0 | 3.5 | 0 | 3.5
[110 empty] | Total: - | 14972.1255 | 15185.6648 | -213.5393 |  | 14909.4 | 14968.5098 | -59.1098
Sum:- | 33090 |  | 11770.27 |  | 78199.4 |  |  |  |  | 1940.8 | 1952.1548 | -11.3548 | 0.98109 |  | 11192.202 |  | 75143.3 |  |  |  |  | 1943.2 | 1952.1548 | -8.9548 | 1.0157 |  | 11239.557 |  | 77375.6 |  |  |  |  | 1920.8 | 1952.1548 | -31.3548 | 0.97484 |  | 11433.509 |  | 77995.9 |  |  |  |  | 1935.6 | 1952.1548 | -16.5548 | 0.98466 |  | 8553.737 |  | 58667.5 |  |  |  |  | 1455.5 | 1446.0406 | 9.4594 | 0.98448 |  | 8554.637 |  | 58255.7 |  |  |  |  | 1443.9 | 1446.0406 | -2.1406 | 0.98357 |  | 8556.164 |  | 58435.9 |  |  |  |  | 1446.3 | 1446.0406 | 0.25943 | 0.9821 |  | 8560.399 |  | 58735.2 |  |  |  |  | 1452.4 | 1446.0406 | 6.3594 | 0.9706 |  | 8115.411 |  | 55390.7 |  |  |  |  | 1370.9 | 1375.7285 | -4.8285 | 0.98482

## 19 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
19-03-2026 19:00 | 0 | 22.1 | 0 | 0 | 1849.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1833.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0.076 | 0.129 | 1849.2 | 0.0215 | 0 | 0.0215 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1381.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1371.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1380.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0 | 0 | 1307.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 19:00 | 0.0215 | 0 | 0.0215 | 0 | 0 | 0 | 0 | 1 | 99.26%
19-03-2026 18:50 | 0 | 25.54 | 0.097 | 0.109 | 1849.2 | 0.018167 | 0 | 0.018167 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0.088 | 0.162 | 1863.8 | 0.027 | 0 | 0.027 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0.069 | 0.076 | 1833.5 | 0.012667 | 0 | 0.012667 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0.066 | 0.19 | 1849.2 | 0.031667 | 0 | 0.031667 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0.083 | 0.087 | 1381.9 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0 | 0 | 1373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0 | 0 | 1371.8 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 19-03-2026 18:50 | 0.1 | 0.088 | 1380.9 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:50 | 0 | 0 | 1307.1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 19-03-2026 18:50 | 0.11867 | 0 | 0.11867 | 0 | 0.2 | 0 | 0.2 | 2 | 98.95%
19-03-2026 18:40 | 0 | 26.4 | 0.061 | 0.087 | 1849.2 | 0.0145 | 0 | 0.0145 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.003 | 0.348 | 1863.8 | 0.058 | 0 | 0.058 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.104 | 0.109 | 1833.5 | 0.018167 | 0 | 0.018167 | 0 | 0.1 | 0 | 0.1 |  | 19-03-2026 18:40 | 0.079 | 0.339 | 1849.2 | 0.0565 | 0 | 0.0565 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.089 | 0.094 | 1381.9 | 0.015667 | 0 | 0.015667 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.061 | 0.078 | 1373 | 0.013 | 0 | 0.013 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.053 | 0.08 | 1371.7 | 0.013333 | 0 | 0.013333 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.082 | 0.1 | 1380.9 | 0.016667 | 0 | 0.016667 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.097 | 0.102 | 1307 | 0.017 | 0 | 0.017 | 0 | 0 | 0 | 0 |  | 19-03-2026 18:40 | 0.22283 | 0 | 0.22283 | 0 | 0.1 | 0 | 0.1 | 3 | 97.59%
19-03-2026 18:30 | 1 | 26.98 | 0.559 | 0.588 | 1849.2 | 0.098 | 0.064505 | 0.033495 | 0.38703 | 0.2 | 0.063582 | 0.13642 |  | 19-03-2026 18:30 | 0.821 | 1.193 | 1863.8 | 0.19883 | 0.064505 | 0.13433 | 0.38703 | 0.2 | 0.063582 | 0.13642 |  | 19-03-2026 18:30 | 0.587 | 0.617 | 1833.4 | 0.10283 | 0.064505 | 0.038329 | 0.38703 | 0.2 | 0.063582 | 0.13642 |  | 19-03-2026 18:30 | 0.643 | 1.245 | 1849.2 | 0.2075 | 0.064505 | 0.143 | 0.38703 | 0.2 | 0.063582 | 0.13642 |  | 19-03-2026 18:30 | 0.286 | 0.449 | 1381.9 | 0.074833 | 0.047781 | 0.027052 | 0.28669 | 0.2 | 0.047098 | 0.1529 |  | 19-03-2026 18:30 | 0.292 | 0.307 | 1373 | 0.051167 | 0.047781 | 0.0033853 | 0.28669 | 0.1 | 0.047098 | 0.052902 |  | 19-03-2026 18:30 | 0.229 | 0.241 | 1371.7 | 0.040167 | 0.047781 | -0.0076147 | 0.28669 | 0.1 | 0.047098 | 0.052902 |  | 19-03-2026 18:30 | 0.407 | 0.721 | 1380.9 | 0.12017 | 0.047781 | 0.072385 | 0.28669 | 0.2 | 0.047098 | 0.1529 |  | 19-03-2026 18:30 | 0.208 | 0.218 | 1307 | 0.036333 | 0.045458 | -0.0091247 | 0.27275 | 0.1 | 0.044808 | 0.055192 |  | 19-03-2026 18:30 | 0.92983 | 0.4946 | 0.43523 | 2.9676 | 1.5 | 0.48753 | 1.0125 | 4 | 98.47%
19-03-2026 18:20 | 4 | 27.26 | 1.705 | 1.793 | 1849 | 0.29883 | 0.25776 | 0.041069 | 1.5466 | 0.3 | 0.25408 | 0.045921 |  | 19-03-2026 18:20 | 1.867 | 2.295 | 1863.6 | 0.3825 | 0.25776 | 0.12474 | 1.5466 | 0.4 | 0.25408 | 0.14592 |  | 19-03-2026 18:20 | 1.721 | 1.809 | 1833.2 | 0.3015 | 0.25776 | 0.043735 | 1.5466 | 0.3 | 0.25408 | 0.045921 |  | 19-03-2026 18:20 | 1.758 | 2.259 | 1849 | 0.3765 | 0.25776 | 0.11874 | 1.5466 | 0.4 | 0.25408 | 0.14592 |  | 19-03-2026 18:20 | 1.12 | 1.32 | 1381.7 | 0.22 | 0.19094 | 0.029063 | 1.1456 | 0.2 | 0.18821 | 0.011794 |  | 19-03-2026 18:20 | 1.13 | 1.188 | 1372.9 | 0.198 | 0.19094 | 0.0070632 | 1.1456 | 0.2 | 0.18821 | 0.011794 |  | 19-03-2026 18:20 | 1.089 | 1.145 | 1371.6 | 0.19083 | 0.19094 | -0.00010344 | 1.1456 | 0.2 | 0.18821 | 0.011794 |  | 19-03-2026 18:20 | 1.233 | 1.437 | 1380.7 | 0.2395 | 0.19094 | 0.048563 | 1.1456 | 0.2 | 0.18821 | 0.011794 |  | 19-03-2026 18:20 | 1.011 | 1.067 | 1306.9 | 0.17783 | 0.18165 | -0.0038194 | 1.0899 | 0.2 | 0.17906 | 0.020945 |  | 19-03-2026 18:20 | 2.3855 | 1.9765 | 0.40904 | 11.8587 | 2.4 | 1.9482 | 0.45181 | 5 | 98.57%
19-03-2026 18:10 | 6 | 28.41 | 2.513 | 2.615 | 1848.7 | 0.43583 | 0.38508 | 0.050755 | 2.3105 | 0.5 | 0.37957 | 0.12043 |  | 19-03-2026 18:10 | 2.86 | 3.066 | 1863.2 | 0.511 | 0.38508 | 0.12592 | 2.3105 | 0.5 | 0.37957 | 0.12043 |  | 19-03-2026 18:10 | 2.552 | 2.694 | 1832.9 | 0.449 | 0.38508 | 0.063922 | 2.3105 | 0.5 | 0.37957 | 0.12043 |  | 19-03-2026 18:10 | 2.596 | 3.084 | 1848.6 | 0.514 | 0.38508 | 0.12892 | 2.3105 | 0.5 | 0.37957 | 0.12043 |  | 19-03-2026 18:10 | 1.743 | 2.018 | 1381.5 | 0.33633 | 0.28524 | 0.05109 | 1.7115 | 0.4 | 0.28116 | 0.11884 |  | 19-03-2026 18:10 | 1.724 | 1.813 | 1372.7 | 0.30217 | 0.28524 | 0.016923 | 1.7115 | 0.4 | 0.28116 | 0.11884 |  | 19-03-2026 18:10 | 1.725 | 1.814 | 1371.4 | 0.30233 | 0.28524 | 0.01709 | 1.7115 | 0.4 | 0.28116 | 0.11884 |  | 19-03-2026 18:10 | 1.834 | 2.226 | 1380.5 | 0.371 | 0.28524 | 0.085757 | 1.7115 | 0.4 | 0.28116 | 0.11884 |  | 19-03-2026 18:10 | 1.595 | 1.677 | 1306.7 | 0.2795 | 0.27137 | 0.0081264 | 1.6282 | 0.3 | 0.26749 | 0.032507 |  | 19-03-2026 18:10 | 3.5012 | 2.9527 | 0.54851 | 17.716 | 3.9 | 2.9104 | 0.98956 | 6 | 98.38%
19-03-2026 18:00 | 10 | 30.42 | 3.601 | 3.784 | 1848.2 | 0.63067 | 0.63723 | -0.0065609 | 3.8234 | 0.9 | 0.62812 | 0.27188 |  | 19-03-2026 18:00 | 4.219 | 4.408 | 1862.7 | 0.73467 | 0.63723 | 0.097439 | 3.8234 | 1 | 0.62812 | 0.37188 |  | 19-03-2026 18:00 | 3.741 | 3.93 | 1832.4 | 0.655 | 0.63723 | 0.017772 | 3.8234 | 0.9 | 0.62812 | 0.27188 |  | 19-03-2026 18:00 | 3.828 | 4.404 | 1848.1 | 0.734 | 0.63723 | 0.096772 | 3.8234 | 0.9 | 0.62812 | 0.27188 |  | 19-03-2026 18:00 | 2.631 | 2.837 | 1381.1 | 0.47283 | 0.47202 | 0.00081291 | 2.8321 | 0.6 | 0.46527 | 0.13473 |  | 19-03-2026 18:00 | 2.597 | 2.731 | 1372.3 | 0.45517 | 0.47202 | -0.016854 | 2.8321 | 0.6 | 0.46527 | 0.13473 |  | 19-03-2026 18:00 | 2.617 | 2.752 | 1371 | 0.45867 | 0.47202 | -0.013354 | 2.8321 | 0.6 | 0.46527 | 0.13473 |  | 19-03-2026 18:00 | 2.717 | 2.976 | 1380.1 | 0.496 | 0.47202 | 0.02398 | 2.8321 | 0.6 | 0.46527 | 0.13473 |  | 19-03-2026 18:00 | 2.44 | 2.565 | 1306.4 | 0.4275 | 0.44907 | -0.021569 | 2.6944 | 0.6 | 0.44265 | 0.15735 |  | 19-03-2026 18:00 | 5.0645 | 4.8861 | 0.17844 | 29.3164 | 6.7 | 4.8162 | 1.8838 | 7 | 98.37%
19-03-2026 17:50 | 20 | 31 | 7.622 | 7.829 | 1847.3 | 1.3048 | 1.2718 | 0.033015 | 7.6309 | 2.3 | 1.2536 | 1.0464 |  | 19-03-2026 17:50 | 8.596 | 9.205 | 1861.7 | 1.5342 | 1.2718 | 0.26235 | 7.6309 | 2.3 | 1.2536 | 1.0464 |  | 19-03-2026 17:50 | 7.564 | 7.886 | 1831.5 | 1.3143 | 1.2718 | 0.042515 | 7.6309 | 2.4 | 1.2536 | 1.1464 |  | 19-03-2026 17:50 | 7.729 | 8.153 | 1847.2 | 1.3588 | 1.2718 | 0.087015 | 7.6309 | 2.4 | 1.2536 | 1.1464 |  | 19-03-2026 17:50 | 5.479 | 5.732 | 1380.5 | 0.95533 | 0.94209 | 0.013246 | 5.6525 | 1.7 | 0.92862 | 0.77138 |  | 19-03-2026 17:50 | 5.444 | 5.704 | 1371.7 | 0.95067 | 0.94209 | 0.0085793 | 5.6525 | 1.7 | 0.92862 | 0.77138 |  | 19-03-2026 17:50 | 5.421 | 5.673 | 1370.4 | 0.9455 | 0.94209 | 0.0034126 | 5.6525 | 1.7 | 0.92862 | 0.77138 |  | 19-03-2026 17:50 | 5.506 | 5.857 | 1379.5 | 0.97617 | 0.94209 | 0.034079 | 5.6525 | 1.7 | 0.92862 | 0.77138 |  | 19-03-2026 17:50 | 5.151 | 5.39 | 1305.8 | 0.89833 | 0.89628 | 0.0020539 | 5.3777 | 1.6 | 0.88346 | 0.71654 |  | 19-03-2026 17:50 | 10.2382 | 9.7519 | 0.48627 | 58.5114 | 17.8 | 9.6124 | 8.1876 | 8 | 97.28%
19-03-2026 17:40 | 55 | 32.43 | 20.94 | 21.375 | 1845 | 3.5625 | 3.4796 | 0.082881 | 20.8777 | 4 | 3.4299 | 0.57014 |  | 19-03-2026 17:40 | 21.577 | 21.981 | 1859.4 | 3.6635 | 3.4796 | 0.18388 | 20.8777 | 4.1 | 3.4299 | 0.67014 |  | 19-03-2026 17:40 | 20.643 | 21.144 | 1829.1 | 3.524 | 3.4796 | 0.044381 | 20.8777 | 3.9 | 3.4299 | 0.47014 |  | 19-03-2026 17:40 | 20.859 | 21.372 | 1844.8 | 3.562 | 3.4796 | 0.082381 | 20.8777 | 4 | 3.4299 | 0.57014 |  | 19-03-2026 17:40 | 15.182 | 15.592 | 1378.8 | 2.5987 | 2.5775 | 0.021171 | 15.465 | 2.9 | 2.5406 | 0.35936 |  | 19-03-2026 17:40 | 15.097 | 15.524 | 1370 | 2.5873 | 2.5775 | 0.0098378 | 15.465 | 2.9 | 2.5406 | 0.35936 |  | 19-03-2026 17:40 | 14.937 | 15.367 | 1368.7 | 2.5612 | 2.5775 | -0.016329 | 15.465 | 2.8 | 2.5406 | 0.25936 |  | 19-03-2026 17:40 | 15.147 | 15.77 | 1377.8 | 2.6283 | 2.5775 | 0.050838 | 15.465 | 3 | 2.5406 | 0.45936 |  | 19-03-2026 17:40 | 14.264 | 14.692 | 1304.2 | 2.4487 | 2.4522 | -0.0035011 | 14.713 | 2.8 | 2.4171 | 0.3829 |  | 19-03-2026 17:40 | 27.1362 | 26.6806 | 0.45554 | 160.0838 | 30.4 | 26.2991 | 4.1009 | 9 | 98.56%
19-03-2026 17:30 | 67 | 33 | 25.569 | 26.123 | 1841 | 4.3538 | 4.2301 | 0.12371 | 25.3808 | 4.5 | 4.1696 | 0.33036 |  | 19-03-2026 17:30 | 26.127 | 26.622 | 1855.3 | 4.437 | 4.2301 | 0.20687 | 25.3808 | 4.6 | 4.1696 | 0.43036 |  | 19-03-2026 17:30 | 25.286 | 25.839 | 1825.2 | 4.3065 | 4.2301 | 0.076374 | 25.3808 | 4.4 | 4.1696 | 0.23036 |  | 19-03-2026 17:30 | 25.543 | 26.089 | 1840.8 | 4.3482 | 4.2301 | 0.11804 | 25.3808 | 4.5 | 4.1696 | 0.33036 |  | 19-03-2026 17:30 | 18.664 | 19.135 | 1375.9 | 3.1892 | 3.1334 | 0.05574 | 18.8006 | 3.3 | 3.0886 | 0.21138 |  | 19-03-2026 17:30 | 18.395 | 18.857 | 1367.1 | 3.1428 | 3.1334 | 0.0094064 | 18.8006 | 3.3 | 3.0886 | 0.21138 |  | 19-03-2026 17:30 | 18.475 | 18.941 | 1365.9 | 3.1568 | 3.1334 | 0.023406 | 18.8006 | 3.3 | 3.0886 | 0.21138 |  | 19-03-2026 17:30 | 18.559 | 19.203 | 1374.8 | 3.2005 | 3.1334 | 0.067073 | 18.8006 | 3.2 | 3.0886 | 0.11138 |  | 19-03-2026 17:30 | 17.568 | 18.029 | 1301.4 | 3.0048 | 2.9811 | 0.023766 | 17.8864 | 3.1 | 2.9384 | 0.16156 |  | 19-03-2026 17:30 | 33.1397 | 32.4353 | 0.70439 | 194.6117 | 34.2 | 31.9715 | 2.2285
19-03-2026 17:20 | 75 | 32.72 | 29.042 | 29.507 | 1836.5 | 4.9178 | 4.74 | 0.17784 | 28.4399 | 5.2 | 4.6722 | 0.52779 |  | 19-03-2026 17:20 | 29.372 | 29.953 | 1850.7 | 4.9922 | 4.74 | 0.25218 | 28.4399 | 5 | 4.6722 | 0.32779 |  | 19-03-2026 17:20 | 28.724 | 29.295 | 1820.8 | 4.8825 | 4.74 | 0.14251 | 28.4399 | 5.1 | 4.6722 | 0.42779 |  | 19-03-2026 17:20 | 29.127 | 29.7 | 1836.3 | 4.95 | 4.74 | 0.21001 | 28.4399 | 5 | 4.6722 | 0.32779 |  | 19-03-2026 17:20 | 21.294 | 21.798 | 1372.6 | 3.633 | 3.5111 | 0.1219 | 21.0666 | 3.7 | 3.4609 | 0.2391 |  | 19-03-2026 17:20 | 21.304 | 21.803 | 1363.8 | 3.6338 | 3.5111 | 0.12273 | 21.0666 | 3.7 | 3.4609 | 0.2391 |  | 19-03-2026 17:20 | 21.107 | 21.602 | 1362.6 | 3.6003 | 3.5111 | 0.089229 | 21.0666 | 3.7 | 3.4609 | 0.2391 |  | 19-03-2026 17:20 | 21.315 | 22.012 | 1371.6 | 3.6687 | 3.5111 | 0.15756 | 21.0666 | 3.8 | 3.4609 | 0.3391 |  | 19-03-2026 17:20 | 20.154 | 20.637 | 1298.3 | 3.4395 | 3.3404 | 0.09912 | 20.0423 | 3.5 | 3.2926 | 0.20739 |  | 19-03-2026 17:20 | 37.7178 | 36.3448 | 1.3731 | 218.0685 | 38.7 | 35.825 | 2.875
19-03-2026 17:10 | 71 | 31.86 | 27.593 | 28.15 | 1831.3 | 4.6917 | 4.5011 | 0.19059 | 27.0064 | 3.2 | 4.4367 | -1.2367 |  | 19-03-2026 17:10 | 27.113 | 28.275 | 1845.7 | 4.7125 | 4.5011 | 0.21143 | 27.0064 | 3.3 | 4.4367 | -1.1367 |  | 19-03-2026 17:10 | 28.124 | 28.689 | 1815.7 | 4.7815 | 4.5011 | 0.28043 | 27.0064 | 3.3 | 4.4367 | -1.1367 |  | 19-03-2026 17:10 | 27.985 | 28.553 | 1831.3 | 4.7588 | 4.5011 | 0.25776 | 27.0064 | 3.3 | 4.4367 | -1.1367 |  | 19-03-2026 17:10 | 20.831 | 21.324 | 1368.9 | 3.554 | 3.3341 | 0.21987 | 20.0048 | 2.4 | 3.2864 | -0.88645 |  | 19-03-2026 17:10 | 20.551 | 21.033 | 1360.1 | 3.5055 | 3.3341 | 0.17137 | 20.0048 | 2.4 | 3.2864 | -0.88645 |  | 19-03-2026 17:10 | 20.46 | 20.95 | 1358.9 | 3.4917 | 3.3341 | 0.15754 | 20.0048 | 2.4 | 3.2864 | -0.88645 |  | 19-03-2026 17:10 | 20.58 | 21.252 | 1367.8 | 3.542 | 3.3341 | 0.20787 | 20.0048 | 2.4 | 3.2864 | -0.88645 |  | 19-03-2026 17:10 | 19.356 | 19.828 | 1294.8 | 3.3047 | 3.172 | 0.13266 | 19.0321 | 2.2 | 3.1266 | -0.92665 |  | 19-03-2026 17:10 | 36.3423 | 34.5128 | 1.8295 | 207.0769 | 24.9 | 34.0193 | -9.1193
19-03-2026 17:00 | 35 | 32.43 | 13.558 | 13.98 | 1828.1 | 2.33 | 2.2143 | 0.1157 | 13.2858 | 2.6 | 2.1826 | 0.41736 |  | 19-03-2026 17:00 | 13.741 | 14.237 | 1842.4 | 2.3728 | 2.2143 | 0.15853 | 13.2858 | 2.7 | 2.1826 | 0.51736 |  | 19-03-2026 17:00 | 13.458 | 13.872 | 1812.4 | 2.312 | 2.2143 | 0.097697 | 13.2858 | 2.5 | 2.1826 | 0.31736 |  | 19-03-2026 17:00 | 13.507 | 14.098 | 1828 | 2.3497 | 2.2143 | 0.13536 | 13.2858 | 2.6 | 2.1826 | 0.41736 |  | 19-03-2026 17:00 | 9.898 | 10.269 | 1366.5 | 1.7115 | 1.6402 | 0.071276 | 9.8413 | 1.9 | 1.6168 | 0.28323 |  | 19-03-2026 17:00 | 9.821 | 10.19 | 1357.7 | 1.6983 | 1.6402 | 0.058109 | 9.8413 | 1.9 | 1.6168 | 0.28323 |  | 19-03-2026 17:00 | 9.829 | 10.195 | 1356.5 | 1.6992 | 1.6402 | 0.058942 | 9.8413 | 1.9 | 1.6168 | 0.28323 |  | 19-03-2026 17:00 | 9.882 | 10.369 | 1365.4 | 1.7282 | 1.6402 | 0.087942 | 9.8413 | 1.9 | 1.6168 | 0.28323 |  | 19-03-2026 17:00 | 9.284 | 9.643 | 1292.6 | 1.6072 | 1.5605 | 0.046696 | 9.3628 | 1.8 | 1.5382 | 0.26184 |  | 19-03-2026 17:00 | 17.8088 | 16.9786 | 0.83025 | 101.8715 | 19.8 | 16.7358 | 3.0642
19-03-2026 16:50 | 47 | 33 | 17.945 | 18.407 | 1825.5 | 3.0678 | 2.9674 | 0.10043 | 17.8044 | 7.1 | 2.925 | 4.175 |  | 19-03-2026 16:50 | 18.15 | 18.625 | 1839.7 | 3.1042 | 2.9674 | 0.13676 | 17.8044 | 3 | 2.925 | 0.075032 |  | 19-03-2026 16:50 | 17.743 | 18.209 | 1809.9 | 3.0348 | 2.9674 | 0.067431 | 17.8044 | 3 | 2.925 | 0.075032 |  | 19-03-2026 16:50 | 17.937 | 18.415 | 1825.4 | 3.0692 | 2.9674 | 0.10176 | 17.8044 | 3 | 2.925 | 0.075032 |  | 19-03-2026 16:50 | 13.044 | 13.459 | 1364.6 | 2.2432 | 2.1981 | 0.045091 | 13.1885 | 2.2 | 2.1666 | 0.033357 |  | 19-03-2026 16:50 | 13.095 | 13.545 | 1355.8 | 2.2575 | 2.1981 | 0.059424 | 13.1885 | 2.1 | 2.1666 | -0.066643 |  | 19-03-2026 16:50 | 12.983 | 13.401 | 1354.6 | 2.2335 | 2.1981 | 0.035424 | 13.1885 | 2.1 | 2.1666 | -0.066643 |  | 19-03-2026 16:50 | 13.143 | 13.906 | 1363.5 | 2.3177 | 2.1981 | 0.11959 | 13.1885 | 2.2 | 2.1666 | 0.033357 |  | 19-03-2026 16:50 | 12.396 | 12.804 | 1290.8 | 2.134 | 2.0912 | 0.042803 | 12.5472 | 2.1 | 2.0613 | 0.038707 |  | 19-03-2026 16:50 | 23.4618 | 22.7531 | 0.70873 | 136.5186 | 26.8 | 22.4277 | 4.3723
19-03-2026 16:40 | 37 | 32.43 | 14.381 | 14.804 | 1822.5 | 2.4673 | 2.3408 | 0.1265 | 14.045 | 0 | 2.3074 | -2.3074 |  | 19-03-2026 16:40 | 15.054 | 15.477 | 1836.7 | 2.5795 | 2.3408 | 0.23867 | 14.045 | 4.2 | 2.3074 | 1.8926 |  | 19-03-2026 16:40 | 14.373 | 14.805 | 1806.9 | 2.4675 | 2.3408 | 0.12667 | 14.045 | 4.1 | 2.3074 | 1.7926 |  | 19-03-2026 16:40 | 14.493 | 14.963 | 1822.4 | 2.4938 | 2.3408 | 0.153 | 14.045 | 4.1 | 2.3074 | 1.7926 |  | 19-03-2026 16:40 | 10.574 | 10.945 | 1362.4 | 1.8242 | 1.734 | 0.090215 | 10.4037 | 3 | 1.7092 | 1.2908 |  | 19-03-2026 16:40 | 10.487 | 10.865 | 1353.7 | 1.8108 | 1.734 | 0.076882 | 10.4037 | 3.1 | 1.7092 | 1.3908 |  | 19-03-2026 16:40 | 10.485 | 10.869 | 1352.5 | 1.8115 | 1.734 | 0.077548 | 10.4037 | 3 | 1.7092 | 1.2908 |  | 19-03-2026 16:40 | 10.633 | 11.15 | 1361.3 | 1.8583 | 1.734 | 0.12438 | 10.4037 | 3 | 1.7092 | 1.2908 |  | 19-03-2026 16:40 | 9.993 | 10.37 | 1288.7 | 1.7283 | 1.6496 | 0.078693 | 9.8978 | 2.8 | 1.6261 | 1.1739 |  | 19-03-2026 16:40 | 19.0413 | 17.9488 | 1.0925 | 107.6927 | 27.3 | 17.6921 | 9.6079
19-03-2026 16:30 | 65 | 31.86 | 28.362 | 28.914 | 1818.4 | 4.819 | 4.1207 | 0.6983 | 24.7242 | 3.6 | 4.0618 | -0.46177 |  | 19-03-2026 16:30 | 28.746 | 29.315 | 1832.5 | 4.8858 | 4.1207 | 0.76513 | 24.7242 | 3.6 | 4.0618 | -0.46177 |  | 19-03-2026 16:30 | 28.504 | 29.068 | 1802.8 | 4.8447 | 4.1207 | 0.72397 | 24.7242 | 3.6 | 4.0618 | -0.46177 |  | 19-03-2026 16:30 | 28.055 | 28.622 | 1818.3 | 4.7703 | 4.1207 | 0.64963 | 24.7242 | 3.6 | 4.0618 | -0.46177 |  | 19-03-2026 16:30 | 20.89 | 21.38 | 1359.4 | 3.5633 | 3.0524 | 0.51096 | 18.3142 | 2.6 | 3.0087 | -0.40872 |  | 19-03-2026 16:30 | 20.704 | 21.189 | 1350.6 | 3.5315 | 3.0524 | 0.47913 | 18.3142 | 2.5 | 3.0087 | -0.50872 |  | 19-03-2026 16:30 | 20.738 | 21.224 | 1349.5 | 3.5373 | 3.0524 | 0.48496 | 18.3142 | 2.6 | 3.0087 | -0.40872 |  | 19-03-2026 16:30 | 20.87 | 21.706 | 1358.3 | 3.6177 | 3.0524 | 0.5653 | 18.3142 | 2.6 | 3.0087 | -0.40872 |  | 19-03-2026 16:30 | 19.575 | 20.05 | 1285.9 | 3.3417 | 2.904 | 0.43771 | 17.4237 | 2.5 | 2.8624 | -0.36243 |  | 19-03-2026 16:30 | 36.9113 | 31.5962 | 5.3151 | 189.5774 | 27.2 | 31.1444 | -3.9444
19-03-2026 16:20 | 44 | 37.31 | 16.938 | 17.39 | 1814.8 | 2.8983 | 2.7349 | 0.16345 | 16.4093 | 3.5 | 2.6958 | 0.80423 |  | 19-03-2026 16:20 | 17.202 | 17.661 | 1828.9 | 2.9435 | 2.7349 | 0.20862 | 16.4093 | 3.7 | 2.6958 | 1.0042 |  | 19-03-2026 16:20 | 16.85 | 17.28 | 1799.2 | 2.88 | 2.7349 | 0.14512 | 16.4093 | 3.5 | 2.6958 | 0.80423 |  | 19-03-2026 16:20 | 17.07 | 17.535 | 1814.7 | 2.9225 | 2.7349 | 0.18762 | 16.4093 | 3.5 | 2.6958 | 0.80423 |  | 19-03-2026 16:20 | 12.358 | 12.77 | 1356.8 | 2.1283 | 2.0258 | 0.1025 | 12.155 | 2.6 | 1.9969 | 0.60313 |  | 19-03-2026 16:20 | 12.421 | 12.838 | 1348.1 | 2.1397 | 2.0258 | 0.11383 | 12.155 | 2.6 | 1.9969 | 0.60313 |  | 19-03-2026 16:20 | 12.295 | 12.709 | 1346.9 | 2.1182 | 2.0258 | 0.092329 | 12.155 | 2.6 | 1.9969 | 0.60313 |  | 19-03-2026 16:20 | 12.454 | 12.863 | 1355.7 | 2.1438 | 2.0258 | 0.118 | 12.155 | 2.6 | 1.9969 | 0.60313 |  | 19-03-2026 16:20 | 11.775 | 12.179 | 1283.4 | 2.0298 | 1.9273 | 0.1025 | 11.564 | 2.4 | 1.8998 | 0.50023 |  | 19-03-2026 16:20 | 22.2042 | 20.9702 | 1.234 | 125.8212 | 27 | 20.6703 | 6.3297
19-03-2026 16:10 | 74 | 38.17 | 29.421 | 30.006 | 1811.3 | 5.001 | 4.5851 | 0.4159 | 27.5106 | 5.8 | 4.5195 | 1.2805 |  | 19-03-2026 16:10 | 30.532 | 30.612 | 1825.2 | 5.102 | 4.5851 | 0.5169 | 27.5106 | 5.7 | 4.5195 | 1.1805 |  | 19-03-2026 16:10 | 29.131 | 29.713 | 1795.7 | 4.9522 | 4.5851 | 0.36706 | 27.5106 | 5.7 | 4.5195 | 1.1805 |  | 19-03-2026 16:10 | 29.554 | 30.148 | 1811.2 | 5.0247 | 4.5851 | 0.43956 | 27.5106 | 5.7 | 4.5195 | 1.1805 |  | 19-03-2026 16:10 | 21.402 | 21.908 | 1354.2 | 3.6513 | 3.3964 | 0.25496 | 20.3782 | 4.2 | 3.3478 | 0.8522 |  | 19-03-2026 16:10 | 21.507 | 22.02 | 1345.5 | 3.67 | 3.3964 | 0.27363 | 20.3782 | 4.2 | 3.3478 | 0.8522 |  | 19-03-2026 16:10 | 21.321 | 21.839 | 1344.3 | 3.6398 | 3.3964 | 0.24346 | 20.3782 | 4.2 | 3.3478 | 0.8522 |  | 19-03-2026 16:10 | 21.562 | 22.135 | 1353.1 | 3.6892 | 3.3964 | 0.29279 | 20.3782 | 4.2 | 3.3478 | 0.8522 |  | 19-03-2026 16:10 | 20.37 | 20.867 | 1281 | 3.4778 | 3.2312 | 0.24661 | 19.3874 | 4.1 | 3.185 | 0.91498 |  | 19-03-2026 16:10 | 38.208 | 35.1571 | 3.0509 | 210.9428 | 43.8 | 34.6544 | 9.1456
19-03-2026 16:00 | 101 | 38.46 | 40.351 | 41.036 | 1805.5 | 6.8393 | 6.2514 | 0.58795 | 37.5083 | 6 | 6.162 | -0.16199 |  | 19-03-2026 16:00 | 40.68 | 41.388 | 1819.5 | 6.898 | 6.2514 | 0.64661 | 37.5083 | 6.1 | 6.162 | -0.061993 |  | 19-03-2026 16:00 | 40.059 | 40.764 | 1790 | 6.794 | 6.2514 | 0.54261 | 37.5083 | 5.9 | 6.162 | -0.26199 |  | 19-03-2026 16:00 | 40.238 | 40.946 | 1805.5 | 6.8243 | 6.2514 | 0.57295 | 37.5083 | 6.1 | 6.162 | -0.061993 |  | 19-03-2026 16:00 | 29.72 | 30.296 | 1350 | 5.0493 | 4.6307 | 0.41868 | 27.7839 | 4.5 | 4.5644 | -0.064439 |  | 19-03-2026 16:00 | 29.559 | 30.138 | 1341.3 | 5.023 | 4.6307 | 0.39234 | 27.7839 | 4.5 | 4.5644 | -0.064439 |  | 19-03-2026 16:00 | 29.451 | 30.021 | 1340.1 | 5.0035 | 4.6307 | 0.37284 | 27.7839 | 4.4 | 4.5644 | -0.16444 |  | 19-03-2026 16:00 | 29.665 | 30.305 | 1348.9 | 5.0508 | 4.6307 | 0.42018 | 27.7839 | 4.4 | 4.5644 | -0.16444 |  | 19-03-2026 16:00 | 28.023 | 28.607 | 1276.9 | 4.7678 | 4.4055 | 0.36234 | 26.433 | 4.1 | 4.3425 | -0.2425 |  | 19-03-2026 16:00 | 52.2502 | 47.9337 | 4.3165 | 287.6021 | 46 | 47.2482 | -1.2482
19-03-2026 15:50 | 94 | 40.47 | 37.743 | 38.415 | 1799.5 | 6.4025 | 5.7752 | 0.62733 | 34.651 | 6.3 | 5.6926 | 0.60742 |  | 19-03-2026 15:50 | 37.939 | 38.619 | 1813.4 | 6.4365 | 5.7752 | 0.66133 | 34.651 | 6.3 | 5.6926 | 0.60742 |  | 19-03-2026 15:50 | 37.09 | 37.784 | 1784.1 | 6.2973 | 5.7752 | 0.52216 | 34.651 | 6.4 | 5.6926 | 0.70742 |  | 19-03-2026 15:50 | 37.666 | 38.349 | 1799.4 | 6.3915 | 5.7752 | 0.61633 | 34.651 | 6.3 | 5.6926 | 0.60742 |  | 19-03-2026 15:50 | 27.878 | 28.236 | 1345.5 | 4.706 | 4.2779 | 0.4281 | 25.6674 | 4.6 | 4.2167 | 0.38327 |  | 19-03-2026 15:50 | 27.617 | 28.181 | 1336.8 | 4.6968 | 4.2779 | 0.41893 | 25.6674 | 4.6 | 4.2167 | 0.38327 |  | 19-03-2026 15:50 | 27.4 | 27.971 | 1335.7 | 4.6618 | 4.2779 | 0.38393 | 25.6674 | 4.7 | 4.2167 | 0.48327 |  | 19-03-2026 15:50 | 27.631 | 28.408 | 1344.5 | 4.7347 | 4.2779 | 0.45676 | 25.6674 | 4.7 | 4.2167 | 0.48327 |  | 19-03-2026 15:50 | 26.08 | 26.639 | 1272.8 | 4.4398 | 4.0699 | 0.36994 | 24.4194 | 4.4 | 4.0117 | 0.3883 |  | 19-03-2026 15:50 | 48.767 | 44.2822 | 4.4848 | 265.6931 | 48.3 | 43.6489 | 4.6511
19-03-2026 15:40 | 86 | 42.19 | 34.714 | 35.35 | 1793.2 | 5.8917 | 5.25 | 0.64163 | 31.5002 | 7.6 | 5.175 | 2.425 |  | 19-03-2026 15:40 | 35.331 | 35.504 | 1807.1 | 5.9173 | 5.25 | 0.6673 | 31.5002 | 7.9 | 5.175 | 2.725 |  | 19-03-2026 15:40 | 34.199 | 34.847 | 1777.7 | 5.8078 | 5.25 | 0.5578 | 31.5002 | 7.5 | 5.175 | 2.325 |  | 19-03-2026 15:40 | 34.531 | 35.175 | 1793.1 | 5.8625 | 5.25 | 0.61246 | 31.5002 | 7.8 | 5.175 | 2.625 |  | 19-03-2026 15:40 | 25.281 | 25.844 | 1340.9 | 4.3073 | 3.8889 | 0.41842 | 23.3335 | 5.6 | 3.8333 | 1.7667 |  | 19-03-2026 15:40 | 25.204 | 25.758 | 1332.2 | 4.293 | 3.8889 | 0.40408 | 23.3335 | 5.6 | 3.8333 | 1.7667 |  | 19-03-2026 15:40 | 24.995 | 25.555 | 1331 | 4.2592 | 3.8889 | 0.37025 | 23.3335 | 5.4 | 3.8333 | 1.5667 |  | 19-03-2026 15:40 | 25.123 | 25.832 | 1339.8 | 4.3053 | 3.8889 | 0.41642 | 23.3335 | 5.6 | 3.8333 | 1.7667 |  | 19-03-2026 15:40 | 23.778 | 24.325 | 1268.4 | 4.0542 | 3.6998 | 0.35434 | 22.1989 | 5.3 | 3.6469 | 1.6531 |  | 19-03-2026 15:40 | 44.6983 | 40.2556 | 4.4427 | 241.5338 | 58.3 | 39.68 | 18.62
19-03-2026 15:30 | 159 | 44.48 | 62.141 | 62.998 | 1785.6 | 10.4997 | 9.6237 | 0.87598 | 57.7421 | 11.5 | 9.4861 | 2.0139 |  | 19-03-2026 15:30 | 65.502 | 66.419 | 1799.2 | 11.0698 | 9.6237 | 1.4461 | 57.7421 | 11 | 9.4861 | 1.5139 |  | 19-03-2026 15:30 | 61.761 | 62.638 | 1770.2 | 10.4397 | 9.6237 | 0.81598 | 57.7421 | 10.8 | 9.4861 | 1.3139 |  | 19-03-2026 15:30 | 62.97 | 63.851 | 1785.3 | 10.6418 | 9.6237 | 1.0181 | 57.7421 | 11 | 9.4861 | 1.5139 |  | 19-03-2026 15:30 | 45.924 | 46.675 | 1335.3 | 7.7792 | 7.1287 | 0.65051 | 42.7719 | 8.2 | 7.0267 | 1.1733 |  | 19-03-2026 15:30 | 45.936 | 46.688 | 1326.6 | 7.7813 | 7.1287 | 0.65268 | 42.7719 | 8.1 | 7.0267 | 1.0733 |  | 19-03-2026 15:30 | 45.535 | 46.28 | 1325.6 | 7.7133 | 7.1287 | 0.58468 | 42.7719 | 8.1 | 7.0267 | 1.0733 |  | 19-03-2026 15:30 | 45.77 | 47.029 | 1334.2 | 7.8382 | 7.1287 | 0.70951 | 42.7719 | 8.1 | 7.0267 | 1.0733 |  | 19-03-2026 15:30 | 43.74 | 44.487 | 1263.1 | 7.4145 | 6.782 | 0.63247 | 40.6922 | 7.7 | 6.6851 | 1.0149 |  | 19-03-2026 15:30 | 81.1775 | 73.7914 | 7.3861 | 442.7484 | 84.5 | 72.7362 | 11.7638
19-03-2026 15:20 | 179 | 46.78 | 70.557 | 71.515 | 1774.1 | 11.9192 | 10.7406 | 1.1786 | 64.4437 | 13.6 | 10.587 | 3.013 |  | 19-03-2026 15:20 | 69.828 | 70.798 | 1788.2 | 11.7997 | 10.7406 | 1.0591 | 64.4437 | 13.9 | 10.587 | 3.313 |  | 19-03-2026 15:20 | 68.489 | 69.433 | 1759.4 | 11.5722 | 10.7406 | 0.83155 | 64.4437 | 13.9 | 10.587 | 3.313 |  | 19-03-2026 15:20 | 69.263 | 70.211 | 1774.3 | 11.7018 | 10.7406 | 0.96122 | 64.4437 | 13.7 | 10.587 | 3.113 |  | 19-03-2026 15:20 | 51.056 | 51.87 | 1327.1 | 8.645 | 7.956 | 0.68899 | 47.7361 | 10.1 | 7.8422 | 2.2578 |  | 19-03-2026 15:20 | 50.803 | 51.619 | 1318.5 | 8.6032 | 7.956 | 0.64716 | 47.7361 | 10.1 | 7.8422 | 2.2578 |  | 19-03-2026 15:20 | 50.507 | 51.335 | 1317.5 | 8.5558 | 7.956 | 0.59982 | 47.7361 | 10 | 7.8422 | 2.1578 |  | 19-03-2026 15:20 | 50.688 | 51.98 | 1326.1 | 8.6633 | 7.956 | 0.70732 | 47.7361 | 10 | 7.8422 | 2.1578 |  | 19-03-2026 15:20 | 48.083 | 48.88 | 1255.4 | 8.1467 | 7.5692 | 0.57751 | 45.415 | 9.5 | 7.4609 | 2.0391 |  | 19-03-2026 15:20 | 89.6068 | 82.3557 | 7.2512 | 494.134 | 104.8 | 81.178 | 23.622
19-03-2026 15:10 | 284 | 47.35 | 107.578 | 108.907 | 1760.5 | 18.1512 | 17.0042 | 1.147 | 102.025 | 24.7 | 16.761 | 7.939 |  | 19-03-2026 15:10 | 109.538 | 111.061 | 1774.3 | 18.5102 | 17.0042 | 1.506 | 102.025 | 25 | 16.761 | 8.239 |  | 19-03-2026 15:10 | 105.746 | 107.257 | 1745.5 | 17.8762 | 17.0042 | 0.87199 | 102.025 | 24.1 | 16.761 | 7.339 |  | 19-03-2026 15:10 | 106.674 | 108.146 | 1760.6 | 18.0243 | 17.0042 | 1.0202 | 102.025 | 24.3 | 16.761 | 7.539 |  | 19-03-2026 15:10 | 78.616 | 79.703 | 1317 | 13.2838 | 12.5957 | 0.68815 | 75.5741 | 18 | 12.4156 | 5.5844 |  | 19-03-2026 15:10 | 78.19 | 79.228 | 1308.4 | 13.2047 | 12.5957 | 0.60898 | 75.5741 | 17.7 | 12.4156 | 5.2844 |  | 19-03-2026 15:10 | 77.562 | 78.592 | 1307.5 | 13.0987 | 12.5957 | 0.50298 | 75.5741 | 17.9 | 12.4156 | 5.4844 |  | 19-03-2026 15:10 | 77.62 | 79.685 | 1316.1 | 13.2808 | 12.5957 | 0.68515 | 75.5741 | 18.1 | 12.4156 | 5.6844 |  | 19-03-2026 15:10 | 73.623 | 74.638 | 1245.9 | 12.4397 | 11.9832 | 0.45643 | 71.8994 | 17 | 11.8119 | 5.1881 |  | 19-03-2026 15:10 | 137.8695 | 130.3827 | 7.4868 | 782.296 | 186.8 | 128.5182 | 58.2818
19-03-2026 15:00 | 361 | 47.64 | 142.199 | 136.582 | 1735.8 | 22.7637 | 21.5907 | 1.173 | 129.544 | 22.5 | 21.2819 | 1.2181 | 1.0411 | 19-03-2026 15:00 | 136.584 | 138.341 | 1749.3 | 23.0568 | 21.5907 | 1.4662 | 129.544 | 23.2 | 21.2819 | 1.9181 | 0.9873 | 19-03-2026 15:00 | 134.082 | 136.352 | 1721.4 | 22.7253 | 21.5907 | 1.1347 | 129.544 | 23 | 21.2819 | 1.7181 | 0.98335 | 19-03-2026 15:00 | 134.726 | 136.445 | 1736.3 | 22.7408 | 21.5907 | 1.1502 | 129.544 | 23.1 | 21.2819 | 1.8181 | 0.9874 | 19-03-2026 15:00 | 100.321 | 101.544 | 1299 | 16.924 | 15.9931 | 0.93092 | 95.9585 | 17.5 | 15.7644 | 1.7356 | 0.98796 | 19-03-2026 15:00 | 99.105 | 100.339 | 1290.7 | 16.7232 | 15.9931 | 0.73009 | 95.9585 | 17.2 | 15.7644 | 1.4356 | 0.9877 | 19-03-2026 15:00 | 99.116 | 100.36 | 1289.6 | 16.7267 | 15.9931 | 0.73359 | 95.9585 | 17.3 | 15.7644 | 1.5356 | 0.9876 | 19-03-2026 15:00 | 98.989 | 101.516 | 1298 | 16.9193 | 15.9931 | 0.92625 | 95.9585 | 17.3 | 15.7644 | 1.5356 | 0.97511 | 19-03-2026 15:00 | 93.697 | 94.883 | 1228.9 | 15.8138 | 15.2154 | 0.5984 | 91.2926 | 16.2 | 14.9979 | 1.2021 | 0.9875 | 19-03-2026 15:00 | 174.3937 | 165.5504 | 8.8433 | 993.3024 | 177.3 | 163.183 | 14.117
19-03-2026 14:50 | 329 | 47.35 | 123.785 | 125.815 | 1713.3 | 20.9692 | 19.6985 | 1.2707 | 118.191 | 20.3 | 19.4168 | 0.88319 | 0.98387 | 19-03-2026 14:50 | 124.668 | 126.284 | 1726.1 | 21.0473 | 19.6985 | 1.3488 | 118.191 | 20.6 | 19.4168 | 1.1832 | 0.9872 | 19-03-2026 14:50 | 123.252 | 125.375 | 1698.4 | 20.8958 | 19.6985 | 1.1973 | 118.191 | 19.6 | 19.4168 | 0.18319 | 0.98307 | 19-03-2026 14:50 | 123.994 | 125.589 | 1713.2 | 20.9315 | 19.6985 | 1.233 | 118.191 | 19.8 | 19.4168 | 0.38319 | 0.9873 | 19-03-2026 14:50 | 92.284 | 93.433 | 1281.5 | 15.5722 | 14.5915 | 0.98069 | 87.5489 | 14.6 | 14.3828 | 0.21718 | 0.9877 | 19-03-2026 14:50 | 91.376 | 92.507 | 1273.5 | 15.4178 | 14.5915 | 0.82635 | 87.5489 | 14.8 | 14.3828 | 0.41718 | 0.98777 | 19-03-2026 14:50 | 91.343 | 92.481 | 1272.3 | 15.4135 | 14.5915 | 0.82202 | 87.5489 | 14.7 | 14.3828 | 0.31718 | 0.98769 | 19-03-2026 14:50 | 91.78 | 94.155 | 1280.7 | 15.6925 | 14.5915 | 1.101 | 87.5489 | 14.7 | 14.3828 | 0.31718 | 0.97478 | 19-03-2026 14:50 | 86.775 | 87.909 | 1212.7 | 14.6515 | 13.882 | 0.76951 | 83.2919 | 14 | 13.6835 | 0.31653 | 0.9871 | 19-03-2026 14:50 | 160.5913 | 151.0419 | 9.5494 | 906.2514 | 153.1 | 148.882 | 4.218
19-03-2026 14:40 | 370 | 47.64 | 138.518 | 140.314 | 1693 | 23.3857 | 22.1289 | 1.2567 | 132.7736 | 27.1 | 21.8125 | 5.2875 | 0.9872 | 19-03-2026 14:40 | 142.733 | 144.642 | 1705.5 | 24.107 | 22.1289 | 1.9781 | 132.7736 | 26.2 | 21.8125 | 4.3875 | 0.9868 | 19-03-2026 14:40 | 135.611 | 137.999 | 1678.8 | 22.9998 | 22.1289 | 0.8709 | 132.7736 | 27 | 21.8125 | 5.1875 | 0.9827 | 19-03-2026 14:40 | 137.091 | 138.925 | 1693.4 | 23.1542 | 22.1289 | 1.0252 | 132.7736 | 27.2 | 21.8125 | 5.3875 | 0.9868 | 19-03-2026 14:40 | 101.179 | 102.501 | 1266.9 | 17.0835 | 16.3918 | 0.6917 | 98.3508 | 20.1 | 16.1574 | 3.9426 | 0.9871 | 19-03-2026 14:40 | 101.343 | 102.657 | 1258.7 | 17.1095 | 16.3918 | 0.7177 | 98.3508 | 19.7 | 16.1574 | 3.5426 | 0.9872 | 19-03-2026 14:40 | 100.54 | 101.823 | 1257.6 | 16.9705 | 16.3918 | 0.5787 | 98.3508 | 19.5 | 16.1574 | 3.3426 | 0.9874 | 19-03-2026 14:40 | 100.98 | 103.84 | 1266 | 17.3067 | 16.3918 | 0.91487 | 98.3508 | 19.6 | 16.1574 | 3.4426 | 0.97246 | 19-03-2026 14:40 | 95.534 | 96.773 | 1198.7 | 16.1288 | 15.5948 | 0.53406 | 93.5686 | 18.5 | 15.3718 | 3.1282 | 0.9872 | 19-03-2026 14:40 | 178.2457 | 169.6777 | 8.568 | 1018.0662 | 204.9 | 167.2513 | 37.6487
19-03-2026 14:30 | 523 | 48.22 | 184.548 | 187.073 | 1665.9 | 31.1788 | 31.2106 | -0.031748 | 187.2635 | 40.3 | 30.7643 | 9.5357 | 0.9865 | 19-03-2026 14:30 | 231.235 | 237.24 | 1679.3 | 39.54 | 31.2106 | 8.3294 | 187.2635 | 40.9 | 30.7643 | 10.1357 | 0.97469 | 19-03-2026 14:30 | 184.811 | 188.951 | 1651.8 | 31.4918 | 31.2106 | 0.28125 | 187.2635 | 39.9 | 30.7643 | 9.1357 | 0.97809 | 19-03-2026 14:30 | 184.332 | 186.345 | 1666.2 | 31.0575 | 31.2106 | -0.15308 | 187.2635 | 40.1 | 30.7643 | 9.3357 | 0.9892 | 19-03-2026 14:30 | 139.293 | 140.283 | 1246.8 | 23.3805 | 23.1189 | 0.26155 | 138.7137 | 30.9 | 22.7883 | 8.1117 | 0.99294 | 19-03-2026 14:30 | 136.415 | 138.254 | 1239 | 23.0423 | 23.1189 | -0.076616 | 138.7137 | 30.5 | 22.7883 | 7.7117 | 0.9867 | 19-03-2026 14:30 | 139.05 | 140.91 | 1238.1 | 23.485 | 23.1189 | 0.36605 | 138.7137 | 30.6 | 22.7883 | 7.8117 | 0.9868 | 19-03-2026 14:30 | 139.797 | 143.807 | 1246.4 | 23.9678 | 23.1189 | 0.84888 | 138.7137 | 31.4 | 22.7883 | 8.6117 | 0.97212 | 19-03-2026 14:30 | 130.815 | 132.578 | 1180.2 | 22.0963 | 21.9948 | 0.10152 | 131.9689 | 29.7 | 21.6803 | 8.0197 | 0.9867 | 19-03-2026 14:30 | 249.2402 | 239.3129 | 9.9272 | 1435.8776 | 314.3 | 235.8908 | 78.4092
19-03-2026 14:20 | 902 | 48.5 | 314.9 | 320.786 | 1625.6 | 53.4643 | 53.7704 | -0.30606 | 322.6224 | 42.2 | 53.0015 | -10.8015 | 0.98165 | 19-03-2026 14:20 | 322.985 | 339.118 | 1638.4 | 56.5197 | 53.7704 | 2.7493 | 322.6224 | 42.4 | 53.0015 | -10.6015 | 0.95243 | 19-03-2026 14:20 | 340.967 | 350.614 | 1611.9 | 58.4357 | 53.7704 | 4.6653 | 322.6224 | 42.8 | 53.0015 | -10.2015 | 0.97249 | 19-03-2026 14:20 | 323.376 | 328.768 | 1626.1 | 54.7947 | 53.7704 | 1.0243 | 322.6224 | 42.9 | 53.0015 | -10.1015 | 0.9836 | 19-03-2026 14:20 | 258.241 | 262.12 | 1215.9 | 43.6867 | 39.8299 | 3.8567 | 238.9795 | 32.5 | 39.2604 | -6.7604 | 0.9852 | 19-03-2026 14:20 | 250.289 | 258.764 | 1208.5 | 43.1273 | 39.8299 | 3.2974 | 238.9795 | 31.9 | 39.2604 | -7.3604 | 0.96725 | 19-03-2026 14:20 | 246.717 | 250.423 | 1207.5 | 41.7372 | 39.8299 | 1.9072 | 238.9795 | 31.9 | 39.2604 | -7.3604 | 0.9852 | 19-03-2026 14:20 | 242.012 | 249.042 | 1215 | 41.507 | 39.8299 | 1.6771 | 238.9795 | 31.2 | 39.2604 | -8.0604 | 0.97177 | 19-03-2026 14:20 | 223.358 | 226.575 | 1150.5 | 37.7625 | 37.8932 | -0.13074 | 227.3594 | 29.5 | 37.3514 | -7.8514 | 0.9858 | 19-03-2026 14:20 | 431.035 | 412.2945 | 18.7405 | 2473.7669 | 327.3 | 406.3987 | -79.0987
19-03-2026 14:10 | 969 | 48.5 | 331.557 | 337.119 | 1583.4 | 56.1865 | 57.7644 | -1.5779 | 346.5865 | 54 | 56.9384 | -2.9384 | 0.9835 | 19-03-2026 14:10 | 338.234 | 344.013 | 1596 | 57.3355 | 57.7644 | -0.42892 | 346.5865 | 53.6 | 56.9384 | -3.3384 | 0.9832 | 19-03-2026 14:10 | 330.702 | 338.952 | 1569.1 | 56.492 | 57.7644 | -1.2724 | 346.5865 | 52.1 | 56.9384 | -4.8384 | 0.97566 | 19-03-2026 14:10 | 333.789 | 339.492 | 1583.2 | 56.582 | 57.7644 | -1.1824 | 346.5865 | 52.4 | 56.9384 | -4.5384 | 0.9832 | 19-03-2026 14:10 | 249.516 | 253.341 | 1183.4 | 42.2235 | 42.7885 | -0.56496 | 256.7308 | 40.9 | 42.1766 | -1.2766 | 0.9849 | 19-03-2026 14:10 | 247.469 | 251.407 | 1176.6 | 41.9012 | 42.7885 | -0.8873 | 256.7308 | 40.1 | 42.1766 | -2.0766 | 0.98434 | 19-03-2026 14:10 | 247.239 | 251.813 | 1175.6 | 41.9688 | 42.7885 | -0.81963 | 256.7308 | 40.6 | 42.1766 | -1.5766 | 0.98184 | 19-03-2026 14:10 | 248.94 | 256.152 | 1183.8 | 42.692 | 42.7885 | -0.096462 | 256.7308 | 40.9 | 42.1766 | -1.2766 | 0.97184 | 19-03-2026 14:10 | 235.777 | 239.392 | 1121 | 39.8987 | 40.7079 | -0.80926 | 244.2475 | 38.3 | 40.1258 | -1.8258 | 0.9849 | 19-03-2026 14:10 | 435.2802 | 442.9195 | -7.6393 | 2657.5168 | 412.9 | 436.5857 | -23.6857
19-03-2026 14:00 | 615 | 48.22 | 229.416 | 232.744 | 1529.4 | 38.7907 | 36.7008 | 2.0899 | 220.2047 | 34.5 | 36.176 | -1.676 | 0.9857 | 19-03-2026 14:00 | 225.023 | 228.311 | 1542.4 | 38.0518 | 36.7008 | 1.3511 | 220.2047 | 35.8 | 36.176 | -0.37596 | 0.9856 | 19-03-2026 14:00 | 212.854 | 217.311 | 1517 | 36.2185 | 36.7008 | -0.48228 | 220.2047 | 35.2 | 36.176 | -0.97596 | 0.97949 | 19-03-2026 14:00 | 222.219 | 225.443 | 1530.8 | 37.5738 | 36.7008 | 0.87305 | 220.2047 | 35.8 | 36.176 | -0.37596 | 0.9857 | 19-03-2026 14:00 | 165.729 | 168.014 | 1142.5 | 28.0023 | 27.1858 | 0.81657 | 163.1146 | 26.6 | 26.797 | -0.19701 | 0.9864 | 19-03-2026 14:00 | 164.192 | 166.439 | 1136.5 | 27.7398 | 27.1858 | 0.55407 | 163.1146 | 26.2 | 26.797 | -0.59701 | 0.9865 | 19-03-2026 14:00 | 164.253 | 166.45 | 1135 | 27.7417 | 27.1858 | 0.5559 | 163.1146 | 26.5 | 26.797 | -0.29701 | 0.9868 | 19-03-2026 14:00 | 167.17 | 171.465 | 1142.9 | 28.5775 | 27.1858 | 1.3917 | 163.1146 | 26.7 | 26.797 | -0.097006 | 0.97495 | 19-03-2026 14:00 | 156.468 | 158.625 | 1082.7 | 26.4375 | 25.8639 | 0.57361 | 155.1833 | 25.1 | 25.494 | -0.39403 | 0.9864 | 19-03-2026 14:00 | 289.1337 | 281.4101 | 7.7236 | 1688.4603 | 272.4 | 277.3859 | -4.9859
19-03-2026 13:50 | 532 | 48.5 | 225.551 | 185.239 | 1494.9 | 30.8732 | 31.7138 | -0.84063 | 190.2828 | 44.5 | 31.2603 | 13.2397 | 1.2176 | 19-03-2026 13:50 | 226.605 | 192.022 | 1506.6 | 32.0037 | 31.7138 | 0.28987 | 190.2828 | 43.8 | 31.2603 | 12.5397 | 1.1801 | 19-03-2026 13:50 | 179.511 | 183.348 | 1481.8 | 30.558 | 31.7138 | -1.1558 | 190.2828 | 43.2 | 31.2603 | 11.9397 | 0.97907 | 19-03-2026 13:50 | 194.346 | 197.225 | 1495 | 32.8708 | 31.7138 | 1.157 | 190.2828 | 42.8 | 31.2603 | 11.5397 | 0.9854 | 19-03-2026 13:50 | 136.287 | 138.222 | 1115.9 | 23.037 | 23.4917 | -0.4547 | 140.9502 | 32.3 | 23.1558 | 9.1442 | 0.986 | 19-03-2026 13:50 | 136.137 | 138.07 | 1110.3 | 23.0117 | 23.4917 | -0.48004 | 140.9502 | 32 | 23.1558 | 8.8442 | 0.986 | 19-03-2026 13:50 | 134.492 | 136.388 | 1108.5 | 22.7313 | 23.4917 | -0.76037 | 140.9502 | 31.8 | 23.1558 | 8.6442 | 0.9861 | 19-03-2026 13:50 | 136.25 | 139.625 | 1116.2 | 23.2708 | 23.4917 | -0.22087 | 140.9502 | 32.1 | 23.1558 | 8.9442 | 0.97583 | 19-03-2026 13:50 | 128.995 | 130.813 | 1057.6 | 21.8022 | 22.3494 | -0.54728 | 134.0967 | 30.9 | 22.0299 | 8.8701 | 0.9861 | 19-03-2026 13:50 | 240.1587 | 243.1715 | -3.0128 | 1459.0288 | 333.4 | 239.6941 | 93.7059
19-03-2026 13:40 | 1001 | 48.5 | 345.971 | 351.347 | 1450.4 | 58.5578 | 59.672 | -1.1142 | 358.0321 | 57.4 | 58.8187 | -1.4187 | 0.9847 | 19-03-2026 13:40 | 344.86 | 350.147 | 1462.8 | 58.3578 | 59.672 | -1.3142 | 358.0321 | 57.9 | 58.8187 | -0.91871 | 0.9849 | 19-03-2026 13:40 | 345.98 | 356.148 | 1438.6 | 59.358 | 59.672 | -0.31402 | 358.0321 | 57.1 | 58.8187 | -1.7187 | 0.97145 | 19-03-2026 13:40 | 334.785 | 340.056 | 1452.2 | 56.676 | 59.672 | -2.996 | 358.0321 | 57.6 | 58.8187 | -1.2187 | 0.9845 | 19-03-2026 13:40 | 277.978 | 282.642 | 1083.6 | 47.107 | 44.2015 | 2.9055 | 265.209 | 44.8 | 43.5694 | 1.2306 | 0.9835 | 19-03-2026 13:40 | 270.074 | 278.105 | 1078.3 | 46.3508 | 44.2015 | 2.1493 | 265.209 | 44.1 | 43.5694 | 0.53058 | 0.97112 | 19-03-2026 13:40 | 258.899 | 263.082 | 1076.7 | 43.847 | 44.2015 | -0.3545 | 265.209 | 44.3 | 43.5694 | 0.73058 | 0.9841 | 19-03-2026 13:40 | 251.847 | 256.265 | 1084.1 | 42.7108 | 44.2015 | -1.4907 | 265.209 | 44.3 | 43.5694 | 0.73058 | 0.98276 | 19-03-2026 13:40 | 248.519 | 252.586 | 1026.7 | 42.0977 | 42.0522 | 0.045417 | 252.3135 | 41.8 | 41.4509 | 0.3491 | 0.9839 | 19-03-2026 13:40 | 455.063 | 457.5463 | -2.4833 | 2745.2779 | 449.3 | 451.0034 | -1.7034
19-03-2026 13:30 | 1062 | 48.5 | 348.316 | 352.827 | 1393 | 58.8045 | 63.3084 | -4.5039 | 379.8503 | 56.4 | 62.4031 | -6.0031 | 0.98721 | 19-03-2026 13:30 | 346.853 | 352.457 | 1404.9 | 58.7428 | 63.3084 | -4.5655 | 379.8503 | 56.1 | 62.4031 | -6.3031 | 0.9841 | 19-03-2026 13:30 | 348.121 | 357.905 | 1381.5 | 59.6508 | 63.3084 | -3.6575 | 379.8503 | 56 | 62.4031 | -6.4031 | 0.97266 | 19-03-2026 13:30 | 346.019 | 351.681 | 1394.6 | 58.6135 | 63.3084 | -4.6949 | 379.8503 | 55.7 | 62.4031 | -6.7031 | 0.9839 | 19-03-2026 13:30 | 266.908 | 271.165 | 1038.8 | 45.1942 | 46.8951 | -1.7009 | 281.3706 | 42.9 | 46.2245 | -3.3245 | 0.9843 | 19-03-2026 13:30 | 263.473 | 268.359 | 1034.2 | 44.7265 | 46.8951 | -2.1686 | 281.3706 | 42.3 | 46.2245 | -3.9245 | 0.98179 | 19-03-2026 13:30 | 260.293 | 264.418 | 1032.4 | 44.0697 | 46.8951 | -2.8254 | 281.3706 | 42.4 | 46.2245 | -3.8245 | 0.9844 | 19-03-2026 13:30 | 259.843 | 266.451 | 1039.8 | 44.4085 | 46.8951 | -2.4866 | 281.3706 | 42.7 | 46.2245 | -3.5245 | 0.9752 | 19-03-2026 13:30 | 249.905 | 253.955 | 984.9 | 42.3258 | 44.6149 | -2.289 | 267.6892 | 39.9 | 43.9769 | -4.0769 | 0.98405 | 19-03-2026 13:30 | 456.5363 | 485.4288 | -28.8924 | 2912.5726 | 434.4 | 478.4871 | -44.0871
19-03-2026 13:20 | 1013 | 48.79 | 338.478 | 344.437 | 1336.6 | 57.4062 | 60.3206 | -2.9144 | 361.9235 | 58.4 | 59.458 | -1.058 | 0.9827 | 19-03-2026 13:20 | 342.721 | 348.825 | 1348.8 | 58.1375 | 60.3206 | -2.1831 | 361.9235 | 56.8 | 59.458 | -2.658 | 0.9825 | 19-03-2026 13:20 | 336.939 | 346.646 | 1325.5 | 57.7743 | 60.3206 | -2.5462 | 361.9235 | 56.6 | 59.458 | -2.858 | 0.972 | 19-03-2026 13:20 | 339.015 | 345.018 | 1338.9 | 57.503 | 60.3206 | -2.8176 | 361.9235 | 57.2 | 59.458 | -2.258 | 0.9826 | 19-03-2026 13:20 | 254.411 | 258.548 | 995.9 | 43.0913 | 44.6819 | -1.5906 | 268.0915 | 42.1 | 44.043 | -1.943 | 0.984 | 19-03-2026 13:20 | 250.528 | 255.068 | 991.9 | 42.5113 | 44.6819 | -2.1706 | 268.0915 | 41.7 | 44.043 | -2.343 | 0.9822 | 19-03-2026 13:20 | 251.042 | 256.271 | 990 | 42.7118 | 44.6819 | -1.9701 | 268.0915 | 41.6 | 44.043 | -2.443 | 0.9796 | 19-03-2026 13:20 | 252.284 | 259.455 | 997.1 | 43.2425 | 44.6819 | -1.4394 | 268.0915 | 41.9 | 44.043 | -2.143 | 0.97236 | 19-03-2026 13:20 | 238.88 | 242.641 | 945 | 40.4402 | 42.5093 | -2.0691 | 255.0558 | 39.7 | 41.9014 | -2.2014 | 0.9845 | 19-03-2026 13:20 | 442.8182 | 462.5193 | -19.7011 | 2775.1158 | 436 | 455.9053 | -19.9053
19-03-2026 13:10 | 1024 | 48.79 | 341.809 | 347.862 | 1278.2 | 57.977 | 60.9756 | -2.9986 | 365.8536 | 54.2 | 60.1036 | -5.9036 | 0.9826 | 19-03-2026 13:10 | 347.098 | 351.891 | 1292 | 58.6485 | 60.9756 | -2.3271 | 365.8536 | 57.7 | 60.1036 | -2.4036 | 0.98638 | 19-03-2026 13:10 | 336.5 | 346.173 | 1268.9 | 57.6955 | 60.9756 | -3.2801 | 365.8536 | 56.9 | 60.1036 | -3.2036 | 0.97206 | 19-03-2026 13:10 | 336.514 | 340.639 | 1281.7 | 56.7732 | 60.9756 | -4.2024 | 365.8536 | 57.3 | 60.1036 | -2.8036 | 0.98789 | 19-03-2026 13:10 | 254.336 | 257.874 | 953.8 | 42.979 | 45.1671 | -2.1881 | 271.0026 | 43 | 44.5212 | -1.5212 | 0.98628 | 19-03-2026 13:10 | 250.757 | 255.53 | 950.2 | 42.5883 | 45.1671 | -2.5788 | 271.0026 | 42.6 | 44.5212 | -1.9212 | 0.98132 | 19-03-2026 13:10 | 251.692 | 257.187 | 948.4 | 42.8645 | 45.1671 | -2.3026 | 271.0026 | 42.5 | 44.5212 | -2.0212 | 0.97863 | 19-03-2026 13:10 | 252.61 | 260.347 | 955.2 | 43.3912 | 45.1671 | -1.7759 | 271.0026 | 42.8 | 44.5212 | -1.7212 | 0.97028 | 19-03-2026 13:10 | 238.757 | 242.615 | 905.3 | 40.4358 | 42.9709 | -2.5351 | 257.8254 | 40.5 | 42.3564 | -1.8564 | 0.9841 | 19-03-2026 13:10 | 443.353 | 467.5417 | -24.1887 | 2805.2503 | 437.5 | 460.8559 | -23.3559
19-03-2026 13:00 | 1072 | 48.79 | 351.732 | 357.488 | 1224 | 59.5813 | 63.8338 | -4.2525 | 383.003 | 60.2 | 62.921 | -2.721 | 0.9839 | 19-03-2026 13:00 | 349.955 | 355.536 | 1234.3 | 59.256 | 63.8338 | -4.5778 | 383.003 | 61.1 | 62.921 | -1.821 | 0.9843 | 19-03-2026 13:00 | 350.825 | 360.58 | 1212 | 60.0967 | 63.8338 | -3.7372 | 383.003 | 58.5 | 62.921 | -4.421 | 0.97295 | 19-03-2026 13:00 | 349.108 | 354.727 | 1224.4 | 59.1212 | 63.8338 | -4.7127 | 383.003 | 58.5 | 62.921 | -4.421 | 0.98416 | 19-03-2026 13:00 | 267.733 | 272.142 | 910.8 | 45.357 | 47.2843 | -1.9273 | 283.7059 | 44.8 | 46.6081 | -1.8081 | 0.9838 | 19-03-2026 13:00 | 264.001 | 268.844 | 907.6 | 44.8073 | 47.2843 | -2.477 | 283.7059 | 44.2 | 46.6081 | -2.4081 | 0.98199 | 19-03-2026 13:00 | 264.637 | 270.288 | 905.9 | 45.048 | 47.2843 | -2.2363 | 283.7059 | 44.3 | 46.6081 | -2.3081 | 0.97909 | 19-03-2026 13:00 | 266.348 | 274.177 | 912.4 | 45.6962 | 47.2843 | -1.5881 | 283.7059 | 44.5 | 46.6081 | -2.1081 | 0.97145 | 19-03-2026 13:00 | 251.577 | 255.668 | 864.8 | 42.6113 | 44.9852 | -2.3738 | 269.911 | 42.1 | 44.3419 | -2.2419 | 0.984 | 19-03-2026 13:00 | 461.575 | 489.4577 | -27.8827 | 2936.7464 | 458.2 | 482.4585 | -24.2585
19-03-2026 12:50 | 1062 | 48.79 | 352.55 | 358.465 | 1163.8 | 59.7442 | 63.2384 | -3.4942 | 379.4302 | 53.4 | 62.3341 | -8.9341 | 0.9835 | 19-03-2026 12:50 | 352.623 | 358.648 | 1173.2 | 59.7747 | 63.2384 | -3.4637 | 379.4302 | 53 | 62.3341 | -9.3341 | 0.9832 | 19-03-2026 12:50 | 352.276 | 362.212 | 1153.5 | 60.3687 | 63.2384 | -2.8697 | 379.4302 | 53.6 | 62.3341 | -8.7341 | 0.97257 | 19-03-2026 12:50 | 352.61 | 358.453 | 1165.9 | 59.7422 | 63.2384 | -3.4962 | 379.4302 | 54.2 | 62.3341 | -8.1341 | 0.9837 | 19-03-2026 12:50 | 269.346 | 273.657 | 866 | 45.6095 | 46.8432 | -1.2337 | 281.0594 | 40.4 | 46.1734 | -5.7734 | 0.98425 | 19-03-2026 12:50 | 265.975 | 270.814 | 863.4 | 45.1357 | 46.8432 | -1.7076 | 281.0594 | 40.6 | 46.1734 | -5.5734 | 0.98213 | 19-03-2026 12:50 | 266.619 | 271.699 | 861.6 | 45.2832 | 46.8432 | -1.5601 | 281.0594 | 40.5 | 46.1734 | -5.6734 | 0.9813 | 19-03-2026 12:50 | 267.975 | 276.078 | 867.9 | 46.013 | 46.8432 | -0.83023 | 281.0594 | 40.8 | 46.1734 | -5.3734 | 0.97065 | 19-03-2026 12:50 | 253.617 | 257.688 | 822.7 | 42.948 | 44.5655 | -1.6175 | 267.3932 | 38.6 | 43.9282 | -5.3282 | 0.9842 | 19-03-2026 12:50 | 464.619 | 484.8919 | -20.2729 | 2909.3514 | 415.1 | 477.9579 | -62.8579
19-03-2026 12:40 | 930 | 49.08 | 296.111 | 302.023 | 1110.4 | 50.3372 | 55.3169 | -4.9797 | 331.9015 | 49.9 | 54.5259 | -4.6259 | 0.98043 | 19-03-2026 12:40 | 320.311 | 325.751 | 1120.2 | 54.2918 | 55.3169 | -1.0251 | 331.9015 | 51.2 | 54.5259 | -3.3259 | 0.9833 | 19-03-2026 12:40 | 314.322 | 322.881 | 1099.9 | 53.8135 | 55.3169 | -1.5034 | 331.9015 | 49.4 | 54.5259 | -5.1259 | 0.97349 | 19-03-2026 12:40 | 315.8 | 321.098 | 1111.7 | 53.5163 | 55.3169 | -1.8006 | 331.9015 | 50.6 | 54.5259 | -3.9259 | 0.9835 | 19-03-2026 12:40 | 236.065 | 239.709 | 825.6 | 39.9515 | 40.9755 | -1.024 | 245.8529 | 37.8 | 40.3895 | -2.5895 | 0.9848 | 19-03-2026 12:40 | 222.57 | 226.606 | 822.8 | 37.7677 | 40.9755 | -3.2078 | 245.8529 | 36.8 | 40.3895 | -3.5895 | 0.98219 | 19-03-2026 12:40 | 225.184 | 229.617 | 821.1 | 38.2695 | 40.9755 | -2.706 | 245.8529 | 36.8 | 40.3895 | -3.5895 | 0.98069 | 19-03-2026 12:40 | 222.769 | 229.913 | 827.1 | 38.3188 | 40.9755 | -2.6567 | 245.8529 | 37 | 40.3895 | -3.3895 | 0.96893 | 19-03-2026 12:40 | 211.135 | 214.263 | 784.1 | 35.7105 | 38.9831 | -3.2726 | 233.8986 | 35.2 | 38.4256 | -3.2256 | 0.9854 | 19-03-2026 12:40 | 401.9768 | 424.1527 | -22.1759 | 2544.9162 | 384.7 | 418.0873 | -33.3873
19-03-2026 12:30 | 921 | 48.79 | 311.447 | 316.745 | 1060.5 | 52.7908 | 54.8423 | -2.0515 | 329.0538 | 54.5 | 54.0581 | 0.44194 | 0.98327 | 19-03-2026 12:30 | 315.316 | 320.639 | 1069 | 53.4398 | 54.8423 | -1.4025 | 329.0538 | 53.8 | 54.0581 | -0.25806 | 0.9834 | 19-03-2026 12:30 | 307.491 | 316.449 | 1050.5 | 52.7415 | 54.8423 | -2.1008 | 329.0538 | 53.2 | 54.0581 | -0.85806 | 0.97169 | 19-03-2026 12:30 | 312.747 | 317.994 | 1061.1 | 52.999 | 54.8423 | -1.8433 | 329.0538 | 53.3 | 54.0581 | -0.75806 | 0.9835 | 19-03-2026 12:30 | 233.661 | 237.34 | 787.8 | 39.5567 | 40.6239 | -1.0673 | 243.7436 | 39.5 | 40.043 | -0.54301 | 0.9845 | 19-03-2026 12:30 | 232.311 | 236.666 | 786 | 39.4443 | 40.6239 | -1.1796 | 243.7436 | 39.3 | 40.043 | -0.74301 | 0.9816 | 19-03-2026 12:30 | 232.131 | 235.862 | 784.3 | 39.3103 | 40.6239 | -1.3136 | 243.7436 | 39.3 | 40.043 | -0.74301 | 0.98418 | 19-03-2026 12:30 | 234.856 | 241.961 | 790.1 | 40.3268 | 40.6239 | -0.2971 | 243.7436 | 40.2 | 40.043 | 0.15699 | 0.97064 | 19-03-2026 12:30 | 223.183 | 226.513 | 748.9 | 37.7522 | 38.6486 | -0.89647 | 231.8918 | 38 | 38.096 | -0.095964 | 0.9853 | 19-03-2026 12:30 | 408.3615 | 420.5136 | -12.1521 | 2523.0815 | 411.1 | 414.5002 | -3.4002
19-03-2026 12:20 | 978 | 49.36 | 332.2 | 337.911 | 1006 | 56.3185 | 58.1097 | -1.7912 | 348.6583 | 57.5 | 57.2788 | 0.22125 | 0.9831 | 19-03-2026 12:20 | 339.608 | 345.552 | 1015.2 | 57.592 | 58.1097 | -0.51772 | 348.6583 | 57.7 | 57.2788 | 0.42125 | 0.9828 | 19-03-2026 12:20 | 328.065 | 337.087 | 997.3 | 56.1812 | 58.1097 | -1.9286 | 348.6583 | 57 | 57.2788 | -0.27875 | 0.97324 | 19-03-2026 12:20 | 331.927 | 337.77 | 1007.8 | 56.295 | 58.1097 | -1.8147 | 348.6583 | 57.4 | 57.2788 | 0.12125 | 0.9827 | 19-03-2026 12:20 | 248.982 | 252.979 | 748.3 | 42.1632 | 43.0442 | -0.88107 | 258.2654 | 43.1 | 42.4287 | 0.67129 | 0.9842 | 19-03-2026 12:20 | 246.81 | 251.003 | 746.7 | 41.8338 | 43.0442 | -1.2104 | 258.2654 | 42.7 | 42.4287 | 0.27129 | 0.9833 | 19-03-2026 12:20 | 247.031 | 251.82 | 745 | 41.97 | 43.0442 | -1.0742 | 258.2654 | 42.6 | 42.4287 | 0.17129 | 0.98098 | 19-03-2026 12:20 | 249.046 | 256.361 | 749.9 | 42.7268 | 43.0442 | -0.31741 | 258.2654 | 42.3 | 42.4287 | -0.12871 | 0.97147 | 19-03-2026 12:20 | 234.66 | 238.379 | 710.9 | 39.7298 | 40.9513 | -1.2214 | 245.7076 | 40.6 | 40.3657 | 0.23434 | 0.9844 | 19-03-2026 12:20 | 434.8103 | 445.5671 | -10.7568 | 2673.4026 | 440.9 | 439.1955 | 1.7045
19-03-2026 12:10 | 1030 | 48.79 | 347.366 | 353.373 | 948.5 | 58.8955 | 61.3329 | -2.4374 | 367.9972 | 56.1 | 60.4558 | -4.3558 | 0.983 | 19-03-2026 12:10 | 351.9 | 357.949 | 957.5 | 59.6582 | 61.3329 | -1.6747 | 367.9972 | 116 | 60.4558 | 55.5442 | 0.9831 | 19-03-2026 12:10 | 343.921 | 352.985 | 940.3 | 58.8308 | 61.3329 | -2.502 | 367.9972 | 56.5 | 60.4558 | -3.9558 | 0.97432 | 19-03-2026 12:10 | 349.341 | 355.455 | 950.4 | 59.2425 | 61.3329 | -2.0904 | 367.9972 | 57.2 | 60.4558 | -3.2558 | 0.9828 | 19-03-2026 12:10 | 259.922 | 264.041 | 705.2 | 44.0068 | 45.4318 | -1.4249 | 272.5905 | 43.2 | 44.7821 | -1.5821 | 0.9844 | 19-03-2026 12:10 | 258.299 | 262.419 | 704 | 43.7365 | 45.4318 | -1.6953 | 272.5905 | 42.9 | 44.7821 | -1.8821 | 0.9843 | 19-03-2026 12:10 | 257.972 | 262.759 | 702.4 | 43.7932 | 45.4318 | -1.6386 | 272.5905 | 42.8 | 44.7821 | -1.9821 | 0.98178 | 19-03-2026 12:10 | 259.646 | 267.038 | 707.6 | 44.5063 | 45.4318 | -0.92542 | 272.5905 | 43.1 | 44.7821 | -1.6821 | 0.97232 | 19-03-2026 12:10 | 246.01 | 249.883 | 670.3 | 41.6472 | 43.2227 | -1.5755 | 259.3361 | 40.8 | 42.6046 | -1.8046 | 0.9845 | 19-03-2026 12:10 | 454.317 | 470.2812 | -15.9642 | 2821.6873 | 498.6 | 463.5562 | 35.0438
19-03-2026 12:00 | 1008 | 49.08 | 343.237 | 349.066 | 892.4 | 58.1777 | 59.9564 | -1.7787 | 359.7384 | 57.7 | 59.099 | -1.399 | 0.9833 |  |  |  |  | 0 | 59.9564 | -59.9564 | 359.7384 | 0 | 59.099 | -59.099 |  | 19-03-2026 12:00 | 340.094 | 349.22 | 883.8 | 58.2033 | 59.9564 | -1.7531 | 359.7384 | 56.4 | 59.099 | -2.699 | 0.97387 | 19-03-2026 12:00 | 344.403 | 350.887 | 893.2 | 58.4812 | 59.9564 | -1.4752 | 359.7384 | 57 | 59.099 | -2.099 | 0.98152 | 19-03-2026 12:00 | 257.058 | 261.105 | 662 | 43.5175 | 44.4121 | -0.89464 | 266.4729 | 41.9 | 43.7771 | -1.8771 | 0.9845 | 19-03-2026 12:00 | 255.855 | 260.145 | 661.1 | 43.3575 | 44.4121 | -1.0546 | 266.4729 | 41.6 | 43.7771 | -2.1771 | 0.98351 | 19-03-2026 12:00 | 254.292 | 259.068 | 659.6 | 43.178 | 44.4121 | -1.2341 | 266.4729 | 41.7 | 43.7771 | -2.0771 | 0.98156 | 19-03-2026 12:00 | 256.216 | 263.509 | 664.5 | 43.9182 | 44.4121 | -0.49398 | 266.4729 | 41.9 | 43.7771 | -1.8771 | 0.97232 | 19-03-2026 12:00 | 243.979 | 247.77 | 629.5 | 41.295 | 42.2527 | -0.95765 | 253.5159 | 39.1 | 41.6484 | -2.5484 | 0.9847 | 19-03-2026 12:00 | 390.1283 | 459.7268 | -69.5985 | 2758.3608 | 377.3 | 453.1527 | -75.8527
19-03-2026 11:50 | 977 | 49.08 | 331.501 | 339.23 | 834.7 | 56.5383 | 58.1125 | -1.5742 | 348.675 | 55 | 57.2815 | -2.2815 | 0.97722 | 19-03-2026 11:50 | 334.251 | 339.928 | 841.5 | 56.6547 | 58.1125 | -1.4578 | 348.675 | 56.6 | 57.2815 | -0.68149 | 0.9833 | 19-03-2026 11:50 | 333.442 | 342.578 | 827.4 | 57.0963 | 58.1125 | -1.0162 | 348.675 | 54.6 | 57.2815 | -2.6815 | 0.97333 | 19-03-2026 11:50 | 334.891 | 340.613 | 836.2 | 56.7688 | 58.1125 | -1.3437 | 348.675 | 55.1 | 57.2815 | -2.1815 | 0.9832 | 19-03-2026 11:50 | 252.767 | 256.721 | 620.1 | 42.7868 | 43.0463 | -0.25946 | 258.2778 | 41.3 | 42.4307 | -1.1307 | 0.9846 | 19-03-2026 11:50 | 249.637 | 253.744 | 619.5 | 42.2907 | 43.0463 | -0.75563 | 258.2778 | 40.9 | 42.4307 | -1.5307 | 0.98381 | 19-03-2026 11:50 | 251.029 | 255.437 | 617.9 | 42.5728 | 43.0463 | -0.47346 | 258.2778 | 40.9 | 42.4307 | -1.5307 | 0.98274 | 19-03-2026 11:50 | 252.753 | 260.192 | 622.6 | 43.3653 | 43.0463 | 0.31904 | 258.2778 | 41.8 | 42.4307 | -0.63073 | 0.97141 | 19-03-2026 11:50 | 239.215 | 242.907 | 590.4 | 40.4845 | 40.9532 | -0.46872 | 245.7193 | 39.6 | 40.3676 | -0.76759 | 0.9848 | 19-03-2026 11:50 | 438.5583 | 445.5884 | -7.03 | 2673.5303 | 425.8 | 439.2165 | -13.4165
19-03-2026 11:40 | 974 | 48.79 | 330.659 | 336.104 | 779.7 | 56.0173 | 57.9983 | -1.9809 | 347.9896 | 53.5 | 57.1689 | -3.6689 | 0.9838 | 19-03-2026 11:40 | 336.702 | 342.351 | 784.9 | 57.0585 | 57.9983 | -0.93977 | 347.9896 | 54.1 | 57.1689 | -3.0689 | 0.9835 | 19-03-2026 11:40 | 333.782 | 342.551 | 772.8 | 57.0918 | 57.9983 | -0.90644 | 347.9896 | 53.9 | 57.1689 | -3.2689 | 0.9744 | 19-03-2026 11:40 | 336.62 | 341.811 | 781.1 | 56.9685 | 57.9983 | -1.0298 | 347.9896 | 54.4 | 57.1689 | -2.7689 | 0.98481 | 19-03-2026 11:40 | 250.264 | 254.075 | 578.8 | 42.3458 | 42.9617 | -0.61585 | 257.7701 | 40.6 | 42.3473 | -1.7473 | 0.985 | 19-03-2026 11:40 | 249.357 | 253.157 | 578.6 | 42.1928 | 42.9617 | -0.76885 | 257.7701 | 40.3 | 42.3473 | -2.0473 | 0.98499 | 19-03-2026 11:40 | 248.206 | 252.804 | 577 | 42.134 | 42.9617 | -0.82768 | 257.7701 | 40.3 | 42.3473 | -2.0473 | 0.98181 | 19-03-2026 11:40 | 249.517 | 256.8 | 580.8 | 42.8 | 42.9617 | -0.16168 | 257.7701 | 40 | 42.3473 | -2.3473 | 0.97164 | 19-03-2026 11:40 | 236.091 | 239.588 | 550.8 | 39.9313 | 40.8727 | -0.94139 | 245.2363 | 37.9 | 40.2882 | -2.3882 | 0.9854 | 19-03-2026 11:40 | 436.5402 | 444.7125 | -8.1724 | 2668.2752 | 415 | 438.3531 | -23.3531
19-03-2026 11:30 | 893 | 48.79 | 310.946 | 315.938 | 726.2 | 52.6563 | 53.175 | -0.51867 | 319.05 | 56 | 52.4146 | 3.5854 | 0.9842 | 19-03-2026 11:30 | 318.951 | 324.203 | 730.8 | 54.0338 | 53.175 | 0.85883 | 319.05 | 54.2 | 52.4146 | 1.7854 | 0.9838 | 19-03-2026 11:30 | 307.624 | 315.416 | 718.9 | 52.5693 | 53.175 | -0.60567 | 319.05 | 53.8 | 52.4146 | 1.3854 | 0.9753 | 19-03-2026 11:30 | 310.488 | 315.537 | 726.7 | 52.5895 | 53.175 | -0.58551 | 319.05 | 54.5 | 52.4146 | 2.0854 | 0.984 | 19-03-2026 11:30 | 233.26 | 236.716 | 538.2 | 39.4527 | 39.3889 | 0.063774 | 236.3334 | 40.5 | 38.8256 | 1.6744 | 0.9854 | 19-03-2026 11:30 | 230.293 | 233.855 | 538.3 | 38.9758 | 39.3889 | -0.41306 | 236.3334 | 40.3 | 38.8256 | 1.4744 | 0.98477 | 19-03-2026 11:30 | 233.488 | 237.812 | 536.7 | 39.6353 | 39.3889 | 0.24644 | 236.3334 | 41 | 38.8256 | 2.1744 | 0.98182 | 19-03-2026 11:30 | 235.894 | 242.819 | 540.8 | 40.4698 | 39.3889 | 1.0809 | 236.3334 | 41.3 | 38.8256 | 2.4744 | 0.97148 | 19-03-2026 11:30 | 221.607 | 224.822 | 512.9 | 37.4703 | 37.4737 | -0.00332 | 224.8419 | 39.1 | 36.9378 | 2.1622 | 0.9857 | 19-03-2026 11:30 | 407.853 | 407.7292 | 0.12375 | 2446.3755 | 420.7 | 401.8987 | 18.8013
19-03-2026 11:20 | 945 | 49.08 | 321.532 | 332.962 | 670.2 | 55.4937 | 56.2091 | -0.71545 | 337.2547 | 50 | 55.4053 | -5.4053 | 0.96567 | 19-03-2026 11:20 | 330.191 | 335.696 | 676.6 | 55.9493 | 56.2091 | -0.25979 | 337.2547 | 53.2 | 55.4053 | -2.2053 | 0.9836 | 19-03-2026 11:20 | 320.167 | 328.974 | 665.1 | 54.829 | 56.2091 | -1.3801 | 337.2547 | 50.5 | 55.4053 | -4.9053 | 0.97323 | 19-03-2026 11:20 | 325.038 | 330.491 | 672.2 | 55.0818 | 56.2091 | -1.1273 | 337.2547 | 50.9 | 55.4053 | -4.5053 | 0.9835 | 19-03-2026 11:20 | 242.436 | 246.153 | 497.7 | 41.0255 | 41.6364 | -0.61088 | 249.8183 | 38.4 | 41.041 | -2.641 | 0.9849 | 19-03-2026 11:20 | 239.709 | 243.73 | 498 | 40.6217 | 41.6364 | -1.0147 | 249.8183 | 38.2 | 41.041 | -2.841 | 0.9835 | 19-03-2026 11:20 | 241.479 | 245.29 | 495.7 | 40.8817 | 41.6364 | -0.75472 | 249.8183 | 37.5 | 41.041 | -3.541 | 0.98446 | 19-03-2026 11:20 | 243.324 | 250.201 | 499.5 | 41.7002 | 41.6364 | 0.063782 | 249.8183 | 37.9 | 41.041 | -3.141 | 0.97251 | 19-03-2026 11:20 | 231.284 | 234.735 | 473.8 | 39.1225 | 39.6119 | -0.48936 | 237.6712 | 35.8 | 39.0454 | -3.2454 | 0.9853 | 19-03-2026 11:20 | 424.7053 | 430.9939 | -6.2885 | 2585.9633 | 392.4 | 424.8307 | -32.4307
19-03-2026 11:10 | 788 | 49.36 | 272.485 | 276.719 | 620.2 | 46.1198 | 46.8205 | -0.70068 | 280.9231 | 49 | 46.151 | 2.849 | 0.9847 | 19-03-2026 11:10 | 269.737 | 273.956 | 623.4 | 45.6593 | 46.8205 | -1.1612 | 280.9231 | 48.1 | 46.151 | 1.949 | 0.9846 | 19-03-2026 11:10 | 271.656 | 278.228 | 614.6 | 46.3713 | 46.8205 | -0.44918 | 280.9231 | 48.3 | 46.151 | 2.149 | 0.97638 | 19-03-2026 11:10 | 271.59 | 275.922 | 621.3 | 45.987 | 46.8205 | -0.83351 | 280.9231 | 48.9 | 46.151 | 2.749 | 0.9843 | 19-03-2026 11:10 | 203.072 | 206.039 | 459.3 | 34.3398 | 34.6819 | -0.34203 | 208.0912 | 35.9 | 34.1859 | 1.7141 | 0.9856 | 19-03-2026 11:10 | 201.662 | 204.753 | 459.8 | 34.1255 | 34.6819 | -0.55636 | 208.0912 | 35.8 | 34.1859 | 1.6141 | 0.9849 | 19-03-2026 11:10 | 201.716 | 204.978 | 458.2 | 34.163 | 34.6819 | -0.51886 | 208.0912 | 35.7 | 34.1859 | 1.5141 | 0.98409 | 19-03-2026 11:10 | 203.43 | 209.114 | 461.6 | 34.8523 | 34.6819 | 0.17047 | 208.0912 | 35.8 | 34.1859 | 1.6141 | 0.97282 | 19-03-2026 11:10 | 192.539 | 195.273 | 438 | 32.5455 | 32.9955 | -0.45 | 197.973 | 34.5 | 32.5237 | 1.9763 | 0.986 | 19-03-2026 11:10 | 354.1637 | 359.005 | -4.8413 | 2154.0299 | 372 | 353.8712 | 18.1288
19-03-2026 11:00 | 871 | 48.79 | 303.619 | 308.431 | 571.2 | 51.4052 | 51.865 | -0.45982 | 311.1899 | 48.2 | 51.1233 | -2.9233 | 0.9844 | 19-03-2026 11:00 | 307.06 | 312.085 | 575.3 | 52.0142 | 51.865 | 0.14918 | 311.1899 | 50 | 51.1233 | -1.1233 | 0.9839 | 19-03-2026 11:00 | 300.27 | 307.914 | 566.3 | 51.319 | 51.865 | -0.54598 | 311.1899 | 47.8 | 51.1233 | -3.3233 | 0.97517 | 19-03-2026 11:00 | 302.955 | 308.016 | 572.4 | 51.336 | 51.865 | -0.52898 | 311.1899 | 48.5 | 51.1233 | -2.6233 | 0.98357 | 19-03-2026 11:00 | 225.09 | 228.425 | 423.4 | 38.0708 | 38.4185 | -0.34767 | 230.511 | 36.3 | 37.8691 | -1.5691 | 0.9854 | 19-03-2026 11:00 | 223.454 | 226.874 | 424 | 37.8123 | 38.4185 | -0.60617 | 230.511 | 36.8 | 37.8691 | -1.0691 | 0.98493 | 19-03-2026 11:00 | 223.572 | 227.331 | 422.5 | 37.8885 | 38.4185 | -0.53001 | 230.511 | 36.2 | 37.8691 | -1.6691 | 0.98346 | 19-03-2026 11:00 | 224.47 | 231.034 | 425.8 | 38.5057 | 38.4185 | 0.087161 | 230.511 | 36.5 | 37.8691 | -1.3691 | 0.97159 | 19-03-2026 11:00 | 213.316 | 216.411 | 403.5 | 36.0685 | 36.5505 | -0.48195 | 219.3027 | 34.2 | 36.0278 | -1.8278 | 0.9857 | 19-03-2026 11:00 | 394.4202 | 397.6844 | -3.2642 | 2386.1064 | 374.5 | 391.9975 | -17.4975
19-03-2026 10:50 | 805 | 48.79 | 280.795 | 285.158 | 523 | 47.5263 | 47.9349 | -0.40858 | 287.6095 | 47.8 | 47.2494 | 0.55055 | 0.9847 | 19-03-2026 10:50 | 285.726 | 290.432 | 525.3 | 48.4053 | 47.9349 | 0.47042 | 287.6095 | 46.9 | 47.2494 | -0.34945 | 0.9838 | 19-03-2026 10:50 | 280.417 | 287.265 | 518.5 | 47.8775 | 47.9349 | -0.057415 | 287.6095 | 47.7 | 47.2494 | 0.45055 | 0.97616 | 19-03-2026 10:50 | 283.154 | 287.612 | 523.9 | 47.9353 | 47.9349 | 0.00041787 | 287.6095 | 48.3 | 47.2494 | 1.0506 | 0.9845 | 19-03-2026 10:50 | 210.592 | 213.625 | 387.1 | 35.6042 | 35.5073 | 0.096822 | 213.0441 | 35.5 | 34.9996 | 0.50041 | 0.9858 | 19-03-2026 10:50 | 209.52 | 212.495 | 387.2 | 35.4158 | 35.5073 | -0.091511 | 213.0441 | 34.8 | 34.9996 | -0.19959 | 0.986 | 19-03-2026 10:50 | 209.764 | 213.256 | 386.3 | 35.5427 | 35.5073 | 0.035322 | 213.0441 | 35.7 | 34.9996 | 0.70041 | 0.98363 | 19-03-2026 10:50 | 211.027 | 217.002 | 389.3 | 36.167 | 35.5073 | 0.65966 | 213.0441 | 36 | 34.9996 | 1.0004 | 0.97247 | 19-03-2026 10:50 | 200.171 | 202.773 | 369.3 | 33.7955 | 33.7808 | 0.014659 | 202.685 | 34.2 | 33.2978 | 0.90223 | 0.98717 | 19-03-2026 10:50 | 368.2697 | 367.5499 | 0.71978 | 2205.2993 | 366.9 | 362.2939 | 4.6061
19-03-2026 10:40 | 843 | 49.36 | 291.603 | 301.423 | 475.2 | 50.2372 | 50.0884 | 0.14873 | 300.5306 | 46.9 | 49.3722 | -2.4722 | 0.96742 | 19-03-2026 10:40 | 297.819 | 303.417 | 478.4 | 50.5695 | 50.0884 | 0.48106 | 300.5306 | 47.2 | 49.3722 | -2.1722 | 0.98155 | 19-03-2026 10:40 | 293.999 | 301.264 | 470.8 | 50.2107 | 50.0884 | 0.12223 | 300.5306 | 46.3 | 49.3722 | -3.0722 | 0.97588 | 19-03-2026 10:40 | 296.515 | 301.153 | 475.6 | 50.1922 | 50.0884 | 0.10373 | 300.5306 | 46.8 | 49.3722 | -2.5722 | 0.9846 | 19-03-2026 10:40 | 220.905 | 224.087 | 351.6 | 37.3478 | 37.1025 | 0.24528 | 222.6153 | 34.8 | 36.572 | -1.772 | 0.9858 | 19-03-2026 10:40 | 219.997 | 223.143 | 352.4 | 37.1905 | 37.1025 | 0.087951 | 222.6153 | 34.8 | 36.572 | -1.772 | 0.9859 | 19-03-2026 10:40 | 218.8 | 222.309 | 350.6 | 37.0515 | 37.1025 | -0.051049 | 222.6153 | 34.1 | 36.572 | -2.472 | 0.98422 | 19-03-2026 10:40 | 220.215 | 226.731 | 353.3 | 37.7885 | 37.1025 | 0.68595 | 222.6153 | 34.3 | 36.572 | -2.272 | 0.97126 | 19-03-2026 10:40 | 208.123 | 211.057 | 335.1 | 35.1762 | 35.2985 | -0.12231 | 211.7909 | 33.1 | 34.7937 | -1.6937 | 0.9861 | 19-03-2026 10:40 | 385.764 | 384.0624 | 1.7016 | 2304.3747 | 358.3 | 378.5703 | -20.2703
19-03-2026 10:30 | 757 | 48.79 | 270.39 | 271.869 | 428.3 | 45.3115 | 45.0767 | 0.23482 | 270.4601 | 45.1 | 44.4321 | 0.66791 | 0.99456 | 19-03-2026 10:30 | 275.278 | 279.442 | 431.2 | 46.5737 | 45.0767 | 1.497 | 270.4601 | 45.5 | 44.4321 | 1.0679 | 0.9851 | 19-03-2026 10:30 | 264.289 | 269.507 | 424.5 | 44.9178 | 45.0767 | -0.15885 | 270.4601 | 44.1 | 44.4321 | -0.33209 | 0.98064 | 19-03-2026 10:30 | 268.549 | 272.55 | 428.8 | 45.425 | 45.0767 | 0.34832 | 270.4601 | 44.6 | 44.4321 | 0.16791 | 0.98532 | 19-03-2026 10:30 | 197.886 | 200.614 | 316.8 | 33.4357 | 33.3901 | 0.04553 | 200.3408 | 33.1 | 32.9127 | 0.18734 | 0.9864 | 19-03-2026 10:30 | 198.557 | 201.559 | 317.6 | 33.5932 | 33.3901 | 0.20303 | 200.3408 | 33 | 32.9127 | 0.087342 | 0.98511 | 19-03-2026 10:30 | 197.277 | 200.685 | 316.5 | 33.4475 | 33.3901 | 0.057363 | 200.3408 | 32.9 | 32.9127 | -0.012658 | 0.98302 | 19-03-2026 10:30 | 198.702 | 204.374 | 319 | 34.0623 | 33.3901 | 0.6722 | 200.3408 | 33.1 | 32.9127 | 0.18734 | 0.97225 | 19-03-2026 10:30 | 188.584 | 191.165 | 302 | 31.8608 | 31.7666 | 0.094254 | 190.5995 | 30.9 | 31.3123 | -0.41232 | 0.9865 | 19-03-2026 10:30 | 348.6275 | 345.6339 | 2.9936 | 2073.8032 | 342.3 | 340.6913 | 1.6087
19-03-2026 10:20 | 716 | 49.08 | 260.385 | 264.274 | 383.2 | 44.0457 | 42.5881 | 1.4576 | 255.5284 | 41.7 | 41.9791 | -0.27906 | 0.98528 | 19-03-2026 10:20 | 261.17 | 264.986 | 385.7 | 44.1643 | 42.5881 | 1.5763 | 255.5284 | 42.7 | 41.9791 | 0.72094 | 0.9856 | 19-03-2026 10:20 | 254.082 | 259.814 | 380.4 | 43.3023 | 42.5881 | 0.71426 | 255.5284 | 41.9 | 41.9791 | -0.079064 | 0.97794 | 19-03-2026 10:20 | 256.817 | 260.622 | 384.2 | 43.437 | 42.5881 | 0.84893 | 255.5284 | 42.2 | 41.9791 | 0.22094 | 0.9854 | 19-03-2026 10:20 | 190.102 | 192.684 | 283.7 | 32.114 | 31.5467 | 0.56728 | 189.2803 | 31.3 | 31.0956 | 0.2044 | 0.9866 | 19-03-2026 10:20 | 190.305 | 192.87 | 284.6 | 32.145 | 31.5467 | 0.59828 | 189.2803 | 31.2 | 31.0956 | 0.1044 | 0.9867 | 19-03-2026 10:20 | 189.004 | 191.573 | 283.6 | 31.9288 | 31.5467 | 0.38211 | 189.2803 | 31.7 | 31.0956 | 0.6044 | 0.98659 | 19-03-2026 10:20 | 190.55 | 195.68 | 285.9 | 32.6133 | 31.5467 | 1.0666 | 189.2803 | 31.8 | 31.0956 | 0.7044 | 0.97378 | 19-03-2026 10:20 | 181.303 | 183.765 | 271.1 | 30.6275 | 30.0128 | 0.6147 | 180.0768 | 30.2 | 29.5836 | 0.61639 | 0.9866 | 19-03-2026 10:20 | 334.378 | 326.552 | 7.826 | 1959.3119 | 324.7 | 321.8823 | 2.8177
19-03-2026 10:10 | 730 | 49.08 | 260.359 | 264.083 | 341.5 | 44.0138 | 43.4208 | 0.59303 | 260.5248 | 43.3 | 42.7999 | 0.50012 | 0.9859 | 19-03-2026 10:10 | 265.65 | 269.531 | 343 | 44.9218 | 43.4208 | 1.501 | 260.5248 | 43 | 42.7999 | 0.20012 | 0.9856 | 19-03-2026 10:10 | 260.434 | 266.239 | 338.5 | 44.3732 | 43.4208 | 0.95237 | 260.5248 | 42.4 | 42.7999 | -0.39988 | 0.9782 | 19-03-2026 10:10 | 262.486 | 266.321 | 342 | 44.3868 | 43.4208 | 0.96603 | 260.5248 | 42.9 | 42.7999 | 0.10012 | 0.9856 | 19-03-2026 10:10 | 196.372 | 198.999 | 252.4 | 33.1665 | 32.1636 | 1.0029 | 192.9813 | 31.9 | 31.7036 | 0.19638 | 0.9868 | 19-03-2026 10:10 | 194.877 | 197.464 | 253.4 | 32.9107 | 32.1636 | 0.74711 | 192.9813 | 31.9 | 31.7036 | 0.19638 | 0.9869 | 19-03-2026 10:10 | 194.64 | 197.224 | 251.9 | 32.8707 | 32.1636 | 0.70711 | 192.9813 | 31.3 | 31.7036 | -0.40362 | 0.9869 | 19-03-2026 10:10 | 195.124 | 200.578 | 254.1 | 33.4297 | 32.1636 | 1.2661 | 192.9813 | 31.6 | 31.7036 | -0.10362 | 0.97281 | 19-03-2026 10:10 | 185.734 | 188.18 | 240.9 | 31.3633 | 30.5996 | 0.76369 | 183.5978 | 30 | 30.1621 | -0.16207 | 0.987 | 19-03-2026 10:10 | 341.4365 | 332.9371 | 8.4994 | 1997.6224 | 328.3 | 328.1761 | 0.12393
19-03-2026 10:00 | 683 | 46.49 | 246.834 | 250.212 | 298.2 | 41.702 | 41.0274 | 0.67462 | 246.1643 | 34.8 | 40.4407 | -5.6407 | 0.9865 | 19-03-2026 10:00 | 248.82 | 252.251 | 300 | 42.0418 | 41.0274 | 1.0145 | 246.1643 | 36.4 | 40.4407 | -4.0407 | 0.9864 | 19-03-2026 10:00 | 246.69 | 251.584 | 296.1 | 41.9307 | 41.0274 | 0.90329 | 246.1643 | 34.5 | 40.4407 | -5.9407 | 0.98055 | 19-03-2026 10:00 | 246.006 | 249.448 | 299.1 | 41.5747 | 41.0274 | 0.54729 | 246.1643 | 34.8 | 40.4407 | -5.6407 | 0.9862 | 19-03-2026 10:00 | 185.032 | 187.412 | 220.5 | 31.2353 | 30.3906 | 0.84468 | 182.3439 | 25.7 | 29.9561 | -4.2561 | 0.9873 | 19-03-2026 10:00 | 184.336 | 186.225 | 221.5 | 31.0375 | 30.3906 | 0.64685 | 182.3439 | 25.8 | 29.9561 | -4.1561 | 0.98986 | 19-03-2026 10:00 | 184.626 | 186.982 | 220.6 | 31.1637 | 30.3906 | 0.77302 | 182.3439 | 25.7 | 29.9561 | -4.2561 | 0.9874 | 19-03-2026 10:00 | 186.036 | 190.971 | 222.5 | 31.8285 | 30.3906 | 1.4379 | 182.3439 | 26.3 | 29.9561 | -3.6561 | 0.97416 | 19-03-2026 10:00 | 176.242 | 178.509 | 210.9 | 29.7515 | 28.9129 | 0.83856 | 173.4776 | 24.9 | 28.4995 | -3.5995 | 0.9873 | 19-03-2026 10:00 | 322.2657 | 314.585 | 7.6806 | 1887.5103 | 268.9 | 310.0865 | -41.1865
19-03-2026 09:50 | 730 | 45.63 | 278.039 | 281.901 | 263.4 | 46.9835 | 43.9934 | 2.9901 | 263.9602 | 29.3 | 43.3643 | -14.0643 |  | 19-03-2026 09:50 | 267.792 | 271.567 | 263.6 | 45.2612 | 43.9934 | 1.2678 | 263.9602 | 28.3 | 43.3643 | -15.0643 |  | 19-03-2026 09:50 | 262.006 | 267.324 | 261.6 | 44.554 | 43.9934 | 0.56064 | 263.9602 | 29.7 | 43.3643 | -13.6643 |  | 19-03-2026 09:50 | 269.546 | 273.373 | 264.3 | 45.5622 | 43.9934 | 1.5688 | 263.9602 | 29.9 | 43.3643 | -13.4643 |  | 19-03-2026 09:50 | 195.49 | 198.025 | 194.8 | 33.0042 | 32.5877 | 0.41649 | 195.5261 | 22.3 | 32.1217 | -9.8217 |  | 19-03-2026 09:50 | 197.127 | 199.663 | 195.7 | 33.2772 | 32.5877 | 0.68949 | 195.5261 | 22.3 | 32.1217 | -9.8217 |  | 19-03-2026 09:50 | 200.216 | 202.771 | 194.9 | 33.7952 | 32.5877 | 1.2075 | 195.5261 | 22.3 | 32.1217 | -9.8217 |  | 19-03-2026 09:50 | 202.908 | 208.038 | 196.2 | 34.673 | 32.5877 | 2.0853 | 195.5261 | 22.2 | 32.1217 | -9.9217 |  | 19-03-2026 09:50 | 193.437 | 195.925 | 186 | 32.6542 | 31.0031 | 1.651 | 186.0188 | 21.1 | 30.5598 | -9.4598 |  | 19-03-2026 09:50 | 349.7645 | 337.3273 | 12.4372 | 2023.9638 | 227.4 | 332.5035 | -105.1035
19-03-2026 09:40 | 279 | 44.77 | 101.045 | 102.283 | 234.1 | 17.0472 | 16.8685 | 0.17872 | 101.2107 | 29.7 | 16.6272 | 13.0728 |  | 19-03-2026 09:40 | 105.095 | 103.344 | 235.3 | 17.224 | 16.8685 | 0.35555 | 101.2107 | 28.6 | 16.6272 | 11.9728 |  | 19-03-2026 09:40 | 99.619 | 100.962 | 231.9 | 16.827 | 16.8685 | -0.04145 | 101.2107 | 28.3 | 16.6272 | 11.6728 |  | 19-03-2026 09:40 | 100.627 | 101.901 | 234.4 | 16.9835 | 16.8685 | 0.11505 | 101.2107 | 28.7 | 16.6272 | 12.0728 |  | 19-03-2026 09:40 | 73.976 | 74.973 | 172.5 | 12.4955 | 12.4951 | 0.00035169 | 74.9709 | 21.1 | 12.3165 | 8.7835 |  | 19-03-2026 09:40 | 74.124 | 75.1 | 173.4 | 12.5167 | 12.4951 | 0.021518 | 74.9709 | 21.2 | 12.3165 | 8.8835 |  | 19-03-2026 09:40 | 73.642 | 74.62 | 172.6 | 12.4367 | 12.4951 | -0.058482 | 74.9709 | 21.5 | 12.3165 | 9.1835 |  | 19-03-2026 09:40 | 74.064 | 75.921 | 174 | 12.6535 | 12.4951 | 0.15835 | 74.9709 | 21.6 | 12.3165 | 9.2835 |  | 19-03-2026 09:40 | 70.442 | 71.399 | 164.9 | 11.8998 | 11.8876 | 0.012247 | 71.3255 | 20.4 | 11.7176 | 8.6824 |  | 19-03-2026 09:40 | 130.0838 | 129.342 | 0.74185 | 776.0519 | 221.1 | 127.4924 | 93.6076
19-03-2026 09:30 | 667 | 47.64 | 290.105 | 294.344 | 204.4 | 49.0573 | 39.8919 | 9.1654 | 239.3513 | 41.2 | 39.3214 | 1.8786 |  | 19-03-2026 09:30 | 246.274 | 251.284 | 206.7 | 41.8807 | 39.8919 | 1.9888 | 239.3513 | 43.1 | 39.3214 | 3.7786 |  | 19-03-2026 09:30 | 236.942 | 240.733 | 203.6 | 40.1222 | 39.8919 | 0.23028 | 239.3513 | 41.8 | 39.3214 | 2.4786 |  | 19-03-2026 09:30 | 243.772 | 249.2 | 205.7 | 41.5333 | 39.8919 | 1.6414 | 239.3513 | 42.3 | 39.3214 | 2.9786 |  | 19-03-2026 09:30 | 176.723 | 179.014 | 151.4 | 29.8357 | 29.5495 | 0.28612 | 177.2973 | 31.5 | 29.127 | 2.373 |  | 19-03-2026 09:30 | 178.781 | 182.799 | 152.2 | 30.4665 | 29.5495 | 0.91696 | 177.2973 | 31.6 | 29.127 | 2.473 |  | 19-03-2026 09:30 | 190.422 | 192.891 | 151.1 | 32.1485 | 29.5495 | 2.599 | 177.2973 | 31.4 | 29.127 | 2.273 |  | 19-03-2026 09:30 | 193.496 | 198.457 | 152.4 | 33.0762 | 29.5495 | 3.5266 | 177.2973 | 31.3 | 29.127 | 2.173 |  | 19-03-2026 09:30 | 181.64 | 184.051 | 144.5 | 30.6752 | 28.1127 | 2.5624 | 168.6764 | 29.6 | 27.7107 | 1.8893 |  | 19-03-2026 09:30 | 328.7955 | 305.8784 | 22.9171 | 1835.2707 | 323.8 | 301.5044 | 22.2956
19-03-2026 09:20 | 544 | 43.91 | 202.742 | 204.803 | 163.2 | 34.1338 | 32.9968 | 1.137 | 197.9809 | 22.7 | 32.525 | -9.825 |  | 19-03-2026 09:20 | 198.071 | 199.932 | 163.6 | 33.322 | 32.9968 | 0.32519 | 197.9809 | 23.4 | 32.525 | -9.125 |  | 19-03-2026 09:20 | 198.361 | 202.216 | 161.8 | 33.7027 | 32.9968 | 0.70585 | 197.9809 | 22.3 | 32.525 | -10.225 |  | 19-03-2026 09:20 | 196.764 | 203.28 | 163.4 | 33.88 | 32.9968 | 0.88319 | 197.9809 | 22.5 | 32.525 | -10.025 |  | 19-03-2026 09:20 | 145.78 | 147.566 | 119.9 | 24.5943 | 24.4421 | 0.15225 | 146.6525 | 16.5 | 24.0926 | -7.5926 |  | 19-03-2026 09:20 | 146.298 | 148.075 | 120.6 | 24.6792 | 24.4421 | 0.23708 | 146.6525 | 16.5 | 24.0926 | -7.5926 |  | 19-03-2026 09:20 | 139.878 | 141.865 | 119.7 | 23.6442 | 24.4421 | -0.79792 | 146.6525 | 16.1 | 24.0926 | -7.9926 |  | 19-03-2026 09:20 | 145.822 | 149.709 | 121.1 | 24.9515 | 24.4421 | 0.50942 | 146.6525 | 16.5 | 24.0926 | -7.5926 |  | 19-03-2026 09:20 | 138.765 | 140.084 | 114.9 | 23.3473 | 23.2536 | 0.093717 | 139.5217 | 15.7 | 22.9211 | -7.2211 |  | 19-03-2026 09:20 | 256.255 | 253.0092 | 3.2458 | 1518.0553 | 172.2 | 249.3912 | -77.1912
19-03-2026 09:10 | 337 | 47.64 | 126.222 | 127.755 | 140.5 | 21.2925 | 20.1553 | 1.1372 | 120.9316 | 34.8 | 19.867 | 14.933 |  | 19-03-2026 09:10 | 222.091 | 225.039 | 140.2 | 37.5065 | 20.1553 | 17.3512 | 120.9316 | 33.6 | 19.867 | 13.733 |  | 19-03-2026 09:10 | 118.809 | 120.569 | 139.5 | 20.0948 | 20.1553 | -0.060437 | 120.9316 | 34.4 | 19.867 | 14.533 |  | 19-03-2026 09:10 | 121.868 | 123.411 | 140.9 | 20.5685 | 20.1553 | 0.41323 | 120.9316 | 34.8 | 19.867 | 14.933 |  | 19-03-2026 09:10 | 91.622 | 92.763 | 103.4 | 15.4605 | 14.9298 | 0.53067 | 89.579 | 25.6 | 14.7163 | 10.8837 |  | 19-03-2026 09:10 | 93.412 | 94.547 | 104.1 | 15.7578 | 14.9298 | 0.828 | 89.579 | 25.6 | 14.7163 | 10.8837 |  | 19-03-2026 09:10 | 90.978 | 92.092 | 103.6 | 15.3487 | 14.9298 | 0.41884 | 89.579 | 25.9 | 14.7163 | 11.1837 |  | 19-03-2026 09:10 | 92.143 | 94.301 | 104.6 | 15.7168 | 14.9298 | 0.787 | 89.579 | 26.2 | 14.7163 | 11.4837 |  | 19-03-2026 09:10 | 87.333 | 88.438 | 99.2 | 14.7397 | 14.2039 | 0.53578 | 85.2233 | 24.8 | 14.0008 | 10.7992 |  | 19-03-2026 09:10 | 176.4858 | 154.5443 | 21.9416 | 927.2657 | 265.7 | 152.3343 | 113.3657
19-03-2026 09:00 | 500 | 39.03 | 187.397 | 189.654 | 105.7 | 31.609 | 30.8827 | 0.72633 | 185.296 | 23.4 | 30.441 | -7.041 |  | 19-03-2026 09:00 | 189.966 | 192.312 | 106.6 | 32.052 | 30.8827 | 1.1693 | 185.296 | 34.6 | 30.441 | 4.159 |  | 19-03-2026 09:00 | 180.873 | 183.107 | 105.1 | 30.5178 | 30.8827 | -0.36484 | 185.296 | 23.4 | 30.441 | -7.041 |  | 19-03-2026 09:00 | 185.892 | 188.169 | 106.1 | 31.3615 | 30.8827 | 0.47883 | 185.296 | 23.7 | 30.441 | -6.741 |  | 19-03-2026 09:00 | 134.544 | 136.123 | 77.8 | 22.6872 | 22.8761 | -0.18889 | 137.2563 | 17.4 | 22.5489 | -5.1489 |  | 19-03-2026 09:00 | 137.576 | 139.177 | 78.5 | 23.1962 | 22.8761 | 0.32011 | 137.2563 | 17.6 | 22.5489 | -4.9489 |  | 19-03-2026 09:00 | 139.651 | 141.29 | 77.7 | 23.5483 | 22.8761 | 0.67228 | 137.2563 | 17 | 22.5489 | -5.5489 |  | 19-03-2026 09:00 | 141.184 | 144.725 | 78.4 | 24.1208 | 22.8761 | 1.2448 | 137.2563 | 17.2 | 22.5489 | -5.3489 |  | 19-03-2026 09:00 | 133.818 | 135.389 | 74.4 | 22.5648 | 21.7637 | 0.8011 | 130.5824 | 16.5 | 21.4525 | -4.9525 |  | 19-03-2026 09:00 | 241.6577 | 236.7986 | 4.859 | 1420.7917 | 190.8 | 233.4124 | -42.6124
19-03-2026 08:50 | 179 | 33.58 | 64.051 | 64.881 | 82.3 | 10.8135 | 11.2778 | -0.46428 | 67.6667 | 10.8 | 11.1165 | -0.31651 | [5 empty] | 0 | 11.2778 | -11.2778 | 67.6667 | 0 | 11.1165 | -11.1165 |  | 19-03-2026 08:50 | 63.287 | 64.121 | 81.7 | 10.6868 | 11.2778 | -0.59095 | 67.6667 | 10.5 | 11.1165 | -0.61651 |  | 19-03-2026 08:50 | 63.522 | 64.365 | 82.4 | 10.7275 | 11.2778 | -0.55028 | 67.6667 | 10.5 | 11.1165 | -0.61651 |  | 19-03-2026 08:50 | 46.863 | 47.581 | 60.4 | 7.9302 | 8.3539 | -0.42374 | 50.1235 | 7.7 | 8.2344 | -0.53445 |  | 19-03-2026 08:50 | 47.02 | 47.736 | 60.9 | 7.956 | 8.3539 | -0.39791 | 50.1235 | 7.8 | 8.2344 | -0.43445 |  | 19-03-2026 08:50 | 46.872 | 47.581 | 60.7 | 7.9302 | 8.3539 | -0.42374 | 50.1235 | 7.8 | 8.2344 | -0.43445 |  | 19-03-2026 08:50 | 47.037 | 48.31 | 61.2 | 8.0517 | 8.3539 | -0.30224 | 50.1235 | 7.9 | 8.2344 | -0.33445 |  | 19-03-2026 08:50 | 44.031 | 44.733 | 57.9 | 7.4555 | 7.9477 | -0.49221 | 47.6863 | 7.4 | 7.8341 | -0.43406 |  | 19-03-2026 08:50 | 71.5513 | 86.4745 | -14.9231 | 518.8468 | 70.4 | 85.2379 | -14.8379
19-03-2026 08:40 | 201 | 34.73 | 69.915 | 70.807 | 71.5 | 11.8012 | 12.6113 | -0.81016 | 75.668 | 18.6 | 12.431 | 6.169 |  | 19-03-2026 08:40 | 71.023 | 71.937 | 72 | 11.9895 | 12.6113 | -0.62183 | 75.668 | 18.5 | 12.431 | 6.069 |  | 19-03-2026 08:40 | 71.752 | 72.668 | 71.2 | 12.1113 | 12.6113 | -0.49999 | 75.668 | 18.2 | 12.431 | 5.769 |  | 19-03-2026 08:40 | 71.854 | 72.778 | 71.9 | 12.1297 | 12.6113 | -0.48166 | 75.668 | 18.6 | 12.431 | 6.169 |  | 19-03-2026 08:40 | 53.285 | 54.064 | 52.7 | 9.0107 | 9.3417 | -0.33106 | 56.0503 | 13.5 | 9.2081 | 4.2919 |  | 19-03-2026 08:40 | 53.432 | 54.196 | 53.1 | 9.0327 | 9.3417 | -0.30906 | 56.0503 | 13.9 | 9.2081 | 4.6919 |  | 19-03-2026 08:40 | 53.567 | 54.35 | 52.9 | 9.0583 | 9.3417 | -0.28339 | 56.0503 | 13.8 | 9.2081 | 4.5919 |  | 19-03-2026 08:40 | 52.649 | 53.984 | 53.3 | 8.9973 | 9.3417 | -0.34439 | 56.0503 | 13.8 | 9.2081 | 4.5919 |  | 19-03-2026 08:40 | 49.918 | 50.668 | 50.5 | 8.4447 | 8.8875 | -0.44283 | 53.325 | 13.2 | 8.7604 | 4.4396 |  | 19-03-2026 08:40 | 92.5753 | 96.6997 | -4.1243 | 580.1981 | 142.1 | 95.3169 | 46.7831
19-03-2026 08:30 | 383 | 33 | 139.672 | 141.262 | 52.9 | 23.5437 | 24.1812 | -0.6375 | 145.087 | 17.7 | 23.8354 | -6.1354 |  | 19-03-2026 08:30 | 139.657 | 141.267 | 53.5 | 23.5445 | 24.1812 | -0.63667 | 145.087 | 18.3 | 23.8354 | -5.5354 |  | 19-03-2026 08:30 | 137.407 | 139.167 | 53 | 23.1945 | 24.1812 | -0.98667 | 145.087 | 17.9 | 23.8354 | -5.9354 |  | 19-03-2026 08:30 | 139.335 | 140.913 | 53.3 | 23.4855 | 24.1812 | -0.69567 | 145.087 | 18.3 | 23.8354 | -5.5354 |  | 19-03-2026 08:30 | 102.24 | 103.377 | 39.2 | 17.2295 | 17.912 | -0.68248 | 107.4719 | 13.5 | 17.6558 | -4.1558 |  | 19-03-2026 08:30 | 103.411 | 104.551 | 39.2 | 17.4252 | 17.912 | -0.48681 | 107.4719 | 13.4 | 17.6558 | -4.2558 |  | 19-03-2026 08:30 | 102.534 | 103.664 | 39.1 | 17.2773 | 17.912 | -0.63464 | 107.4719 | 13.3 | 17.6558 | -4.3558 |  | 19-03-2026 08:30 | 103.606 | 106.117 | 39.5 | 17.6862 | 17.912 | -0.22581 | 107.4719 | 13.5 | 17.6558 | -4.1558 |  | 19-03-2026 08:30 | 98.568 | 99.664 | 37.3 | 16.6107 | 17.041 | -0.43036 | 102.2462 | 12.7 | 16.7973 | -4.0973 |  | 19-03-2026 08:30 | 179.997 | 185.4136 | -5.4166 | 1112.4817 | 138.6 | 182.7622 | -44.1622
19-03-2026 08:20 | 306 | 30.42 | 110.584 | 111.791 | 35.2 | 18.6318 | 19.4992 | -0.86733 | 116.995 | 12.5 | 19.2203 | -6.7203 |  | 19-03-2026 08:20 | 102.757 | 110.178 | 35.2 | 18.363 | 19.4992 | -1.1362 | 116.995 | 12.3 | 19.2203 | -6.9203 |  | 19-03-2026 08:20 | 109.493 | 110.7 | 35.1 | 18.45 | 19.4992 | -1.0492 | 116.995 | 12.4 | 19.2203 | -6.8203 |  | 19-03-2026 08:20 | 109.087 | 110.311 | 35 | 18.3852 | 19.4992 | -1.114 | 116.995 | 12.4 | 19.2203 | -6.8203 |  | 19-03-2026 08:20 | 80.571 | 81.5 | 25.7 | 13.5833 | 14.4438 | -0.86049 | 86.663 | 9.2 | 14.2373 | -5.0373 |  | 19-03-2026 08:20 | 81.238 | 82.142 | 25.8 | 13.6903 | 14.4438 | -0.75349 | 86.663 | 9.2 | 14.2373 | -5.0373 |  | 19-03-2026 08:20 | 81.101 | 82.028 | 25.8 | 13.6713 | 14.4438 | -0.77249 | 86.663 | 9.3 | 14.2373 | -4.9373 |  | 19-03-2026 08:20 | 81.948 | 83.947 | 26 | 13.9912 | 14.4438 | -0.45266 | 86.663 | 9.4 | 14.2373 | -4.8373 |  | 19-03-2026 08:20 | 77.763 | 78.652 | 24.6 | 13.1087 | 13.7415 | -0.63284 | 82.4491 | 8.9 | 13.545 | -4.645 |  | 19-03-2026 08:20 | 141.8748 | 149.5135 | -7.6386 | 897.0808 | 95.6 | 147.3754 | -51.7754
19-03-2026 08:10 | 134 | 28.7 | 47.964 | 48.68 | 22.7 | 8.1133 | 8.5912 | -0.47791 | 51.5475 | 9.7 | 8.4684 | 1.2316 |  | 19-03-2026 08:10 | 47.732 | 48.43 | 22.9 | 8.0717 | 8.5912 | -0.51958 | 51.5475 | 9.9 | 8.4684 | 1.4316 |  | 19-03-2026 08:10 | 46.999 | 47.724 | 22.7 | 7.954 | 8.5912 | -0.63725 | 51.5475 | 9.8 | 8.4684 | 1.3316 |  | 19-03-2026 08:10 | 46.912 | 47.646 | 22.6 | 7.941 | 8.5912 | -0.65025 | 51.5475 | 9.6 | 8.4684 | 1.1316 |  | 19-03-2026 08:10 | 34.871 | 35.467 | 16.5 | 5.9112 | 6.3639 | -0.45272 | 38.1833 | 7.1 | 6.2729 | 0.82712 |  | 19-03-2026 08:10 | 34.783 | 35.359 | 16.6 | 5.8932 | 6.3639 | -0.47072 | 38.1833 | 7.2 | 6.2729 | 0.92712 |  | 19-03-2026 08:10 | 34.977 | 35.567 | 16.5 | 5.9278 | 6.3639 | -0.43605 | 38.1833 | 7.2 | 6.2729 | 0.92712 |  | 19-03-2026 08:10 | 35.089 | 36.029 | 16.6 | 6.0048 | 6.3639 | -0.35905 | 38.1833 | 7.2 | 6.2729 | 0.92712 |  | 19-03-2026 08:10 | 33.095 | 33.667 | 15.7 | 5.6112 | 6.0545 | -0.44328 | 36.3267 | 6.9 | 5.9679 | 0.93213 |  | 19-03-2026 08:10 | 61.4282 | 65.875 | -4.4468 | 395.2499 | 74.6 | 64.933 | 9.667
19-03-2026 08:00 | 113 | 26.12 | 39.69 | 40.327 | 13 | 6.7212 | 7.3111 | -0.58997 | 43.8668 | 5.3 | 7.2066 | -1.9066 |  | 19-03-2026 08:00 | 40.416 | 41.069 | 13 | 6.8448 | 7.3111 | -0.4663 | 43.8668 | 5.3 | 7.2066 | -1.9066 |  | 19-03-2026 08:00 | 39.424 | 40.073 | 12.9 | 6.6788 | 7.3111 | -0.6323 | 43.8668 | 5.2 | 7.2066 | -2.0066 |  | 19-03-2026 08:00 | 39.803 | 40.446 | 13 | 6.741 | 7.3111 | -0.57014 | 43.8668 | 5.3 | 7.2066 | -1.9066 |  | 19-03-2026 08:00 | 29.168 | 29.7 | 9.4 | 4.95 | 5.4157 | -0.46566 | 32.4939 | 3.9 | 5.3382 | -1.4382 |  | 19-03-2026 08:00 | 29.339 | 29.865 | 9.4 | 4.9775 | 5.4157 | -0.43816 | 32.4939 | 3.8 | 5.3382 | -1.5382 |  | 19-03-2026 08:00 | 29.354 | 29.874 | 9.3 | 4.979 | 5.4157 | -0.43666 | 32.4939 | 3.7 | 5.3382 | -1.6382 |  | 19-03-2026 08:00 | 29.67 | 30.366 | 9.4 | 5.061 | 5.4157 | -0.35466 | 32.4939 | 3.8 | 5.3382 | -1.5382 |  | 19-03-2026 08:00 | 28.111 | 28.638 | 8.8 | 4.773 | 5.1523 | -0.37933 | 30.914 | 3.6 | 5.0786 | -1.4786 |  | 19-03-2026 08:00 | 51.7263 | 56.0595 | -4.3332 | 336.357 | 39.9 | 55.2579 | -15.3579
19-03-2026 07:50 | 70 | 24.39 | 24.606 | 25.118 | 7.7 | 4.1863 | 4.5566 | -0.37022 | 27.3393 | 3.2 | 4.4914 | -1.2914 |  | 19-03-2026 07:50 | 24.368 | 24.91 | 7.7 | 4.1517 | 4.5566 | -0.40489 | 27.3393 | 3.2 | 4.4914 | -1.2914 |  | 19-03-2026 07:50 | 24.468 | 24.998 | 7.7 | 4.1663 | 4.5566 | -0.39022 | 27.3393 | 3.2 | 4.4914 | -1.2914 |  | 19-03-2026 07:50 | 24.646 | 25.164 | 7.7 | 4.194 | 4.5566 | -0.36255 | 27.3393 | 3.2 | 4.4914 | -1.2914 |  | 19-03-2026 07:50 | 17.952 | 18.522 | 5.5 | 3.087 | 3.3752 | -0.28823 | 20.2514 | 2.3 | 3.327 | -1.027 |  | 19-03-2026 07:50 | 17.975 | 18.406 | 5.6 | 3.0677 | 3.3752 | -0.30756 | 20.2514 | 2.4 | 3.327 | -0.92696 |  | 19-03-2026 07:50 | 17.977 | 18.415 | 5.6 | 3.0692 | 3.3752 | -0.30606 | 20.2514 | 2.4 | 3.327 | -0.92696 |  | 19-03-2026 07:50 | 17.953 | 18.8 | 5.6 | 3.1333 | 3.3752 | -0.24189 | 20.2514 | 2.4 | 3.327 | -0.92696 |  | 19-03-2026 07:50 | 16.962 | 17.383 | 5.2 | 2.8972 | 3.2111 | -0.31394 | 19.2667 | 2.2 | 3.1652 | -0.96519 |  | 19-03-2026 07:50 | 31.9527 | 34.9382 | -2.9856 | 209.6294 | 24.5 | 34.4386 | -9.9386
19-03-2026 07:40 | 46 | 23.82 | 15.276 | 15.674 | 4.5 | 2.6123 | 3.0003 | -0.38793 | 18.0016 | 2.1 | 2.9574 | -0.85736 |  | 19-03-2026 07:40 | 15.158 | 15.95 | 4.5 | 2.6583 | 3.0003 | -0.34193 | 18.0016 | 2.1 | 2.9574 | -0.85736 |  | 19-03-2026 07:40 | 15.265 | 15.669 | 4.5 | 2.6115 | 3.0003 | -0.38877 | 18.0016 | 2.1 | 2.9574 | -0.85736 |  | 19-03-2026 07:40 | 15.327 | 16.093 | 4.5 | 2.6822 | 3.0003 | -0.3181 | 18.0016 | 2.1 | 2.9574 | -0.85736 |  | 19-03-2026 07:40 | 11.139 | 11.573 | 3.2 | 1.9288 | 2.2224 | -0.29359 | 13.3345 | 1.5 | 2.1906 | -0.69064 |  | 19-03-2026 07:40 | 11.167 | 11.536 | 3.2 | 1.9227 | 2.2224 | -0.29975 | 13.3345 | 1.5 | 2.1906 | -0.69064 |  | 19-03-2026 07:40 | 11.157 | 11.537 | 3.2 | 1.9228 | 2.2224 | -0.29959 | 13.3345 | 1.5 | 2.1906 | -0.69064 |  | 19-03-2026 07:40 | 11.203 | 11.984 | 3.2 | 1.9973 | 2.2224 | -0.22509 | 13.3345 | 1.5 | 2.1906 | -0.69064 |  | 19-03-2026 07:40 | 10.444 | 10.808 | 3 | 1.8013 | 2.1144 | -0.31302 | 12.6861 | 1.5 | 2.0841 | -0.58412 |  | 19-03-2026 07:40 | 20.1373 | 23.0051 | -2.8678 | 138.0307 | 15.9 | 22.6761 | -6.7761
19-03-2026 07:30 | 33 | 23.53 | 10.919 | 11.301 | 2.4 | 1.8835 | 2.1545 | -0.27104 | 12.9273 | 1.5 | 2.1237 | -0.62373 |  | 19-03-2026 07:30 | 10.852 | 11.923 | 2.4 | 1.9872 | 2.1545 | -0.16738 | 12.9273 | 1.5 | 2.1237 | -0.62373 |  | 19-03-2026 07:30 | 10.901 | 11.281 | 2.4 | 1.8802 | 2.1545 | -0.27438 | 12.9273 | 1.5 | 2.1237 | -0.62373 |  | 19-03-2026 07:30 | 10.991 | 12.095 | 2.4 | 2.0158 | 2.1545 | -0.13871 | 12.9273 | 1.5 | 2.1237 | -0.62373 |  | 19-03-2026 07:30 | 7.929 | 8.562 | 1.7 | 1.427 | 1.596 | -0.16896 | 9.5757 | 1.1 | 1.5731 | -0.47313 |  | 19-03-2026 07:30 | 7.949 | 8.262 | 1.7 | 1.377 | 1.596 | -0.21896 | 9.5757 | 1.1 | 1.5731 | -0.47313 |  | 19-03-2026 07:30 | 7.866 | 8.18 | 1.7 | 1.3633 | 1.596 | -0.23262 | 9.5757 | 1.1 | 1.5731 | -0.47313 |  | 19-03-2026 07:30 | 7.947 | 8.353 | 1.7 | 1.3922 | 1.596 | -0.20379 | 9.5757 | 1.1 | 1.5731 | -0.47313 |  | 19-03-2026 07:30 | 7.492 | 7.8 | 1.5 | 1.3 | 1.5184 | -0.21836 | 9.1101 | 1 | 1.4966 | -0.49664 |  | 19-03-2026 07:30 | 14.6262 | 16.5204 | -1.8942 | 99.1221 | 11.4 | 16.2841 | -4.8841
19-03-2026 07:20 | 21 | 23.53 | 6.782 | 7.071 | 0.9 | 1.1785 | 1.3711 | -0.19257 | 8.2264 | 0.8 | 1.3515 | -0.55147 |  | 19-03-2026 07:20 | 6.231 | 7.2 | 0.9 | 1.2 | 1.3711 | -0.17107 | 8.2264 | 0.8 | 1.3515 | -0.55147 |  | 19-03-2026 07:20 | 6.821 | 7.116 | 0.9 | 1.186 | 1.3711 | -0.18507 | 8.2264 | 0.8 | 1.3515 | -0.55147 |  | 19-03-2026 07:20 | 6.86 | 7.762 | 0.9 | 1.2937 | 1.3711 | -0.077405 | 8.2264 | 0.8 | 1.3515 | -0.55147 |  | 19-03-2026 07:20 | 4.89 | 5.474 | 0.6 | 0.91233 | 1.0156 | -0.10328 | 6.0937 | 0.6 | 1.0011 | -0.40109 |  | 19-03-2026 07:20 | 4.893 | 5.118 | 0.6 | 0.853 | 1.0156 | -0.16261 | 6.0937 | 0.6 | 1.0011 | -0.40109 |  | 19-03-2026 07:20 | 4.933 | 5.13 | 0.6 | 0.855 | 1.0156 | -0.16061 | 6.0937 | 0.6 | 1.0011 | -0.40109 |  | 19-03-2026 07:20 | 4.911 | 5.26 | 0.6 | 0.87667 | 1.0156 | -0.13894 | 6.0937 | 0.6 | 1.0011 | -0.40109 |  | 19-03-2026 07:20 | 4.558 | 4.773 | 0.5 | 0.7955 | 0.96623 | -0.17073 | 5.7974 | 0.5 | 0.95241 | -0.45241 |  | 19-03-2026 07:20 | 9.1507 | 10.513 | -1.3623 | 63.0777 | 6.1 | 10.3626 | -4.2626
19-03-2026 07:10 | 9 | 23.25 | 2.652 | 2.788 | 0.1 | 0.46467 | 0.58818 | -0.12351 | 3.5291 | 0.1 | 0.57976 | -0.47976 |  | 19-03-2026 07:10 | 2.898 | 3.662 | 0.1 | 0.61033 | 0.58818 | 0.022158 | 3.5291 | 0.1 | 0.57976 | -0.47976 |  | 19-03-2026 07:10 | 2.804 | 2.948 | 0.1 | 0.49133 | 0.58818 | -0.096842 | 3.5291 | 0.1 | 0.57976 | -0.47976 |  | 19-03-2026 07:10 | 2.832 | 3.769 | 0.1 | 0.62817 | 0.58818 | 0.039991 | 3.5291 | 0.1 | 0.57976 | -0.47976 |  | 19-03-2026 07:10 | 1.937 | 2.373 | 0 | 0.3955 | 0.43569 | -0.040185 | 2.6141 | 0 | 0.42946 | -0.42946 |  | 19-03-2026 07:10 | 1.925 | 2.021 | 0 | 0.33683 | 0.43569 | -0.098852 | 2.6141 | 0 | 0.42946 | -0.42946 |  | 19-03-2026 07:10 | 1.937 | 2.037 | 0 | 0.3395 | 0.43569 | -0.096185 | 2.6141 | 0 | 0.42946 | -0.42946 |  | 19-03-2026 07:10 | 1.99 | 2.309 | 0 | 0.38483 | 0.43569 | -0.050852 | 2.6141 | 0 | 0.42946 | -0.42946 |  | 19-03-2026 07:10 | 1.753 | 1.843 | 0 | 0.30717 | 0.4145 | -0.10733 | 2.487 | 0 | 0.40857 | -0.40857 |  | 19-03-2026 07:10 | 3.9583 | 4.5099 | -0.55161 | 27.0597 | 0.4 | 4.4455 | -4.0455
19-03-2026 07:00 | 3 | 23.25 | 0 | 0 | 0 | 0 | 0.19606 | -0.19606 | 1.1764 | 0 | 0.19325 | -0.19325 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.19606 | -0.19606 | 1.1764 | 0 | 0.19325 | -0.19325 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.19606 | -0.19606 | 1.1764 | 0 | 0.19325 | -0.19325 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.19606 | -0.19606 | 1.1764 | 0 | 0.19325 | -0.19325 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.14523 | -0.14523 | 0.87137 | 0 | 0.14315 | -0.14315 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.14523 | -0.14523 | 0.87137 | 0 | 0.14315 | -0.14315 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.14523 | -0.14523 | 0.87137 | 0 | 0.14315 | -0.14315 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.14523 | -0.14523 | 0.87137 | 0 | 0.14315 | -0.14315 |  | 19-03-2026 07:00 | 0 | 0 | 0 | 0 | 0.13817 | -0.13817 | 0.829 | 0 | 0.13619 | -0.13619 |  | 19-03-2026 07:00 | 0 | 1.5033 | -1.5033 | 9.0199 | 0 | 1.4818 | -1.4818
[110 empty] | Total: - | 14459.4623 | 14592.4051 | -132.9428 |  | 14210.4 | 14383.7337 | -173.3337
Sum:- | 31753 |  | 11191.451 |  | 77744 |  |  |  |  | 1849.2 | 1875.8898 | -26.6898 | 0.99256 |  | 10985.934 |  | 75506.6 |  |  |  |  | 1863.8 | 1875.8898 | -12.0898 | 0.98953 |  | 11024.925 |  | 77080.1 |  |  |  |  | 1833.5 | 1875.8898 | -42.3898 | 0.97585 |  | 11103.136 |  | 77779.3 |  |  |  |  | 1849.2 | 1875.8898 | -26.6898 | 0.98466 |  | 8320.051 |  | 58022.3 |  |  |  |  | 1381.9 | 1389.548 | -7.648 | 0.98569 |  | 8251.072 |  | 57733.3 |  |  |  |  | 1373 | 1389.548 | -16.548 | 0.98375 |  | 8242.419 |  | 57653.3 |  |  |  |  | 1371.8 | 1389.548 | -17.748 | 0.98374 |  | 8286.541 |  | 58047 |  |  |  |  | 1380.9 | 1389.548 | -8.648 | 0.97275 |  | 7852.544 |  | 54970.6 |  |  |  |  | 1307.1 | 1321.9828 | -14.8828 | 0.98562

## 20 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
20-03-2026 19:00 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace |  | 0.072 | 0.06 | 2490.2 | 0.01 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.086 | 0.352 | 2514.6 | 0.058667 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.069 | 0.073 | 2476.5 | 0.012167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.086 | 0.243 | 2506.6 | 0.0405 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.052 | 0.086 | 1876.9 | 0.014333 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.078 | 0.082 | 1870 | 0.013667 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.086 | 0.102 | 1864.9 | 0.017 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.065 | 0.09 | 1877 | 0.015 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.093 | 0.098 | 1782.1 | 0.016333 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 20-03-2026 19:00 | 0.19767 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 1 | 98.5%
20-03-2026 18:50 |  |  | 0.977 | 1.027 | 2490.2 | 0.17117 | 0 | 0.17117 | 0 | 0.4 | 0 | 0.4 |  | 20-03-2026 18:50 | 1.36 | 1.681 | 2514.6 | 0.28017 | 0 | 0.28017 | 0 | 0.5 | 0 | 0.5 |  | 20-03-2026 18:50 | 1.016 | 1.068 | 2476.5 | 0.178 | 0 | 0.178 | 0 | 0.4 | 0 | 0.4 |  | 20-03-2026 18:50 | 1.047 | 1.654 | 2506.5 | 0.27567 | 0 | 0.27567 | 0 | 0.4 | 0 | 0.4 |  | 20-03-2026 18:50 | 0.56 | 0.726 | 1876.9 | 0.121 | 0 | 0.121 | 0 | 0.3 | 0 | 0.3 |  | 20-03-2026 18:50 | 0.603 | 0.634 | 1870 | 0.10567 | 0 | 0.10567 | 0 | 0.3 | 0 | 0.3 |  | 20-03-2026 18:50 | 0.531 | 0.558 | 1864.8 | 0.093 | 0 | 0.093 | 0 | 0.2 | 0 | 0.2 |  | 20-03-2026 18:50 | 0.645 | 0.992 | 1877 | 0.16533 | 0 | 0.16533 | 0 | 0.3 | 0 | 0.3 |  | 20-03-2026 18:50 | 0.52 | 0.549 | 1782.1 | 0.0915 | 0 | 0.0915 | 0 | 0.2 | 0 | 0.2 |  | 20-03-2026 18:50 | 1.4815 | 0 | 1.4815 | 0 | 3 | 0 | 3 | 2 | 98.33%
20-03-2026 18:40 |  |  | 4.123 | 4.326 | 2489.8 | 0.721 | 0 | 0.721 | 0 | 1.1 | 0 | 1.1 |  | 20-03-2026 18:40 | 4.348 | 4.71 | 2514.1 | 0.785 | 0 | 0.785 | 0 | 1.1 | 0 | 1.1 |  | 20-03-2026 18:40 | 4.051 | 4.254 | 2476.1 | 0.709 | 0 | 0.709 | 0 | 1.1 | 0 | 1.1 |  | 20-03-2026 18:40 | 4.17 | 4.416 | 2506.1 | 0.736 | 0 | 0.736 | 0 | 1.1 | 0 | 1.1 |  | 20-03-2026 18:40 | 2.934 | 3.136 | 1876.6 | 0.52267 | 0 | 0.52267 | 0 | 0.8 | 0 | 0.8 |  | 20-03-2026 18:40 | 2.881 | 3.011 | 1869.7 | 0.50183 | 0 | 0.50183 | 0 | 0.8 | 0 | 0.8 |  | 20-03-2026 18:40 | 2.932 | 3.083 | 1864.6 | 0.51383 | 0 | 0.51383 | 0 | 0.8 | 0 | 0.8 |  | 20-03-2026 18:40 | 2.932 | 3.147 | 1876.7 | 0.5245 | 0 | 0.5245 | 0 | 0.8 | 0 | 0.8 |  | 20-03-2026 18:40 | 2.697 | 2.836 | 1781.9 | 0.47267 | 0 | 0.47267 | 0 | 0.7 | 0 | 0.7 |  | 20-03-2026 18:40 | 5.4865 | 0 | 5.4865 | 0 | 8.3 | 0 | 8.3 | 3 | 97.44%
20-03-2026 18:30 |  |  | 9.066 | 9.421 | 2488.7 | 1.5702 | 0 | 1.5702 | 0 | 2 | 0 | 2 |  | 20-03-2026 18:30 | 9.459 | 9.605 | 2513 | 1.6008 | 0 | 1.6008 | 0 | 2.1 | 0 | 2.1 |  | 20-03-2026 18:30 | 9.091 | 9.452 | 2475 | 1.5753 | 0 | 1.5753 | 0 | 2 | 0 | 2 |  | 20-03-2026 18:30 | 9.172 | 9.555 | 2505 | 1.5925 | 0 | 1.5925 | 0 | 2 | 0 | 2 |  | 20-03-2026 18:30 | 6.595 | 6.883 | 1875.8 | 1.1472 | 0 | 1.1472 | 0 | 1.5 | 0 | 1.5 |  | 20-03-2026 18:30 | 6.515 | 6.798 | 1868.9 | 1.133 | 0 | 1.133 | 0 | 1.5 | 0 | 1.5 |  | 20-03-2026 18:30 | 6.417 | 6.703 | 1863.8 | 1.1172 | 0 | 1.1172 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 18:30 | 6.345 | 6.701 | 1875.9 | 1.1168 | 0 | 1.1168 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 18:30 | 5.967 | 6.238 | 1781.2 | 1.0397 | 0 | 1.0397 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 18:30 | 11.8927 | 0 | 11.8927 | 0 | 15.3 | 0 | 15.3 | 4 | 98.63%
20-03-2026 18:20 |  |  | 16.111 | 16.539 | 2486.7 | 2.7565 | 0 | 2.7565 | 0 | 3.6 | 0 | 3.6 |  | 20-03-2026 18:20 | 16.861 | 17.306 | 2510.9 | 2.8843 | 0 | 2.8843 | 0 | 3.7 | 0 | 3.7 |  | 20-03-2026 18:20 | 16.229 | 16.661 | 2473 | 2.7768 | 0 | 2.7768 | 0 | 3.6 | 0 | 3.6 |  | 20-03-2026 18:20 | 16.48 | 16.911 | 2503 | 2.8185 | 0 | 2.8185 | 0 | 3.7 | 0 | 3.7 |  | 20-03-2026 18:20 | 12.14 | 12.541 | 1874.3 | 2.0902 | 0 | 2.0902 | 0 | 2.7 | 0 | 2.7 |  | 20-03-2026 18:20 | 11.8 | 12.199 | 1867.4 | 2.0332 | 0 | 2.0332 | 0 | 2.6 | 0 | 2.6 |  | 20-03-2026 18:20 | 11.717 | 12.114 | 1862.4 | 2.019 | 0 | 2.019 | 0 | 2.7 | 0 | 2.7 |  | 20-03-2026 18:20 | 10.937 | 11.371 | 1874.5 | 1.8952 | 0 | 1.8952 | 0 | 2.4 | 0 | 2.4 |  | 20-03-2026 18:20 | 10.73 | 11.115 | 1779.8 | 1.8525 | 0 | 1.8525 | 0 | 2.4 | 0 | 2.4 |  | 20-03-2026 18:20 | 21.1262 | 0 | 21.1262 | 0 | 27.4 | 0 | 27.4 | 5 | 98.47%
20-03-2026 18:10 |  |  | 26.107 | 26.652 | 2483.1 | 4.442 | 0 | 4.442 | 0 | 4.9 | 0 | 4.9 |  | 20-03-2026 18:10 | 27.36 | 27.735 | 2507.2 | 4.6225 | 0 | 4.6225 | 0 | 5.2 | 0 | 5.2 |  | 20-03-2026 18:10 | 26.38 | 26.929 | 2469.4 | 4.4882 | 0 | 4.4882 | 0 | 5.1 | 0 | 5.1 |  | 20-03-2026 18:10 | 26.778 | 27.33 | 2499.3 | 4.555 | 0 | 4.555 | 0 | 5.2 | 0 | 5.2 |  | 20-03-2026 18:10 | 19.917 | 20.392 | 1871.6 | 3.3987 | 0 | 3.3987 | 0 | 3.8 | 0 | 3.8 |  | 20-03-2026 18:10 | 19.41 | 19.879 | 1864.8 | 3.3132 | 0 | 3.3132 | 0 | 3.8 | 0 | 3.8 |  | 20-03-2026 18:10 | 19.319 | 19.785 | 1859.7 | 3.2975 | 0 | 3.2975 | 0 | 3.7 | 0 | 3.7 |  | 20-03-2026 18:10 | 17.217 | 17.881 | 1872.1 | 2.9802 | 0 | 2.9802 | 0 | 3.4 | 0 | 3.4 |  | 20-03-2026 18:10 | 17.799 | 18.242 | 1777.4 | 3.0403 | 0 | 3.0403 | 0 | 3.5 | 0 | 3.5 |  | 20-03-2026 18:10 | 34.1375 | 0 | 34.1375 | 0 | 38.6 | 0 | 38.6 | 6 | 98.25%
20-03-2026 18:00 |  |  | 36.585 | 37.203 | 2478.2 | 6.2005 | 0 | 6.2005 | 0 | 7.1 | 0 | 7.1 |  | 20-03-2026 18:00 | 37.733 | 38.382 | 2502 | 6.397 | 0 | 6.397 | 0 | 7.3 | 0 | 7.3 |  | 20-03-2026 18:00 | 37.185 | 37.817 | 2464.3 | 6.3028 | 0 | 6.3028 | 0 | 7.1 | 0 | 7.1 |  | 20-03-2026 18:00 | 37.241 | 37.885 | 2494.1 | 6.3142 | 0 | 6.3142 | 0 | 7.2 | 0 | 7.2 |  | 20-03-2026 18:00 | 27.88 | 28.426 | 1867.8 | 4.7377 | 0 | 4.7377 | 0 | 5.4 | 0 | 5.4 |  | 20-03-2026 18:00 | 27.092 | 27.628 | 1861 | 4.6047 | 0 | 4.6047 | 0 | 5.2 | 0 | 5.2 |  | 20-03-2026 18:00 | 27.05 | 27.588 | 1856 | 4.598 | 0 | 4.598 | 0 | 5.2 | 0 | 5.2 |  | 20-03-2026 18:00 | 25.312 | 26.268 | 1868.7 | 4.378 | 0 | 4.378 | 0 | 5.1 | 0 | 5.1 |  | 20-03-2026 18:00 | 25.48 | 26.008 | 1773.9 | 4.3347 | 0 | 4.3347 | 0 | 4.9 | 0 | 4.9 |  | 20-03-2026 18:00 | 47.8675 | 0 | 47.8675 | 0 | 54.5 | 0 | 54.5 | 7 | 98.12%
20-03-2026 17:50 |  |  | 49.854 | 50.593 | 2471.1 | 8.4322 | 0 | 8.4322 | 0 | 9.5 | 0 | 9.5 |  | 20-03-2026 17:50 | 52.022 | 52.356 | 2494.7 | 8.726 | 0 | 8.726 | 0 | 9.2 | 0 | 9.2 |  | 20-03-2026 17:50 | 50.039 | 50.796 | 2457.2 | 8.466 | 0 | 8.466 | 0 | 9.4 | 0 | 9.4 |  | 20-03-2026 17:50 | 50.871 | 51.673 | 2486.9 | 8.6122 | 0 | 8.6122 | 0 | 9.1 | 0 | 9.1 |  | 20-03-2026 17:50 | 37.984 | 38.625 | 1862.4 | 6.4375 | 0 | 6.4375 | 0 | 6.9 | 0 | 6.9 |  | 20-03-2026 17:50 | 36.978 | 37.602 | 1855.8 | 6.267 | 0 | 6.267 | 0 | 6.5 | 0 | 6.5 |  | 20-03-2026 17:50 | 36.913 | 37.536 | 1850.8 | 6.256 | 0 | 6.256 | 0 | 6.7 | 0 | 6.7 |  | 20-03-2026 17:50 | 36.667 | 37.579 | 1863.6 | 6.2632 | 0 | 6.2632 | 0 | 6.3 | 0 | 6.3 |  | 20-03-2026 17:50 | 34.775 | 35.373 | 1769 | 5.8955 | 0 | 5.8955 | 0 | 6 | 0 | 6 |  | 20-03-2026 17:50 | 65.3555 | 0 | 65.3555 | 0 | 69.6 | 0 | 69.6 | 8 | 97.09%
20-03-2026 17:40 |  |  | 52.049 | 55.784 | 2461.6 | 9.2973 | 0 | 9.2973 | 0 | 10.2 | 0 | 10.2 |  | 20-03-2026 17:40 | 56.761 | 57.59 | 2485.5 | 9.5983 | 0 | 9.5983 | 0 | 10.4 | 0 | 10.4 |  | 20-03-2026 17:40 | 59.422 | 60.342 | 2447.8 | 10.057 | 0 | 10.057 | 0 | 10.1 | 0 | 10.1 |  | 20-03-2026 17:40 | 58.451 | 59.293 | 2477.8 | 9.8822 | 0 | 9.8822 | 0 | 10 | 0 | 10 |  | 20-03-2026 17:40 | 46.053 | 46.792 | 1855.5 | 7.7987 | 0 | 7.7987 | 0 | 7.6 | 0 | 7.6 |  | 20-03-2026 17:40 | 42.071 | 43.737 | 1849.3 | 7.2895 | 0 | 7.2895 | 0 | 7.5 | 0 | 7.5 |  | 20-03-2026 17:40 | 44.506 | 45.225 | 1844.1 | 7.5375 | 0 | 7.5375 | 0 | 7.6 | 0 | 7.6 |  | 20-03-2026 17:40 | 42.011 | 43.191 | 1857.3 | 7.1985 | 0 | 7.1985 | 0 | 7.7 | 0 | 7.7 |  | 20-03-2026 17:40 | 37.888 | 38.505 | 1763 | 6.4175 | 0 | 6.4175 | 0 | 7.2 | 0 | 7.2 |  | 20-03-2026 17:40 | 75.0765 | 0 | 75.0765 | 0 | 78.3 | 0 | 78.3 | 9 | 98.5%
20-03-2026 17:30 |  |  | 83.304 | 84.316 | 2451.4 | 14.0527 | 0 | 14.0527 | 0 | 15.5 | 0 | 15.5 |  | 20-03-2026 17:30 | 84.559 | 85.612 | 2475.1 | 14.2687 | 0 | 14.2687 | 0 | 15.3 | 0 | 15.3 |  | 20-03-2026 17:30 | 83.679 | 85.049 | 2437.7 | 14.1748 | 0 | 14.1748 | 0 | 15.2 | 0 | 15.2 |  | 20-03-2026 17:30 | 83.648 | 84.5 | 2467.8 | 14.0833 | 0 | 14.0833 | 0 | 15.3 | 0 | 15.3 |  | 20-03-2026 17:30 | 62.778 | 63.618 | 1847.9 | 10.603 | 0 | 10.603 | 0 | 11.3 | 0 | 11.3 |  | 20-03-2026 17:30 | 61.177 | 61.989 | 1841.8 | 10.3315 | 0 | 10.3315 | 0 | 11 | 0 | 11 |  | 20-03-2026 17:30 | 61.384 | 62.199 | 1836.5 | 10.3665 | 0 | 10.3665 | 0 | 11 | 0 | 11 |  | 20-03-2026 17:30 | 61.186 | 62.953 | 1849.6 | 10.4922 | 0 | 10.4922 | 0 | 11.3 | 0 | 11.3 |  | 20-03-2026 17:30 | 57.818 | 58.657 | 1755.8 | 9.7762 | 0 | 9.7762 | 0 | 10.6 | 0 | 10.6 |  | 20-03-2026 17:30 | 108.1488 | 0 | 108.1488 | 0 | 116.5 | 0 | 116.5
20-03-2026 17:20 |  |  | 102.642 | 103.836 | 2435.9 | 17.306 | 0 | 17.306 | 0 | 15.5 | 0 | 15.5 |  | 20-03-2026 17:20 | 103.659 | 104.918 | 2459.8 | 17.4863 | 0 | 17.4863 | 0 | 16.5 | 0 | 16.5 |  | 20-03-2026 17:20 | 102.303 | 103.956 | 2422.5 | 17.326 | 0 | 17.326 | 0 | 16.1 | 0 | 16.1 |  | 20-03-2026 17:20 | 102.265 | 103.497 | 2452.5 | 17.2495 | 0 | 17.2495 | 0 | 16.4 | 0 | 16.4 |  | 20-03-2026 17:20 | 76.403 | 77.37 | 1836.6 | 12.895 | 0 | 12.895 | 0 | 12.1 | 0 | 12.1 |  | 20-03-2026 17:20 | 75.144 | 76.08 | 1830.8 | 12.68 | 0 | 12.68 | 0 | 12.1 | 0 | 12.1 |  | 20-03-2026 17:20 | 74.924 | 75.865 | 1825.5 | 12.6442 | 0 | 12.6442 | 0 | 11.8 | 0 | 11.8 |  | 20-03-2026 17:20 | 74.692 | 76.47 | 1838.3 | 12.745 | 0 | 12.745 | 0 | 11.9 | 0 | 11.9 |  | 20-03-2026 17:20 | 70.666 | 71.597 | 1745.2 | 11.9328 | 0 | 11.9328 | 0 | 11.5 | 0 | 11.5 |  | 20-03-2026 17:20 | 132.2648 | 0 | 132.2648 | 0 | 123.9 | 0 | 123.9
20-03-2026 17:10 |  |  | 54.679 | 55.523 | 2420.4 | 9.2538 | 0 | 9.2538 | 0 | 15.8 | 0 | 15.8 |  | 20-03-2026 17:10 | 56.497 | 57.375 | 2443.3 | 9.5625 | 0 | 9.5625 | 0 | 16.5 | 0 | 16.5 |  | 20-03-2026 17:10 | 54.755 | 55.611 | 2406.4 | 9.2685 | 0 | 9.2685 | 0 | 15.5 | 0 | 15.5 |  | 20-03-2026 17:10 | 55.126 | 55.988 | 2436.1 | 9.3313 | 0 | 9.3313 | 0 | 15.6 | 0 | 15.6 |  | 20-03-2026 17:10 | 40.996 | 41.709 | 1824.5 | 6.9515 | 0 | 6.9515 | 0 | 11.4 | 0 | 11.4 |  | 20-03-2026 17:10 | 40.57 | 41.28 | 1818.7 | 6.88 | 0 | 6.88 | 0 | 11.2 | 0 | 11.2 |  | 20-03-2026 17:10 | 40.315 | 41.093 | 1813.7 | 6.8488 | 0 | 6.8488 | 0 | 10.9 | 0 | 10.9 |  | 20-03-2026 17:10 | 40.375 | 41.642 | 1826.4 | 6.9403 | 0 | 6.9403 | 0 | 10.7 | 0 | 10.7 |  | 20-03-2026 17:10 | 38.228 | 38.909 | 1733.7 | 6.4848 | 0 | 6.4848 | 0 | 10.2 | 0 | 10.2 |  | 20-03-2026 17:10 | 71.5217 | 0 | 71.5217 | 0 | 117.8 | 0 | 117.8
20-03-2026 17:00 |  |  | 63.098 | 63.987 | 2404.6 | 10.6645 | 0 | 10.6645 | 0 | 20.2 | 0 | 20.2 |  | 20-03-2026 17:00 | 108.1 | 110.762 | 2426.8 | 18.4603 | 0 | 18.4603 | 0 | 20.1 | 0 | 20.1 |  | 20-03-2026 17:00 | 106.17 | 108.563 | 2390.9 | 18.0938 | 0 | 18.0938 | 0 | 20.5 | 0 | 20.5 |  | 20-03-2026 17:00 | 126.084 | 127.654 | 2420.5 | 21.2757 | 0 | 21.2757 | 0 | 21.2 | 0 | 21.2 |  | 20-03-2026 17:00 | 91.956 | 93.082 | 1813.1 | 15.5137 | 0 | 15.5137 | 0 | 15 | 0 | 15 |  | 20-03-2026 17:00 | 92.377 | 93.49 | 1807.5 | 15.5817 | 0 | 15.5817 | 0 | 15.5 | 0 | 15.5 |  | 20-03-2026 17:00 | 89.113 | 90.214 | 1802.8 | 15.0357 | 0 | 15.0357 | 0 | 14.9 | 0 | 14.9 |  | 20-03-2026 17:00 | 84.981 | 86.742 | 1815.7 | 14.457 | 0 | 14.457 | 0 | 15.2 | 0 | 15.2 |  | 20-03-2026 17:00 | 87.725 | 88.835 | 1723.5 | 14.8058 | 0 | 14.8058 | 0 | 14.8 | 0 | 14.8 |  | 20-03-2026 17:00 | 143.8882 | 0 | 143.8882 | 0 | 157.4 | 0 | 157.4
20-03-2026 16:50 |  |  | 152.812 | 154.731 | 2384.4 | 25.7885 | 0 | 25.7885 | 0 | 58 | 0 | 58 |  | 20-03-2026 16:50 | 155.018 | 157.067 | 2406.7 | 26.1778 | 0 | 26.1778 | 0 | 28 | 0 | 28 |  | 20-03-2026 16:50 | 153.595 | 156.274 | 2370.4 | 26.0457 | 0 | 26.0457 | 0 | 26.5 | 0 | 26.5 |  | 20-03-2026 16:50 | 154.392 | 156.394 | 2399.3 | 26.0657 | 0 | 26.0657 | 0 | 26.9 | 0 | 26.9 |  | 20-03-2026 16:50 | 113.898 | 115.34 | 1798.1 | 19.2233 | 0 | 19.2233 | 0 | 20.1 | 0 | 20.1 |  | 20-03-2026 16:50 | 113.37 | 114.77 | 1792 | 19.1283 | 0 | 19.1283 | 0 | 19.9 | 0 | 19.9 |  | 20-03-2026 16:50 | 113.414 | 114.826 | 1787.9 | 19.1377 | 0 | 19.1377 | 0 | 19.9 | 0 | 19.9 |  | 20-03-2026 16:50 | 113.598 | 116.864 | 1800.5 | 19.4773 | 0 | 19.4773 | 0 | 19.8 | 0 | 19.8 |  | 20-03-2026 16:50 | 107.344 | 108.692 | 1708.7 | 18.1153 | 0 | 18.1153 | 0 | 19.1 | 0 | 19.1 |  | 20-03-2026 16:50 | 199.1597 | 0 | 199.1597 | 0 | 238.2 | 0 | 238.2
20-03-2026 16:40 |  |  | 175.763 | 178.06 | 2357.2 | 29.6767 | 0 | 29.6767 | 0 | 0 | 0 | 0 |  | 20-03-2026 16:40 | 177.096 | 179.465 | 2378.7 | 29.9108 | 0 | 29.9108 | 0 | 30.3 | 0 | 30.3 |  | 20-03-2026 16:40 | 175.595 | 179.163 | 2343.9 | 29.8605 | 0 | 29.8605 | 0 | 30.3 | 0 | 30.3 |  | 20-03-2026 16:40 | 175.66 | 177.992 | 2372.4 | 29.6653 | 0 | 29.6653 | 0 | 30.4 | 0 | 30.4 |  | 20-03-2026 16:40 | 132.017 | 133.702 | 1778 | 22.2837 | 0 | 22.2837 | 0 | 22.7 | 0 | 22.7 |  | 20-03-2026 16:40 | 129.851 | 131.495 | 1772.1 | 21.9158 | 0 | 21.9158 | 0 | 22.4 | 0 | 22.4 |  | 20-03-2026 16:40 | 129.626 | 131.267 | 1768 | 21.8778 | 0 | 21.8778 | 0 | 22.4 | 0 | 22.4 |  | 20-03-2026 16:40 | 129.736 | 133.191 | 1780.7 | 22.1985 | 0 | 22.1985 | 0 | 22.8 | 0 | 22.8 |  | 20-03-2026 16:40 | 123.187 | 124.746 | 1689.6 | 20.791 | 0 | 20.791 | 0 | 21.3 | 0 | 21.3 |  | 20-03-2026 16:40 | 228.1802 | 0 | 228.1802 | 0 | 202.6 | 0 | 202.6
20-03-2026 16:30 |  |  | 181.937 | 184.333 | 2326.4 | 30.7222 | 0 | 30.7222 | 0 | 30.7 | 0 | 30.7 |  | 20-03-2026 16:30 | 180.962 | 186.483 | 2348.4 | 31.0805 | 0 | 31.0805 | 0 | 31.3 | 0 | 31.3 |  | 20-03-2026 16:30 | 183.238 | 187.261 | 2313.6 | 31.2102 | 0 | 31.2102 | 0 | 31.1 | 0 | 31.1 |  | 20-03-2026 16:30 | 183.066 | 185.534 | 2342 | 30.9223 | 0 | 30.9223 | 0 | 31.1 | 0 | 31.1 |  | 20-03-2026 16:30 | 136.972 | 138.734 | 1755.3 | 23.1223 | 0 | 23.1223 | 0 | 23.4 | 0 | 23.4 |  | 20-03-2026 16:30 | 135.49 | 137.247 | 1749.7 | 22.8745 | 0 | 22.8745 | 0 | 22.9 | 0 | 22.9 |  | 20-03-2026 16:30 | 136.258 | 137.997 | 1745.6 | 22.9995 | 0 | 22.9995 | 0 | 22.9 | 0 | 22.9 |  | 20-03-2026 16:30 | 136.187 | 139.534 | 1757.9 | 23.2557 | 0 | 23.2557 | 0 | 22.7 | 0 | 22.7 |  | 20-03-2026 16:30 | 128.227 | 129.876 | 1668.3 | 21.646 | 0 | 21.646 | 0 | 21.4 | 0 | 21.4 |  | 20-03-2026 16:30 | 237.8332 | 0 | 237.8332 | 0 | 237.5 | 0 | 237.5
20-03-2026 16:20 |  |  | 195.795 | 198.454 | 2295.7 | 33.0757 | 0 | 33.0757 | 0 | 33.5 | 0 | 33.5 |  | 20-03-2026 16:20 | 199.389 | 202.118 | 2317.1 | 33.6863 | 0 | 33.6863 | 0 | 33.4 | 0 | 33.4 |  | 20-03-2026 16:20 | 194.634 | 198.754 | 2282.5 | 33.1257 | 0 | 33.1257 | 0 | 33 | 0 | 33 |  | 20-03-2026 16:20 | 194.499 | 197.141 | 2310.9 | 32.8568 | 0 | 32.8568 | 0 | 33 | 0 | 33 |  | 20-03-2026 16:20 | 145.424 | 147.324 | 1731.9 | 24.554 | 0 | 24.554 | 0 | 24.7 | 0 | 24.7 |  | 20-03-2026 16:20 | 142.853 | 144.72 | 1726.8 | 24.12 | 0 | 24.12 | 0 | 24.3 | 0 | 24.3 |  | 20-03-2026 16:20 | 142.511 | 144.373 | 1722.7 | 24.0622 | 0 | 24.0622 | 0 | 24.3 | 0 | 24.3 |  | 20-03-2026 16:20 | 141.866 | 145.595 | 1735.2 | 24.2658 | 0 | 24.2658 | 0 | 24.6 | 0 | 24.6 |  | 20-03-2026 16:20 | 134.925 | 136.674 | 1646.9 | 22.779 | 0 | 22.779 | 0 | 23.2 | 0 | 23.2 |  | 20-03-2026 16:20 | 252.5255 | 0 | 252.5255 | 0 | 254 | 0 | 254
20-03-2026 16:10 |  |  | 206.961 | 209.751 | 2262.2 | 34.9585 | 0 | 34.9585 | 0 | 34.4 | 0 | 34.4 |  | 20-03-2026 16:10 | 207.834 | 210.721 | 2283.7 | 35.1202 | 0 | 35.1202 | 0 | 34.9 | 0 | 34.9 |  | 20-03-2026 16:10 | 206.555 | 211.075 | 2249.5 | 35.1792 | 0 | 35.1792 | 0 | 34.6 | 0 | 34.6 |  | 20-03-2026 16:10 | 206.666 | 209.537 | 2277.9 | 34.9228 | 0 | 34.9228 | 0 | 34.5 | 0 | 34.5 |  | 20-03-2026 16:10 | 155.98 | 158.018 | 1707.2 | 26.3363 | 0 | 26.3363 | 0 | 26.4 | 0 | 26.4 |  | 20-03-2026 16:10 | 152.493 | 154.486 | 1702.5 | 25.7477 | 0 | 25.7477 | 0 | 25.9 | 0 | 25.9 |  | 20-03-2026 16:10 | 153.169 | 155.171 | 1698.4 | 25.8618 | 0 | 25.8618 | 0 | 26 | 0 | 26 |  | 20-03-2026 16:10 | 153.18 | 157.274 | 1710.6 | 26.2123 | 0 | 26.2123 | 0 | 25.6 | 0 | 25.6 |  | 20-03-2026 16:10 | 144.315 | 146.201 | 1623.7 | 24.3668 | 0 | 24.3668 | 0 | 24.2 | 0 | 24.2 |  | 20-03-2026 16:10 | 268.7057 | 0 | 268.7057 | 0 | 266.5 | 0 | 266.5
20-03-2026 16:00 |  |  | 211.886 | 214.851 | 2227.8 | 35.8085 | 0 | 35.8085 | 0 | 38.2 | 0 | 38.2 |  | 20-03-2026 16:00 | 211.79 | 214.841 | 2248.8 | 35.8068 | 0 | 35.8068 | 0 | 39.4 | 0 | 39.4 |  | 20-03-2026 16:00 | 211.513 | 216.708 | 2214.9 | 36.118 | 0 | 36.118 | 0 | 38.1 | 0 | 38.1 |  | 20-03-2026 16:00 | 214.909 | 217.983 | 2243.4 | 36.3305 | 0 | 36.3305 | 0 | 38.4 | 0 | 38.4 |  | 20-03-2026 16:00 | 159.159 | 161.304 | 1680.8 | 26.884 | 0 | 26.884 | 0 | 28 | 0 | 28 |  | 20-03-2026 16:00 | 158.505 | 160.826 | 1676.6 | 26.8043 | 0 | 26.8043 | 0 | 27.7 | 0 | 27.7 |  | 20-03-2026 16:00 | 158.809 | 161.33 | 1672.4 | 26.8883 | 0 | 26.8883 | 0 | 27.4 | 0 | 27.4 |  | 20-03-2026 16:00 | 159.269 | 163.664 | 1685 | 27.2773 | 0 | 27.2773 | 0 | 27.2 | 0 | 27.2 |  | 20-03-2026 16:00 | 149.424 | 151.438 | 1599.5 | 25.2397 | 0 | 25.2397 | 0 | 26 | 0 | 26 |  | 20-03-2026 16:00 | 277.1575 | 0 | 277.1575 | 0 | 290.4 | 0 | 290.4
20-03-2026 15:50 |  |  | 245.806 | 249.499 | 2189.6 | 41.5832 | 0 | 41.5832 | 0 | 41.8 | 0 | 41.8 |  | 20-03-2026 15:50 | 250.051 | 253.833 | 2209.4 | 42.3055 | 0 | 42.3055 | 0 | 42.3 | 0 | 42.3 |  | 20-03-2026 15:50 | 244.67 | 250.417 | 2176.8 | 41.7362 | 0 | 41.7362 | 0 | 41.8 | 0 | 41.8 |  | 20-03-2026 15:50 | 247.5 | 251.244 | 2205 | 41.874 | 0 | 41.874 | 0 | 42 | 0 | 42 |  | 20-03-2026 15:50 | 184.463 | 187.051 | 1652.8 | 31.1752 | 0 | 31.1752 | 0 | 31.6 | 0 | 31.6 |  | 20-03-2026 15:50 | 182.271 | 185.063 | 1648.9 | 30.8438 | 0 | 30.8438 | 0 | 31.1 | 0 | 31.1 |  | 20-03-2026 15:50 | 181.64 | 184.596 | 1645 | 30.766 | 0 | 30.766 | 0 | 31.2 | 0 | 31.2 |  | 20-03-2026 15:50 | 181.958 | 187.048 | 1657.8 | 31.1747 | 0 | 31.1747 | 0 | 31.2 | 0 | 31.2 |  | 20-03-2026 15:50 | 173.203 | 175.279 | 1573.5 | 29.2132 | 0 | 29.2132 | 0 | 29.5 | 0 | 29.5 |  | 20-03-2026 15:50 | 320.6717 | 0 | 320.6717 | 0 | 322.5 | 0 | 322.5
20-03-2026 15:40 |  |  | 245.274 | 248.883 | 2147.8 | 41.4805 | 0 | 41.4805 | 0 | 42.2 | 0 | 42.2 |  | 20-03-2026 15:40 | 244.364 | 248.01 | 2167.1 | 41.335 | 0 | 41.335 | 0 | 43.1 | 0 | 43.1 |  | 20-03-2026 15:40 | 245.278 | 251.247 | 2135 | 41.8745 | 0 | 41.8745 | 0 | 41.5 | 0 | 41.5 |  | 20-03-2026 15:40 | 243.141 | 246.941 | 2163 | 41.1568 | 0 | 41.1568 | 0 | 41.6 | 0 | 41.6 |  | 20-03-2026 15:40 | 186.441 | 189.012 | 1621.2 | 31.502 | 0 | 31.502 | 0 | 31.2 | 0 | 31.2 |  | 20-03-2026 15:40 | 181.779 | 184.304 | 1617.8 | 30.7173 | 0 | 30.7173 | 0 | 31.1 | 0 | 31.1 |  | 20-03-2026 15:40 | 184.308 | 187.065 | 1613.8 | 31.1775 | 0 | 31.1775 | 0 | 31.1 | 0 | 31.1 |  | 20-03-2026 15:40 | 183.877 | 189.184 | 1626.6 | 31.5307 | 0 | 31.5307 | 0 | 31.2 | 0 | 31.2 |  | 20-03-2026 15:40 | 172.846 | 175.247 | 1544 | 29.2078 | 0 | 29.2078 | 0 | 29.4 | 0 | 29.4 |  | 20-03-2026 15:40 | 319.9822 | 0 | 319.9822 | 0 | 322.4 | 0 | 322.4
20-03-2026 15:30 |  |  | 255.006 | 258.758 | 2105.6 | 43.1263 | 0 | 43.1263 | 0 | 43.1 | 0 | 43.1 |  | 20-03-2026 15:30 | 252.655 | 256.45 | 2124 | 42.7417 | 0 | 42.7417 | 0 | 41.7 | 0 | 41.7 |  | 20-03-2026 15:30 | 257.189 | 263.441 | 2093.5 | 43.9068 | 0 | 43.9068 | 0 | 43 | 0 | 43 |  | 20-03-2026 15:30 | 256.318 | 260.195 | 2121.4 | 43.3658 | 0 | 43.3658 | 0 | 43.1 | 0 | 43.1 |  | 20-03-2026 15:30 | 192.85 | 195.549 | 1590 | 32.5915 | 0 | 32.5915 | 0 | 32.5 | 0 | 32.5 |  | 20-03-2026 15:30 | 189.967 | 192.7 | 1586.7 | 32.1167 | 0 | 32.1167 | 0 | 31.4 | 0 | 31.4 |  | 20-03-2026 15:30 | 189.902 | 192.734 | 1582.7 | 32.1223 | 0 | 32.1223 | 0 | 32.2 | 0 | 32.2 |  | 20-03-2026 15:30 | 189.759 | 195.22 | 1595.4 | 32.5367 | 0 | 32.5367 | 0 | 32.2 | 0 | 32.2 |  | 20-03-2026 15:30 | 179.791 | 182.307 | 1514.6 | 30.3845 | 0 | 30.3845 | 0 | 30.3 | 0 | 30.3 |  | 20-03-2026 15:30 | 332.8923 | 0 | 332.8923 | 0 | 329.5 | 0 | 329.5
20-03-2026 15:20 |  |  | 272.568 | 276.691 | 2062.5 | 46.1152 | 0 | 46.1152 | 0 | 40.2 | 0 | 40.2 |  | 20-03-2026 15:20 | 275.883 | 280.975 | 2082.3 | 46.8292 | 0 | 46.8292 | 0 | 41.7 | 0 | 41.7 |  | 20-03-2026 15:20 | 273.253 | 279.864 | 2050.5 | 46.644 | 0 | 46.644 | 0 | 39.4 | 0 | 39.4 |  | 20-03-2026 15:20 | 274.771 | 279.069 | 2078.3 | 46.5115 | 0 | 46.5115 | 0 | 40.4 | 0 | 40.4 |  | 20-03-2026 15:20 | 205.872 | 208.816 | 1557.5 | 34.8027 | 0 | 34.8027 | 0 | 30 | 0 | 30 |  | 20-03-2026 15:20 | 203.215 | 206.249 | 1555.3 | 34.3748 | 0 | 34.3748 | 0 | 29.8 | 0 | 29.8 |  | 20-03-2026 15:20 | 203.329 | 206.726 | 1550.5 | 34.4543 | 0 | 34.4543 | 0 | 29.2 | 0 | 29.2 |  | 20-03-2026 15:20 | 203.853 | 209.625 | 1563.2 | 34.9375 | 0 | 34.9375 | 0 | 29.7 | 0 | 29.7 |  | 20-03-2026 15:20 | 193.457 | 196.14 | 1484.3 | 32.69 | 0 | 32.69 | 0 | 28.4 | 0 | 28.4 |  | 20-03-2026 15:20 | 357.3592 | 0 | 357.3592 | 0 | 308.8 | 0 | 308.8
20-03-2026 15:10 |  |  | 282.418 | 286.804 | 2022.3 | 47.8007 | 0 | 47.8007 | 0 | 46.5 | 0 | 46.5 |  | 20-03-2026 15:10 | 284.515 | 288.638 | 2040.6 | 48.1063 | 0 | 48.1063 | 0 | 48.7 | 0 | 48.7 |  | 20-03-2026 15:10 | 280.548 | 287.973 | 2011.1 | 47.9955 | 0 | 47.9955 | 0 | 46.8 | 0 | 46.8 |  | 20-03-2026 15:10 | 281.089 | 285.66 | 2037.9 | 47.61 | 0 | 47.61 | 0 | 47.6 | 0 | 47.6 |  | 20-03-2026 15:10 | 211.908 | 215.026 | 1527.5 | 35.8377 | 0 | 35.8377 | 0 | 36 | 0 | 36 |  | 20-03-2026 15:10 | 208.207 | 211.737 | 1525.5 | 35.2895 | 0 | 35.2895 | 0 | 35.6 | 0 | 35.6 |  | 20-03-2026 15:10 | 209.309 | 213.09 | 1521.3 | 35.515 | 0 | 35.515 | 0 | 35.5 | 0 | 35.5 |  | 20-03-2026 15:10 | 209.61 | 215.463 | 1533.5 | 35.9105 | 0 | 35.9105 | 0 | 35.2 | 0 | 35.2 |  | 20-03-2026 15:10 | 197.987 | 200.88 | 1455.9 | 33.48 | 0 | 33.48 | 0 | 33.5 | 0 | 33.5 |  | 20-03-2026 15:10 | 367.5452 | 0 | 367.5452 | 0 | 365.4 | 0 | 365.4
20-03-2026 15:00 |  |  | 286.703 | 287.578 | 1975.8 | 47.9297 | 0 | 47.9297 | 0 | 49.1 | 0 | 49.1 | 0.99696 | 20-03-2026 15:00 | 291.858 | 296.634 | 1991.9 | 49.439 | 0 | 49.439 | 0 | 50.9 | 0 | 50.9 | 0.9839 | 20-03-2026 15:00 | 228 | 231.355 | 1964.3 | 38.5592 | 0 | 38.5592 | 0 | 49.4 | 0 | 49.4 | 0.9855 | 20-03-2026 15:00 | 282.488 | 265.107 | 1990.3 | 44.1845 | 0 | 44.1845 | 0 | 50.2 | 0 | 50.2 | 1.0656 | 20-03-2026 15:00 | 196.945 | 199.741 | 1491.5 | 33.2902 | 0 | 33.2902 | 0 | 36.8 | 0 | 36.8 | 0.986 | 20-03-2026 15:00 | 200.376 | 204.534 | 1489.9 | 34.089 | 0 | 34.089 | 0 | 37.2 | 0 | 37.2 | 0.97967 | 20-03-2026 15:00 | 212.983 | 217.286 | 1485.8 | 36.2143 | 0 | 36.2143 | 0 | 37.1 | 0 | 37.1 | 0.9802 | 20-03-2026 15:00 | 217.501 | 223.646 | 1498.3 | 37.2743 | 0 | 37.2743 | 0 | 37.4 | 0 | 37.4 | 0.97252 | 20-03-2026 15:00 | 207.031 | 210.056 | 1422.4 | 35.0093 | 0 | 35.0093 | 0 | 35.5 | 0 | 35.5 | 0.9856 | 20-03-2026 15:00 | 355.9895 | 0 | 355.9895 | 0 | 383.6 | 0 | 383.6
20-03-2026 14:50 |  |  | 307.034 | 311.778 | 1926.7 | 51.963 | 0 | 51.963 | 0 | 51.8 | 0 | 51.8 | 0.98478 | 20-03-2026 14:50 | 311.858 | 316.888 | 1941 | 52.8147 | 0 | 52.8147 | 0 | 49.9 | 0 | 49.9 | 0.98413 | 20-03-2026 14:50 | 305.211 | 313.182 | 1914.9 | 52.197 | 0 | 52.197 | 0 | 51.7 | 0 | 51.7 | 0.97455 | 20-03-2026 14:50 | 308.189 | 313.359 | 1940.1 | 52.2265 | 0 | 52.2265 | 0 | 52.4 | 0 | 52.4 | 0.9835 | 20-03-2026 14:50 | 229.982 | 233.228 | 1454.7 | 38.8713 | 0 | 38.8713 | 0 | 39.7 | 0 | 39.7 | 0.98608 | 20-03-2026 14:50 | 227.437 | 231.218 | 1452.7 | 38.5363 | 0 | 38.5363 | 0 | 38.2 | 0 | 38.2 | 0.98365 | 20-03-2026 14:50 | 226.194 | 230.11 | 1448.7 | 38.3517 | 0 | 38.3517 | 0 | 38.1 | 0 | 38.1 | 0.98298 | 20-03-2026 14:50 | 226.694 | 233.122 | 1460.9 | 38.8537 | 0 | 38.8537 | 0 | 38.4 | 0 | 38.4 | 0.97243 | 20-03-2026 14:50 | 216.429 | 219.658 | 1386.9 | 36.6097 | 0 | 36.6097 | 0 | 36.5 | 0 | 36.5 | 0.9853 | 20-03-2026 14:50 | 400.4238 | 0 | 400.4238 | 0 | 396.7 | 0 | 396.7
20-03-2026 14:40 |  |  | 314.312 | 315.69 | 1874.9 | 52.615 | 0 | 52.615 | 0 | 53.3 | 0 | 53.3 | 0.99563 | 20-03-2026 14:40 | 315.409 | 320.766 | 1891.1 | 53.461 | 0 | 53.461 | 0 | 55.5 | 0 | 55.5 | 0.9833 | 20-03-2026 14:40 | 308.375 | 316.567 | 1863.2 | 52.7612 | 0 | 52.7612 | 0 | 53.1 | 0 | 53.1 | 0.97412 | 20-03-2026 14:40 | 313.268 | 318.556 | 1887.7 | 53.0927 | 0 | 53.0927 | 0 | 54.3 | 0 | 54.3 | 0.9834 | 20-03-2026 14:40 | 233.52 | 237.148 | 1415 | 39.5247 | 0 | 39.5247 | 0 | 40.1 | 0 | 40.1 | 0.9847 | 20-03-2026 14:40 | 230.774 | 234.537 | 1414.5 | 39.0895 | 0 | 39.0895 | 0 | 40.7 | 0 | 40.7 | 0.98396 | 20-03-2026 14:40 | 230.497 | 234.416 | 1410.6 | 39.0693 | 0 | 39.0693 | 0 | 40.2 | 0 | 40.2 | 0.98328 | 20-03-2026 14:40 | 232.779 | 239.494 | 1422.5 | 39.9157 | 0 | 39.9157 | 0 | 40.4 | 0 | 40.4 | 0.97196 | 20-03-2026 14:40 | 220.025 | 223.33 | 1350.4 | 37.2217 | 0 | 37.2217 | 0 | 38.1 | 0 | 38.1 | 0.9852 | 20-03-2026 14:40 | 406.7507 | 0 | 406.7507 | 0 | 415.7 | 0 | 415.7
20-03-2026 14:30 |  |  | 332.454 | 338.628 | 1821.6 | 56.438 | 0 | 56.438 | 0 | 57.7 | 0 | 57.7 | 0.98177 | 20-03-2026 14:30 | 334.928 | 341.607 | 1835.6 | 56.9345 | 0 | 56.9345 | 0 | 55.3 | 0 | 55.3 | 0.98045 | 20-03-2026 14:30 | 332.452 | 341.907 | 1810.1 | 56.9845 | 0 | 56.9845 | 0 | 53.7 | 0 | 53.7 | 0.97235 | 20-03-2026 14:30 | 333.227 | 339.024 | 1833.4 | 56.504 | 0 | 56.504 | 0 | 53.7 | 0 | 53.7 | 0.9829 | 20-03-2026 14:30 | 251.303 | 255.234 | 1374.9 | 42.539 | 0 | 42.539 | 0 | 40.1 | 0 | 40.1 | 0.9846 | 20-03-2026 14:30 | 246.432 | 251.013 | 1373.8 | 41.8355 | 0 | 41.8355 | 0 | 39.1 | 0 | 39.1 | 0.98175 | 20-03-2026 14:30 | 248.908 | 253.852 | 1370.4 | 42.3087 | 0 | 42.3087 | 0 | 39.2 | 0 | 39.2 | 0.98052 | 20-03-2026 14:30 | 249.965 | 257.375 | 1382.1 | 42.8958 | 0 | 42.8958 | 0 | 39 | 0 | 39 | 0.97121 | 20-03-2026 14:30 | 234.672 | 238.265 | 1312.3 | 39.7108 | 0 | 39.7108 | 0 | 37.4 | 0 | 37.4 | 0.98492 | 20-03-2026 14:30 | 436.1508 | 0 | 436.1508 | 0 | 415.2 | 0 | 415.2
20-03-2026 14:20 |  |  | 336.477 | 342.192 | 1763.9 | 57.032 | 0 | 57.032 | 0 | 54.9 | 0 | 54.9 | 0.9833 | 20-03-2026 14:20 | 341.238 | 347.21 | 1780.3 | 57.8683 | 0 | 57.8683 | 0 | 58.6 | 0 | 58.6 | 0.9828 | 20-03-2026 14:20 | 333.819 | 343.265 | 1756.4 | 57.2108 | 0 | 57.2108 | 0 | 56.7 | 0 | 56.7 | 0.97248 | 20-03-2026 14:20 | 337.678 | 343.588 | 1779.7 | 57.2647 | 0 | 57.2647 | 0 | 57.2 | 0 | 57.2 | 0.9828 | 20-03-2026 14:20 | 252.469 | 256.47 | 1334.8 | 42.745 | 0 | 42.745 | 0 | 42.4 | 0 | 42.4 | 0.9844 | 20-03-2026 14:20 | 249.944 | 254.518 | 1334.7 | 42.4197 | 0 | 42.4197 | 0 | 41.8 | 0 | 41.8 | 0.98203 | 20-03-2026 14:20 | 249.142 | 254.236 | 1331.2 | 42.3727 | 0 | 42.3727 | 0 | 41.9 | 0 | 41.9 | 0.97996 | 20-03-2026 14:20 | 250.047 | 257.278 | 1343.1 | 42.8797 | 0 | 42.8797 | 0 | 42.1 | 0 | 42.1 | 0.97189 | 20-03-2026 14:20 | 237.424 | 241.248 | 1274.9 | 40.208 | 0 | 40.208 | 0 | 39.7 | 0 | 39.7 | 0.98415 | 20-03-2026 14:20 | 440.0008 | 0 | 440.0008 | 0 | 435.3 | 0 | 435.3
20-03-2026 14:10 |  |  | 338.796 | 344.655 | 1709 | 57.4425 | 0 | 57.4425 | 0 | 56.3 | 0 | 56.3 | 0.983 | 20-03-2026 14:10 | 0 | 0 | 1721.7 | 0 | 0 | 0 | 0 | 55.3 | 0 | 55.3 |  | 20-03-2026 14:10 | 337.76 | 347.317 | 1699.7 | 57.8862 | 0 | 57.8862 | 0 | 56.7 | 0 | 56.7 | 0.97248 | 20-03-2026 14:10 | 339.879 | 345.933 | 1722.5 | 57.6555 | 0 | 57.6555 | 0 | 56.6 | 0 | 56.6 | 0.9825 | 20-03-2026 14:10 | 255.888 | 259.987 | 1292.4 | 43.3312 | 0 | 43.3312 | 0 | 43.3 | 0 | 43.3 | 0.98423 | 20-03-2026 14:10 | 251.91 | 256.616 | 1292.9 | 42.7693 | 0 | 42.7693 | 0 | 43.4 | 0 | 43.4 | 0.98166 | 20-03-2026 14:10 | 252.61 | 257.709 | 1289.3 | 42.9515 | 0 | 42.9515 | 0 | 43.5 | 0 | 43.5 | 0.98021 | 20-03-2026 14:10 | 253.564 | 260.971 | 1301 | 43.4952 | 0 | 43.4952 | 0 | 43.6 | 0 | 43.6 | 0.97162 | 20-03-2026 14:10 | 239.484 | 243.279 | 1235.2 | 40.5465 | 0 | 40.5465 | 0 | 41.3 | 0 | 41.3 | 0.9844 | 20-03-2026 14:10 | 386.0778 | 0 | 386.0778 | 0 | 440 | 0 | 440
20-03-2026 14:00 |  |  | 347.603 | 352.642 | 1652.7 | 58.7737 | 0 | 58.7737 | 0 | 58.2 | 0 | 58.2 | 0.98571 | 20-03-2026 14:00 | 344.725 | 350.244 | 1666.4 | 58.374 | 0 | 58.374 | 0 | 57.9 | 0 | 57.9 | 0.98424 | 20-03-2026 14:00 | 345.547 | 355.594 | 1643 | 59.2657 | 0 | 59.2657 | 0 | 58.1 | 0 | 58.1 | 0.97175 | 20-03-2026 14:00 | 343.933 | 349.383 | 1665.9 | 58.2305 | 0 | 58.2305 | 0 | 57.8 | 0 | 57.8 | 0.9844 | 20-03-2026 14:00 | 273.429 | 277.903 | 1249.1 | 46.3172 | 0 | 46.3172 | 0 | 45.8 | 0 | 45.8 | 0.9839 | 20-03-2026 14:00 | 270.144 | 275.413 | 1249.5 | 45.9022 | 0 | 45.9022 | 0 | 43.8 | 0 | 43.8 | 0.98087 | 20-03-2026 14:00 | 270.037 | 275.802 | 1245.8 | 45.967 | 0 | 45.967 | 0 | 43.7 | 0 | 43.7 | 0.9791 | 20-03-2026 14:00 | 272.212 | 280.802 | 1257.4 | 46.8003 | 0 | 46.8003 | 0 | 43.9 | 0 | 43.9 | 0.96941 | 20-03-2026 14:00 | 255.51 | 259.638 | 1193.9 | 43.273 | 0 | 43.273 | 0 | 42 | 0 | 42 | 0.9841 | 20-03-2026 14:00 | 462.9035 | 0 | 462.9035 | 0 | 451.2 | 0 | 451.2
20-03-2026 13:50 |  |  | 349.128 | 354.877 | 1594.5 | 59.1462 | 0 | 59.1462 | 0 | 58.8 | 0 | 58.8 | 0.9838 | 20-03-2026 13:50 | 347.404 | 352.981 | 1608.5 | 58.8302 | 0 | 58.8302 | 0 | 60.1 | 0 | 60.1 | 0.9842 | 20-03-2026 13:50 | 348.45 | 358.208 | 1584.9 | 59.7013 | 0 | 59.7013 | 0 | 58 | 0 | 58 | 0.97276 | 20-03-2026 13:50 | 346.663 | 352.371 | 1608.1 | 58.7285 | 0 | 58.7285 | 0 | 57.7 | 0 | 57.7 | 0.9838 | 20-03-2026 13:50 | 267.99 | 272.348 | 1203.3 | 45.3913 | 0 | 45.3913 | 0 | 43.8 | 0 | 43.8 | 0.984 | 20-03-2026 13:50 | 263.907 | 268.924 | 1205.7 | 44.8207 | 0 | 44.8207 | 0 | 44 | 0 | 44 | 0.98134 | 20-03-2026 13:50 | 263.035 | 268.084 | 1202.1 | 44.6807 | 0 | 44.6807 | 0 | 44.6 | 0 | 44.6 | 0.98117 | 20-03-2026 13:50 | 263.248 | 271.439 | 1213.5 | 45.2398 | 0 | 45.2398 | 0 | 44.8 | 0 | 44.8 | 0.96982 | 20-03-2026 13:50 | 250.016 | 254.107 | 1151.9 | 42.3512 | 0 | 42.3512 | 0 | 41.9 | 0 | 41.9 | 0.9839 | 20-03-2026 13:50 | 458.8898 | 0 | 458.8898 | 0 | 453.7 | 0 | 453.7
20-03-2026 13:40 |  |  | 348.674 | 354.128 | 1535.7 | 59.0213 | 0 | 59.0213 | 0 | 57.1 | 0 | 57.1 | 0.9846 | 20-03-2026 13:40 | 347.428 | 352.515 | 1548.4 | 58.7525 | 0 | 58.7525 | 0 | 55.3 | 0 | 55.3 | 0.98557 | 20-03-2026 13:40 | 348.062 | 357.711 | 1526.9 | 59.6185 | 0 | 59.6185 | 0 | 57.6 | 0 | 57.6 | 0.97303 | 20-03-2026 13:40 | 346.436 | 352.105 | 1550.4 | 58.6842 | 0 | 58.6842 | 0 | 57.4 | 0 | 57.4 | 0.9839 | 20-03-2026 13:40 | 271.927 | 276.461 | 1159.5 | 46.0768 | 0 | 46.0768 | 0 | 46.4 | 0 | 46.4 | 0.9836 | 20-03-2026 13:40 | 269.06 | 273.856 | 1161.7 | 45.6427 | 0 | 45.6427 | 0 | 46 | 0 | 46 | 0.98249 | 20-03-2026 13:40 | 269.331 | 275.061 | 1157.5 | 45.8435 | 0 | 45.8435 | 0 | 45.5 | 0 | 45.5 | 0.97917 | 20-03-2026 13:40 | 270.499 | 278.537 | 1168.7 | 46.4228 | 0 | 46.4228 | 0 | 45.8 | 0 | 45.8 | 0.97114 | 20-03-2026 13:40 | 256.119 | 260.428 | 1110 | 43.4047 | 0 | 43.4047 | 0 | 43.3 | 0 | 43.3 | 0.98345 | 20-03-2026 13:40 | 463.467 | 0 | 463.467 | 0 | 454.4 | 0 | 454.4
20-03-2026 13:30 |  |  | 344.097 | 349.302 | 1478.6 | 58.217 | 0 | 58.217 | 0 | 57.6 | 0 | 57.6 | 0.9851 | 20-03-2026 13:30 | 342.066 | 347.487 | 1493.1 | 57.9145 | 0 | 57.9145 | 0 | 57.3 | 0 | 57.3 | 0.9844 | 20-03-2026 13:30 | 342.927 | 352.554 | 1469.3 | 58.759 | 0 | 58.759 | 0 | 57.6 | 0 | 57.6 | 0.97269 | 20-03-2026 13:30 | 338.589 | 347.134 | 1493 | 57.8557 | 0 | 57.8557 | 0 | 57.2 | 0 | 57.2 | 0.97538 | 20-03-2026 13:30 | 272.762 | 277.225 | 1113.1 | 46.2042 | 0 | 46.2042 | 0 | 45.1 | 0 | 45.1 | 0.9839 | 20-03-2026 13:30 | 259.238 | 265.988 | 1115.7 | 44.3313 | 0 | 44.3313 | 0 | 45.3 | 0 | 45.3 | 0.97462 | 20-03-2026 13:30 | 269.358 | 274.996 | 1112 | 45.8327 | 0 | 45.8327 | 0 | 44.7 | 0 | 44.7 | 0.9795 | 20-03-2026 13:30 | 271.039 | 279.223 | 1122.9 | 46.5372 | 0 | 46.5372 | 0 | 45.5 | 0 | 45.5 | 0.97069 | 20-03-2026 13:30 | 255.301 | 259.452 | 1066.7 | 43.242 | 0 | 43.242 | 0 | 42.9 | 0 | 42.9 | 0.984 | 20-03-2026 13:30 | 458.8935 | 0 | 458.8935 | 0 | 453.2 | 0 | 453.2
20-03-2026 13:20 |  |  | 345.723 | 350.966 | 1421 | 58.4943 | 0 | 58.4943 | 0 | 47 | 0 | 47 | 0.98506 | 20-03-2026 13:20 | 344.259 | 349.324 | 1435.8 | 58.2207 | 0 | 58.2207 | 0 | 52.4 | 0 | 52.4 | 0.9855 | 20-03-2026 13:20 | 345.513 | 355.267 | 1411.7 | 59.2112 | 0 | 59.2112 | 0 | 49.8 | 0 | 49.8 | 0.97254 | 20-03-2026 13:20 | 343.44 | 348.67 | 1435.8 | 58.1117 | 0 | 58.1117 | 0 | 54.3 | 0 | 54.3 | 0.985 | 20-03-2026 13:20 | 272.58 | 276.928 | 1068 | 46.1547 | 0 | 46.1547 | 0 | 42.5 | 0 | 42.5 | 0.9843 | 20-03-2026 13:20 | 269.18 | 274.229 | 1070.4 | 45.7048 | 0 | 45.7048 | 0 | 41.8 | 0 | 41.8 | 0.98159 | 20-03-2026 13:20 | 268.677 | 274.132 | 1067.3 | 45.6887 | 0 | 45.6887 | 0 | 45.3 | 0 | 45.3 | 0.9801 | 20-03-2026 13:20 | 269.245 | 277.713 | 1077.4 | 46.2855 | 0 | 46.2855 | 0 | 45.4 | 0 | 45.4 | 0.96951 | 20-03-2026 13:20 | 254.891 | 258.904 | 1023.8 | 43.1507 | 0 | 43.1507 | 0 | 41.7 | 0 | 41.7 | 0.9845 | 20-03-2026 13:20 | 461.0222 | 0 | 461.0222 | 0 | 420.2 | 0 | 420.2
20-03-2026 13:10 |  |  | 206.116 | 208.746 | 1374 | 34.791 | 0 | 34.791 | 0 | 30.8 | 0 | 30.8 | 0.9874 | 20-03-2026 13:10 | 117.941 | 120.674 | 1383.4 | 20.1123 | 0 | 20.1123 | 0 | 35.1 | 0 | 35.1 | 0.97735 | 20-03-2026 13:10 | 155.795 | 158.443 | 1361.9 | 26.4072 | 0 | 26.4072 | 0 | 31.6 | 0 | 31.6 | 0.98329 | 20-03-2026 13:10 | 175.249 | 177.629 | 1381.5 | 29.6048 | 0 | 29.6048 | 0 | 35.7 | 0 | 35.7 | 0.9866 | 20-03-2026 13:10 | 117.066 | 119.628 | 1025.5 | 19.938 | 0 | 19.938 | 0 | 25.4 | 0 | 25.4 | 0.97858 | 20-03-2026 13:10 | 100.01 | 101.645 | 1028.6 | 16.9408 | 0 | 16.9408 | 0 | 27.2 | 0 | 27.2 | 0.98391 | 20-03-2026 13:10 | 111.043 | 114.956 | 1022 | 19.1593 | 0 | 19.1593 | 0 | 24.1 | 0 | 24.1 | 0.96596 | 20-03-2026 13:10 | 120.693 | 127.983 | 1032 | 21.3305 | 0 | 21.3305 | 0 | 25.5 | 0 | 25.5 | 0.94304 | 20-03-2026 13:10 | 82.788 | 83.938 | 982.1 | 13.9897 | 0 | 13.9897 | 0 | 26.1 | 0 | 26.1 | 0.9863 | 20-03-2026 13:10 | 202.2737 | 0 | 202.2737 | 0 | 261.5 | 0 | 261.5
20-03-2026 13:00 |  |  | 351.307 | 356.76 | 1343.2 | 59.46 | 0 | 59.46 | 0 | 51.5 | 0 | 51.5 | 0.98472 | 20-03-2026 13:00 | 348.812 | 354.196 | 1348.3 | 59.0327 | 0 | 59.0327 | 0 | 50.3 | 0 | 50.3 | 0.9848 | 20-03-2026 13:00 | 350.449 | 360.626 | 1330.3 | 60.1043 | 0 | 60.1043 | 0 | 49.5 | 0 | 49.5 | 0.97178 | 20-03-2026 13:00 | 348.896 | 354.281 | 1345.8 | 59.0468 | 0 | 59.0468 | 0 | 51.8 | 0 | 51.8 | 0.9848 | 20-03-2026 13:00 | 279.082 | 283.562 | 1000.1 | 47.2603 | 0 | 47.2603 | 0 | 37.7 | 0 | 37.7 | 0.9842 | 20-03-2026 13:00 | 274.498 | 280.246 | 1001.4 | 46.7077 | 0 | 46.7077 | 0 | 39.8 | 0 | 39.8 | 0.97949 | 20-03-2026 13:00 | 277.207 | 282.929 | 997.9 | 47.1548 | 0 | 47.1548 | 0 | 38.4 | 0 | 38.4 | 0.97978 | 20-03-2026 13:00 | 278.408 | 286.834 | 1006.5 | 47.8057 | 0 | 47.8057 | 0 | 40 | 0 | 40 | 0.97062 | 20-03-2026 13:00 | 261.169 | 265.335 | 956 | 44.2225 | 0 | 44.2225 | 0 | 39.5 | 0 | 39.5 | 0.9843 | 20-03-2026 13:00 | 470.7948 | 0 | 470.7948 | 0 | 398.5 | 0 | 398.5
20-03-2026 12:50 |  |  | 351.483 | 356.247 | 1291.7 | 59.3745 | 0 | 59.3745 | 0 | 57.5 | 0 | 57.5 | 0.98663 | 20-03-2026 12:50 | 343.631 | 349.467 | 1298 | 58.2445 | 0 | 58.2445 | 0 | 57.9 | 0 | 57.9 | 0.9833 | 20-03-2026 12:50 | 321.267 | 330.141 | 1280.8 | 55.0235 | 0 | 55.0235 | 0 | 58 | 0 | 58 | 0.97312 | 20-03-2026 12:50 | 230.436 | 233.826 | 1294 | 38.971 | 0 | 38.971 | 0 | 58.4 | 0 | 58.4 | 0.9855 | 20-03-2026 12:50 | 229.42 | 232.89 | 962.4 | 38.815 | 0 | 38.815 | 0 | 43.9 | 0 | 43.9 | 0.9851 | 20-03-2026 12:50 | 223.921 | 228.938 | 961.6 | 38.1563 | 0 | 38.1563 | 0 | 43.9 | 0 | 43.9 | 0.97809 | 20-03-2026 12:50 | 246.421 | 251.376 | 959.5 | 41.896 | 0 | 41.896 | 0 | 44.1 | 0 | 44.1 | 0.98029 | 20-03-2026 12:50 | 230.501 | 234.313 | 966.5 | 39.0522 | 0 | 39.0522 | 0 | 44.5 | 0 | 44.5 | 0.98373 | 20-03-2026 12:50 | 249.039 | 252.934 | 916.5 | 42.1557 | 0 | 42.1557 | 0 | 42 | 0 | 42 | 0.9846 | 20-03-2026 12:50 | 411.6887 | 0 | 411.6887 | 0 | 450.2 | 0 | 450.2
20-03-2026 12:40 |  |  | 352.441 | 358.317 | 1234.2 | 59.7195 | 0 | 59.7195 | 0 | 55.9 | 0 | 55.9 | 0.9836 | 20-03-2026 12:40 | 352.442 | 358.173 | 1240.1 | 59.6955 | 0 | 59.6955 | 0 | 55 | 0 | 55 | 0.984 | 20-03-2026 12:40 | 351.599 | 361.638 | 1222.8 | 60.273 | 0 | 60.273 | 0 | 56 | 0 | 56 | 0.97224 | 20-03-2026 12:40 | 351.605 | 357.25 | 1235.6 | 59.5417 | 0 | 59.5417 | 0 | 55.2 | 0 | 55.2 | 0.9842 | 20-03-2026 12:40 | 266.717 | 270.944 | 918.5 | 45.1573 | 0 | 45.1573 | 0 | 42.1 | 0 | 42.1 | 0.9844 | 20-03-2026 12:40 | 265.362 | 270.051 | 917.7 | 45.0085 | 0 | 45.0085 | 0 | 41.7 | 0 | 41.7 | 0.98264 | 20-03-2026 12:40 | 266.278 | 271.362 | 915.4 | 45.227 | 0 | 45.227 | 0 | 40.8 | 0 | 40.8 | 0.98126 | 20-03-2026 12:40 | 267.409 | 275.36 | 922 | 45.8933 | 0 | 45.8933 | 0 | 41.4 | 0 | 41.4 | 0.97113 | 20-03-2026 12:40 | 252.388 | 256.388 | 874.5 | 42.7313 | 0 | 42.7313 | 0 | 40.2 | 0 | 40.2 | 0.9844 | 20-03-2026 12:40 | 463.2472 | 0 | 463.2472 | 0 | 428.3 | 0 | 428.3
20-03-2026 12:30 |  |  | 348.223 | 353.957 | 1178.3 | 58.9928 | 0 | 58.9928 | 0 | 59.2 | 0 | 59.2 | 0.9838 | 20-03-2026 12:30 | 346.383 | 352.051 | 1185.1 | 58.6752 | 0 | 58.6752 | 0 | 59.8 | 0 | 59.8 | 0.9839 | 20-03-2026 12:30 | 347.448 | 357.343 | 1166.8 | 59.5572 | 0 | 59.5572 | 0 | 57.2 | 0 | 57.2 | 0.97231 | 20-03-2026 12:30 | 345.337 | 351.024 | 1180.4 | 58.504 | 0 | 58.504 | 0 | 57.4 | 0 | 57.4 | 0.9838 | 20-03-2026 12:30 | 264.096 | 268.336 | 876.4 | 44.7227 | 0 | 44.7227 | 0 | 43.3 | 0 | 43.3 | 0.9842 | 20-03-2026 12:30 | 260.815 | 265.752 | 876 | 44.292 | 0 | 44.292 | 0 | 42.8 | 0 | 42.8 | 0.98142 | 20-03-2026 12:30 | 262.156 | 267.288 | 874.6 | 44.548 | 0 | 44.548 | 0 | 43 | 0 | 43 | 0.9808 | 20-03-2026 12:30 | 263.226 | 271.231 | 880.6 | 45.2052 | 0 | 45.2052 | 0 | 43.1 | 0 | 43.1 | 0.97049 | 20-03-2026 12:30 | 248.453 | 252.39 | 834.3 | 42.065 | 0 | 42.065 | 0 | 40.7 | 0 | 40.7 | 0.9844 | 20-03-2026 12:30 | 456.562 | 0 | 456.562 | 0 | 446.5 | 0 | 446.5
20-03-2026 12:20 |  |  | 347.056 | 353.022 | 1119.1 | 58.837 | 0 | 58.837 | 0 | 57.7 | 0 | 57.7 | 0.9831 | 20-03-2026 12:20 | 346.38 | 352.048 | 1125.3 | 58.6747 | 0 | 58.6747 | 0 | 55.5 | 0 | 55.5 | 0.9839 | 20-03-2026 12:20 | 344.677 | 354.493 | 1109.6 | 59.0822 | 0 | 59.0822 | 0 | 57.1 | 0 | 57.1 | 0.97231 | 20-03-2026 12:20 | 345.511 | 351.2 | 1123 | 58.5333 | 0 | 58.5333 | 0 | 57.6 | 0 | 57.6 | 0.9838 | 20-03-2026 12:20 | 260.92 | 265.055 | 833.1 | 44.1758 | 0 | 44.1758 | 0 | 43.2 | 0 | 43.2 | 0.9844 | 20-03-2026 12:20 | 258.434 | 263.36 | 833.2 | 43.8933 | 0 | 43.8933 | 0 | 42.9 | 0 | 42.9 | 0.9813 | 20-03-2026 12:20 | 258.845 | 264.046 | 831.6 | 44.0077 | 0 | 44.0077 | 0 | 43.4 | 0 | 43.4 | 0.9803 | 20-03-2026 12:20 | 259.294 | 266.785 | 837.5 | 44.4642 | 0 | 44.4642 | 0 | 43.6 | 0 | 43.6 | 0.97192 | 20-03-2026 12:20 | 245.352 | 249.164 | 793.6 | 41.5273 | 0 | 41.5273 | 0 | 41.3 | 0 | 41.3 | 0.9847 | 20-03-2026 12:20 | 453.1955 | 0 | 453.1955 | 0 | 442.3 | 0 | 442.3
20-03-2026 12:10 |  |  | 347.297 | 353.284 | 1061.4 | 58.8807 | 0 | 58.8807 | 0 | 56.3 | 0 | 56.3 | 0.98305 | 20-03-2026 12:10 | 348.098 | 355.267 | 1069.8 | 59.2112 | 0 | 59.2112 | 0 | 57.7 | 0 | 57.7 | 0.97982 | 20-03-2026 12:10 | 344.922 | 354.54 | 1052.5 | 59.09 | 0 | 59.09 | 0 | 56.9 | 0 | 56.9 | 0.97287 | 20-03-2026 12:10 | 347.959 | 353.977 | 1065.4 | 58.9962 | 0 | 58.9962 | 0 | 58.2 | 0 | 58.2 | 0.983 | 20-03-2026 12:10 | 260.577 | 264.653 | 789.9 | 44.1088 | 0 | 44.1088 | 0 | 43.6 | 0 | 43.6 | 0.9846 | 20-03-2026 12:10 | 257.6 | 262.343 | 790.3 | 43.7238 | 0 | 43.7238 | 0 | 43.1 | 0 | 43.1 | 0.98192 | 20-03-2026 12:10 | 258.295 | 263.306 | 788.2 | 43.8843 | 0 | 43.8843 | 0 | 42.6 | 0 | 42.6 | 0.98097 | 20-03-2026 12:10 | 258.967 | 266.712 | 793.9 | 44.452 | 0 | 44.452 | 0 | 42.8 | 0 | 42.8 | 0.97096 | 20-03-2026 12:10 | 244.787 | 248.609 | 752.3 | 41.4348 | 0 | 41.4348 | 0 | 40.4 | 0 | 40.4 | 0.98463 | 20-03-2026 12:10 | 453.7818 | 0 | 453.7818 | 0 | 441.6 | 0 | 441.6
20-03-2026 12:00 |  |  | 341.297 | 347.129 | 1005.1 | 57.8548 | 0 | 57.8548 | 0 | 56.6 | 0 | 56.6 | 0.9832 | 20-03-2026 12:00 | 346.577 | 351.605 | 1012.1 | 58.6008 | 0 | 58.6008 | 0 | 58.9 | 0 | 58.9 | 0.9857 | 20-03-2026 12:00 | 339.767 | 349.111 | 995.6 | 58.1852 | 0 | 58.1852 | 0 | 56.1 | 0 | 56.1 | 0.97323 | 20-03-2026 12:00 | 342.622 | 348.512 | 1007.2 | 58.0853 | 0 | 58.0853 | 0 | 56.8 | 0 | 56.8 | 0.9831 | 20-03-2026 12:00 | 256.066 | 260.045 | 746.3 | 43.3408 | 0 | 43.3408 | 0 | 42.4 | 0 | 42.4 | 0.9847 | 20-03-2026 12:00 | 253.068 | 257.772 | 747.2 | 42.962 | 0 | 42.962 | 0 | 42 | 0 | 42 | 0.98175 | 20-03-2026 12:00 | 253.779 | 258.626 | 745.6 | 43.1043 | 0 | 43.1043 | 0 | 42 | 0 | 42 | 0.98126 | 20-03-2026 12:00 | 255.343 | 263.29 | 751.1 | 43.8817 | 0 | 43.8817 | 0 | 42.4 | 0 | 42.4 | 0.96982 | 20-03-2026 12:00 | 241.197 | 244.945 | 711.9 | 40.8242 | 0 | 40.8242 | 0 | 40 | 0 | 40 | 0.9847 | 20-03-2026 12:00 | 446.8392 | 0 | 446.8392 | 0 | 437.2 | 0 | 437.2
20-03-2026 11:50 |  |  | 336.761 | 342.446 | 948.5 | 57.0743 | 0 | 57.0743 | 0 | 57.2 | 0 | 57.2 | 0.9834 | 20-03-2026 11:50 | 342.307 | 348.661 | 953.2 | 58.1102 | 0 | 58.1102 | 0 | 57 | 0 | 57 | 0.98178 | 20-03-2026 11:50 | 334.209 | 343.555 | 939.5 | 57.2592 | 0 | 57.2592 | 0 | 56 | 0 | 56 | 0.9728 | 20-03-2026 11:50 | 339.013 | 344.841 | 950.4 | 57.4735 | 0 | 57.4735 | 0 | 55.8 | 0 | 55.8 | 0.9831 | 20-03-2026 11:50 | 252.434 | 256.382 | 703.9 | 42.7303 | 0 | 42.7303 | 0 | 41.6 | 0 | 41.6 | 0.9846 | 20-03-2026 11:50 | 250.978 | 255.247 | 705.2 | 42.5412 | 0 | 42.5412 | 0 | 41.3 | 0 | 41.3 | 0.98328 | 20-03-2026 11:50 | 250.525 | 255.185 | 703.6 | 42.5308 | 0 | 42.5308 | 0 | 41.9 | 0 | 41.9 | 0.98174 | 20-03-2026 11:50 | 252.581 | 260.025 | 708.7 | 43.3375 | 0 | 43.3375 | 0 | 42 | 0 | 42 | 0.97137 | 20-03-2026 11:50 | 238.496 | 242.177 | 671.9 | 40.3628 | 0 | 40.3628 | 0 | 39.8 | 0 | 39.8 | 0.9848 | 20-03-2026 11:50 | 441.4198 | 0 | 441.4198 | 0 | 432.6 | 0 | 432.6
20-03-2026 11:40 |  |  | 336.002 | 341.657 | 891.3 | 56.9428 | 0 | 56.9428 | 0 | 55.5 | 0 | 55.5 | 0.98345 | 20-03-2026 11:40 | 339.211 | 345.042 | 896.2 | 57.507 | 0 | 57.507 | 0 | 54.5 | 0 | 54.5 | 0.9831 | 20-03-2026 11:40 | 334.196 | 343.462 | 883.5 | 57.2437 | 0 | 57.2437 | 0 | 55.2 | 0 | 55.2 | 0.97302 | 20-03-2026 11:40 | 337.09 | 342.85 | 894.6 | 57.1417 | 0 | 57.1417 | 0 | 55.6 | 0 | 55.6 | 0.9832 | 20-03-2026 11:40 | 251.936 | 255.825 | 662.3 | 42.6375 | 0 | 42.6375 | 0 | 42.1 | 0 | 42.1 | 0.9848 | 20-03-2026 11:40 | 250.076 | 254.341 | 663.9 | 42.3902 | 0 | 42.3902 | 0 | 41.8 | 0 | 41.8 | 0.98323 | 20-03-2026 11:40 | 250.281 | 255.065 | 661.7 | 42.5108 | 0 | 42.5108 | 0 | 41.2 | 0 | 41.2 | 0.98124 | 20-03-2026 11:40 | 252.393 | 259.875 | 666.7 | 43.3125 | 0 | 43.3125 | 0 | 41.6 | 0 | 41.6 | 0.97121 | 20-03-2026 11:40 | 239.061 | 242.702 | 632.1 | 40.4503 | 0 | 40.4503 | 0 | 39.4 | 0 | 39.4 | 0.985 | 20-03-2026 11:40 | 440.1365 | 0 | 440.1365 | 0 | 426.9 | 0 | 426.9
20-03-2026 11:30 |  |  | 331.676 | 337.206 | 835.8 | 56.201 | 0 | 56.201 | 0 | 54.6 | 0 | 54.6 | 0.9836 | 20-03-2026 11:30 | 334.502 | 340.963 | 841.7 | 56.8272 | 0 | 56.8272 | 0 | 55.2 | 0 | 55.2 | 0.98105 | 20-03-2026 11:30 | 329.159 | 338.428 | 828.3 | 56.4047 | 0 | 56.4047 | 0 | 55 | 0 | 55 | 0.97261 | 20-03-2026 11:30 | 332.624 | 338.289 | 839 | 56.3815 | 0 | 56.3815 | 0 | 55.6 | 0 | 55.6 | 0.98325 | 20-03-2026 11:30 | 248.153 | 251.937 | 620.2 | 41.9895 | 0 | 41.9895 | 0 | 40.9 | 0 | 40.9 | 0.98498 | 20-03-2026 11:30 | 246.553 | 250.861 | 622.1 | 41.8102 | 0 | 41.8102 | 0 | 40.6 | 0 | 40.6 | 0.98283 | 20-03-2026 11:30 | 246.602 | 251.019 | 620.5 | 41.8365 | 0 | 41.8365 | 0 | 40.6 | 0 | 40.6 | 0.9824 | 20-03-2026 11:30 | 248.381 | 255.633 | 625.1 | 42.6055 | 0 | 42.6055 | 0 | 40.9 | 0 | 40.9 | 0.97163 | 20-03-2026 11:30 | 235.073 | 238.677 | 592.7 | 39.7795 | 0 | 39.7795 | 0 | 38.7 | 0 | 38.7 | 0.9849 | 20-03-2026 11:30 | 433.8355 | 0 | 433.8355 | 0 | 422.1 | 0 | 422.1
20-03-2026 11:20 |  |  | 326.475 | 331.851 | 781.2 | 55.3085 | 0 | 55.3085 | 0 | 53.4 | 0 | 53.4 | 0.9838 | 20-03-2026 11:20 | 329.444 | 335.039 | 786.5 | 55.8398 | 0 | 55.8398 | 0 | 55.5 | 0 | 55.5 | 0.9833 | 20-03-2026 11:20 | 324.349 | 332.827 | 773.3 | 55.4712 | 0 | 55.4712 | 0 | 52.9 | 0 | 52.9 | 0.97453 | 20-03-2026 11:20 | 327.054 | 332.609 | 783.4 | 55.4348 | 0 | 55.4348 | 0 | 53.4 | 0 | 53.4 | 0.9833 | 20-03-2026 11:20 | 244.296 | 248.041 | 579.3 | 41.3402 | 0 | 41.3402 | 0 | 39.9 | 0 | 39.9 | 0.9849 | 20-03-2026 11:20 | 242.632 | 246.753 | 581.5 | 41.1255 | 0 | 41.1255 | 0 | 40.2 | 0 | 40.2 | 0.9833 | 20-03-2026 11:20 | 242.995 | 247.208 | 579.9 | 41.2013 | 0 | 41.2013 | 0 | 40.4 | 0 | 40.4 | 0.98296 | 20-03-2026 11:20 | 244.506 | 251.676 | 584.2 | 41.946 | 0 | 41.946 | 0 | 40.5 | 0 | 40.5 | 0.97151 | 20-03-2026 11:20 | 231.072 | 234.567 | 554 | 39.0945 | 0 | 39.0945 | 0 | 38.4 | 0 | 38.4 | 0.9851 | 20-03-2026 11:20 | 426.7618 | 0 | 426.7618 | 0 | 414.6 | 0 | 414.6
20-03-2026 11:10 |  |  | 318.534 | 323.779 | 727.8 | 53.9632 | 0 | 53.9632 | 0 | 52.9 | 0 | 52.9 | 0.9838 | 20-03-2026 11:10 | 320.806 | 326.188 | 731 | 54.3647 | 0 | 54.3647 | 0 | 52.6 | 0 | 52.6 | 0.9835 | 20-03-2026 11:10 | 315.911 | 324.201 | 720.4 | 54.0335 | 0 | 54.0335 | 0 | 52.5 | 0 | 52.5 | 0.97443 | 20-03-2026 11:10 | 318.796 | 324.144 | 730 | 54.024 | 0 | 54.024 | 0 | 53 | 0 | 53 | 0.9835 | 20-03-2026 11:10 | 238.372 | 242.002 | 539.4 | 40.3337 | 0 | 40.3337 | 0 | 39.6 | 0 | 39.6 | 0.985 | 20-03-2026 11:10 | 236.827 | 240.943 | 541.3 | 40.1572 | 0 | 40.1572 | 0 | 38.8 | 0 | 38.8 | 0.98292 | 20-03-2026 11:10 | 237.243 | 241.6 | 539.5 | 40.2667 | 0 | 40.2667 | 0 | 38.7 | 0 | 38.7 | 0.98197 | 20-03-2026 11:10 | 239.097 | 246.301 | 543.7 | 41.0502 | 0 | 41.0502 | 0 | 39.1 | 0 | 39.1 | 0.97075 | 20-03-2026 11:10 | 226.453 | 229.855 | 515.6 | 38.3092 | 0 | 38.3092 | 0 | 37.5 | 0 | 37.5 | 0.9852 | 20-03-2026 11:10 | 416.5022 | 0 | 416.5022 | 0 | 404.7 | 0 | 404.7
20-03-2026 11:00 |  |  | 314.468 | 319.616 | 674.9 | 53.2693 | 0 | 53.2693 | 0 | 51.8 | 0 | 51.8 | 0.98389 | 20-03-2026 11:00 | 317.071 | 322.629 | 678.4 | 53.7715 | 0 | 53.7715 | 0 | 52.9 | 0 | 52.9 | 0.98277 | 20-03-2026 11:00 | 311.929 | 319.974 | 667.9 | 53.329 | 0 | 53.329 | 0 | 51.3 | 0 | 51.3 | 0.97486 | 20-03-2026 11:00 | 315.199 | 320.422 | 677 | 53.4037 | 0 | 53.4037 | 0 | 51.9 | 0 | 51.9 | 0.9837 | 20-03-2026 11:00 | 235.082 | 238.613 | 499.8 | 39.7688 | 0 | 39.7688 | 0 | 39.2 | 0 | 39.2 | 0.9852 | 20-03-2026 11:00 | 233.387 | 237.017 | 502.5 | 39.5028 | 0 | 39.5028 | 0 | 39.1 | 0 | 39.1 | 0.98468 | 20-03-2026 11:00 | 233.664 | 237.468 | 500.8 | 39.578 | 0 | 39.578 | 0 | 39.1 | 0 | 39.1 | 0.98398 | 20-03-2026 11:00 | 234.803 | 241.362 | 504.6 | 40.227 | 0 | 40.227 | 0 | 39.3 | 0 | 39.3 | 0.97283 | 20-03-2026 11:00 | 222.085 | 225.353 | 478.1 | 37.5588 | 0 | 37.5588 | 0 | 36.6 | 0 | 36.6 | 0.9855 | 20-03-2026 11:00 | 410.409 | 0 | 410.409 | 0 | 401.2 | 0 | 401.2
20-03-2026 10:50 |  |  | 308.943 | 313.871 | 623.1 | 52.3118 | 0 | 52.3118 | 0 | 51.6 | 0 | 51.6 | 0.9843 | 20-03-2026 10:50 | 311.422 | 316.986 | 625.5 | 52.831 | 0 | 52.831 | 0 | 50.8 | 0 | 50.8 | 0.98245 | 20-03-2026 10:50 | 306.457 | 314.028 | 616.6 | 52.338 | 0 | 52.338 | 0 | 50.4 | 0 | 50.4 | 0.97589 | 20-03-2026 10:50 | 310.207 | 315.251 | 625.1 | 52.5418 | 0 | 52.5418 | 0 | 51.2 | 0 | 51.2 | 0.984 | 20-03-2026 10:50 | 230.674 | 234.064 | 460.6 | 39.0107 | 0 | 39.0107 | 0 | 37.4 | 0 | 37.4 | 0.98552 | 20-03-2026 10:50 | 229.81 | 233.299 | 463.4 | 38.8832 | 0 | 38.8832 | 0 | 37.8 | 0 | 37.8 | 0.98504 | 20-03-2026 10:50 | 229.638 | 233.67 | 461.7 | 38.945 | 0 | 38.945 | 0 | 37.8 | 0 | 37.8 | 0.98274 | 20-03-2026 10:50 | 230.793 | 237.357 | 465.3 | 39.5595 | 0 | 39.5595 | 0 | 38 | 0 | 38 | 0.97235 | 20-03-2026 10:50 | 219.191 | 222.371 | 441.5 | 37.0618 | 0 | 37.0618 | 0 | 36.2 | 0 | 36.2 | 0.9857 | 20-03-2026 10:50 | 403.4828 | 0 | 403.4828 | 0 | 391.2 | 0 | 391.2
20-03-2026 10:40 |  |  | 301.609 | 306.42 | 571.5 | 51.07 | 0 | 51.07 | 0 | 50 | 0 | 50 | 0.9843 | 20-03-2026 10:40 | 303.724 | 309.736 | 574.7 | 51.6227 | 0 | 51.6227 | 0 | 49.9 | 0 | 49.9 | 0.98059 | 20-03-2026 10:40 | 298.234 | 305.764 | 566.2 | 50.9607 | 0 | 50.9607 | 0 | 49.7 | 0 | 49.7 | 0.97537 | 20-03-2026 10:40 | 302.869 | 307.762 | 573.9 | 51.2937 | 0 | 51.2937 | 0 | 50.3 | 0 | 50.3 | 0.9841 | 20-03-2026 10:40 | 224.265 | 227.519 | 423.2 | 37.9198 | 0 | 37.9198 | 0 | 37.3 | 0 | 37.3 | 0.9857 | 20-03-2026 10:40 | 224.645 | 228.003 | 425.6 | 38.0005 | 0 | 38.0005 | 0 | 36.8 | 0 | 36.8 | 0.98527 | 20-03-2026 10:40 | 223.165 | 226.994 | 423.9 | 37.8323 | 0 | 37.8323 | 0 | 36.6 | 0 | 36.6 | 0.98313 | 20-03-2026 10:40 | 224.614 | 231.073 | 427.3 | 38.5122 | 0 | 38.5122 | 0 | 37 | 0 | 37 | 0.97205 | 20-03-2026 10:40 | 213.59 | 216.711 | 405.3 | 36.1185 | 0 | 36.1185 | 0 | 35 | 0 | 35 | 0.9856 | 20-03-2026 10:40 | 393.3303 | 0 | 393.3303 | 0 | 382.6 | 0 | 382.6
20-03-2026 10:30 |  |  | 291.349 | 295.876 | 521.5 | 49.3127 | 0 | 49.3127 | 0 | 47.4 | 0 | 47.4 | 0.9847 | 20-03-2026 10:30 | 294.285 | 299.012 | 524.8 | 49.8353 | 0 | 49.8353 | 0 | 49.1 | 0 | 49.1 | 0.98419 | 20-03-2026 10:30 | 288.249 | 295.514 | 516.5 | 49.2523 | 0 | 49.2523 | 0 | 46.8 | 0 | 46.8 | 0.97542 | 20-03-2026 10:30 | 293.75 | 298.375 | 523.6 | 49.7292 | 0 | 49.7292 | 0 | 48.2 | 0 | 48.2 | 0.9845 | 20-03-2026 10:30 | 217.194 | 220.3 | 385.9 | 36.7167 | 0 | 36.7167 | 0 | 35.6 | 0 | 35.6 | 0.9859 | 20-03-2026 10:30 | 218.048 | 221.409 | 388.8 | 36.9015 | 0 | 36.9015 | 0 | 35.7 | 0 | 35.7 | 0.98482 | 20-03-2026 10:30 | 216.854 | 220.338 | 387.3 | 36.723 | 0 | 36.723 | 0 | 35.5 | 0 | 35.5 | 0.98419 | 20-03-2026 10:30 | 219.197 | 225.354 | 390.3 | 37.559 | 0 | 37.559 | 0 | 35.7 | 0 | 35.7 | 0.97268 | 20-03-2026 10:30 | 208.186 | 211.163 | 370.3 | 35.1938 | 0 | 35.1938 | 0 | 34.5 | 0 | 34.5 | 0.9859 | 20-03-2026 10:30 | 381.2235 | 0 | 381.2235 | 0 | 368.5 | 0 | 368.5
20-03-2026 10:20 |  |  | 284.951 | 289.32 | 474.1 | 48.22 | 0 | 48.22 | 0 | 46.8 | 0 | 46.8 | 0.9849 | 20-03-2026 10:20 | 286.783 | 291.526 | 475.7 | 48.5877 | 0 | 48.5877 | 0 | 46.7 | 0 | 46.7 | 0.98373 | 20-03-2026 10:20 | 281.987 | 288.919 | 469.7 | 48.1532 | 0 | 48.1532 | 0 | 46.4 | 0 | 46.4 | 0.97601 | 20-03-2026 10:20 | 286.097 | 290.572 | 475.4 | 48.4287 | 0 | 48.4287 | 0 | 46.4 | 0 | 46.4 | 0.9846 | 20-03-2026 10:20 | 211.328 | 214.329 | 350.3 | 35.7215 | 0 | 35.7215 | 0 | 34.3 | 0 | 34.3 | 0.986 | 20-03-2026 10:20 | 211.579 | 214.642 | 353.1 | 35.7737 | 0 | 35.7737 | 0 | 34.4 | 0 | 34.4 | 0.98573 | 20-03-2026 10:20 | 210.763 | 214.07 | 351.8 | 35.6783 | 0 | 35.6783 | 0 | 34.3 | 0 | 34.3 | 0.98455 | 20-03-2026 10:20 | 212.333 | 218.533 | 354.6 | 36.4222 | 0 | 36.4222 | 0 | 34.5 | 0 | 34.5 | 0.97163 | 20-03-2026 10:20 | 201.445 | 204.285 | 335.8 | 34.0475 | 0 | 34.0475 | 0 | 32.2 | 0 | 32.2 | 0.9861 | 20-03-2026 10:20 | 371.0327 | 0 | 371.0327 | 0 | 356 | 0 | 356
20-03-2026 10:10 |  |  | 272.975 | 277.048 | 427.3 | 46.1747 | 0 | 46.1747 | 0 | 44.2 | 0 | 44.2 | 0.9853 | 20-03-2026 10:10 | 276.108 | 280.313 | 429 | 46.7188 | 0 | 46.7188 | 0 | 44.9 | 0 | 44.9 | 0.985 | 20-03-2026 10:10 | 269.596 | 275.848 | 423.3 | 45.9747 | 0 | 45.9747 | 0 | 43.8 | 0 | 43.8 | 0.97734 | 20-03-2026 10:10 | 274.656 | 278.839 | 429 | 46.4732 | 0 | 46.4732 | 0 | 44.2 | 0 | 44.2 | 0.985 | 20-03-2026 10:10 | 202.149 | 204.936 | 316 | 34.156 | 0 | 34.156 | 0 | 33 | 0 | 33 | 0.9864 | 20-03-2026 10:10 | 203.672 | 206.548 | 318.7 | 34.4247 | 0 | 34.4247 | 0 | 32.9 | 0 | 32.9 | 0.98608 | 20-03-2026 10:10 | 202.267 | 205.33 | 317.5 | 34.2217 | 0 | 34.2217 | 0 | 32.9 | 0 | 32.9 | 0.98508 | 20-03-2026 10:10 | 204.524 | 210.27 | 320.1 | 35.045 | 0 | 35.045 | 0 | 33.2 | 0 | 33.2 | 0.97267 | 20-03-2026 10:10 | 194.268 | 196.934 | 303.6 | 32.8223 | 0 | 32.8223 | 0 | 31.4 | 0 | 31.4 | 0.98646 | 20-03-2026 10:10 | 356.011 | 0 | 356.011 | 0 | 340.5 | 0 | 340.5
20-03-2026 10:00 |  |  | 256.018 | 259.706 | 383.1 | 43.2843 | 0 | 43.2843 | 0 | 42.8 | 0 | 42.8 | 0.9858 | 20-03-2026 10:00 | 259.64 | 263.406 | 384.1 | 43.901 | 0 | 43.901 | 0 | 44 | 0 | 44 | 0.9857 | 20-03-2026 10:00 | 254.701 | 260.236 | 379.5 | 43.3727 | 0 | 43.3727 | 0 | 42.1 | 0 | 42.1 | 0.97873 | 20-03-2026 10:00 | 257.97 | 261.792 | 384.8 | 43.632 | 0 | 43.632 | 0 | 42.6 | 0 | 42.6 | 0.9854 | 20-03-2026 10:00 | 191.158 | 193.735 | 283 | 32.2892 | 0 | 32.2892 | 0 | 31.4 | 0 | 31.4 | 0.9867 | 20-03-2026 10:00 | 191.163 | 193.759 | 285.8 | 32.2932 | 0 | 32.2932 | 0 | 31.6 | 0 | 31.6 | 0.9866 | 20-03-2026 10:00 | 190.831 | 193.483 | 284.6 | 32.2472 | 0 | 32.2472 | 0 | 31.5 | 0 | 31.5 | 0.98629 | 20-03-2026 10:00 | 192.564 | 197.688 | 286.9 | 32.948 | 0 | 32.948 | 0 | 31.8 | 0 | 31.8 | 0.97408 | 20-03-2026 10:00 | 182.152 | 184.645 | 272.2 | 30.7742 | 0 | 30.7742 | 0 | 30.6 | 0 | 30.6 | 0.9865 | 20-03-2026 10:00 | 334.7417 | 0 | 334.7417 | 0 | 328.4 | 0 | 328.4
20-03-2026 09:50 |  |  | 247.701 | 251.244 | 340.3 | 41.874 | 0 | 41.874 | 0 | 39 | 0 | 39 |  | 20-03-2026 09:50 | 248.334 | 251.937 | 340.1 | 41.9895 | 0 | 41.9895 | 0 | 38.7 | 0 | 38.7 |  | 20-03-2026 09:50 | 246.474 | 251.903 | 337.4 | 41.9838 | 0 | 41.9838 | 0 | 39.6 | 0 | 39.6 |  | 20-03-2026 09:50 | 248.658 | 252.425 | 342.2 | 42.0708 | 0 | 42.0708 | 0 | 40.8 | 0 | 40.8 |  | 20-03-2026 09:50 | 184.955 | 187.448 | 251.6 | 31.2413 | 0 | 31.2413 | 0 | 30.2 | 0 | 30.2 |  | 20-03-2026 09:50 | 184.75 | 187.24 | 254.2 | 31.2067 | 0 | 31.2067 | 0 | 30.3 | 0 | 30.3 |  | 20-03-2026 09:50 | 184.659 | 187.129 | 253.1 | 31.1882 | 0 | 31.1882 | 0 | 30.2 | 0 | 30.2 |  | 20-03-2026 09:50 | 185.91 | 191.174 | 255.1 | 31.8623 | 0 | 31.8623 | 0 | 30.4 | 0 | 30.4 |  | 20-03-2026 09:50 | 175.974 | 178.346 | 241.6 | 29.7243 | 0 | 29.7243 | 0 | 28.4 | 0 | 28.4 |  | 20-03-2026 09:50 | 323.141 | 0 | 323.141 | 0 | 307.6 | 0 | 307.6
20-03-2026 09:40 |  |  | 236.463 | 239.772 | 301.3 | 39.962 | 0 | 39.962 | 0 | 39.4 | 0 | 39.4 |  | 20-03-2026 09:40 | 236.064 | 239.44 | 301.4 | 39.9067 | 0 | 39.9067 | 0 | 38.7 | 0 | 38.7 |  | 20-03-2026 09:40 | 234.277 | 239.341 | 297.8 | 39.8902 | 0 | 39.8902 | 0 | 38 | 0 | 38 |  | 20-03-2026 09:40 | 235.262 | 238.602 | 301.4 | 39.767 | 0 | 39.767 | 0 | 38 | 0 | 38 |  | 20-03-2026 09:40 | 175.187 | 177.476 | 221.4 | 29.5793 | 0 | 29.5793 | 0 | 28.1 | 0 | 28.1 |  | 20-03-2026 09:40 | 175.628 | 177.959 | 223.9 | 29.6598 | 0 | 29.6598 | 0 | 28.3 | 0 | 28.3 |  | 20-03-2026 09:40 | 175.213 | 177.521 | 222.9 | 29.5868 | 0 | 29.5868 | 0 | 28.1 | 0 | 28.1 |  | 20-03-2026 09:40 | 176.682 | 181.412 | 224.7 | 30.2353 | 0 | 30.2353 | 0 | 28.3 | 0 | 28.3 |  | 20-03-2026 09:40 | 167.601 | 169.819 | 213.2 | 28.3032 | 0 | 28.3032 | 0 | 26.9 | 0 | 26.9 |  | 20-03-2026 09:40 | 306.8903 | 0 | 306.8903 | 0 | 293.8 | 0 | 293.8
20-03-2026 09:30 |  |  | 221.053 | 224.033 | 261.9 | 37.3388 | 0 | 37.3388 | 0 | 34.4 | 0 | 34.4 |  | 20-03-2026 09:30 | 223.052 | 226.127 | 262.7 | 37.6878 | 0 | 37.6878 | 0 | 37.1 | 0 | 37.1 |  | 20-03-2026 09:30 | 220.258 | 224.521 | 259.8 | 37.4202 | 0 | 37.4202 | 0 | 35.1 | 0 | 35.1 |  | 20-03-2026 09:30 | 223.165 | 226.242 | 263.4 | 37.707 | 0 | 37.707 | 0 | 35.6 | 0 | 35.6 |  | 20-03-2026 09:30 | 164.822 | 166.942 | 193.3 | 27.8237 | 0 | 27.8237 | 0 | 26.2 | 0 | 26.2 |  | 20-03-2026 09:30 | 165.699 | 167.847 | 195.6 | 27.9745 | 0 | 27.9745 | 0 | 26.4 | 0 | 26.4 |  | 20-03-2026 09:30 | 164.707 | 166.843 | 194.8 | 27.8072 | 0 | 27.8072 | 0 | 26.3 | 0 | 26.3 |  | 20-03-2026 09:30 | 166.067 | 170.671 | 196.4 | 28.4452 | 0 | 28.4452 | 0 | 27.3 | 0 | 27.3 |  | 20-03-2026 09:30 | 156.39 | 158.418 | 186.3 | 26.403 | 0 | 26.403 | 0 | 25.4 | 0 | 25.4 |  | 20-03-2026 09:30 | 288.6073 | 0 | 288.6073 | 0 | 273.8 | 0 | 273.8
20-03-2026 09:20 |  |  | 205.765 | 208.454 | 227.5 | 34.7423 | 0 | 34.7423 | 0 | 33 | 0 | 33 |  | 20-03-2026 09:20 | 204.694 | 209.078 | 225.6 | 34.8463 | 0 | 34.8463 | 0 | 32.8 | 0 | 32.8 |  | 20-03-2026 09:20 | 203.89 | 207.809 | 224.7 | 34.6348 | 0 | 34.6348 | 0 | 32.4 | 0 | 32.4 |  | 20-03-2026 09:20 | 205.696 | 208.426 | 227.8 | 34.7377 | 0 | 34.7377 | 0 | 33.2 | 0 | 33.2 |  | 20-03-2026 09:20 | 151.872 | 153.763 | 167.1 | 25.6272 | 0 | 25.6272 | 0 | 24.5 | 0 | 24.5 |  | 20-03-2026 09:20 | 152.791 | 154.694 | 169.2 | 25.7823 | 0 | 25.7823 | 0 | 24.7 | 0 | 24.7 |  | 20-03-2026 09:20 | 152.109 | 154.037 | 168.5 | 25.6728 | 0 | 25.6728 | 0 | 24.6 | 0 | 24.6 |  | 20-03-2026 09:20 | 152.52 | 156.574 | 169.1 | 26.0957 | 0 | 26.0957 | 0 | 23.7 | 0 | 23.7 |  | 20-03-2026 09:20 | 144.232 | 146.073 | 160.9 | 24.3455 | 0 | 24.3455 | 0 | 23.1 | 0 | 23.1 |  | 20-03-2026 09:20 | 266.4847 | 0 | 266.4847 | 0 | 252 | 0 | 252
20-03-2026 09:10 |  |  | 192.443 | 194.899 | 194.5 | 32.4832 | 0 | 32.4832 | 0 | 31.2 | 0 | 31.2 |  | 20-03-2026 09:10 | 190.632 | 195.914 | 192.8 | 32.6523 | 0 | 32.6523 | 0 | 30.4 | 0 | 30.4 |  | 20-03-2026 09:10 | 190.129 | 193.353 | 192.3 | 32.2255 | 0 | 32.2255 | 0 | 30.8 | 0 | 30.8 |  | 20-03-2026 09:10 | 193.384 | 195.891 | 194.6 | 32.6485 | 0 | 32.6485 | 0 | 30.9 | 0 | 30.9 |  | 20-03-2026 09:10 | 141.849 | 143.601 | 142.6 | 23.9335 | 0 | 23.9335 | 0 | 23.1 | 0 | 23.1 |  | 20-03-2026 09:10 | 143.761 | 145.522 | 144.5 | 24.2537 | 0 | 24.2537 | 0 | 23 | 0 | 23 |  | 20-03-2026 09:10 | 142.363 | 144.107 | 143.9 | 24.0178 | 0 | 24.0178 | 0 | 22.9 | 0 | 22.9 |  | 20-03-2026 09:10 | 143.541 | 147.174 | 145.4 | 24.529 | 0 | 24.529 | 0 | 22.9 | 0 | 22.9 |  | 20-03-2026 09:10 | 135.338 | 137.01 | 137.8 | 22.835 | 0 | 22.835 | 0 | 22 | 0 | 22 |  | 20-03-2026 09:10 | 249.5785 | 0 | 249.5785 | 0 | 237.2 | 0 | 237.2
20-03-2026 09:00 |  |  | 177.602 | 179.796 | 163.3 | 29.966 | 0 | 29.966 | 0 | 28.9 | 0 | 28.9 |  | 20-03-2026 09:00 | 177.64 | 180.939 | 162.4 | 30.1565 | 0 | 30.1565 | 0 | 28.3 | 0 | 28.3 |  | 20-03-2026 09:00 | 175.774 | 178.948 | 161.5 | 29.8247 | 0 | 29.8247 | 0 | 28.3 | 0 | 28.3 |  | 20-03-2026 09:00 | 178.63 | 180.873 | 163.7 | 30.1455 | 0 | 30.1455 | 0 | 28.7 | 0 | 28.7 |  | 20-03-2026 09:00 | 130.82 | 132.287 | 119.5 | 22.0478 | 0 | 22.0478 | 0 | 20.8 | 0 | 20.8 |  | 20-03-2026 09:00 | 132.687 | 134.285 | 121.5 | 22.3808 | 0 | 22.3808 | 0 | 21.3 | 0 | 21.3 |  | 20-03-2026 09:00 | 131.498 | 133.095 | 121 | 22.1825 | 0 | 22.1825 | 0 | 21.1 | 0 | 21.1 |  | 20-03-2026 09:00 | 132.449 | 136.116 | 122.5 | 22.686 | 0 | 22.686 | 0 | 21.3 | 0 | 21.3 |  | 20-03-2026 09:00 | 125.203 | 126.944 | 115.8 | 21.1573 | 0 | 21.1573 | 0 | 20 | 0 | 20 |  | 20-03-2026 09:00 | 230.5472 | 0 | 230.5472 | 0 | 218.7 | 0 | 218.7
20-03-2026 08:50 |  |  | 161.369 | 163.312 | 134.4 | 27.2187 | 0 | 27.2187 | 0 | 25 | 0 | 25 |  | 20-03-2026 08:50 | 162.399 | 164.388 | 134.1 | 27.398 | 0 | 27.398 | 0 | 25.8 | 0 | 25.8 |  | 20-03-2026 08:50 | 159.876 | 162.465 | 133.2 | 27.0775 | 0 | 27.0775 | 0 | 25.1 | 0 | 25.1 |  | 20-03-2026 08:50 | 162.091 | 163.997 | 135 | 27.3328 | 0 | 27.3328 | 0 | 25.5 | 0 | 25.5 |  | 20-03-2026 08:50 | 119.156 | 120.542 | 98.7 | 20.0903 | 0 | 20.0903 | 0 | 18.7 | 0 | 18.7 |  | 20-03-2026 08:50 | 120.383 | 121.771 | 100.2 | 20.2952 | 0 | 20.2952 | 0 | 18.9 | 0 | 18.9 |  | 20-03-2026 08:50 | 118.984 | 120.38 | 99.9 | 20.0633 | 0 | 20.0633 | 0 | 19 | 0 | 19 |  | 20-03-2026 08:50 | 120.81 | 123.843 | 101.2 | 20.6405 | 0 | 20.6405 | 0 | 19.2 | 0 | 19.2 |  | 20-03-2026 08:50 | 114.667 | 116.013 | 95.8 | 19.3355 | 0 | 19.3355 | 0 | 18.2 | 0 | 18.2 |  | 20-03-2026 08:50 | 209.4518 | 0 | 209.4518 | 0 | 195.4 | 0 | 195.4
20-03-2026 08:40 |  |  | 147.311 | 149.025 | 109.4 | 24.8375 | 0 | 24.8375 | 0 | 22.5 | 0 | 22.5 |  | 20-03-2026 08:40 | 147.742 | 149.491 | 108.3 | 24.9152 | 0 | 24.9152 | 0 | 22.9 | 0 | 22.9 |  | 20-03-2026 08:40 | 145.878 | 147.774 | 108.1 | 24.629 | 0 | 24.629 | 0 | 22.8 | 0 | 22.8 |  | 20-03-2026 08:40 | 148.126 | 149.821 | 109.5 | 24.9702 | 0 | 24.9702 | 0 | 23.1 | 0 | 23.1 |  | 20-03-2026 08:40 | 108.62 | 109.861 | 80 | 18.3102 | 0 | 18.3102 | 0 | 17 | 0 | 17 |  | 20-03-2026 08:40 | 110.303 | 111.552 | 81.3 | 18.592 | 0 | 18.592 | 0 | 17.2 | 0 | 17.2 |  | 20-03-2026 08:40 | 108.237 | 109.485 | 80.9 | 18.2475 | 0 | 18.2475 | 0 | 16.9 | 0 | 16.9 |  | 20-03-2026 08:40 | 110.11 | 112.994 | 82 | 18.8323 | 0 | 18.8323 | 0 | 17.1 | 0 | 17.1 |  | 20-03-2026 08:40 | 104.654 | 105.861 | 77.6 | 17.6435 | 0 | 17.6435 | 0 | 16.2 | 0 | 16.2 |  | 20-03-2026 08:40 | 190.9773 | 0 | 190.9773 | 0 | 175.7 | 0 | 175.7
20-03-2026 08:30 |  |  | 129.47 | 130.897 | 86.9 | 21.8162 | 0 | 21.8162 | 0 | 20.1 | 0 | 20.1 |  | 20-03-2026 08:30 | 128.755 | 130.641 | 85.4 | 21.7735 | 0 | 21.7735 | 0 | 19.9 | 0 | 19.9 |  | 20-03-2026 08:30 | 127.5 | 129.307 | 85.3 | 21.5512 | 0 | 21.5512 | 0 | 19.8 | 0 | 19.8 |  | 20-03-2026 08:30 | 129.29 | 130.728 | 86.4 | 21.788 | 0 | 21.788 | 0 | 20.1 | 0 | 20.1 |  | 20-03-2026 08:30 | 94.869 | 95.924 | 63 | 15.9873 | 0 | 15.9873 | 0 | 14.7 | 0 | 14.7 |  | 20-03-2026 08:30 | 95.145 | 96.194 | 64.1 | 16.0323 | 0 | 16.0323 | 0 | 14.7 | 0 | 14.7 |  | 20-03-2026 08:30 | 95.776 | 96.831 | 64 | 16.1385 | 0 | 16.1385 | 0 | 14.7 | 0 | 14.7 |  | 20-03-2026 08:30 | 96.429 | 98.947 | 64.9 | 16.4912 | 0 | 16.4912 | 0 | 14.9 | 0 | 14.9 |  | 20-03-2026 08:30 | 91.618 | 92.646 | 61.4 | 15.441 | 0 | 15.441 | 0 | 14.2 | 0 | 14.2 |  | 20-03-2026 08:30 | 167.0192 | 0 | 167.0192 | 0 | 153.1 | 0 | 153.1
20-03-2026 08:20 |  |  | 112.408 | 113.601 | 66.8 | 18.9335 | 0 | 18.9335 | 0 | 17.5 | 0 | 17.5 |  | 20-03-2026 08:20 | 111.926 | 113.137 | 65.5 | 18.8562 | 0 | 18.8562 | 0 | 17.9 | 0 | 17.9 |  | 20-03-2026 08:20 | 110.523 | 112.042 | 65.5 | 18.6737 | 0 | 18.6737 | 0 | 17.2 | 0 | 17.2 |  | 20-03-2026 08:20 | 112.396 | 113.612 | 66.3 | 18.9353 | 0 | 18.9353 | 0 | 17.5 | 0 | 17.5 |  | 20-03-2026 08:20 | 82.192 | 83.106 | 48.3 | 13.851 | 0 | 13.851 | 0 | 12.8 | 0 | 12.8 |  | 20-03-2026 08:20 | 82.149 | 83.054 | 49.4 | 13.8423 | 0 | 13.8423 | 0 | 13 | 0 | 13 |  | 20-03-2026 08:20 | 83.079 | 83.986 | 49.3 | 13.9977 | 0 | 13.9977 | 0 | 13 | 0 | 13 |  | 20-03-2026 08:20 | 83.909 | 86.031 | 50 | 14.3385 | 0 | 14.3385 | 0 | 13.1 | 0 | 13.1 |  | 20-03-2026 08:20 | 79.729 | 80.64 | 47.2 | 13.44 | 0 | 13.44 | 0 | 12.4 | 0 | 12.4 |  | 20-03-2026 08:20 | 144.8682 | 0 | 144.8682 | 0 | 134.4 | 0 | 134.4
20-03-2026 08:10 |  |  | 95.82 | 96.798 | 49.3 | 16.133 | 0 | 16.133 | 0 | 14.6 | 0 | 14.6 |  | 20-03-2026 08:10 | 94.204 | 95.204 | 47.6 | 15.8673 | 0 | 15.8673 | 0 | 14.4 | 0 | 14.4 |  | 20-03-2026 08:10 | 94.584 | 95.62 | 48.3 | 15.9367 | 0 | 15.9367 | 0 | 14.1 | 0 | 14.1 |  | 20-03-2026 08:10 | 96.225 | 97.236 | 48.8 | 16.206 | 0 | 16.206 | 0 | 14.5 | 0 | 14.5 |  | 20-03-2026 08:10 | 70.156 | 70.897 | 35.5 | 11.8162 | 0 | 11.8162 | 0 | 10.6 | 0 | 10.6 |  | 20-03-2026 08:10 | 71.457 | 72.252 | 36.4 | 12.042 | 0 | 12.042 | 0 | 10.8 | 0 | 10.8 |  | 20-03-2026 08:10 | 71.24 | 72.047 | 36.3 | 12.0078 | 0 | 12.0078 | 0 | 10.7 | 0 | 10.7 |  | 20-03-2026 08:10 | 72.088 | 73.928 | 36.9 | 12.3213 | 0 | 12.3213 | 0 | 10.9 | 0 | 10.9 |  | 20-03-2026 08:10 | 68.375 | 69.163 | 34.8 | 11.5272 | 0 | 11.5272 | 0 | 10.4 | 0 | 10.4 |  | 20-03-2026 08:10 | 123.8575 | 0 | 123.8575 | 0 | 111 | 0 | 111
20-03-2026 08:00 |  |  | 78.188 | 79.026 | 34.7 | 13.171 | 0 | 13.171 | 0 | 11.8 | 0 | 11.8 |  | 20-03-2026 08:00 | 77.871 | 78.737 | 33.2 | 13.1228 | 0 | 13.1228 | 0 | 11.7 | 0 | 11.7 |  | 20-03-2026 08:00 | 77.069 | 77.918 | 34.2 | 12.9863 | 0 | 12.9863 | 0 | 11.6 | 0 | 11.6 |  | 20-03-2026 08:00 | 77.861 | 78.727 | 34.3 | 13.1212 | 0 | 13.1212 | 0 | 11.6 | 0 | 11.6 |  | 20-03-2026 08:00 | 56.636 | 57.434 | 24.9 | 9.5723 | 0 | 9.5723 | 0 | 8.4 | 0 | 8.4 |  | 20-03-2026 08:00 | 58.067 | 58.76 | 25.6 | 9.7933 | 0 | 9.7933 | 0 | 8.7 | 0 | 8.7 |  | 20-03-2026 08:00 | 57.901 | 58.616 | 25.6 | 9.7693 | 0 | 9.7693 | 0 | 8.8 | 0 | 8.8 |  | 20-03-2026 08:00 | 58.529 | 60.242 | 26 | 10.0403 | 0 | 10.0403 | 0 | 8.9 | 0 | 8.9 |  | 20-03-2026 08:00 | 55.484 | 56.175 | 24.4 | 9.3625 | 0 | 9.3625 | 0 | 8.3 | 0 | 8.3 |  | 20-03-2026 08:00 | 100.9392 | 0 | 100.9392 | 0 | 89.8 | 0 | 89.8
20-03-2026 07:50 |  |  | 63.85 | 64.58 | 22.9 | 10.7633 | 0 | 10.7633 | 0 | 9.3 | 0 | 9.3 |  | 20-03-2026 07:50 | 62.825 | 63.538 | 21.5 | 10.5897 | 0 | 10.5897 | 0 | 9.1 | 0 | 9.1 |  | 20-03-2026 07:50 | 62.996 | 63.735 | 22.6 | 10.6225 | 0 | 10.6225 | 0 | 9.2 | 0 | 9.2 |  | 20-03-2026 07:50 | 63.906 | 64.649 | 22.7 | 10.7748 | 0 | 10.7748 | 0 | 9.3 | 0 | 9.3 |  | 20-03-2026 07:50 | 46.457 | 47.098 | 16.5 | 7.8497 | 0 | 7.8497 | 0 | 6.8 | 0 | 6.8 |  | 20-03-2026 07:50 | 47.799 | 48.433 | 16.9 | 8.0722 | 0 | 8.0722 | 0 | 7 | 0 | 7 |  | 20-03-2026 07:50 | 47.418 | 48.067 | 16.8 | 8.0112 | 0 | 8.0112 | 0 | 6.9 | 0 | 6.9 |  | 20-03-2026 07:50 | 48.133 | 49.312 | 17.1 | 8.2187 | 0 | 8.2187 | 0 | 7 | 0 | 7 |  | 20-03-2026 07:50 | 45.667 | 46.297 | 16.1 | 7.7162 | 0 | 7.7162 | 0 | 6.7 | 0 | 6.7 |  | 20-03-2026 07:50 | 82.6182 | 0 | 82.6182 | 0 | 71.3 | 0 | 71.3
20-03-2026 07:40 |  |  | 47.939 | 48.514 | 13.6 | 8.0857 | 0 | 8.0857 | 0 | 6.9 | 0 | 6.9 |  | 20-03-2026 07:40 | 46.86 | 47.552 | 12.4 | 7.9253 | 0 | 7.9253 | 0 | 6.7 | 0 | 6.7 |  | 20-03-2026 07:40 | 47.102 | 47.737 | 13.4 | 7.9562 | 0 | 7.9562 | 0 | 6.7 | 0 | 6.7 |  | 20-03-2026 07:40 | 47.654 | 48.306 | 13.4 | 8.051 | 0 | 8.051 | 0 | 6.7 | 0 | 6.7 |  | 20-03-2026 07:40 | 34.719 | 35.255 | 9.7 | 5.8758 | 0 | 5.8758 | 0 | 4.9 | 0 | 4.9 |  | 20-03-2026 07:40 | 35.564 | 36.052 | 9.9 | 6.0087 | 0 | 6.0087 | 0 | 5 | 0 | 5 |  | 20-03-2026 07:40 | 35.462 | 35.987 | 9.9 | 5.9978 | 0 | 5.9978 | 0 | 5 | 0 | 5 |  | 20-03-2026 07:40 | 36.018 | 37.001 | 10.1 | 6.1668 | 0 | 6.1668 | 0 | 5.1 | 0 | 5.1 |  | 20-03-2026 07:40 | 34.101 | 34.627 | 9.4 | 5.7712 | 0 | 5.7712 | 0 | 4.8 | 0 | 4.8 |  | 20-03-2026 07:40 | 61.8385 | 0 | 61.8385 | 0 | 51.8 | 0 | 51.8
20-03-2026 07:30 |  |  | 33.581 | 34.099 | 6.7 | 5.6832 | 0 | 5.6832 | 0 | 4 | 0 | 4 |  | 20-03-2026 07:30 | 33.204 | 33.796 | 5.7 | 5.6327 | 0 | 5.6327 | 0 | 4.1 | 0 | 4.1 |  | 20-03-2026 07:30 | 33.097 | 33.625 | 6.7 | 5.6042 | 0 | 5.6042 | 0 | 4 | 0 | 4 |  | 20-03-2026 07:30 | 33.192 | 33.718 | 6.7 | 5.6197 | 0 | 5.6197 | 0 | 4 | 0 | 4 |  | 20-03-2026 07:30 | 24.371 | 24.925 | 4.8 | 4.1542 | 0 | 4.1542 | 0 | 2.9 | 0 | 2.9 |  | 20-03-2026 07:30 | 25.071 | 25.533 | 4.9 | 4.2555 | 0 | 4.2555 | 0 | 3 | 0 | 3 |  | 20-03-2026 07:30 | 25.101 | 25.572 | 4.9 | 4.262 | 0 | 4.262 | 0 | 3 | 0 | 3 |  | 20-03-2026 07:30 | 25.58 | 26.454 | 5 | 4.409 | 0 | 4.409 | 0 | 3 | 0 | 3 |  | 20-03-2026 07:30 | 23.568 | 24.029 | 4.6 | 4.0048 | 0 | 4.0048 | 0 | 2.8 | 0 | 2.8 |  | 20-03-2026 07:30 | 43.6252 | 0 | 43.6252 | 0 | 30.8 | 0 | 30.8
20-03-2026 07:20 |  |  | 16.434 | 16.826 | 2.7 | 2.8043 | 0 | 2.8043 | 0 | 1.9 | 0 | 1.9 |  | 20-03-2026 07:20 | 16.043 | 16.74 | 1.6 | 2.79 | 0 | 2.79 | 0 | 1.6 | 0 | 1.6 |  | 20-03-2026 07:20 | 16.404 | 16.802 | 2.7 | 2.8003 | 0 | 2.8003 | 0 | 1.9 | 0 | 1.9 |  | 20-03-2026 07:20 | 16.266 | 16.849 | 2.7 | 2.8082 | 0 | 2.8082 | 0 | 1.9 | 0 | 1.9 |  | 20-03-2026 07:20 | 11.94 | 12.562 | 1.9 | 2.0937 | 0 | 2.0937 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 07:20 | 12.198 | 12.567 | 1.9 | 2.0945 | 0 | 2.0945 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 07:20 | 12.25 | 12.625 | 1.9 | 2.1042 | 0 | 2.1042 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 07:20 | 12.505 | 13.14 | 2 | 2.19 | 0 | 2.19 | 0 | 1.4 | 0 | 1.4 |  | 20-03-2026 07:20 | 11.384 | 11.739 | 1.8 | 1.9565 | 0 | 1.9565 | 0 | 1.3 | 0 | 1.3 |  | 20-03-2026 07:20 | 21.6417 | 0 | 21.6417 | 0 | 14.2 | 0 | 14.2
20-03-2026 07:10 |  |  | 6.445 | 6.716 | 0.8 | 1.1193 | 0 | 1.1193 | 0 | 0.7 | 0 | 0.7 |  | 20-03-2026 07:10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:10 | 6.318 | 6.589 | 0.8 | 1.0982 | 0 | 1.0982 | 0 | 0.7 | 0 | 0.7 |  | 20-03-2026 07:10 | 6.361 | 7.14 | 0.8 | 1.19 | 0 | 1.19 | 0 | 0.7 | 0 | 0.7 |  | 20-03-2026 07:10 | 4.581 | 5.248 | 0.5 | 0.87467 | 0 | 0.87467 | 0 | 0.5 | 0 | 0.5 |  | 20-03-2026 07:10 | 4.582 | 4.792 | 0.5 | 0.79867 | 0 | 0.79867 | 0 | 0.5 | 0 | 0.5 |  | 20-03-2026 07:10 | 4.586 | 4.772 | 0.5 | 0.79533 | 0 | 0.79533 | 0 | 0.5 | 0 | 0.5 |  | 20-03-2026 07:10 | 4.675 | 4.902 | 0.6 | 0.817 | 0 | 0.817 | 0 | 0.6 | 0 | 0.6 |  | 20-03-2026 07:10 | 4.335 | 4.534 | 0.5 | 0.75567 | 0 | 0.75567 | 0 | 0.5 | 0 | 0.5 |  | 20-03-2026 07:10 | 7.4488 | 0 | 7.4488 | 0 | 4.7 | 0 | 4.7
20-03-2026 07:00 |  |  | 3.172 | 3.354 | 0.1 | 0.559 | 0 | 0.559 | 0 | 0.1 | 0 | 0.1 |  | 20-03-2026 07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 3.153 | 3.31 | 0.1 | 0.55167 | 0 | 0.55167 | 0 | 0.1 | 0 | 0.1 |  | 20-03-2026 07:00 | 3.132 | 3.873 | 0.1 | 0.6455 | 0 | 0.6455 | 0 | 0.1 | 0 | 0.1 |  | 20-03-2026 07:00 | 2.202 | 2.846 | 0 | 0.47433 | 0 | 0.47433 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 2.189 | 2.301 | 0 | 0.3835 | 0 | 0.3835 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 2.226 | 2.34 | 0 | 0.39 | 0 | 0.39 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 2.299 | 2.679 | 0 | 0.4465 | 0 | 0.4465 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 2.016 | 2.12 | 0 | 0.35333 | 0 | 0.35333 | 0 | 0 | 0 | 0 |  | 20-03-2026 07:00 | 3.8038 | 0 | 3.8038 | 0 | 0.3 | 0 | 0.3
[110 empty] | Total: - | 19601.6347 | #VALUE! | #VALUE! |  | 19258.6 | #VALUE! | #VALUE!
|  |  | 15077.889 |  | 94672 |  |  |  |  | 2490.2 | #VALUE! | #VALUE! | 0.98505 |  | 14747.347 |  | 95445.4 |  |  |  |  | 2514.6 | #VALUE! | #VALUE! | 0.98328 |  | 14912.776 |  | 94058.8 |  |  |  |  | 2476.5 | #VALUE! | #VALUE! | 0.9744 |  | 15001.455 |  | 95259.5 |  |  |  |  | 2506.5 | #VALUE! | #VALUE! | 0.98631 |  | 11316.416 |  | 71171.9 |  |  |  |  | 1876.9 | #VALUE! | #VALUE! | 0.9847 |  | 11206.4 |  | 71099 |  |  |  |  | 1870 | #VALUE! | #VALUE! | 0.98251 |  | 11259.915 |  | 70900.4 |  |  |  |  | 1864.8 | #VALUE! | #VALUE! | 0.9812 |  | 11300.932 |  | 71443.6 |  |  |  |  | 1877 | #VALUE! | #VALUE! | 0.97092 |  | 10698.575 |  | 67809.5 |  |  |  |  | 1782.1 | #VALUE! | #VALUE! | 0.98498

## 21 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inverter No. | Efficiency
21-03-2026 19:00 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace |  | 0.054 | 0.087 | 2096.1 | 0.0145 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.072 | 0.172 | 2116.5 | 0.028667 | #VALUE! | #VALUE! | #VALUE! | 0.1 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.069 | 0.094 | 2084.2 | 0.015667 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.075 | 0.23 | 2100.7 | 0.038333 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.098 | 0.103 | 1571.8 | 0.017167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.08 | 0.102 | 1560.7 | 0.017 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.069 | 0.098 | 1558.4 | 0.016333 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.06 | 0.169 | 1566.6 | 0.028167 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.067 | 0.07 | 1483 | 0.011667 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! |  | 21-03-2026 19:00 | 0.1875 | #VALUE! | #VALUE! | #VALUE! | 0.1 | #VALUE! | #VALUE! | 1 | 97.83%
21-03-2026 18:50 |  |  | 0.443 | 0.466 | 2096.1 | 0.077667 | 0 | 0.077667 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:50 | 0.567 | 1.155 | 2116.4 | 0.1925 | 0 | 0.1925 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:50 | 0.453 | 0.476 | 2084.2 | 0.079333 | 0 | 0.079333 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:50 | 0.463 | 1.032 | 2100.6 | 0.172 | 0 | 0.172 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:50 | 0.204 | 0.444 | 1571.8 | 0.074 | 0 | 0.074 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 18:50 | 0.174 | 0.183 | 1560.7 | 0.0305 | 0 | 0.0305 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 18:50 | 0.073 | 0.09 | 1558.4 | 0.015 | 0 | 0.015 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 18:50 | 0.306 | 0.722 | 1566.6 | 0.12033 | 0 | 0.12033 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:50 | 0.147 | 0.155 | 1483 | 0.025833 | 0 | 0.025833 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 18:50 | 0.78717 | 0 | 0.78717 | 0 | 2.3 | 0 | 2.3 | 2 | 98.59%
21-03-2026 18:40 |  |  | 2.945 | 3.096 | 2095.8 | 0.516 | 0 | 0.516 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:40 | 3.185 | 3.713 | 2116.1 | 0.61883 | 0 | 0.61883 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:40 | 2.94 | 3.094 | 2083.9 | 0.51567 | 0 | 0.51567 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:40 | 3.03 | 3.425 | 2100.3 | 0.57083 | 0 | 0.57083 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:40 | 2.039 | 2.194 | 1571.6 | 0.36567 | 0 | 0.36567 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:40 | 2.033 | 2.138 | 1560.5 | 0.35633 | 0 | 0.35633 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:40 | 1.989 | 2.091 | 1558.2 | 0.3485 | 0 | 0.3485 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:40 | 2.151 | 2.411 | 1566.3 | 0.40183 | 0 | 0.40183 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:40 | 1.949 | 2.049 | 1482.8 | 0.3415 | 0 | 0.3415 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 18:40 | 4.0352 | 0 | 4.0352 | 0 | 5.2 | 0 | 5.2 | 3 | 97.58%
21-03-2026 18:30 |  |  | 3.929 | 4.108 | 2095.1 | 0.68467 | 0 | 0.68467 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:30 | 4.372 | 4.628 | 2115.4 | 0.77133 | 0 | 0.77133 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:30 | 4.207 | 4.421 | 2083.2 | 0.73683 | 0 | 0.73683 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:30 | 4.316 | 4.821 | 2099.6 | 0.8035 | 0 | 0.8035 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:30 | 2.986 | 3.162 | 1571.1 | 0.527 | 0 | 0.527 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 18:30 | 2.944 | 3.095 | 1560 | 0.51583 | 0 | 0.51583 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:30 | 2.957 | 3.109 | 1557.7 | 0.51817 | 0 | 0.51817 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:30 | 3.08 | 3.536 | 1565.8 | 0.58933 | 0 | 0.58933 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 18:30 | 2.804 | 2.948 | 1482.4 | 0.49133 | 0 | 0.49133 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 18:30 | 5.638 | 0 | 5.638 | 0 | 3.7 | 0 | 3.7 | 4 | 98.47%
21-03-2026 18:20 |  |  | 3.889 | 4.086 | 2094.6 | 0.681 | 0 | 0.681 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:20 | 4.106 | 4.625 | 2114.9 | 0.77083 | 0 | 0.77083 | 0 | 0.8 | 0 | 0.8 |  | 21-03-2026 18:20 | 3.913 | 4.114 | 2082.7 | 0.68567 | 0 | 0.68567 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:20 | 3.972 | 4.307 | 2099.1 | 0.71783 | 0 | 0.71783 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 18:20 | 2.797 | 2.941 | 1570.7 | 0.49017 | 0 | 0.49017 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:20 | 2.74 | 2.831 | 1559.7 | 0.47183 | 0 | 0.47183 | 0 | 0.5 | 0 | 0.5 |  | 21-03-2026 18:20 | 2.732 | 2.872 | 1557.4 | 0.47867 | 0 | 0.47867 | 0 | 0.6 | 0 | 0.6 |  | 21-03-2026 18:20 | 2.845 | 3.195 | 1565.5 | 0.5325 | 0 | 0.5325 | 0 | 0.6 | 0 | 0.6 |  | 21-03-2026 18:20 | 2.6 | 2.734 | 1482 | 0.45567 | 0 | 0.45567 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 18:20 | 5.2842 | 0 | 5.2842 | 0 | 5.5 | 0 | 5.5 | 5 | 98.58%
21-03-2026 18:10 |  |  | 6.027 | 6.308 | 2093.9 | 1.0513 | 0 | 1.0513 | 0 | 1.2 | 0 | 1.2 |  | 21-03-2026 18:10 | 6.598 | 6.992 | 2114.1 | 1.1653 | 0 | 1.1653 | 0 | 1.3 | 0 | 1.3 |  | 21-03-2026 18:10 | 5.987 | 6.268 | 2082 | 1.0447 | 0 | 1.0447 | 0 | 1.2 | 0 | 1.2 |  | 21-03-2026 18:10 | 6.041 | 6.381 | 2098.4 | 1.0635 | 0 | 1.0635 | 0 | 1.3 | 0 | 1.3 |  | 21-03-2026 18:10 | 4.329 | 4.609 | 1570.2 | 0.76817 | 0 | 0.76817 | 0 | 0.9 | 0 | 0.9 |  | 21-03-2026 18:10 | 4.284 | 4.498 | 1559.2 | 0.74967 | 0 | 0.74967 | 0 | 0.9 | 0 | 0.9 |  | 21-03-2026 18:10 | 4.154 | 4.365 | 1556.8 | 0.7275 | 0 | 0.7275 | 0 | 0.8 | 0 | 0.8 |  | 21-03-2026 18:10 | 4.4 | 4.84 | 1564.9 | 0.80667 | 0 | 0.80667 | 0 | 0.9 | 0 | 0.9 |  | 21-03-2026 18:10 | 4.092 | 4.306 | 1481.6 | 0.71767 | 0 | 0.71767 | 0 | 0.9 | 0 | 0.9 |  | 21-03-2026 18:10 | 8.0945 | 0 | 8.0945 | 0 | 9.4 | 0 | 9.4 | 6 | 98.39%
21-03-2026 18:00 |  |  | 9.226 | 9.599 | 2092.7 | 1.5998 | 0 | 1.5998 | 0 | 1.9 | 0 | 1.9 |  | 21-03-2026 18:00 | 9.321 | 9.827 | 2112.8 | 1.6378 | 0 | 1.6378 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 18:00 | 9.01 | 9.418 | 2080.8 | 1.5697 | 0 | 1.5697 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 18:00 | 9.163 | 9.537 | 2097.1 | 1.5895 | 0 | 1.5895 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 18:00 | 6.61 | 6.906 | 1569.3 | 1.151 | 0 | 1.151 | 0 | 1.3 | 0 | 1.3 |  | 21-03-2026 18:00 | 6.582 | 6.88 | 1558.3 | 1.1467 | 0 | 1.1467 | 0 | 1.3 | 0 | 1.3 |  | 21-03-2026 18:00 | 6.578 | 6.87 | 1556 | 1.145 | 0 | 1.145 | 0 | 1.4 | 0 | 1.4 |  | 21-03-2026 18:00 | 6.695 | 7.117 | 1564 | 1.1862 | 0 | 1.1862 | 0 | 1.3 | 0 | 1.3 |  | 21-03-2026 18:00 | 6.203 | 6.489 | 1480.7 | 1.0815 | 0 | 1.0815 | 0 | 1.2 | 0 | 1.2 |  | 21-03-2026 18:00 | 12.1072 | 0 | 12.1072 | 0 | 13.8 | 0 | 13.8 | 7 | 98.33%
21-03-2026 17:50 |  |  | 11.438 | 11.848 | 2090.8 | 1.9747 | 0 | 1.9747 | 0 | 2.3 | 0 | 2.3 |  | 21-03-2026 17:50 | 11.643 | 12.104 | 2111 | 2.0173 | 0 | 2.0173 | 0 | 2.5 | 0 | 2.5 |  | 21-03-2026 17:50 | 11.338 | 11.735 | 2079 | 1.9558 | 0 | 1.9558 | 0 | 2.4 | 0 | 2.4 |  | 21-03-2026 17:50 | 11.489 | 11.911 | 2095.3 | 1.9852 | 0 | 1.9852 | 0 | 2.4 | 0 | 2.4 |  | 21-03-2026 17:50 | 8.254 | 8.599 | 1568 | 1.4332 | 0 | 1.4332 | 0 | 1.7 | 0 | 1.7 |  | 21-03-2026 17:50 | 8.292 | 8.635 | 1557 | 1.4392 | 0 | 1.4392 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 17:50 | 8.228 | 8.572 | 1554.6 | 1.4287 | 0 | 1.4287 | 0 | 1.7 | 0 | 1.7 |  | 21-03-2026 17:50 | 8.426 | 8.833 | 1562.7 | 1.4722 | 0 | 1.4722 | 0 | 1.7 | 0 | 1.7 |  | 21-03-2026 17:50 | 7.839 | 8.173 | 1479.5 | 1.3622 | 0 | 1.3622 | 0 | 1.7 | 0 | 1.7 |  | 21-03-2026 17:50 | 15.0683 | 0 | 15.0683 | 0 | 18.2 | 0 | 18.2 | 8 | 97.04%
21-03-2026 17:40 |  |  | 17.794 | 18.26 | 2088.5 | 3.0433 | 0 | 3.0433 | 0 | 3.2 | 0 | 3.2 |  | 21-03-2026 17:40 | 18.054 | 18.538 | 2108.5 | 3.0897 | 0 | 3.0897 | 0 | 3.3 | 0 | 3.3 |  | 21-03-2026 17:40 | 17.71 | 18.188 | 2076.6 | 3.0313 | 0 | 3.0313 | 0 | 3.2 | 0 | 3.2 |  | 21-03-2026 17:40 | 17.866 | 18.347 | 2092.9 | 3.0578 | 0 | 3.0578 | 0 | 3.2 | 0 | 3.2 |  | 21-03-2026 17:40 | 12.963 | 13.389 | 1566.3 | 2.2315 | 0 | 2.2315 | 0 | 2.4 | 0 | 2.4 |  | 21-03-2026 17:40 | 12.918 | 13.326 | 1555.2 | 2.221 | 0 | 2.221 | 0 | 2.3 | 0 | 2.3 |  | 21-03-2026 17:40 | 12.907 | 13.328 | 1552.9 | 2.2213 | 0 | 2.2213 | 0 | 2.3 | 0 | 2.3 |  | 21-03-2026 17:40 | 13.058 | 13.716 | 1561 | 2.286 | 0 | 2.286 | 0 | 2.4 | 0 | 2.4 |  | 21-03-2026 17:40 | 12.234 | 12.658 | 1477.8 | 2.1097 | 0 | 2.1097 | 0 | 2.1 | 0 | 2.1 |  | 21-03-2026 17:40 | 23.2917 | 0 | 23.2917 | 0 | 24.4 | 0 | 24.4 | 9 | 98.57%
21-03-2026 17:30 |  |  | 20.954 | 21.474 | 2085.3 | 3.579 | 0 | 3.579 | 0 | 4.1 | 0 | 4.1 |  | 21-03-2026 17:30 | 22.644 | 23.194 | 2105.2 | 3.8657 | 0 | 3.8657 | 0 | 4 | 0 | 4 |  | 21-03-2026 17:30 | 20.956 | 21.478 | 2073.4 | 3.5797 | 0 | 3.5797 | 0 | 4 | 0 | 4 |  | 21-03-2026 17:30 | 21.129 | 21.674 | 2089.7 | 3.6123 | 0 | 3.6123 | 0 | 4 | 0 | 4 |  | 21-03-2026 17:30 | 15.39 | 15.817 | 1563.9 | 2.6362 | 0 | 2.6362 | 0 | 2.9 | 0 | 2.9 |  | 21-03-2026 17:30 | 15.312 | 15.735 | 1552.9 | 2.6225 | 0 | 2.6225 | 0 | 2.9 | 0 | 2.9 |  | 21-03-2026 17:30 | 15.257 | 15.684 | 1550.6 | 2.614 | 0 | 2.614 | 0 | 2.9 | 0 | 2.9 |  | 21-03-2026 17:30 | 15.29 | 16.043 | 1558.6 | 2.6738 | 0 | 2.6738 | 0 | 2.9 | 0 | 2.9 |  | 21-03-2026 17:30 | 14.475 | 14.933 | 1475.7 | 2.4888 | 0 | 2.4888 | 0 | 2.8 | 0 | 2.8 |  | 21-03-2026 17:30 | 27.672 | 0 | 27.672 | 0 | 30.5 | 0 | 30.5
21-03-2026 17:20 |  |  | 25.708 | 26.278 | 2081.2 | 4.3797 | 0 | 4.3797 | 0 | 4.7 | 0 | 4.7 |  | 21-03-2026 17:20 | 25.204 | 26.425 | 2101.2 | 4.4042 | 0 | 4.4042 | 0 | 4.7 | 0 | 4.7 |  | 21-03-2026 17:20 | 25.523 | 26.102 | 2069.4 | 4.3503 | 0 | 4.3503 | 0 | 4.5 | 0 | 4.5 |  | 21-03-2026 17:20 | 25.732 | 26.314 | 2085.7 | 4.3857 | 0 | 4.3857 | 0 | 4.7 | 0 | 4.7 |  | 21-03-2026 17:20 | 18.823 | 19.304 | 1561 | 3.2173 | 0 | 3.2173 | 0 | 3.4 | 0 | 3.4 |  | 21-03-2026 17:20 | 18.745 | 19.228 | 1550 | 3.2047 | 0 | 3.2047 | 0 | 3.4 | 0 | 3.4 |  | 21-03-2026 17:20 | 18.648 | 19.126 | 1547.7 | 3.1877 | 0 | 3.1877 | 0 | 3.4 | 0 | 3.4 |  | 21-03-2026 17:20 | 18.721 | 19.363 | 1555.7 | 3.2272 | 0 | 3.2272 | 0 | 3.4 | 0 | 3.4 |  | 21-03-2026 17:20 | 17.654 | 18.123 | 1472.9 | 3.0205 | 0 | 3.0205 | 0 | 3.2 | 0 | 3.2 |  | 21-03-2026 17:20 | 33.3772 | 0 | 33.3772 | 0 | 35.4 | 0 | 35.4
21-03-2026 17:10 |  |  | 26.044 | 27.901 | 2076.5 | 4.6502 | 0 | 4.6502 | 0 | 5.8 | 0 | 5.8 |  | 21-03-2026 17:10 | 27.686 | 28.289 | 2096.5 | 4.7148 | 0 | 4.7148 | 0 | 5.9 | 0 | 5.9 |  | 21-03-2026 17:10 | 27.606 | 28.204 | 2064.9 | 4.7007 | 0 | 4.7007 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 17:10 | 27.485 | 28.086 | 2081 | 4.681 | 0 | 4.681 | 0 | 6 | 0 | 6 |  | 21-03-2026 17:10 | 20.317 | 20.829 | 1557.6 | 3.4715 | 0 | 3.4715 | 0 | 4.4 | 0 | 4.4 |  | 21-03-2026 17:10 | 20.094 | 20.58 | 1546.6 | 3.43 | 0 | 3.43 | 0 | 4.4 | 0 | 4.4 |  | 21-03-2026 17:10 | 20.155 | 20.663 | 1544.3 | 3.4438 | 0 | 3.4438 | 0 | 4.3 | 0 | 4.3 |  | 21-03-2026 17:10 | 20.267 | 21.249 | 1552.3 | 3.5415 | 0 | 3.5415 | 0 | 4.3 | 0 | 4.3 |  | 21-03-2026 17:10 | 18.947 | 19.439 | 1469.7 | 3.2398 | 0 | 3.2398 | 0 | 4.1 | 0 | 4.1 |  | 21-03-2026 17:10 | 35.8733 | 0 | 35.8733 | 0 | 45.3 | 0 | 45.3
21-03-2026 17:00 |  |  | 57.475 | 58.354 | 2070.7 | 9.7257 | 0 | 9.7257 | 0 | 8.4 | 0 | 8.4 |  | 21-03-2026 17:00 | 57.895 | 58.819 | 2090.6 | 9.8032 | 0 | 9.8032 | 0 | 8.5 | 0 | 8.5 |  | 21-03-2026 17:00 | 57.207 | 58.087 | 2058.8 | 9.6812 | 0 | 9.6812 | 0 | 8.1 | 0 | 8.1 |  | 21-03-2026 17:00 | 57.517 | 58.399 | 2075 | 9.7332 | 0 | 9.7332 | 0 | 8.2 | 0 | 8.2 |  | 21-03-2026 17:00 | 42.593 | 43.325 | 1553.2 | 7.2208 | 0 | 7.2208 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 17:00 | 42.281 | 43.003 | 1542.2 | 7.1672 | 0 | 7.1672 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 17:00 | 42.095 | 42.832 | 1540 | 7.1387 | 0 | 7.1387 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 17:00 | 42.285 | 43.625 | 1548 | 7.2708 | 0 | 7.2708 | 0 | 6.2 | 0 | 6.2 |  | 21-03-2026 17:00 | 39.885 | 40.578 | 1465.6 | 6.763 | 0 | 6.763 | 0 | 6 | 0 | 6 |  | 21-03-2026 17:00 | 74.5037 | 0 | 74.5037 | 0 | 63.7 | 0 | 63.7
21-03-2026 16:50 |  |  | 65.048 | 61.342 | 2062.3 | 10.2237 | 0 | 10.2237 | 0 | 28.6 | 0 | 28.6 |  | 21-03-2026 16:50 | 60.968 | 61.852 | 2082.1 | 10.3087 | 0 | 10.3087 | 0 | 28.8 | 0 | 28.8 |  | 21-03-2026 16:50 | 59.689 | 60.616 | 2050.7 | 10.1027 | 0 | 10.1027 | 0 | 13.4 | 0 | 13.4 |  | 21-03-2026 16:50 | 60.262 | 61.155 | 2066.8 | 10.1925 | 0 | 10.1925 | 0 | 13.6 | 0 | 13.6 |  | 21-03-2026 16:50 | 44.088 | 44.85 | 1547.1 | 7.475 | 0 | 7.475 | 0 | 10 | 0 | 10 |  | 21-03-2026 16:50 | 44.798 | 45.677 | 1536.1 | 7.6128 | 0 | 7.6128 | 0 | 9.9 | 0 | 9.9 |  | 21-03-2026 16:50 | 44.364 | 45.117 | 1533.9 | 7.5195 | 0 | 7.5195 | 0 | 9.8 | 0 | 9.8 |  | 21-03-2026 16:50 | 44.552 | 45.819 | 1541.8 | 7.6365 | 0 | 7.6365 | 0 | 9.8 | 0 | 9.8 |  | 21-03-2026 16:50 | 43.691 | 44.451 | 1459.6 | 7.4085 | 0 | 7.4085 | 0 | 9.2 | 0 | 9.2 |  | 21-03-2026 16:50 | 78.4798 | 0 | 78.4798 | 0 | 133.1 | 0 | 133.1
21-03-2026 16:40 |  |  | 73.952 | 74.949 | 2048.7 | 12.4915 | 0 | 12.4915 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21-03-2026 16:40 | 73.105 | 74.128 | 2037.3 | 12.3547 | 0 | 12.3547 | 0 | 15 | 0 | 15 |  | 21-03-2026 16:40 | 73.65 | 74.673 | 2053.2 | 12.4455 | 0 | 12.4455 | 0 | 15 | 0 | 15 |  | 21-03-2026 16:40 | 54.261 | 55.121 | 1537.1 | 9.1868 | 0 | 9.1868 | 0 | 11.1 | 0 | 11.1 |  | 21-03-2026 16:40 | 53.994 | 54.844 | 1526.2 | 9.1407 | 0 | 9.1407 | 0 | 11 | 0 | 11 |  | 21-03-2026 16:40 | 53.625 | 54.475 | 1524.1 | 9.0792 | 0 | 9.0792 | 0 | 11 | 0 | 11 |  | 21-03-2026 16:40 | 53.104 | 54.77 | 1532 | 9.1283 | 0 | 9.1283 | 0 | 11.2 | 0 | 11.2 |  | 21-03-2026 16:40 | 51.327 | 52.167 | 1450.4 | 8.6945 | 0 | 8.6945 | 0 | 10.4 | 0 | 10.4 |  | 21-03-2026 16:40 | 82.5212 | 0 | 82.5212 | 0 | 84.7 | 0 | 84.7
21-03-2026 16:30 |  |  | 82.861 | 86.181 | 2033.7 | 14.3635 | 0 | 14.3635 | 0 | 16.2 | 0 | 16.2 |  | 21-03-2026 16:30 | 85.861 | 87.027 | 2053.3 | 14.5045 | 0 | 14.5045 | 0 | 15.7 | 0 | 15.7 |  | 21-03-2026 16:30 | 84.617 | 86.237 | 2022.3 | 14.3728 | 0 | 14.3728 | 0 | 15.7 | 0 | 15.7 |  | 21-03-2026 16:30 | 85.282 | 86.432 | 2038.2 | 14.4053 | 0 | 14.4053 | 0 | 15.7 | 0 | 15.7 |  | 21-03-2026 16:30 | 63.202 | 64.106 | 1526 | 10.6843 | 0 | 10.6843 | 0 | 11.7 | 0 | 11.7 |  | 21-03-2026 16:30 | 62.888 | 63.787 | 1515.2 | 10.6312 | 0 | 10.6312 | 0 | 11.6 | 0 | 11.6 |  | 21-03-2026 16:30 | 62.521 | 63.409 | 1513.1 | 10.5682 | 0 | 10.5682 | 0 | 11.5 | 0 | 11.5 |  | 21-03-2026 16:30 | 62.684 | 64.496 | 1520.8 | 10.7493 | 0 | 10.7493 | 0 | 11.4 | 0 | 11.4 |  | 21-03-2026 16:30 | 59.216 | 60.118 | 1440 | 10.0197 | 0 | 10.0197 | 0 | 10.8 | 0 | 10.8 |  | 21-03-2026 16:30 | 110.2988 | 0 | 110.2988 | 0 | 120.3 | 0 | 120.3
21-03-2026 16:20 |  |  | 105.838 | 107.167 | 2017.5 | 17.8612 | 0 | 17.8612 | 0 | 15.4 | 0 | 15.4 |  | 21-03-2026 16:20 | 107.05 | 108.438 | 2037.6 | 18.073 | 0 | 18.073 | 0 | 16.4 | 0 | 16.4 |  | 21-03-2026 16:20 | 105.949 | 107.736 | 2006.6 | 17.956 | 0 | 17.956 | 0 | 15.7 | 0 | 15.7 |  | 21-03-2026 16:20 | 106.074 | 107.449 | 2022.5 | 17.9082 | 0 | 17.9082 | 0 | 15.9 | 0 | 15.9 |  | 21-03-2026 16:20 | 79.216 | 80.284 | 1514.3 | 13.3807 | 0 | 13.3807 | 0 | 11.7 | 0 | 11.7 |  | 21-03-2026 16:20 | 78.162 | 79.216 | 1503.6 | 13.2027 | 0 | 13.2027 | 0 | 11.8 | 0 | 11.8 |  | 21-03-2026 16:20 | 78.249 | 79.304 | 1501.6 | 13.2173 | 0 | 13.2173 | 0 | 11.7 | 0 | 11.7 |  | 21-03-2026 16:20 | 78.57 | 80.905 | 1509.4 | 13.4842 | 0 | 13.4842 | 0 | 11.7 | 0 | 11.7 |  | 21-03-2026 16:20 | 74.027 | 75.048 | 1429.2 | 12.508 | 0 | 12.508 | 0 | 11.2 | 0 | 11.2 |  | 21-03-2026 16:20 | 137.5912 | 0 | 137.5912 | 0 | 121.5 | 0 | 121.5
21-03-2026 16:10 |  |  | 87.759 | 88.978 | 2002.1 | 14.8297 | 0 | 14.8297 | 0 | 33.5 | 0 | 33.5 |  | 21-03-2026 16:10 | 0 | 0 | 2021.2 | 0 | 0 | 0 | 0 | 34.9 | 0 | 34.9 |  | 21-03-2026 16:10 | 96.659 | 99.356 | 1990.9 | 16.5593 | 0 | 16.5593 | 0 | 33.2 | 0 | 33.2 |  | 21-03-2026 16:10 | 101.733 | 102.353 | 2006.6 | 17.0588 | 0 | 17.0588 | 0 | 33.5 | 0 | 33.5 |  | 21-03-2026 16:10 | 71.865 | 80.765 | 1502.6 | 13.4608 | 0 | 13.4608 | 0 | 24.9 | 0 | 24.9 |  | 21-03-2026 16:10 | 75.784 | 76.852 | 1491.8 | 12.8087 | 0 | 12.8087 | 0 | 24.5 | 0 | 24.5 |  | 21-03-2026 16:10 | 75.769 | 77.421 | 1489.9 | 12.9035 | 0 | 12.9035 | 0 | 24.4 | 0 | 24.4 |  | 21-03-2026 16:10 | 83.853 | 86.679 | 1497.7 | 14.4465 | 0 | 14.4465 | 0 | 24.6 | 0 | 24.6 |  | 21-03-2026 16:10 | 77.674 | 78.825 | 1418 | 13.1375 | 0 | 13.1375 | 0 | 23.4 | 0 | 23.4 |  | 21-03-2026 16:10 | 115.2048 | 0 | 115.2048 | 0 | 256.9 | 0 | 256.9
21-03-2026 16:00 |  |  | 206.764 | 209.657 | 1968.6 | 34.9428 | 0 | 34.9428 | 0 | 39.3 | 0 | 39.3 |  | 21-03-2026 16:00 | 168.374 | 174.402 | 1986.3 | 29.067 | 0 | 29.067 | 0 | 39.1 | 0 | 39.1 |  | 21-03-2026 16:00 | 215.843 | 221.781 | 1957.7 | 36.9635 | 0 | 36.9635 | 0 | 39.8 | 0 | 39.8 |  | 21-03-2026 16:00 | 217.689 | 220.847 | 1973.1 | 36.8078 | 0 | 36.8078 | 0 | 40.1 | 0 | 40.1 |  | 21-03-2026 16:00 | 165.654 | 167.921 | 1477.7 | 27.9868 | 0 | 27.9868 | 0 | 29.9 | 0 | 29.9 |  | 21-03-2026 16:00 | 163.633 | 166.131 | 1467.3 | 27.6885 | 0 | 27.6885 | 0 | 29.6 | 0 | 29.6 |  | 21-03-2026 16:00 | 164.323 | 166.673 | 1465.5 | 27.7788 | 0 | 27.7788 | 0 | 29.5 | 0 | 29.5 |  | 21-03-2026 16:00 | 165.209 | 169.689 | 1473.1 | 28.2815 | 0 | 28.2815 | 0 | 29.6 | 0 | 29.6 |  | 21-03-2026 16:00 | 156.713 | 158.858 | 1394.6 | 26.4763 | 0 | 26.4763 | 0 | 28.5 | 0 | 28.5 |  | 21-03-2026 16:00 | 275.9932 | 0 | 275.9932 | 0 | 305.4 | 0 | 305.4
21-03-2026 15:50 |  |  | 280.968 | 285.218 | 1929.3 | 47.5363 | 0 | 47.5363 | 0 | 34.3 | 0 | 34.3 |  | 21-03-2026 15:50 | 280.992 | 285.3 | 1947.2 | 47.55 | 0 | 47.55 | 0 | 33.9 | 0 | 33.9 |  | 21-03-2026 15:50 | 280.301 | 287.339 | 1917.9 | 47.8898 | 0 | 47.8898 | 0 | 33.6 | 0 | 33.6 |  | 21-03-2026 15:50 | 281.395 | 285.738 | 1933 | 47.623 | 0 | 47.623 | 0 | 33.8 | 0 | 33.8 |  | 21-03-2026 15:50 | 210.108 | 213.005 | 1447.8 | 35.5008 | 0 | 35.5008 | 0 | 25.4 | 0 | 25.4 |  | 21-03-2026 15:50 | 206.858 | 209.876 | 1437.7 | 34.9793 | 0 | 34.9793 | 0 | 25 | 0 | 25 |  | 21-03-2026 15:50 | 206.603 | 209.994 | 1436 | 34.999 | 0 | 34.999 | 0 | 25.1 | 0 | 25.1 |  | 21-03-2026 15:50 | 206.832 | 212.846 | 1443.5 | 35.4743 | 0 | 35.4743 | 0 | 25.2 | 0 | 25.2 |  | 21-03-2026 15:50 | 196.326 | 199.033 | 1366.1 | 33.1722 | 0 | 33.1722 | 0 | 23.3 | 0 | 23.3 |  | 21-03-2026 15:50 | 364.7248 | 0 | 364.7248 | 0 | 259.6 | 0 | 259.6
21-03-2026 15:40 |  |  | 149.217 | 151.152 | 1895 | 25.192 | 0 | 25.192 | 0 | 23.6 | 0 | 23.6 |  | 21-03-2026 15:40 | 150.352 | 152.363 | 1913.3 | 25.3938 | 0 | 25.3938 | 0 | 24.3 | 0 | 24.3 |  | 21-03-2026 15:40 | 147.406 | 150.247 | 1884.3 | 25.0412 | 0 | 25.0412 | 0 | 23.4 | 0 | 23.4 |  | 21-03-2026 15:40 | 148.657 | 150.646 | 1899.2 | 25.1077 | 0 | 25.1077 | 0 | 23.5 | 0 | 23.5 |  | 21-03-2026 15:40 | 109.125 | 110.529 | 1422.4 | 18.4215 | 0 | 18.4215 | 0 | 17.5 | 0 | 17.5 |  | 21-03-2026 15:40 | 107.978 | 109.367 | 1412.7 | 18.2278 | 0 | 18.2278 | 0 | 17.2 | 0 | 17.2 |  | 21-03-2026 15:40 | 106.159 | 107.514 | 1410.9 | 17.919 | 0 | 17.919 | 0 | 17.6 | 0 | 17.6 |  | 21-03-2026 15:40 | 105.609 | 108.81 | 1418.3 | 18.135 | 0 | 18.135 | 0 | 17.6 | 0 | 17.6 |  | 21-03-2026 15:40 | 103.677 | 105.021 | 1342.8 | 17.5035 | 0 | 17.5035 | 0 | 16.7 | 0 | 16.7 |  | 21-03-2026 15:40 | 190.9415 | 0 | 190.9415 | 0 | 181.4 | 0 | 181.4
21-03-2026 15:30 |  |  | 228.528 | 231.82 | 1871.4 | 38.6367 | 0 | 38.6367 | 0 | 39.5 | 0 | 39.5 |  | 21-03-2026 15:30 | 256.027 | 259.926 | 1889 | 43.321 | 0 | 43.321 | 0 | 40.2 | 0 | 40.2 |  | 21-03-2026 15:30 | 223.344 | 227.33 | 1860.9 | 37.8883 | 0 | 37.8883 | 0 | 39.6 | 0 | 39.6 |  | 21-03-2026 15:30 | 225.956 | 229.257 | 1875.7 | 38.2095 | 0 | 38.2095 | 0 | 39.7 | 0 | 39.7 |  | 21-03-2026 15:30 | 165.445 | 167.709 | 1404.9 | 27.9515 | 0 | 27.9515 | 0 | 29.6 | 0 | 29.6 |  | 21-03-2026 15:30 | 164.998 | 167.222 | 1395.5 | 27.8703 | 0 | 27.8703 | 0 | 29.1 | 0 | 29.1 |  | 21-03-2026 15:30 | 166.787 | 169.515 | 1393.3 | 28.2525 | 0 | 28.2525 | 0 | 29 | 0 | 29 |  | 21-03-2026 15:30 | 167.762 | 172.833 | 1400.7 | 28.8055 | 0 | 28.8055 | 0 | 28.9 | 0 | 28.9 |  | 21-03-2026 15:30 | 158.613 | 160.784 | 1326.1 | 26.7973 | 0 | 26.7973 | 0 | 27.4 | 0 | 27.4 |  | 21-03-2026 15:30 | 297.7327 | 0 | 297.7327 | 0 | 303 | 0 | 303
21-03-2026 15:20 |  |  | 177.532 | 211.725 | 1831.9 | 35.2875 | 0 | 35.2875 | 0 | 24.8 | 0 | 24.8 |  | 21-03-2026 15:20 | 204.853 | 208.622 | 1848.8 | 34.7703 | 0 | 34.7703 | 0 | 26.5 | 0 | 26.5 |  | 21-03-2026 15:20 | 239.345 | 244.836 | 1821.3 | 40.806 | 0 | 40.806 | 0 | 25.2 | 0 | 25.2 |  | 21-03-2026 15:20 | 233.597 | 236.962 | 1836 | 39.4937 | 0 | 39.4937 | 0 | 25.8 | 0 | 25.8 |  | 21-03-2026 15:20 | 181.744 | 184.212 | 1375.3 | 30.702 | 0 | 30.702 | 0 | 19.3 | 0 | 19.3 |  | 21-03-2026 15:20 | 161.505 | 181.619 | 1366.4 | 30.2698 | 0 | 30.2698 | 0 | 19 | 0 | 19 |  | 21-03-2026 15:20 | 171.174 | 174.871 | 1364.3 | 29.1452 | 0 | 29.1452 | 0 | 18.6 | 0 | 18.6 |  | 21-03-2026 15:20 | 171.709 | 177.253 | 1371.8 | 29.5422 | 0 | 29.5422 | 0 | 18.6 | 0 | 18.6 |  | 21-03-2026 15:20 | 161.027 | 162.339 | 1298.7 | 27.0565 | 0 | 27.0565 | 0 | 17.6 | 0 | 17.6 |  | 21-03-2026 15:20 | 297.0732 | 0 | 297.0732 | 0 | 195.4 | 0 | 195.4
21-03-2026 15:10 |  |  | 197.065 | 199.904 | 1807.1 | 33.3173 | 0 | 33.3173 | 0 | 42.4 | 0 | 42.4 |  | 21-03-2026 15:10 | 190.786 | 193.554 | 1822.3 | 32.259 | 0 | 32.259 | 0 | 42.4 | 0 | 42.4 |  | 21-03-2026 15:10 | 216.127 | 221.462 | 1796.1 | 36.9103 | 0 | 36.9103 | 0 | 42.1 | 0 | 42.1 |  | 21-03-2026 15:10 | 200.504 | 203.454 | 1810.2 | 33.909 | 0 | 33.909 | 0 | 42.8 | 0 | 42.8 |  | 21-03-2026 15:10 | 155.571 | 157.791 | 1356 | 26.2985 | 0 | 26.2985 | 0 | 31.8 | 0 | 31.8 |  | 21-03-2026 15:10 | 150.532 | 153.62 | 1347.4 | 25.6033 | 0 | 25.6033 | 0 | 31.4 | 0 | 31.4 |  | 21-03-2026 15:10 | 151.405 | 153.508 | 1345.7 | 25.5847 | 0 | 25.5847 | 0 | 31.3 | 0 | 31.3 |  | 21-03-2026 15:10 | 148.841 | 152.789 | 1353.2 | 25.4648 | 0 | 25.4648 | 0 | 31.4 | 0 | 31.4 |  | 21-03-2026 15:10 | 141.233 | 143.25 | 1281.1 | 23.875 | 0 | 23.875 | 0 | 29.7 | 0 | 29.7 |  | 21-03-2026 15:10 | 263.222 | 0 | 263.222 | 0 | 325.3 | 0 | 325.3
21-03-2026 15:00 |  |  | 292.357 | 297.081 | 1764.7 | 49.5135 | 0 | 49.5135 | 0 | 50.5 | 0 | 50.5 | 0.9841 | 21-03-2026 15:00 | 296.056 | 300.901 | 1779.9 | 50.1502 | 0 | 50.1502 | 0 | 49.8 | 0 | 49.8 | 0.9839 | 21-03-2026 15:00 | 290.245 | 297.576 | 1754 | 49.596 | 0 | 49.596 | 0 | 49.5 | 0 | 49.5 | 0.97536 | 21-03-2026 15:00 | 292.52 | 297.337 | 1767.4 | 49.5562 | 0 | 49.5562 | 0 | 49.1 | 0 | 49.1 | 0.9838 | 21-03-2026 15:00 | 218.151 | 221.406 | 1324.2 | 36.901 | 0 | 36.901 | 0 | 36.6 | 0 | 36.6 | 0.9853 | 21-03-2026 15:00 | 215.068 | 218.54 | 1316 | 36.4233 | 0 | 36.4233 | 0 | 36.1 | 0 | 36.1 | 0.98411 | 21-03-2026 15:00 | 214.755 | 218.023 | 1314.4 | 36.3372 | 0 | 36.3372 | 0 | 36.1 | 0 | 36.1 | 0.98501 | 21-03-2026 15:00 | 215.247 | 221.106 | 1321.8 | 36.851 | 0 | 36.851 | 0 | 36.2 | 0 | 36.2 | 0.9735 | 21-03-2026 15:00 | 203.927 | 206.969 | 1251.4 | 34.4948 | 0 | 34.4948 | 0 | 34.3 | 0 | 34.3 | 0.9853 | 21-03-2026 15:00 | 379.8232 | 0 | 379.8232 | 0 | 378.2 | 0 | 378.2
21-03-2026 14:50 |  |  | 299.512 | 304.297 | 1714.2 | 50.7162 | 0 | 50.7162 | 0 | 51.4 | 0 | 51.4 | 0.98428 | 21-03-2026 14:50 | 303.015 | 308.005 | 1730.1 | 51.3342 | 0 | 51.3342 | 0 | 50.6 | 0 | 50.6 | 0.9838 | 21-03-2026 14:50 | 298.073 | 305.734 | 1704.5 | 50.9557 | 0 | 50.9557 | 0 | 49 | 0 | 49 | 0.97494 | 21-03-2026 14:50 | 299.107 | 304.063 | 1718.3 | 50.6772 | 0 | 50.6772 | 0 | 50.1 | 0 | 50.1 | 0.9837 | 21-03-2026 14:50 | 223.874 | 227.191 | 1287.6 | 37.8652 | 0 | 37.8652 | 0 | 37.5 | 0 | 37.5 | 0.9854 | 21-03-2026 14:50 | 220.125 | 223.687 | 1279.9 | 37.2812 | 0 | 37.2812 | 0 | 37 | 0 | 37 | 0.98408 | 21-03-2026 14:50 | 220.305 | 224.428 | 1278.3 | 37.4047 | 0 | 37.4047 | 0 | 36.9 | 0 | 36.9 | 0.98163 | 21-03-2026 14:50 | 220.918 | 227.322 | 1285.6 | 37.887 | 0 | 37.887 | 0 | 37 | 0 | 37 | 0.97183 | 21-03-2026 14:50 | 209.079 | 212.198 | 1217.1 | 35.3663 | 0 | 35.3663 | 0 | 35.2 | 0 | 35.2 | 0.9853 | 21-03-2026 14:50 | 389.4875 | 0 | 389.4875 | 0 | 384.7 | 0 | 384.7
21-03-2026 14:40 |  |  | 302.719 | 307.766 | 1662.8 | 51.2943 | 0 | 51.2943 | 0 | 48.4 | 0 | 48.4 | 0.9836 | 21-03-2026 14:40 | 306.953 | 312.23 | 1679.5 | 52.0383 | 0 | 52.0383 | 0 | 54 | 0 | 54 | 0.9831 | 21-03-2026 14:40 | 299.936 | 307.823 | 1655.5 | 51.3038 | 0 | 51.3038 | 0 | 51.5 | 0 | 51.5 | 0.97438 | 21-03-2026 14:40 | 303.964 | 309.158 | 1668.2 | 51.5263 | 0 | 51.5263 | 0 | 51.3 | 0 | 51.3 | 0.9832 | 21-03-2026 14:40 | 226.066 | 229.625 | 1250.1 | 38.2708 | 0 | 38.2708 | 0 | 38.2 | 0 | 38.2 | 0.9845 | 21-03-2026 14:40 | 224.379 | 228.221 | 1242.9 | 38.0368 | 0 | 38.0368 | 0 | 37.9 | 0 | 37.9 | 0.98317 | 21-03-2026 14:40 | 223.731 | 227.65 | 1241.4 | 37.9417 | 0 | 37.9417 | 0 | 37.7 | 0 | 37.7 | 0.98278 | 21-03-2026 14:40 | 225.166 | 231.661 | 1248.6 | 38.6102 | 0 | 38.6102 | 0 | 38.1 | 0 | 38.1 | 0.97196 | 21-03-2026 14:40 | 213.585 | 216.838 | 1181.9 | 36.1397 | 0 | 36.1397 | 0 | 36 | 0 | 36 | 0.985 | 21-03-2026 14:40 | 395.162 | 0 | 395.162 | 0 | 393.1 | 0 | 393.1
21-03-2026 14:30 |  |  | 311.486 | 316.712 | 1614.4 | 52.7853 | 0 | 52.7853 | 0 | 53.6 | 0 | 53.6 | 0.9835 | 21-03-2026 14:30 | 316.632 | 322.081 | 1625.5 | 53.6802 | 0 | 53.6802 | 0 | 50.8 | 0 | 50.8 | 0.98308 | 21-03-2026 14:30 | 309.975 | 318.333 | 1604 | 53.0555 | 0 | 53.0555 | 0 | 51.9 | 0 | 51.9 | 0.97374 | 21-03-2026 14:30 | 312.312 | 317.649 | 1616.9 | 52.9415 | 0 | 52.9415 | 0 | 52.3 | 0 | 52.3 | 0.9832 | 21-03-2026 14:30 | 233.689 | 237.344 | 1211.9 | 39.5573 | 0 | 39.5573 | 0 | 39.1 | 0 | 39.1 | 0.9846 | 21-03-2026 14:30 | 230.822 | 235.109 | 1205 | 39.1848 | 0 | 39.1848 | 0 | 38.6 | 0 | 38.6 | 0.98177 | 21-03-2026 14:30 | 230.662 | 234.889 | 1203.7 | 39.1482 | 0 | 39.1482 | 0 | 38.6 | 0 | 38.6 | 0.982 | 21-03-2026 14:30 | 231.993 | 238.655 | 1210.5 | 39.7758 | 0 | 39.7758 | 0 | 38.8 | 0 | 38.8 | 0.97209 | 21-03-2026 14:30 | 219.608 | 222.922 | 1145.9 | 37.1537 | 0 | 37.1537 | 0 | 36.7 | 0 | 36.7 | 0.98513 | 21-03-2026 14:30 | 407.2823 | 0 | 407.2823 | 0 | 400.4 | 0 | 400.4
21-03-2026 14:20 |  |  | 315.282 | 325.783 | 1560.8 | 54.2972 | 0 | 54.2972 | 0 | 52.4 | 0 | 52.4 | 0.96777 | 21-03-2026 14:20 | 324.76 | 330.376 | 1574.7 | 55.0627 | 0 | 55.0627 | 0 | 53.7 | 0 | 53.7 | 0.983 | 21-03-2026 14:20 | 318.801 | 327.532 | 1552.1 | 54.5887 | 0 | 54.5887 | 0 | 53.5 | 0 | 53.5 | 0.97334 | 21-03-2026 14:20 | 320.958 | 326.475 | 1564.6 | 54.4125 | 0 | 54.4125 | 0 | 53.9 | 0 | 53.9 | 0.9831 | 21-03-2026 14:20 | 240.045 | 243.8 | 1172.8 | 40.6333 | 0 | 40.6333 | 0 | 40.3 | 0 | 40.3 | 0.9846 | 21-03-2026 14:20 | 236.545 | 240.668 | 1166.4 | 40.1113 | 0 | 40.1113 | 0 | 39.7 | 0 | 39.7 | 0.98287 | 21-03-2026 14:20 | 237.068 | 241.349 | 1165.1 | 40.2248 | 0 | 40.2248 | 0 | 39.8 | 0 | 39.8 | 0.98226 | 21-03-2026 14:20 | 238.488 | 245.479 | 1171.7 | 40.9132 | 0 | 40.9132 | 0 | 40 | 0 | 40 | 0.97152 | 21-03-2026 14:20 | 224.753 | 228.176 | 1109.2 | 38.0293 | 0 | 38.0293 | 0 | 37.8 | 0 | 37.8 | 0.985 | 21-03-2026 14:20 | 418.273 | 0 | 418.273 | 0 | 411.1 | 0 | 411.1
21-03-2026 14:10 |  |  | 326.945 | 332.498 | 1508.4 | 55.4163 | 0 | 55.4163 | 0 | 55.6 | 0 | 55.6 | 0.9833 | 21-03-2026 14:10 | 332.256 | 337.968 | 1521 | 56.328 | 0 | 56.328 | 0 | 57.2 | 0 | 57.2 | 0.9831 | 21-03-2026 14:10 | 324.581 | 333.395 | 1498.6 | 55.5658 | 0 | 55.5658 | 0 | 54.5 | 0 | 54.5 | 0.97356 | 21-03-2026 14:10 | 327.836 | 333.54 | 1510.7 | 55.59 | 0 | 55.59 | 0 | 54.9 | 0 | 54.9 | 0.9829 | 21-03-2026 14:10 | 244.831 | 248.686 | 1132.5 | 41.4477 | 0 | 41.4477 | 0 | 41.1 | 0 | 41.1 | 0.9845 | 21-03-2026 14:10 | 241.348 | 245.31 | 1126.7 | 40.885 | 0 | 40.885 | 0 | 40.5 | 0 | 40.5 | 0.98385 | 21-03-2026 14:10 | 241.727 | 246.428 | 1125.3 | 41.0713 | 0 | 41.0713 | 0 | 40.6 | 0 | 40.6 | 0.98092 | 21-03-2026 14:10 | 242.756 | 249.925 | 1131.7 | 41.6542 | 0 | 41.6542 | 0 | 40.7 | 0 | 40.7 | 0.97132 | 21-03-2026 14:10 | 229.349 | 232.936 | 1071.4 | 38.8227 | 0 | 38.8227 | 0 | 39 | 0 | 39 | 0.9846 | 21-03-2026 14:10 | 426.781 | 0 | 426.781 | 0 | 424.1 | 0 | 424.1
21-03-2026 14:00 |  |  | 333.496 | 339.16 | 1452.8 | 56.5267 | 0 | 56.5267 | 0 | 55.5 | 0 | 55.5 | 0.9833 | 21-03-2026 14:00 | 339.977 | 345.892 | 1463.8 | 57.6487 | 0 | 57.6487 | 0 | 112.1 | 0 | 112.1 | 0.9829 | 21-03-2026 14:00 | 331.782 | 341.193 | 1444.1 | 56.8655 | 0 | 56.8655 | 0 | 55.1 | 0 | 55.1 | 0.97242 | 21-03-2026 14:00 | 334.263 | 340.078 | 1455.8 | 56.6797 | 0 | 56.6797 | 0 | 55.5 | 0 | 55.5 | 0.9829 | 21-03-2026 14:00 | 250.003 | 253.939 | 1091.4 | 42.3232 | 0 | 42.3232 | 0 | 41.5 | 0 | 41.5 | 0.9845 | 21-03-2026 14:00 | 246.777 | 251.29 | 1086.2 | 41.8817 | 0 | 41.8817 | 0 | 41.6 | 0 | 41.6 | 0.98204 | 21-03-2026 14:00 | 246.435 | 251.069 | 1084.7 | 41.8448 | 0 | 41.8448 | 0 | 41.5 | 0 | 41.5 | 0.98154 | 21-03-2026 14:00 | 247.877 | 255.24 | 1091 | 42.54 | 0 | 42.54 | 0 | 41.7 | 0 | 41.7 | 0.97115 | 21-03-2026 14:00 | 234.599 | 238.244 | 1032.4 | 39.7073 | 0 | 39.7073 | 0 | 39 | 0 | 39 | 0.9847 | 21-03-2026 14:00 | 436.0175 | 0 | 436.0175 | 0 | 483.5 | 0 | 483.5
21-03-2026 13:50 |  |  | 334.116 | 339.825 | 1397.3 | 56.6375 | 0 | 56.6375 | 0 | 56.2 | 0 | 56.2 | 0.9832 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21-03-2026 13:50 | 332.48 | 341.743 | 1389 | 56.9572 | 0 | 56.9572 | 0 | 55.9 | 0 | 55.9 | 0.97289 | 21-03-2026 13:50 | 333.332 | 339.166 | 1400.3 | 56.5277 | 0 | 56.5277 | 0 | 56.3 | 0 | 56.3 | 0.9828 | 21-03-2026 13:50 | 251.473 | 255.356 | 1049.9 | 42.5593 | 0 | 42.5593 | 0 | 42.2 | 0 | 42.2 | 0.98479 | 21-03-2026 13:50 | 247.06 | 251.486 | 1044.6 | 41.9143 | 0 | 41.9143 | 0 | 41 | 0 | 41 | 0.9824 | 21-03-2026 13:50 | 248.358 | 253.06 | 1043.2 | 42.1767 | 0 | 42.1767 | 0 | 41.7 | 0 | 41.7 | 0.98142 | 21-03-2026 13:50 | 249.763 | 257.382 | 1049.3 | 42.897 | 0 | 42.897 | 0 | 42 | 0 | 42 | 0.9704 | 21-03-2026 13:50 | 235.383 | 239.065 | 993.4 | 39.8442 | 0 | 39.8442 | 0 | 39.6 | 0 | 39.6 | 0.9846 | 21-03-2026 13:50 | 379.5138 | 0 | 379.5138 | 0 | 374.9 | 0 | 374.9
21-03-2026 13:40 |  |  | 343.983 | 349.967 | 1341.1 | 58.3278 | 0 | 58.3278 | 0 | 56.5 | 0 | 56.5 | 0.9829 | 21-03-2026 13:40 | 347.503 | 354.995 | 1351.7 | 59.1658 | 0 | 59.1658 | 0 | 56.6 | 0 | 56.6 | 0.9789 | 21-03-2026 13:40 | 341.195 | 350.644 | 1333.1 | 58.4407 | 0 | 58.4407 | 0 | 56.4 | 0 | 56.4 | 0.97305 | 21-03-2026 13:40 | 344.56 | 350.662 | 1344 | 58.4437 | 0 | 58.4437 | 0 | 56.7 | 0 | 56.7 | 0.9826 | 21-03-2026 13:40 | 256.501 | 260.566 | 1007.7 | 43.4277 | 0 | 43.4277 | 0 | 42.6 | 0 | 42.6 | 0.9844 | 21-03-2026 13:40 | 253.769 | 258.583 | 1003.6 | 43.0972 | 0 | 43.0972 | 0 | 42 | 0 | 42 | 0.98138 | 21-03-2026 13:40 | 255.157 | 259.956 | 1001.5 | 43.326 | 0 | 43.326 | 0 | 41.5 | 0 | 41.5 | 0.98154 | 21-03-2026 13:40 | 255.882 | 263.638 | 1007.3 | 43.9397 | 0 | 43.9397 | 0 | 41.6 | 0 | 41.6 | 0.97058 | 21-03-2026 13:40 | 242.37 | 246.211 | 953.8 | 41.0352 | 0 | 41.0352 | 0 | 39.3 | 0 | 39.3 | 0.9844 | 21-03-2026 13:40 | 449.2037 | 0 | 449.2037 | 0 | 433.2 | 0 | 433.2
21-03-2026 13:30 |  |  | 322.213 | 330.41 | 1284.6 | 55.0683 | 0 | 55.0683 | 0 | 57.6 | 0 | 57.6 | 0.97519 | 21-03-2026 13:30 | 325.519 | 331.115 | 1295.1 | 55.1858 | 0 | 55.1858 | 0 | 57.9 | 0 | 57.9 | 0.9831 | 21-03-2026 13:30 | 323.011 | 331.046 | 1276.7 | 55.1743 | 0 | 55.1743 | 0 | 56.5 | 0 | 56.5 | 0.97573 | 21-03-2026 13:30 | 324.959 | 330.545 | 1287.3 | 55.0908 | 0 | 55.0908 | 0 | 56.8 | 0 | 56.8 | 0.9831 | 21-03-2026 13:30 | 241.993 | 245.753 | 965.1 | 40.9588 | 0 | 40.9588 | 0 | 42.9 | 0 | 42.9 | 0.9847 | 21-03-2026 13:30 | 240.226 | 244.229 | 961.6 | 40.7048 | 0 | 40.7048 | 0 | 43 | 0 | 43 | 0.98361 | 21-03-2026 13:30 | 240.618 | 245.655 | 960 | 40.9425 | 0 | 40.9425 | 0 | 43.1 | 0 | 43.1 | 0.9795 | 21-03-2026 13:30 | 242.467 | 249.96 | 965.7 | 41.66 | 0 | 41.66 | 0 | 43.3 | 0 | 43.3 | 0.97002 | 21-03-2026 13:30 | 228.093 | 231.59 | 914.5 | 38.5983 | 0 | 38.5983 | 0 | 41 | 0 | 41 | 0.9849 | 21-03-2026 13:30 | 423.3838 | 0 | 423.3838 | 0 | 442.1 | 0 | 442.1
21-03-2026 13:20 |  |  | 340.709 | 346.46 | 1227 | 57.7433 | 0 | 57.7433 | 0 | 53.7 | 0 | 53.7 | 0.9834 | 21-03-2026 13:20 | 351.282 | 357.357 | 1237.2 | 59.5595 | 0 | 59.5595 | 0 | 55.1 | 0 | 55.1 | 0.983 | 21-03-2026 13:20 | 339.364 | 348.164 | 1220.2 | 58.0273 | 0 | 58.0273 | 0 | 54.6 | 0 | 54.6 | 0.97472 | 21-03-2026 13:20 | 341.702 | 347.576 | 1230.5 | 57.9293 | 0 | 57.9293 | 0 | 54.6 | 0 | 54.6 | 0.9831 | 21-03-2026 13:20 | 256.307 | 260.316 | 922.2 | 43.386 | 0 | 43.386 | 0 | 41.8 | 0 | 41.8 | 0.9846 | 21-03-2026 13:20 | 250.482 | 255.365 | 918.6 | 42.5608 | 0 | 42.5608 | 0 | 40.9 | 0 | 40.9 | 0.98088 | 21-03-2026 13:20 | 249.06 | 254.676 | 916.9 | 42.446 | 0 | 42.446 | 0 | 41.1 | 0 | 41.1 | 0.97795 | 21-03-2026 13:20 | 250.088 | 258.161 | 922.4 | 43.0268 | 0 | 43.0268 | 0 | 41.2 | 0 | 41.2 | 0.96873 | 21-03-2026 13:20 | 236.901 | 240.533 | 873.5 | 40.0888 | 0 | 40.0888 | 0 | 38.9 | 0 | 38.9 | 0.9849 | 21-03-2026 13:20 | 444.768 | 0 | 444.768 | 0 | 421.9 | 0 | 421.9
21-03-2026 13:10 |  |  | 191.044 | 193.678 | 1173.3 | 32.2797 | 0 | 32.2797 | 0 | 44 | 0 | 44 | 0.9864 | 21-03-2026 13:10 | 180.03 | 182.586 | 1182.1 | 30.431 | 0 | 30.431 | 0 | 42.8 | 0 | 42.8 | 0.986 | 21-03-2026 13:10 | 190.987 | 196.103 | 1165.6 | 32.6838 | 0 | 32.6838 | 0 | 43.1 | 0 | 43.1 | 0.97391 | 21-03-2026 13:10 | 186.591 | 188.223 | 1175.9 | 31.3705 | 0 | 31.3705 | 0 | 42.9 | 0 | 42.9 | 0.99133 | 21-03-2026 13:10 | 145.297 | 147.256 | 880.4 | 24.5427 | 0 | 24.5427 | 0 | 32 | 0 | 32 | 0.9867 | 21-03-2026 13:10 | 134.88 | 136.698 | 877.7 | 22.783 | 0 | 22.783 | 0 | 31.4 | 0 | 31.4 | 0.9867 | 21-03-2026 13:10 | 136.34 | 138.495 | 875.8 | 23.0825 | 0 | 23.0825 | 0 | 31.7 | 0 | 31.7 | 0.98444 | 21-03-2026 13:10 | 135.518 | 139.728 | 881.2 | 23.288 | 0 | 23.288 | 0 | 31.8 | 0 | 31.8 | 0.96987 | 21-03-2026 13:10 | 127.553 | 129.272 | 834.6 | 21.5453 | 0 | 21.5453 | 0 | 30.1 | 0 | 30.1 | 0.9867 | 21-03-2026 13:10 | 242.0065 | 0 | 242.0065 | 0 | 329.8 | 0 | 329.8
21-03-2026 13:00 |  |  | 248.961 | 252.675 | 1129.3 | 42.1125 | 0 | 42.1125 | 0 | 49.5 | 0 | 49.5 | 0.9853 | 21-03-2026 13:00 | 237.16 | 240.747 | 1139.3 | 40.1245 | 0 | 40.1245 | 0 | 50.9 | 0 | 50.9 | 0.9851 | 21-03-2026 13:00 | 228.712 | 235.919 | 1122.5 | 39.3198 | 0 | 39.3198 | 0 | 49 | 0 | 49 | 0.96945 | 21-03-2026 13:00 | 236.959 | 240.543 | 1133 | 40.0905 | 0 | 40.0905 | 0 | 49.8 | 0 | 49.8 | 0.9851 | 21-03-2026 13:00 | 184.382 | 187.534 | 848.4 | 31.2557 | 0 | 31.2557 | 0 | 39.4 | 0 | 39.4 | 0.98319 | 21-03-2026 13:00 | 180.272 | 183.585 | 846.3 | 30.5975 | 0 | 30.5975 | 0 | 39 | 0 | 39 | 0.98195 | 21-03-2026 13:00 | 174.197 | 177.023 | 844.1 | 29.5038 | 0 | 29.5038 | 0 | 38.5 | 0 | 38.5 | 0.98404 | 21-03-2026 13:00 | 173.873 | 180.942 | 849.4 | 30.157 | 0 | 30.157 | 0 | 38.6 | 0 | 38.6 | 0.96093 | 21-03-2026 13:00 | 163.417 | 165.83 | 804.5 | 27.6383 | 0 | 27.6383 | 0 | 36.5 | 0 | 36.5 | 0.98545 | 21-03-2026 13:00 | 310.7997 | 0 | 310.7997 | 0 | 391.2 | 0 | 391.2
21-03-2026 12:50 |  |  | 352.361 | 357.328 | 1079.8 | 59.5547 | 0 | 59.5547 | 0 | 42.5 | 0 | 42.5 | 0.9861 | 21-03-2026 12:50 | 0 | 357.293 | 1088.4 | 59.5488 | 0 | 59.5488 | 0 | 42.7 | 0 | 42.7 |  | 21-03-2026 12:50 | 352.089 | 361.5 | 1073.5 | 60.25 | 0 | 60.25 | 0 | 43.1 | 0 | 43.1 | 0.97397 | 21-03-2026 12:50 | 352.245 | 357.145 | 1083.2 | 59.5242 | 0 | 59.5242 | 0 | 43.7 | 0 | 43.7 | 0.98628 | 21-03-2026 12:50 | 294.837 | 299.286 | 809 | 49.881 | 0 | 49.881 | 0 | 33.3 | 0 | 33.3 | 0.98513 | 21-03-2026 12:50 | 288.674 | 293.424 | 807.3 | 48.904 | 0 | 48.904 | 0 | 32.8 | 0 | 32.8 | 0.98381 | 21-03-2026 12:50 | 290.982 | 296.904 | 805.6 | 49.484 | 0 | 49.484 | 0 | 33 | 0 | 33 | 0.98005 | 21-03-2026 12:50 | 290.119 | 299.015 | 810.8 | 49.8358 | 0 | 49.8358 | 0 | 33.1 | 0 | 33.1 | 0.97025 | 21-03-2026 12:50 | 272.199 | 276.4 | 768 | 46.0667 | 0 | 46.0667 | 0 | 31.3 | 0 | 31.3 | 0.9848 | 21-03-2026 12:50 | 483.0492 | 0 | 483.0492 | 0 | 335.5 | 0 | 335.5
21-03-2026 12:40 |  |  | 165.932 | 167.806 | 1037.3 | 27.9677 | 0 | 27.9677 | 0 | 23.8 | 0 | 23.8 | 0.98883 | 21-03-2026 12:40 | 163.885 | 168.804 | 1045.7 | 28.134 | 0 | 28.134 | 0 | 24 | 0 | 24 | 0.97086 | 21-03-2026 12:40 | 162.575 | 166.273 | 1030.4 | 27.7122 | 0 | 27.7122 | 0 | 23.7 | 0 | 23.7 | 0.97776 | 21-03-2026 12:40 | 163.43 | 165.583 | 1039.5 | 27.5972 | 0 | 27.5972 | 0 | 23.7 | 0 | 23.7 | 0.987 | 21-03-2026 12:40 | 121.923 | 123.466 | 775.7 | 20.5777 | 0 | 20.5777 | 0 | 17.7 | 0 | 17.7 | 0.9875 | 21-03-2026 12:40 | 120.479 | 121.992 | 774.5 | 20.332 | 0 | 20.332 | 0 | 17.5 | 0 | 17.5 | 0.9876 | 21-03-2026 12:40 | 120.707 | 122.223 | 772.6 | 20.3705 | 0 | 20.3705 | 0 | 17.5 | 0 | 17.5 | 0.9876 | 21-03-2026 12:40 | 121.23 | 124.644 | 777.7 | 20.774 | 0 | 20.774 | 0 | 17.6 | 0 | 17.6 | 0.97261 | 21-03-2026 12:40 | 114.272 | 115.73 | 736.7 | 19.2883 | 0 | 19.2883 | 0 | 16.6 | 0 | 16.6 | 0.9874 | 21-03-2026 12:40 | 212.7535 | 0 | 212.7535 | 0 | 182.1 | 0 | 182.1
21-03-2026 12:30 |  |  | 143.662 | 145.102 | 1013.5 | 24.1837 | 0 | 24.1837 | 0 | 30.5 | 0 | 30.5 | 0.99008 | 21-03-2026 12:30 | 144.396 | 146.328 | 1021.7 | 24.388 | 0 | 24.388 | 0 | 30.7 | 0 | 30.7 | 0.9868 | 21-03-2026 12:30 | 141.931 | 144.598 | 1006.7 | 24.0997 | 0 | 24.0997 | 0 | 30.2 | 0 | 30.2 | 0.98156 | 21-03-2026 12:30 | 143.335 | 145.238 | 1015.8 | 24.2063 | 0 | 24.2063 | 0 | 30 | 0 | 30 | 0.9869 | 21-03-2026 12:30 | 106.335 | 107.703 | 758 | 17.9505 | 0 | 17.9505 | 0 | 22.3 | 0 | 22.3 | 0.9873 | 21-03-2026 12:30 | 105.399 | 106.755 | 757 | 17.7925 | 0 | 17.7925 | 0 | 22.1 | 0 | 22.1 | 0.9873 | 21-03-2026 12:30 | 105.115 | 106.467 | 755.1 | 17.7445 | 0 | 17.7445 | 0 | 22 | 0 | 22 | 0.9873 | 21-03-2026 12:30 | 105.688 | 108.634 | 760.1 | 18.1057 | 0 | 18.1057 | 0 | 22.1 | 0 | 22.1 | 0.97288 | 21-03-2026 12:30 | 99.872 | 101.187 | 720.1 | 16.8645 | 0 | 16.8645 | 0 | 20.9 | 0 | 20.9 | 0.987 | 21-03-2026 12:30 | 185.3353 | 0 | 185.3353 | 0 | 230.8 | 0 | 230.8
21-03-2026 12:20 |  |  | 193.054 | 195.736 | 983 | 32.6227 | 0 | 32.6227 | 0 | 38.4 | 0 | 38.4 | 0.9863 | 21-03-2026 12:20 | 194.764 | 197.529 | 991 | 32.9215 | 0 | 32.9215 | 0 | 38.9 | 0 | 38.9 | 0.986 | 21-03-2026 12:20 | 190.438 | 194.433 | 976.5 | 32.4055 | 0 | 32.4055 | 0 | 38.1 | 0 | 38.1 | 0.97945 | 21-03-2026 12:20 | 192.004 | 194.73 | 985.8 | 32.455 | 0 | 32.455 | 0 | 39.2 | 0 | 39.2 | 0.986 | 21-03-2026 12:20 | 142.377 | 144.282 | 735.7 | 24.047 | 0 | 24.047 | 0 | 29.2 | 0 | 29.2 | 0.9868 | 21-03-2026 12:20 | 140.803 | 142.701 | 734.9 | 23.7835 | 0 | 23.7835 | 0 | 28.9 | 0 | 28.9 | 0.9867 | 21-03-2026 12:20 | 140.526 | 142.53 | 733.1 | 23.755 | 0 | 23.755 | 0 | 28.8 | 0 | 28.8 | 0.98594 | 21-03-2026 12:20 | 141.062 | 145.035 | 738 | 24.1725 | 0 | 24.1725 | 0 | 29 | 0 | 29 | 0.97261 | 21-03-2026 12:20 | 133.382 | 135.184 | 699.2 | 22.5307 | 0 | 22.5307 | 0 | 27.4 | 0 | 27.4 | 0.98667 | 21-03-2026 12:20 | 248.6933 | 0 | 248.6933 | 0 | 297.9 | 0 | 297.9
21-03-2026 12:10 |  |  | 298.689 | 303.638 | 944.6 | 50.6063 | 0 | 50.6063 | 0 | 58.3 | 0 | 58.3 | 0.9837 | 21-03-2026 12:10 | 274.836 | 280.986 | 952.1 | 46.831 | 0 | 46.831 | 0 | 59.2 | 0 | 59.2 | 0.97811 | 21-03-2026 12:10 | 274.303 | 283.326 | 938.4 | 47.221 | 0 | 47.221 | 0 | 57.4 | 0 | 57.4 | 0.96815 | 21-03-2026 12:10 | 285.304 | 290.061 | 946.6 | 48.3435 | 0 | 48.3435 | 0 | 57.6 | 0 | 57.6 | 0.9836 | 21-03-2026 12:10 | 203.29 | 206.302 | 706.5 | 34.3837 | 0 | 34.3837 | 0 | 46.3 | 0 | 46.3 | 0.9854 | 21-03-2026 12:10 | 201.613 | 204.662 | 706 | 34.1103 | 0 | 34.1103 | 0 | 45.8 | 0 | 45.8 | 0.9851 | 21-03-2026 12:10 | 196.02 | 199.359 | 704.3 | 33.2265 | 0 | 33.2265 | 0 | 45.8 | 0 | 45.8 | 0.98325 | 21-03-2026 12:10 | 198.545 | 204.728 | 709 | 34.1213 | 0 | 34.1213 | 0 | 46 | 0 | 46 | 0.9698 | 21-03-2026 12:10 | 187.127 | 189.919 | 671.8 | 31.6532 | 0 | 31.6532 | 0 | 43.4 | 0 | 43.4 | 0.9853 | 21-03-2026 12:10 | 360.4968 | 0 | 360.4968 | 0 | 459.8 | 0 | 459.8
21-03-2026 12:00 |  |  | 338.11 | 343.782 | 886.3 | 57.297 | 0 | 57.297 | 0 | 55.9 | 0 | 55.9 | 0.9835 | 21-03-2026 12:00 | 352.302 | 343.301 | 892.9 | 57.2168 | 0 | 57.2168 | 0 | 55.6 | 0 | 55.6 | 1.0262 | 21-03-2026 12:00 | 352.053 | 361.902 | 881 | 60.317 | 0 | 60.317 | 0 | 56.4 | 0 | 56.4 | 0.97279 | 21-03-2026 12:00 | 351.628 | 357.782 | 889 | 59.6303 | 0 | 59.6303 | 0 | 55.9 | 0 | 55.9 | 0.9828 | 21-03-2026 12:00 | 267.043 | 271.22 | 660.2 | 45.2033 | 0 | 45.2033 | 0 | 42.4 | 0 | 42.4 | 0.9846 | 21-03-2026 12:00 | 264.66 | 270.412 | 660.2 | 45.0687 | 0 | 45.0687 | 0 | 42 | 0 | 42 | 0.97873 | 21-03-2026 12:00 | 267.617 | 272.536 | 658.5 | 45.4227 | 0 | 45.4227 | 0 | 42.1 | 0 | 42.1 | 0.98195 | 21-03-2026 12:00 | 268.963 | 277.104 | 663 | 46.184 | 0 | 46.184 | 0 | 42.2 | 0 | 42.2 | 0.97062 | 21-03-2026 12:00 | 254.859 | 259.181 | 628.4 | 43.1968 | 0 | 43.1968 | 0 | 40 | 0 | 40 | 0.98332 | 21-03-2026 12:00 | 459.5367 | 0 | 459.5367 | 0 | 432.5 | 0 | 432.5
21-03-2026 11:50 |  |  | 352.849 | 358.55 | 830.4 | 59.7583 | 0 | 59.7583 | 0 | 57.8 | 0 | 57.8 | 0.9841 | 21-03-2026 11:50 | 352.839 | 358.613 | 837.3 | 59.7688 | 0 | 59.7688 | 0 | 58.7 | 0 | 58.7 | 0.9839 | 21-03-2026 11:50 | 339.463 | 347.684 | 824.6 | 57.9473 | 0 | 57.9473 | 0 | 57.1 | 0 | 57.1 | 0.97635 | 21-03-2026 11:50 | 348.254 | 355.93 | 833.1 | 59.3217 | 0 | 59.3217 | 0 | 57.3 | 0 | 57.3 | 0.97843 | 21-03-2026 11:50 | 251.796 | 255.656 | 617.8 | 42.6093 | 0 | 42.6093 | 0 | 44 | 0 | 44 | 0.9849 | 21-03-2026 11:50 | 251.093 | 257.105 | 618.2 | 42.8508 | 0 | 42.8508 | 0 | 43.6 | 0 | 43.6 | 0.97662 | 21-03-2026 11:50 | 246.858 | 251.642 | 616.4 | 41.9403 | 0 | 41.9403 | 0 | 44.7 | 0 | 44.7 | 0.98099 | 21-03-2026 11:50 | 247.549 | 255.874 | 620.8 | 42.6457 | 0 | 42.6457 | 0 | 44.4 | 0 | 44.4 | 0.96746 | 21-03-2026 11:50 | 246.961 | 237.044 | 588.4 | 39.5073 | 0 | 39.5073 | 0 | 42 | 0 | 42 | 1.0418 | 21-03-2026 11:50 | 446.3497 | 0 | 446.3497 | 0 | 449.6 | 0 | 449.6
21-03-2026 11:40 |  |  | 294.521 | 297.784 | 772.6 | 49.6307 | 0 | 49.6307 | 0 | 46.6 | 0 | 46.6 | 0.98904 | 21-03-2026 11:40 | 274.851 | 279.093 | 778.6 | 46.5155 | 0 | 46.5155 | 0 | 50.3 | 0 | 50.3 | 0.9848 | 21-03-2026 11:40 | 305.064 | 310.059 | 767.5 | 51.6765 | 0 | 51.6765 | 0 | 47.8 | 0 | 47.8 | 0.98389 | 21-03-2026 11:40 | 310.257 | 315.238 | 775.8 | 52.5397 | 0 | 52.5397 | 0 | 48.2 | 0 | 48.2 | 0.9842 | 21-03-2026 11:40 | 226.356 | 229.64 | 573.8 | 38.2733 | 0 | 38.2733 | 0 | 35.9 | 0 | 35.9 | 0.9857 | 21-03-2026 11:40 | 224.722 | 232.445 | 574.6 | 38.7408 | 0 | 38.7408 | 0 | 35.6 | 0 | 35.6 | 0.96677 | 21-03-2026 11:40 | 215.832 | 222.893 | 571.7 | 37.1488 | 0 | 37.1488 | 0 | 34.5 | 0 | 34.5 | 0.96832 | 21-03-2026 11:40 | 230.035 | 236.994 | 576.4 | 39.499 | 0 | 39.499 | 0 | 35.2 | 0 | 35.2 | 0.97064 | 21-03-2026 11:40 | 213.271 | 218.112 | 546.4 | 36.352 | 0 | 36.352 | 0 | 33.2 | 0 | 33.2 | 0.9778 | 21-03-2026 11:40 | 390.3763 | 0 | 390.3763 | 0 | 367.3 | 0 | 367.3
21-03-2026 11:30 |  |  | 336.22 | 341.618 | 726 | 56.9363 | 0 | 56.9363 | 0 | 56 | 0 | 56 | 0.9842 | 21-03-2026 11:30 | 316.913 | 326.459 | 728.3 | 54.4098 | 0 | 54.4098 | 0 | 52 | 0 | 52 | 0.97076 | 21-03-2026 11:30 | 329.403 | 338.503 | 719.7 | 56.4172 | 0 | 56.4172 | 0 | 53.4 | 0 | 53.4 | 0.97312 | 21-03-2026 11:30 | 334.088 | 339.658 | 727.6 | 56.6097 | 0 | 56.6097 | 0 | 53.9 | 0 | 53.9 | 0.9836 | 21-03-2026 11:30 | 250.594 | 254.359 | 537.9 | 42.3932 | 0 | 42.3932 | 0 | 40.3 | 0 | 40.3 | 0.9852 | 21-03-2026 11:30 | 247.681 | 251.867 | 539 | 41.9778 | 0 | 41.9778 | 0 | 39.9 | 0 | 39.9 | 0.98338 | 21-03-2026 11:30 | 248.509 | 252.505 | 537.2 | 42.0842 | 0 | 42.0842 | 0 | 39.9 | 0 | 39.9 | 0.98417 | 21-03-2026 11:30 | 248.916 | 256.067 | 541.2 | 42.6778 | 0 | 42.6778 | 0 | 40 | 0 | 40 | 0.97207 | 21-03-2026 11:30 | 236.272 | 239.797 | 513.2 | 39.9662 | 0 | 39.9662 | 0 | 38.4 | 0 | 38.4 | 0.9853 | 21-03-2026 11:30 | 433.4722 | 0 | 433.4722 | 0 | 413.8 | 0 | 413.8
21-03-2026 11:20 |  |  | 296.342 | 300.855 | 670 | 50.1425 | 0 | 50.1425 | 0 | 43.5 | 0 | 43.5 | 0.985 | 21-03-2026 11:20 | 299.34 | 304.022 | 676.3 | 50.6703 | 0 | 50.6703 | 0 | 44.5 | 0 | 44.5 | 0.9846 | 21-03-2026 11:20 | 295.364 | 303.015 | 666.3 | 50.5025 | 0 | 50.5025 | 0 | 44 | 0 | 44 | 0.97475 | 21-03-2026 11:20 | 299.587 | 304.335 | 673.7 | 50.7225 | 0 | 50.7225 | 0 | 44.4 | 0 | 44.4 | 0.9844 | 21-03-2026 11:20 | 225.517 | 228.696 | 497.6 | 38.116 | 0 | 38.116 | 0 | 33.2 | 0 | 33.2 | 0.9861 | 21-03-2026 11:20 | 223.126 | 226.248 | 499.1 | 37.708 | 0 | 37.708 | 0 | 33.3 | 0 | 33.3 | 0.9862 | 21-03-2026 11:20 | 226.723 | 230.411 | 497.3 | 38.4018 | 0 | 38.4018 | 0 | 33.3 | 0 | 33.3 | 0.98399 | 21-03-2026 11:20 | 223.614 | 235.047 | 501.2 | 39.1745 | 0 | 39.1745 | 0 | 33.5 | 0 | 33.5 | 0.95136 | 21-03-2026 11:20 | 211.727 | 214.733 | 474.8 | 35.7888 | 0 | 35.7888 | 0 | 31.2 | 0 | 31.2 | 0.986 | 21-03-2026 11:20 | 391.227 | 0 | 391.227 | 0 | 340.9 | 0 | 340.9
21-03-2026 11:10 |  |  | 224.338 | 227.408 | 626.5 | 37.9013 | 0 | 37.9013 | 0 | 38.4 | 0 | 38.4 | 0.9865 | 21-03-2026 11:10 | 223.067 | 225.739 | 631.8 | 37.6232 | 0 | 37.6232 | 0 | 39.7 | 0 | 39.7 | 0.98816 | 21-03-2026 11:10 | 225.206 | 230.365 | 622.3 | 38.3942 | 0 | 38.3942 | 0 | 38.5 | 0 | 38.5 | 0.97761 | 21-03-2026 11:10 | 227.492 | 230.366 | 629.3 | 38.3943 | 0 | 38.3943 | 0 | 38.8 | 0 | 38.8 | 0.98752 | 21-03-2026 11:10 | 170.423 | 172.668 | 464.4 | 28.778 | 0 | 28.778 | 0 | 28.8 | 0 | 28.8 | 0.987 | 21-03-2026 11:10 | 167.794 | 169.75 | 465.8 | 28.2917 | 0 | 28.2917 | 0 | 28.3 | 0 | 28.3 | 0.98848 | 21-03-2026 11:10 | 169.171 | 171.543 | 464 | 28.5905 | 0 | 28.5905 | 0 | 28.3 | 0 | 28.3 | 0.98617 | 21-03-2026 11:10 | 170.828 | 175.672 | 467.7 | 29.2787 | 0 | 29.2787 | 0 | 28.4 | 0 | 28.4 | 0.97243 | 21-03-2026 11:10 | 161.224 | 163.348 | 443.6 | 27.2247 | 0 | 27.2247 | 0 | 26.8 | 0 | 26.8 | 0.987 | 21-03-2026 11:10 | 294.4765 | 0 | 294.4765 | 0 | 296 | 0 | 296
21-03-2026 11:00 |  |  | 235.616 | 238.961 | 588.1 | 39.8268 | 0 | 39.8268 | 0 | 42 | 0 | 42 | 0.986 | 21-03-2026 11:00 | 229.882 | 233.193 | 592.1 | 38.8655 | 0 | 38.8655 | 0 | 42.5 | 0 | 42.5 | 0.9858 | 21-03-2026 11:00 | 233.271 | 238.422 | 583.8 | 39.737 | 0 | 39.737 | 0 | 41.7 | 0 | 41.7 | 0.9784 | 21-03-2026 11:00 | 232.773 | 236.126 | 590.5 | 39.3543 | 0 | 39.3543 | 0 | 42 | 0 | 42 | 0.9858 | 21-03-2026 11:00 | 173.083 | 175.398 | 435.6 | 29.233 | 0 | 29.233 | 0 | 31.1 | 0 | 31.1 | 0.9868 | 21-03-2026 11:00 | 171.334 | 173.608 | 437.5 | 28.9347 | 0 | 28.9347 | 0 | 31.1 | 0 | 31.1 | 0.9869 | 21-03-2026 11:00 | 171.832 | 174.422 | 435.7 | 29.0703 | 0 | 29.0703 | 0 | 31 | 0 | 31 | 0.98515 | 21-03-2026 11:00 | 171.608 | 176.376 | 439.3 | 29.396 | 0 | 29.396 | 0 | 31.1 | 0 | 31.1 | 0.97297 | 21-03-2026 11:00 | 161.455 | 163.598 | 416.8 | 27.2663 | 0 | 27.2663 | 0 | 29.5 | 0 | 29.5 | 0.9869 | 21-03-2026 11:00 | 301.684 | 0 | 301.684 | 0 | 322 | 0 | 322
21-03-2026 10:50 |  |  | 257.595 | 261.332 | 546.1 | 43.5553 | 0 | 43.5553 | 0 | 37.5 | 0 | 37.5 | 0.9857 | 21-03-2026 10:50 | 237.841 | 241.682 | 549.6 | 40.2803 | 0 | 40.2803 | 0 | 36.7 | 0 | 36.7 | 0.98411 | 21-03-2026 10:50 | 254.329 | 260.86 | 542.1 | 43.4767 | 0 | 43.4767 | 0 | 37.2 | 0 | 37.2 | 0.97496 | 21-03-2026 10:50 | 257.484 | 261.272 | 548.5 | 43.5453 | 0 | 43.5453 | 0 | 37.6 | 0 | 37.6 | 0.9855 | 21-03-2026 10:50 | 191.403 | 194.003 | 404.5 | 32.3338 | 0 | 32.3338 | 0 | 27.9 | 0 | 27.9 | 0.9866 | 21-03-2026 10:50 | 189.341 | 191.993 | 406.4 | 31.9988 | 0 | 31.9988 | 0 | 27.7 | 0 | 27.7 | 0.98619 | 21-03-2026 10:50 | 190.559 | 193.139 | 404.7 | 32.1898 | 0 | 32.1898 | 0 | 27.7 | 0 | 27.7 | 0.98664 | 21-03-2026 10:50 | 192.637 | 198.169 | 408.2 | 33.0282 | 0 | 33.0282 | 0 | 28 | 0 | 28 | 0.97208 | 21-03-2026 10:50 | 182.484 | 184.962 | 387.3 | 30.827 | 0 | 30.827 | 0 | 26.9 | 0 | 26.9 | 0.9866 | 21-03-2026 10:50 | 331.2353 | 0 | 331.2353 | 0 | 287.2 | 0 | 287.2
21-03-2026 10:40 |  |  | 223.024 | 226.053 | 508.6 | 37.6755 | 0 | 37.6755 | 0 | 35.8 | 0 | 35.8 | 0.9866 | 21-03-2026 10:40 | 228.216 | 224.856 | 512.9 | 37.476 | 0 | 37.476 | 0 | 36.1 | 0 | 36.1 | 1.0149 | 21-03-2026 10:40 | 217.133 | 221.339 | 504.9 | 36.8898 | 0 | 36.8898 | 0 | 35.2 | 0 | 35.2 | 0.981 | 21-03-2026 10:40 | 219.328 | 222.322 | 510.9 | 37.0537 | 0 | 37.0537 | 0 | 35.4 | 0 | 35.4 | 0.98653 | 21-03-2026 10:40 | 160.847 | 162.933 | 376.6 | 27.1555 | 0 | 27.1555 | 0 | 26.4 | 0 | 26.4 | 0.9872 | 21-03-2026 10:40 | 161.492 | 163.586 | 378.7 | 27.2643 | 0 | 27.2643 | 0 | 26.2 | 0 | 26.2 | 0.9872 | 21-03-2026 10:40 | 159.101 | 161.164 | 377 | 26.8607 | 0 | 26.8607 | 0 | 26.5 | 0 | 26.5 | 0.9872 | 21-03-2026 10:40 | 160.126 | 164.656 | 380.2 | 27.4427 | 0 | 27.4427 | 0 | 26.6 | 0 | 26.6 | 0.97249 | 21-03-2026 10:40 | 153.423 | 155.444 | 360.4 | 25.9073 | 0 | 25.9073 | 0 | 24.8 | 0 | 24.8 | 0.987 | 21-03-2026 10:40 | 283.7255 | 0 | 283.7255 | 0 | 273 | 0 | 273
21-03-2026 10:30 |  |  | 204.393 | 207.127 | 472.8 | 34.5212 | 0 | 34.5212 | 0 | 34.7 | 0 | 34.7 | 0.9868 | 21-03-2026 10:30 | 202.663 | 205.436 | 476.8 | 34.2393 | 0 | 34.2393 | 0 | 34.8 | 0 | 34.8 | 0.9865 | 21-03-2026 10:30 | 199.704 | 203.51 | 469.7 | 33.9183 | 0 | 33.9183 | 0 | 34.5 | 0 | 34.5 | 0.9813 | 21-03-2026 10:30 | 201.251 | 204.005 | 475.5 | 34.0008 | 0 | 34.0008 | 0 | 35.2 | 0 | 35.2 | 0.9865 | 21-03-2026 10:30 | 148.81 | 150.724 | 350.2 | 25.1207 | 0 | 25.1207 | 0 | 26.1 | 0 | 26.1 | 0.9873 | 21-03-2026 10:30 | 148.386 | 150.295 | 352.5 | 25.0492 | 0 | 25.0492 | 0 | 26.2 | 0 | 26.2 | 0.9873 | 21-03-2026 10:30 | 147.72 | 149.62 | 350.5 | 24.9367 | 0 | 24.9367 | 0 | 25.8 | 0 | 25.8 | 0.9873 | 21-03-2026 10:30 | 148.412 | 152.443 | 353.6 | 25.4072 | 0 | 25.4072 | 0 | 26 | 0 | 26 | 0.97356 | 21-03-2026 10:30 | 140.538 | 142.375 | 335.6 | 23.7292 | 0 | 23.7292 | 0 | 24.6 | 0 | 24.6 | 0.9871 | 21-03-2026 10:30 | 260.9225 | 0 | 260.9225 | 0 | 267.9 | 0 | 267.9
21-03-2026 10:20 |  |  | 127.966 | 129.586 | 438.1 | 21.5977 | 0 | 21.5977 | 0 | 33.4 | 0 | 33.4 | 0.9875 | 21-03-2026 10:20 | 130.016 | 131.628 | 442 | 21.938 | 0 | 21.938 | 0 | 33.6 | 0 | 33.6 | 0.98775 | 21-03-2026 10:20 | 128.564 | 131.087 | 435.2 | 21.8478 | 0 | 21.8478 | 0 | 33.3 | 0 | 33.3 | 0.98075 | 21-03-2026 10:20 | 129.665 | 131.346 | 440.3 | 21.891 | 0 | 21.891 | 0 | 33.4 | 0 | 33.4 | 0.9872 | 21-03-2026 10:20 | 96.49 | 97.692 | 324.1 | 16.282 | 0 | 16.282 | 0 | 24.7 | 0 | 24.7 | 0.9877 | 21-03-2026 10:20 | 96.123 | 97.32 | 326.3 | 16.22 | 0 | 16.22 | 0 | 24.6 | 0 | 24.6 | 0.9877 | 21-03-2026 10:20 | 96.118 | 97.325 | 324.7 | 16.2208 | 0 | 16.2208 | 0 | 24.5 | 0 | 24.5 | 0.9876 | 21-03-2026 10:20 | 96.728 | 99.66 | 327.6 | 16.61 | 0 | 16.61 | 0 | 24.6 | 0 | 24.6 | 0.97058 | 21-03-2026 10:20 | 91.625 | 92.785 | 311 | 15.4642 | 0 | 15.4642 | 0 | 23.4 | 0 | 23.4 | 0.9875 | 21-03-2026 10:20 | 168.0715 | 0 | 168.0715 | 0 | 255.5 | 0 | 255.5
21-03-2026 10:10 |  |  | 118.709 | 149.386 | 404.7 | 24.8977 | 0 | 24.8977 | 0 | 29.6 | 0 | 29.6 | 0.79465 | 21-03-2026 10:10 | 154.733 | 156.771 | 408.4 | 26.1285 | 0 | 26.1285 | 0 | 29.6 | 0 | 29.6 | 0.987 | 21-03-2026 10:10 | 157.419 | 160.773 | 401.9 | 26.7955 | 0 | 26.7955 | 0 | 29 | 0 | 29 | 0.97914 | 21-03-2026 10:10 | 156.223 | 158.265 | 406.9 | 26.3775 | 0 | 26.3775 | 0 | 29.9 | 0 | 29.9 | 0.9871 | 21-03-2026 10:10 | 118.794 | 119.798 | 299.4 | 19.9663 | 0 | 19.9663 | 0 | 22.1 | 0 | 22.1 | 0.99162 | 21-03-2026 10:10 | 116.741 | 118.009 | 301.7 | 19.6682 | 0 | 19.6682 | 0 | 22 | 0 | 22 | 0.98926 | 21-03-2026 10:10 | 117.845 | 119.3 | 300.2 | 19.8833 | 0 | 19.8833 | 0 | 22.9 | 0 | 22.9 | 0.9878 | 21-03-2026 10:10 | 117.742 | 121.334 | 303 | 20.2223 | 0 | 20.2223 | 0 | 22 | 0 | 22 | 0.9704 | 21-03-2026 10:10 | 105.62 | 112.671 | 287.6 | 18.7785 | 0 | 18.7785 | 0 | 20.9 | 0 | 20.9 | 0.93742 | 21-03-2026 10:10 | 202.7178 | 0 | 202.7178 | 0 | 228 | 0 | 228
21-03-2026 10:00 |  |  | 270.284 | 274.391 | 375.1 | 45.7318 | 0 | 45.7318 | 0 | 39.8 | 0 | 39.8 | 0.98503 | 21-03-2026 10:00 | 266.163 | 270.107 | 378.8 | 45.0178 | 0 | 45.0178 | 0 | 40.7 | 0 | 40.7 | 0.9854 | 21-03-2026 10:00 | 267.783 | 274.083 | 372.9 | 45.6805 | 0 | 45.6805 | 0 | 40.1 | 0 | 40.1 | 0.97701 | 21-03-2026 10:00 | 271.264 | 275.339 | 377 | 45.8898 | 0 | 45.8898 | 0 | 39.8 | 0 | 39.8 | 0.9852 | 21-03-2026 10:00 | 201.886 | 204.628 | 277.3 | 34.1047 | 0 | 34.1047 | 0 | 29.6 | 0 | 29.6 | 0.9866 | 21-03-2026 10:00 | 201.554 | 204.333 | 279.7 | 34.0555 | 0 | 34.0555 | 0 | 29.5 | 0 | 29.5 | 0.9864 | 21-03-2026 10:00 | 202.303 | 205.39 | 277.3 | 34.2317 | 0 | 34.2317 | 0 | 28.6 | 0 | 28.6 | 0.98497 | 21-03-2026 10:00 | 202.9 | 208.363 | 281 | 34.7272 | 0 | 34.7272 | 0 | 29.7 | 0 | 29.7 | 0.97378 | 21-03-2026 10:00 | 192.416 | 195.089 | 266.7 | 32.5148 | 0 | 32.5148 | 0 | 28.1 | 0 | 28.1 | 0.9863 | 21-03-2026 10:00 | 351.9538 | 0 | 351.9538 | 0 | 305.9 | 0 | 305.9
21-03-2026 09:50 |  |  | 212.634 | 215.566 | 335.3 | 35.9277 | 0 | 35.9277 | 0 | 36.2 | 0 | 36.2 |  | 21-03-2026 09:50 | 184.649 | 188.644 | 338.1 | 31.4407 | 0 | 31.4407 | 0 | 36 | 0 | 36 |  | 21-03-2026 09:50 | 209.781 | 213.724 | 332.8 | 35.6207 | 0 | 35.6207 | 0 | 33.9 | 0 | 33.9 |  | 21-03-2026 09:50 | 212.923 | 215.902 | 337.2 | 35.9837 | 0 | 35.9837 | 0 | 34.3 | 0 | 34.3 |  | 21-03-2026 09:50 | 155.358 | 157.42 | 247.7 | 26.2367 | 0 | 26.2367 | 0 | 25.3 | 0 | 25.3 |  | 21-03-2026 09:50 | 156.88 | 158.93 | 250.2 | 26.4883 | 0 | 26.4883 | 0 | 25.4 | 0 | 25.4 |  | 21-03-2026 09:50 | 154.16 | 156.19 | 248.7 | 26.0317 | 0 | 26.0317 | 0 | 25.2 | 0 | 25.2 |  | 21-03-2026 09:50 | 155.342 | 158.987 | 251.3 | 26.4978 | 0 | 26.4978 | 0 | 25.3 | 0 | 25.3 |  | 21-03-2026 09:50 | 148.101 | 150.067 | 238.6 | 25.0112 | 0 | 25.0112 | 0 | 24 | 0 | 24 |  | 21-03-2026 09:50 | 269.2383 | 0 | 269.2383 | 0 | 265.6 | 0 | 265.6
21-03-2026 09:40 |  |  | 224.31 | 227.393 | 299.1 | 37.8988 | 0 | 37.8988 | 0 | 36.8 | 0 | 36.8 |  | 21-03-2026 09:40 | 224.605 | 227.817 | 302.1 | 37.9695 | 0 | 37.9695 | 0 | 38.2 | 0 | 38.2 |  | 21-03-2026 09:40 | 214.229 | 218.493 | 298.9 | 36.4155 | 0 | 36.4155 | 0 | 38.4 | 0 | 38.4 |  | 21-03-2026 09:40 | 217.536 | 220.625 | 302.9 | 36.7708 | 0 | 36.7708 | 0 | 38.9 | 0 | 38.9 |  | 21-03-2026 09:40 | 158.726 | 161.216 | 222.4 | 26.8693 | 0 | 26.8693 | 0 | 28.8 | 0 | 28.8 |  | 21-03-2026 09:40 | 160.001 | 162.593 | 224.8 | 27.0988 | 0 | 27.0988 | 0 | 28.8 | 0 | 28.8 |  | 21-03-2026 09:40 | 158.056 | 160.17 | 223.5 | 26.695 | 0 | 26.695 | 0 | 28.7 | 0 | 28.7 |  | 21-03-2026 09:40 | 159.553 | 163.731 | 226 | 27.2885 | 0 | 27.2885 | 0 | 29.4 | 0 | 29.4 |  | 21-03-2026 09:40 | 151.672 | 153.716 | 214.6 | 25.6193 | 0 | 25.6193 | 0 | 27.9 | 0 | 27.9 |  | 21-03-2026 09:40 | 282.6257 | 0 | 282.6257 | 0 | 295.9 | 0 | 295.9
21-03-2026 09:30 |  |  | 233.68 | 236.974 | 262.3 | 39.4957 | 0 | 39.4957 | 0 | 37.2 | 0 | 37.2 |  | 21-03-2026 09:30 | 234.449 | 238.845 | 263.9 | 39.8075 | 0 | 39.8075 | 0 | 37.7 | 0 | 37.7 |  | 21-03-2026 09:30 | 234.346 | 239.372 | 260.5 | 39.8953 | 0 | 39.8953 | 0 | 37.1 | 0 | 37.1 |  | 21-03-2026 09:30 | 237.15 | 240.566 | 264 | 40.0943 | 0 | 40.0943 | 0 | 37.5 | 0 | 37.5 |  | 21-03-2026 09:30 | 175.385 | 177.731 | 193.6 | 29.6218 | 0 | 29.6218 | 0 | 27.7 | 0 | 27.7 |  | 21-03-2026 09:30 | 175.898 | 178.233 | 196 | 29.7055 | 0 | 29.7055 | 0 | 27.8 | 0 | 27.8 |  | 21-03-2026 09:30 | 175.204 | 177.512 | 194.8 | 29.5853 | 0 | 29.5853 | 0 | 27.7 | 0 | 27.7 |  | 21-03-2026 09:30 | 176.425 | 181.248 | 196.6 | 30.208 | 0 | 30.208 | 0 | 27.5 | 0 | 27.5 |  | 21-03-2026 09:30 | 167.719 | 169.98 | 186.7 | 28.33 | 0 | 28.33 | 0 | 26.5 | 0 | 26.5 |  | 21-03-2026 09:30 | 306.7435 | 0 | 306.7435 | 0 | 286.7 | 0 | 286.7
21-03-2026 09:20 |  |  | 218.131 | 221.049 | 225.1 | 36.8415 | 0 | 36.8415 | 0 | 35.6 | 0 | 35.6 |  | 21-03-2026 09:20 | 220.411 | 223.44 | 226.2 | 37.24 | 0 | 37.24 | 0 | 35.5 | 0 | 35.5 |  | 21-03-2026 09:20 | 216.599 | 220.751 | 223.4 | 36.7918 | 0 | 36.7918 | 0 | 35.3 | 0 | 35.3 |  | 21-03-2026 09:20 | 219.441 | 222.444 | 226.5 | 37.074 | 0 | 37.074 | 0 | 35.9 | 0 | 35.9 |  | 21-03-2026 09:20 | 161.856 | 163.955 | 165.9 | 27.3258 | 0 | 27.3258 | 0 | 26.4 | 0 | 26.4 |  | 21-03-2026 09:20 | 162.849 | 164.961 | 168.2 | 27.4935 | 0 | 27.4935 | 0 | 26.6 | 0 | 26.6 |  | 21-03-2026 09:20 | 162.006 | 164.09 | 167.1 | 27.3483 | 0 | 27.3483 | 0 | 26.8 | 0 | 26.8 |  | 21-03-2026 09:20 | 162.989 | 167.333 | 169.1 | 27.8888 | 0 | 27.8888 | 0 | 27.1 | 0 | 27.1 |  | 21-03-2026 09:20 | 154.982 | 156.992 | 160.2 | 26.1653 | 0 | 26.1653 | 0 | 25.4 | 0 | 25.4 |  | 21-03-2026 09:20 | 284.1692 | 0 | 284.1692 | 0 | 274.6 | 0 | 274.6
21-03-2026 09:10 |  |  | 165.74 | 167.787 | 189.5 | 27.9645 | 0 | 27.9645 | 0 | 16.6 | 0 | 16.6 |  | 21-03-2026 09:10 | 150.272 | 152.159 | 190.7 | 25.3598 | 0 | 25.3598 | 0 | 16.9 | 0 | 16.9 |  | 21-03-2026 09:10 | 168.371 | 171.683 | 188.1 | 28.6138 | 0 | 28.6138 | 0 | 16.4 | 0 | 16.4 |  | 21-03-2026 09:10 | 169.64 | 171.022 | 190.6 | 28.5037 | 0 | 28.5037 | 0 | 16.6 | 0 | 16.6 |  | 21-03-2026 09:10 | 128.096 | 130.275 | 139.5 | 21.7125 | 0 | 21.7125 | 0 | 12.2 | 0 | 12.2 |  | 21-03-2026 09:10 | 128.397 | 129.72 | 141.6 | 21.62 | 0 | 21.62 | 0 | 12.4 | 0 | 12.4 |  | 21-03-2026 09:10 | 123.156 | 124.723 | 140.3 | 20.7872 | 0 | 20.7872 | 0 | 12.1 | 0 | 12.1 |  | 21-03-2026 09:10 | 123.934 | 127.706 | 142 | 21.2843 | 0 | 21.2843 | 0 | 12.2 | 0 | 12.2 |  | 21-03-2026 09:10 | 117.332 | 118.757 | 134.8 | 19.7928 | 0 | 19.7928 | 0 | 11.6 | 0 | 11.6 |  | 21-03-2026 09:10 | 215.6387 | 0 | 215.6387 | 0 | 127 | 0 | 127
21-03-2026 09:00 |  |  | 156.93 | 158.916 | 172.9 | 26.486 | 0 | 26.486 | 0 | 31.5 | 0 | 31.5 |  | 21-03-2026 09:00 | 160.29 | 162.368 | 173.8 | 27.0613 | 0 | 27.0613 | 0 | 31.6 | 0 | 31.6 |  | 21-03-2026 09:00 | 150.994 | 153.239 | 171.7 | 25.5398 | 0 | 25.5398 | 0 | 31.4 | 0 | 31.4 |  | 21-03-2026 09:00 | 155.255 | 157.268 | 174 | 26.2113 | 0 | 26.2113 | 0 | 31.9 | 0 | 31.9 |  | 21-03-2026 09:00 | 112.833 | 114.227 | 127.3 | 19.0378 | 0 | 19.0378 | 0 | 23.5 | 0 | 23.5 |  | 21-03-2026 09:00 | 114.378 | 115.802 | 129.2 | 19.3003 | 0 | 19.3003 | 0 | 23.6 | 0 | 23.6 |  | 21-03-2026 09:00 | 114.817 | 116.247 | 128.2 | 19.3745 | 0 | 19.3745 | 0 | 23.6 | 0 | 23.6 |  | 21-03-2026 09:00 | 116.074 | 119.241 | 129.8 | 19.8735 | 0 | 19.8735 | 0 | 23.9 | 0 | 23.9 |  | 21-03-2026 09:00 | 110.408 | 111.817 | 123.2 | 18.6362 | 0 | 18.6362 | 0 | 22.7 | 0 | 22.7 |  | 21-03-2026 09:00 | 201.5208 | 0 | 201.5208 | 0 | 243.7 | 0 | 243.7
21-03-2026 08:50 |  |  | 182.663 | 184.919 | 141.4 | 30.8198 | 0 | 30.8198 | 0 | 24.7 | 0 | 24.7 |  | 21-03-2026 08:50 | 181.585 | 183.884 | 142.2 | 30.6473 | 0 | 30.6473 | 0 | 25.4 | 0 | 25.4 |  | 21-03-2026 08:50 | 179.61 | 182.629 | 140.3 | 30.4382 | 0 | 30.4382 | 0 | 25.3 | 0 | 25.3 |  | 21-03-2026 08:50 | 181.015 | 183.325 | 142.1 | 30.5542 | 0 | 30.5542 | 0 | 25.6 | 0 | 25.6 |  | 21-03-2026 08:50 | 133.143 | 134.76 | 103.8 | 22.46 | 0 | 22.46 | 0 | 18.8 | 0 | 18.8 |  | 21-03-2026 08:50 | 133.757 | 135.368 | 105.6 | 22.5613 | 0 | 22.5613 | 0 | 19 | 0 | 19 |  | 21-03-2026 08:50 | 132.576 | 134.186 | 104.6 | 22.3643 | 0 | 22.3643 | 0 | 18.6 | 0 | 18.6 |  | 21-03-2026 08:50 | 133.503 | 136.944 | 105.9 | 22.824 | 0 | 22.824 | 0 | 18.7 | 0 | 18.7 |  | 21-03-2026 08:50 | 126.97 | 128.477 | 100.5 | 21.4128 | 0 | 21.4128 | 0 | 17.8 | 0 | 17.8 |  | 21-03-2026 08:50 | 234.082 | 0 | 234.082 | 0 | 193.9 | 0 | 193.9
21-03-2026 08:40 |  |  | 136.776 | 138.367 | 116.7 | 23.0612 | 0 | 23.0612 | 0 | 23.8 | 0 | 23.8 |  | 21-03-2026 08:40 | 135.281 | 136.896 | 116.8 | 22.816 | 0 | 22.816 | 0 | 23.8 | 0 | 23.8 |  | 21-03-2026 08:40 | 129.932 | 132.033 | 115 | 22.0055 | 0 | 22.0055 | 0 | 23.1 | 0 | 23.1 |  | 21-03-2026 08:40 | 129.139 | 130.681 | 116.5 | 21.7802 | 0 | 21.7802 | 0 | 23.5 | 0 | 23.5 |  | 21-03-2026 08:40 | 97.43 | 98.665 | 85 | 16.4442 | 0 | 16.4442 | 0 | 17.4 | 0 | 17.4 |  | 21-03-2026 08:40 | 97.157 | 98.287 | 86.6 | 16.3812 | 0 | 16.3812 | 0 | 17.7 | 0 | 17.7 |  | 21-03-2026 08:40 | 98.542 | 99.709 | 86 | 16.6182 | 0 | 16.6182 | 0 | 17.5 | 0 | 17.5 |  | 21-03-2026 08:40 | 98.983 | 101.995 | 87.2 | 16.9992 | 0 | 16.9992 | 0 | 17.7 | 0 | 17.7 |  | 21-03-2026 08:40 | 93.785 | 94.905 | 82.7 | 15.8175 | 0 | 15.8175 | 0 | 17 | 0 | 17 |  | 21-03-2026 08:40 | 171.923 | 0 | 171.923 | 0 | 181.5 | 0 | 181.5
21-03-2026 08:30 |  |  | 143.468 | 144.544 | 92.9 | 24.0907 | 0 | 24.0907 | 0 | 22.2 | 0 | 22.2 |  | 21-03-2026 08:30 | 142.905 | 144.568 | 93 | 24.0947 | 0 | 24.0947 | 0 | 22.4 | 0 | 22.4 |  | 21-03-2026 08:30 | 141.455 | 143.389 | 91.9 | 23.8982 | 0 | 23.8982 | 0 | 22 | 0 | 22 |  | 21-03-2026 08:30 | 142.731 | 144.362 | 93 | 24.0603 | 0 | 24.0603 | 0 | 22.4 | 0 | 22.4 |  | 21-03-2026 08:30 | 104.183 | 105.374 | 67.6 | 17.5623 | 0 | 17.5623 | 0 | 16.1 | 0 | 16.1 |  | 21-03-2026 08:30 | 105.426 | 106.647 | 68.9 | 17.7745 | 0 | 17.7745 | 0 | 16.3 | 0 | 16.3 |  | 21-03-2026 08:30 | 104.238 | 105.429 | 68.5 | 17.5715 | 0 | 17.5715 | 0 | 16.4 | 0 | 16.4 |  | 21-03-2026 08:30 | 104.741 | 107.495 | 69.5 | 17.9158 | 0 | 17.9158 | 0 | 16.6 | 0 | 16.6 |  | 21-03-2026 08:30 | 100.351 | 101.488 | 65.7 | 16.9147 | 0 | 16.9147 | 0 | 15.6 | 0 | 15.6 |  | 21-03-2026 08:30 | 183.8827 | 0 | 183.8827 | 0 | 170 | 0 | 170
21-03-2026 08:20 |  |  | 121.898 | 123.216 | 70.7 | 20.536 | 0 | 20.536 | 0 | 18.5 | 0 | 18.5 |  | 21-03-2026 08:20 | 119.888 | 121.209 | 70.6 | 20.2015 | 0 | 20.2015 | 0 | 18.8 | 0 | 18.8 |  | 21-03-2026 08:20 | 120.884 | 122.506 | 69.9 | 20.4177 | 0 | 20.4177 | 0 | 18.4 | 0 | 18.4 |  | 21-03-2026 08:20 | 122.735 | 124.088 | 70.6 | 20.6813 | 0 | 20.6813 | 0 | 18.6 | 0 | 18.6 |  | 21-03-2026 08:20 | 89.575 | 90.553 | 51.5 | 15.0922 | 0 | 15.0922 | 0 | 13.6 | 0 | 13.6 |  | 21-03-2026 08:20 | 90.915 | 91.889 | 52.6 | 15.3148 | 0 | 15.3148 | 0 | 13.9 | 0 | 13.9 |  | 21-03-2026 08:20 | 90.089 | 91.073 | 52.1 | 15.1788 | 0 | 15.1788 | 0 | 13.5 | 0 | 13.5 |  | 21-03-2026 08:20 | 90.902 | 93.328 | 52.9 | 15.5547 | 0 | 15.5547 | 0 | 13.6 | 0 | 13.6 |  | 21-03-2026 08:20 | 86.891 | 87.857 | 50.1 | 14.6428 | 0 | 14.6428 | 0 | 13 | 0 | 13 |  | 21-03-2026 08:20 | 157.6198 | 0 | 157.6198 | 0 | 141.9 | 0 | 141.9
21-03-2026 08:10 |  |  | 100.934 | 101.974 | 52.2 | 16.9957 | 0 | 16.9957 | 0 | 15.3 | 0 | 15.3 |  | 21-03-2026 08:10 | 101.078 | 102.281 | 51.8 | 17.0468 | 0 | 17.0468 | 0 | 14.8 | 0 | 14.8 |  | 21-03-2026 08:10 | 99.535 | 100.624 | 51.5 | 16.7707 | 0 | 16.7707 | 0 | 14.8 | 0 | 14.8 |  | 21-03-2026 08:10 | 101.458 | 102.545 | 52 | 17.0908 | 0 | 17.0908 | 0 | 15.3 | 0 | 15.3 |  | 21-03-2026 08:10 | 74.096 | 74.935 | 37.9 | 12.4892 | 0 | 12.4892 | 0 | 11.2 | 0 | 11.2 |  | 21-03-2026 08:10 | 75.537 | 76.369 | 38.7 | 12.7282 | 0 | 12.7282 | 0 | 11.4 | 0 | 11.4 |  | 21-03-2026 08:10 | 74.859 | 75.707 | 38.6 | 12.6178 | 0 | 12.6178 | 0 | 11.3 | 0 | 11.3 |  | 21-03-2026 08:10 | 75.715 | 77.596 | 39.3 | 12.9327 | 0 | 12.9327 | 0 | 11.4 | 0 | 11.4 |  | 21-03-2026 08:10 | 72.36 | 73.18 | 37.1 | 12.1967 | 0 | 12.1967 | 0 | 11 | 0 | 11 |  | 21-03-2026 08:10 | 130.8685 | 0 | 130.8685 | 0 | 116.5 | 0 | 116.5
21-03-2026 08:00 |  |  | 82.27 | 83.151 | 36.9 | 13.8585 | 0 | 13.8585 | 0 | 10.7 | 0 | 10.7 |  | 21-03-2026 08:00 | 82.232 | 83.224 | 37 | 13.8707 | 0 | 13.8707 | 0 | 10.9 | 0 | 10.9 |  | 21-03-2026 08:00 | 81.228 | 82.369 | 36.7 | 13.7282 | 0 | 13.7282 | 0 | 10.8 | 0 | 10.8 |  | 21-03-2026 08:00 | 82.379 | 83.27 | 36.7 | 13.8783 | 0 | 13.8783 | 0 | 10.7 | 0 | 10.7 |  | 21-03-2026 08:00 | 59.945 | 60.667 | 26.7 | 10.1112 | 0 | 10.1112 | 0 | 7.8 | 0 | 7.8 |  | 21-03-2026 08:00 | 61.282 | 61.982 | 27.3 | 10.3303 | 0 | 10.3303 | 0 | 8 | 0 | 8 |  | 21-03-2026 08:00 | 61.046 | 61.762 | 27.3 | 10.2937 | 0 | 10.2937 | 0 | 8 | 0 | 8 |  | 21-03-2026 08:00 | 61.664 | 63.423 | 27.9 | 10.5705 | 0 | 10.5705 | 0 | 8.1 | 0 | 8.1 |  | 21-03-2026 08:00 | 58.9 | 59.609 | 26.1 | 9.9348 | 0 | 9.9348 | 0 | 7.7 | 0 | 7.7 |  | 21-03-2026 08:00 | 106.5762 | 0 | 106.5762 | 0 | 82.7 | 0 | 82.7
21-03-2026 07:50 |  |  | 25.15 | 25.648 | 26.2 | 4.2747 | 0 | 4.2747 | 0 | 7.6 | 0 | 7.6 |  | 21-03-2026 07:50 | 24.772 | 25.493 | 26.1 | 4.2488 | 0 | 4.2488 | 0 | 7.4 | 0 | 7.4 |  | 21-03-2026 07:50 | 24.82 | 25.329 | 25.9 | 4.2215 | 0 | 4.2215 | 0 | 7.2 | 0 | 7.2 |  | 21-03-2026 07:50 | 24.607 | 25.159 | 26 | 4.1932 | 0 | 4.1932 | 0 | 7.4 | 0 | 7.4 |  | 21-03-2026 07:50 | 18.028 | 18.588 | 18.9 | 3.098 | 0 | 3.098 | 0 | 5.4 | 0 | 5.4 |  | 21-03-2026 07:50 | 18.075 | 18.443 | 19.3 | 3.0738 | 0 | 3.0738 | 0 | 5.5 | 0 | 5.5 |  | 21-03-2026 07:50 | 18.092 | 18.524 | 19.3 | 3.0873 | 0 | 3.0873 | 0 | 5.5 | 0 | 5.5 |  | 21-03-2026 07:50 | 18.056 | 18.734 | 19.8 | 3.1223 | 0 | 3.1223 | 0 | 5.6 | 0 | 5.6 |  | 21-03-2026 07:50 | 17.074 | 17.496 | 18.4 | 2.916 | 0 | 2.916 | 0 | 5.3 | 0 | 5.3 |  | 21-03-2026 07:50 | 32.2357 | 0 | 32.2357 | 0 | 56.9 | 0 | 56.9
21-03-2026 07:40 |  |  | 52.427 | 53.096 | 18.6 | 8.8493 | 0 | 8.8493 | 0 | 8.5 | 0 | 8.5 |  | 21-03-2026 07:40 | 52.122 | 52.893 | 18.7 | 8.8155 | 0 | 8.8155 | 0 | 9 | 0 | 9 |  | 21-03-2026 07:40 | 51.618 | 52.256 | 18.7 | 8.7093 | 0 | 8.7093 | 0 | 8.6 | 0 | 8.6 |  | 21-03-2026 07:40 | 52.306 | 52.995 | 18.6 | 8.8325 | 0 | 8.8325 | 0 | 8.6 | 0 | 8.6 |  | 21-03-2026 07:40 | 37.951 | 38.529 | 13.5 | 6.4215 | 0 | 6.4215 | 0 | 6.2 | 0 | 6.2 |  | 21-03-2026 07:40 | 39.076 | 39.643 | 13.8 | 6.6072 | 0 | 6.6072 | 0 | 6.4 | 0 | 6.4 |  | 21-03-2026 07:40 | 38.893 | 39.469 | 13.8 | 6.5782 | 0 | 6.5782 | 0 | 6.4 | 0 | 6.4 |  | 21-03-2026 07:40 | 39.385 | 40.543 | 14.2 | 6.7572 | 0 | 6.7572 | 0 | 6.4 | 0 | 6.4 |  | 21-03-2026 07:40 | 37.519 | 38.083 | 13.1 | 6.3472 | 0 | 6.3472 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 07:40 | 67.9178 | 0 | 67.9178 | 0 | 66.2 | 0 | 66.2
21-03-2026 07:30 |  |  | 51.735 | 52.349 | 10.1 | 8.7248 | 0 | 8.7248 | 0 | 6 | 0 | 6 |  | 21-03-2026 07:30 | 50.805 | 51.692 | 9.7 | 8.6153 | 0 | 8.6153 | 0 | 5.7 | 0 | 5.7 |  | 21-03-2026 07:30 | 51.055 | 51.727 | 10.1 | 8.6212 | 0 | 8.6212 | 0 | 6.1 | 0 | 6.1 |  | 21-03-2026 07:30 | 51.188 | 51.867 | 10 | 8.6445 | 0 | 8.6445 | 0 | 6 | 0 | 6 |  | 21-03-2026 07:30 | 37.586 | 38.155 | 7.3 | 6.3592 | 0 | 6.3592 | 0 | 4.5 | 0 | 4.5 |  | 21-03-2026 07:30 | 38.42 | 38.985 | 7.4 | 6.4975 | 0 | 6.4975 | 0 | 4.5 | 0 | 4.5 |  | 21-03-2026 07:30 | 38.387 | 38.968 | 7.4 | 6.4947 | 0 | 6.4947 | 0 | 4.5 | 0 | 4.5 |  | 21-03-2026 07:30 | 38.838 | 39.917 | 7.8 | 6.6528 | 0 | 6.6528 | 0 | 4.6 | 0 | 4.6 |  | 21-03-2026 07:30 | 36.512 | 37.068 | 7 | 6.178 | 0 | 6.178 | 0 | 4.3 | 0 | 4.3 |  | 21-03-2026 07:30 | 66.788 | 0 | 66.788 | 0 | 46.2 | 0 | 46.2
21-03-2026 07:20 |  |  | 27.648 | 28.122 | 4.1 | 4.687 | 0 | 4.687 | 0 | 2.6 | 0 | 2.6 |  | 21-03-2026 07:20 | 26.693 | 27.328 | 4 | 4.5547 | 0 | 4.5547 | 0 | 2.5 | 0 | 2.5 |  | 21-03-2026 07:20 | 27.126 | 27.62 | 4 | 4.6033 | 0 | 4.6033 | 0 | 2.6 | 0 | 2.6 |  | 21-03-2026 07:20 | 26.75 | 27.301 | 4 | 4.5502 | 0 | 4.5502 | 0 | 2.6 | 0 | 2.6 |  | 21-03-2026 07:20 | 19.886 | 20.553 | 2.8 | 3.4255 | 0 | 3.4255 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 07:20 | 20.33 | 20.758 | 2.9 | 3.4597 | 0 | 3.4597 | 0 | 1.9 | 0 | 1.9 |  | 21-03-2026 07:20 | 20.536 | 20.974 | 2.9 | 3.4957 | 0 | 3.4957 | 0 | 1.9 | 0 | 1.9 |  | 21-03-2026 07:20 | 20.85 | 21.553 | 3.2 | 3.5922 | 0 | 3.5922 | 0 | 1.9 | 0 | 1.9 |  | 21-03-2026 07:20 | 19.195 | 19.617 | 2.7 | 3.2695 | 0 | 3.2695 | 0 | 1.8 | 0 | 1.8 |  | 21-03-2026 07:20 | 35.6377 | 0 | 35.6377 | 0 | 19.6 | 0 | 19.6
21-03-2026 07:10 |  |  | 9.669 | 10.013 | 1.5 | 1.6688 | 0 | 1.6688 | 0 | 1.1 | 0 | 1.1 |  | 21-03-2026 07:10 | 9.629 | 10.341 | 1.5 | 1.7235 | 0 | 1.7235 | 0 | 1.1 | 0 | 1.1 |  | 21-03-2026 07:10 | 9.488 | 9.83 | 1.4 | 1.6383 | 0 | 1.6383 | 0 | 1 | 0 | 1 |  | 21-03-2026 07:10 | 9.41 | 10.283 | 1.4 | 1.7138 | 0 | 1.7138 | 0 | 1.1 | 0 | 1.1 |  | 21-03-2026 07:10 | 6.857 | 7.558 | 1 | 1.2597 | 0 | 1.2597 | 0 | 0.8 | 0 | 0.8 |  | 21-03-2026 07:10 | 6.899 | 7.176 | 1 | 1.196 | 0 | 1.196 | 0 | 0.8 | 0 | 0.8 |  | 21-03-2026 07:10 | 6.982 | 7.263 | 1 | 1.2105 | 0 | 1.2105 | 0 | 0.8 | 0 | 0.8 |  | 21-03-2026 07:10 | 7.134 | 7.837 | 1.3 | 1.3062 | 0 | 1.3062 | 0 | 0.9 | 0 | 0.9 |  | 21-03-2026 07:10 | 6.517 | 6.784 | 0.9 | 1.1307 | 0 | 1.1307 | 0 | 0.7 | 0 | 0.7 |  | 21-03-2026 07:10 | 12.8475 | 0 | 12.8475 | 0 | 8.3 | 0 | 8.3
21-03-2026 07:00 |  |  | 4.388 | 4.59 | 0.4 | 0.765 | 0 | 0.765 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 07:00 | 4.347 | 4.987 | 0.4 | 0.83117 | 0 | 0.83117 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 07:00 | 4.362 | 4.566 | 0.4 | 0.761 | 0 | 0.761 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 07:00 | 4.337 | 5.183 | 0.3 | 0.86383 | 0 | 0.86383 | 0 | 0.3 | 0 | 0.3 |  | 21-03-2026 07:00 | 3.046 | 3.623 | 0.2 | 0.60383 | 0 | 0.60383 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 07:00 | 3.056 | 3.204 | 0.2 | 0.534 | 0 | 0.534 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 07:00 | 3.087 | 3.24 | 0.2 | 0.54 | 0 | 0.54 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 07:00 | 3.202 | 3.535 | 0.4 | 0.58917 | 0 | 0.58917 | 0 | 0.4 | 0 | 0.4 |  | 21-03-2026 07:00 | 2.894 | 3.038 | 0.2 | 0.50633 | 0 | 0.50633 | 0 | 0.2 | 0 | 0.2 |  | 21-03-2026 07:00 | 5.9943 | 0 | 5.9943 | 0 | 2.7 | 0 | 2.7
[110 empty] | Total: - | 16134.5913 | #VALUE! | #VALUE! |  | 16137.9 | #VALUE! | #VALUE!
Sum:- | 0 |  | 12388.397 |  | 82415 |  |  |  |  | 2096.1 | #VALUE! | #VALUE! | 0.97825 |  | 11510.473 |  | 79671.5 |  |  |  |  | 2116.5 | #VALUE! | #VALUE! | 0.98589 |  | 12399.971 |  | 81927.6 |  |  |  |  | 2084.2 | #VALUE! | #VALUE! | 0.97579 |  | 12497.752 |  | 82618.2 |  |  |  |  | 2100.6 | #VALUE! | #VALUE! | 0.98469 |  | 9336.078 |  | 61738.8 |  |  |  |  | 1571.8 | #VALUE! | #VALUE! | 0.98585 |  | 9238.71 |  | 61452.1 |  |  |  |  | 1560.7 | #VALUE! | #VALUE! | 0.98388 |  | 9223.498 |  | 61335.9 |  |  |  |  | 1558.4 | #VALUE! | #VALUE! | 0.98327 |  | 9280.337 |  | 61699.5 |  |  |  |  | 1566.6 | #VALUE! | #VALUE! | 0.9704 |  | 8788.946 |  | 58425.5 |  |  |  |  | 1483 | #VALUE! | #VALUE! | 0.98572

## 22 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual | Inverter No. | Efficiency
22-03-2026 19:00 | 2 | 30.42 | 0 | 0 | 1885.3 | 0 | 0.12745 | -0.12745 | 0.76467 | 0 | 0.12562 | -0.12562 |  | 22-03-2026 19:00 | 0 | 0 | 1898.5 | 0 | 0.12745 | -0.12745 | 0.76467 | 0 | 0.12562 | -0.12562 |  | 22-03-2026 19:00 | 0 | 0 | 1869.2 | 0 | 0.12745 | -0.12745 | 0.76467 | 0 | 0.12562 | -0.12562 |  | 22-03-2026 19:00 | 0 | 0 | 1886 | 0 | 0.12745 | -0.12745 | 0.76467 | 0 | 0.12562 | -0.12562 |  | 22-03-2026 19:00 | 0 | 0 | 1407.4 | 0 | 0.094404 | -0.094404 | 0.56642 | 0 | 0.093054 | -0.093054 |  | 22-03-2026 19:00 | 0 | 0 | 1399.8 | 0 | 0.094404 | -0.094404 | 0.56642 | 0 | 0.093054 | -0.093054 |  | 22-03-2026 19:00 | 0 | 0 | 1398.2 | 0 | 0.094404 | -0.094404 | 0.56642 | 0 | 0.093054 | -0.093054 |  | 22-03-2026 19:00 | 0 | 0 | 1407.4 | 0 | 0.094404 | -0.094404 | 0.56642 | 0 | 0.093054 | -0.093054 |  | 22-03-2026 19:00 | 0 | 0 | 1331.7 | 0 | 0.089814 | -0.089814 | 0.53888 | 0 | 0.088529 | -0.088529 |  | 22-03-2026 19:00 | 0 | 0.97721 | -0.97721 | 5.8633 | 0 | 0.96324 | -0.96324 | 0 | 1 | 98.68%
22-03-2026 18:50 | 0 | 31.28 | 0 | 0 | 1885.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1898.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1869.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1407.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1399.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1398.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1407.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 1331.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22-03-2026 18:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 98.9%
22-03-2026 18:40 | 0 | 32.43 | 0.49 | 0.515 | 1885.3 | 0.085833 | 0 | 0.085833 | 0 | 0.2 | 0 | 0.2 |  | 22-03-2026 18:40 | 0.711 | 1.092 | 1898.5 | 0.182 | 0 | 0.182 | 0 | 0.2 | 0 | 0.2 |  | 22-03-2026 18:40 | 0.536 | 0.564 | 1869.2 | 0.094 | 0 | 0.094 | 0 | 0.2 | 0 | 0.2 |  | 22-03-2026 18:40 | 0.553 | 1.058 | 1886 | 0.17633 | 0 | 0.17633 | 0 | 0.2 | 0 | 0.2 |  | 22-03-2026 18:40 | 0.202 | 0.448 | 1407.4 | 0.074667 | 0 | 0.074667 | 0 | 0.1 | 0 | 0.1 |  | 22-03-2026 18:40 | 0.219 | 0.23 | 1399.8 | 0.038333 | 0 | 0.038333 | 0 | 0.1 | 0 | 0.1 |  | 22-03-2026 18:40 | 0.153 | 0.161 | 1398.2 | 0.026833 | 0 | 0.026833 | 0 | 0.1 | 0 | 0.1 |  | 22-03-2026 18:40 | 0.36 | 0.714 | 1407.4 | 0.119 | 0 | 0.119 | 0 | 0.1 | 0 | 0.1 |  | 22-03-2026 18:40 | 0.208 | 0.219 | 1331.7 | 0.0365 | 0 | 0.0365 | 0 | 0.1 | 0 | 0.1 |  | 22-03-2026 18:40 | 0.8335 | 0 | 0.8335 | 0 | 1.3 | 0 | 1.3 | -0.4665 | 3 | 97.31%
22-03-2026 18:30 | 3 | 45.35 | 2.122 | 2.118 | 1885.1 | 0.353 | 0.18099 | 0.17201 | 1.0859 | 0.7 | 0.1784 | 0.5216 |  | 22-03-2026 18:30 | 2.043 | 2.625 | 1898.3 | 0.4375 | 0.18099 | 0.25651 | 1.0859 | 0.8 | 0.1784 | 0.6216 |  | 22-03-2026 18:30 | 2.013 | 2.116 | 1869 | 0.35267 | 0.18099 | 0.17168 | 1.0859 | 0.7 | 0.1784 | 0.5216 |  | 22-03-2026 18:30 | 1.916 | 2.35 | 1885.8 | 0.39167 | 0.18099 | 0.21068 | 1.0859 | 0.7 | 0.1784 | 0.5216 |  | 22-03-2026 18:30 | 1.361 | 1.492 | 1407.3 | 0.24867 | 0.13406 | 0.1146 | 0.80438 | 0.5 | 0.13215 | 0.36785 |  | 22-03-2026 18:30 | 1.33 | 1.398 | 1399.7 | 0.233 | 0.13406 | 0.098937 | 0.80438 | 0.5 | 0.13215 | 0.36785 |  | 22-03-2026 18:30 | 1.323 | 1.4 | 1398.1 | 0.23333 | 0.13406 | 0.09927 | 0.80438 | 0.5 | 0.13215 | 0.36785 |  | 22-03-2026 18:30 | 1.461 | 1.792 | 1407.3 | 0.29867 | 0.13406 | 0.1646 | 0.80438 | 0.5 | 0.13215 | 0.36785 |  | 22-03-2026 18:30 | 1.22 | 1.283 | 1331.6 | 0.21383 | 0.12754 | 0.086289 | 0.76527 | 0.4 | 0.12572 | 0.27428 |  | 22-03-2026 18:30 | 2.7623 | 1.3877 | 1.3746 | 8.3264 | 5.3 | 1.3679 | 3.9321 | -2.5377 | 4 | 98.29%
22-03-2026 18:20 | 20 | 46.49 | 7.951 | 8.29 | 1884.4 | 1.3817 | 1.2014 | 0.18028 | 7.2083 | 2 | 1.1842 | 0.81579 |  | 22-03-2026 18:20 | 8.744 | 9.12 | 1897.5 | 1.52 | 1.2014 | 0.31861 | 7.2083 | 2 | 1.1842 | 0.81579 |  | 22-03-2026 18:20 | 7.658 | 7.999 | 1868.3 | 1.3332 | 1.2014 | 0.13178 | 7.2083 | 1.9 | 1.1842 | 0.71579 |  | 22-03-2026 18:20 | 7.709 | 8.042 | 1885.1 | 1.3403 | 1.2014 | 0.13895 | 7.2083 | 1.9 | 1.1842 | 0.71579 |  | 22-03-2026 18:20 | 5.693 | 5.961 | 1406.8 | 0.9935 | 0.88992 | 0.10358 | 5.3395 | 1.4 | 0.87719 | 0.52281 |  | 22-03-2026 18:20 | 5.464 | 5.718 | 1399.2 | 0.953 | 0.88992 | 0.063083 | 5.3395 | 1.4 | 0.87719 | 0.52281 |  | 22-03-2026 18:20 | 5.57 | 5.81 | 1397.6 | 0.96833 | 0.88992 | 0.078417 | 5.3395 | 1.4 | 0.87719 | 0.52281 |  | 22-03-2026 18:20 | 5.548 | 6.086 | 1406.8 | 1.0143 | 0.88992 | 0.12442 | 5.3395 | 1.4 | 0.87719 | 0.52281 |  | 22-03-2026 18:20 | 5.125 | 5.403 | 1331.2 | 0.9005 | 0.84665 | 0.053855 | 5.0799 | 1.4 | 0.83454 | 0.56546 |  | 22-03-2026 18:20 | 10.4048 | 9.2119 | 1.193 | 55.2712 | 14.8 | 9.0801 | 5.7199 | -4.3952 | 5 | 98.52%
22-03-2026 18:10 | 34 | 47.93 | 12.512 | 12.94 | 1882.4 | 2.1567 | 2.0312 | 0.12544 | 12.1874 | 2.4 | 2.0022 | 0.39782 |  | 22-03-2026 18:10 | 12.73 | 13.295 | 1895.5 | 2.2158 | 2.0312 | 0.18461 | 12.1874 | 2.5 | 2.0022 | 0.49782 |  | 22-03-2026 18:10 | 12.525 | 12.96 | 1866.4 | 2.16 | 2.0312 | 0.12877 | 12.1874 | 2.4 | 2.0022 | 0.39782 |  | 22-03-2026 18:10 | 12.639 | 13.069 | 1883.2 | 2.1782 | 2.0312 | 0.14694 | 12.1874 | 2.5 | 2.0022 | 0.49782 |  | 22-03-2026 18:10 | 9.227 | 9.595 | 1405.4 | 1.5992 | 1.5046 | 0.094554 | 9.0277 | 1.7 | 1.4831 | 0.2169 |  | 22-03-2026 18:10 | 9.052 | 9.412 | 1397.8 | 1.5687 | 1.5046 | 0.064054 | 9.0277 | 1.8 | 1.4831 | 0.3169 |  | 22-03-2026 18:10 | 9.127 | 9.491 | 1396.2 | 1.5818 | 1.5046 | 0.07722 | 9.0277 | 1.8 | 1.4831 | 0.3169 |  | 22-03-2026 18:10 | 9.084 | 9.676 | 1405.4 | 1.6127 | 1.5046 | 0.10805 | 9.0277 | 1.8 | 1.4831 | 0.3169 |  | 22-03-2026 18:10 | 8.501 | 8.851 | 1329.8 | 1.4752 | 1.4315 | 0.043714 | 8.5887 | 1.6 | 1.411 | 0.18902 |  | 22-03-2026 18:10 | 16.5482 | 15.5748 | 0.97335 | 93.4489 | 18.5 | 15.3521 | 3.1479 | -1.9518 | 6 | 98.31%
22-03-2026 18:00 | 54 | 48.79 | 19.772 | 20.169 | 1880 | 3.3615 | 3.2155 | 0.14599 | 19.2931 | 3.9 | 3.1695 | 0.73047 |  | 22-03-2026 18:00 | 20.465 | 21.12 | 1893 | 3.52 | 3.2155 | 0.30449 | 19.2931 | 3.8 | 3.1695 | 0.63047 |  | 22-03-2026 18:00 | 19.436 | 19.943 | 1864 | 3.3238 | 3.2155 | 0.10832 | 19.2931 | 3.8 | 3.1695 | 0.63047 |  | 22-03-2026 18:00 | 19.892 | 20.408 | 1880.7 | 3.4013 | 3.2155 | 0.18582 | 19.2931 | 3.8 | 3.1695 | 0.63047 |  | 22-03-2026 18:00 | 14.488 | 14.925 | 1403.7 | 2.4875 | 2.3819 | 0.10564 | 14.2912 | 2.8 | 2.3478 | 0.4522 |  | 22-03-2026 18:00 | 14.366 | 14.807 | 1396 | 2.4678 | 2.3819 | 0.085974 | 14.2912 | 2.7 | 2.3478 | 0.3522 |  | 22-03-2026 18:00 | 14.34 | 14.788 | 1394.4 | 2.4647 | 2.3819 | 0.082808 | 14.2912 | 2.7 | 2.3478 | 0.3522 |  | 22-03-2026 18:00 | 14.455 | 15.229 | 1403.6 | 2.5382 | 2.3819 | 0.15631 | 14.2912 | 2.7 | 2.3478 | 0.3522 |  | 22-03-2026 18:00 | 13.612 | 14.046 | 1328.2 | 2.341 | 2.266 | 0.074956 | 13.5963 | 2.6 | 2.2336 | 0.36636 |  | 22-03-2026 18:00 | 25.9058 | 24.6555 | 1.2503 | 147.9331 | 28.8 | 24.3029 | 4.4971 | -2.8942 | 7 | 98.16%
22-03-2026 17:50 | 68 | 49.94 | 25.013 | 25.584 | 1876.1 | 4.264 | 4.0314 | 0.23262 | 24.1883 | 4.6 | 3.9737 | 0.62627 |  | 22-03-2026 17:50 | 25.176 | 25.824 | 1889.2 | 4.304 | 4.0314 | 0.27262 | 24.1883 | 4.6 | 3.9737 | 0.62627 |  | 22-03-2026 17:50 | 24.703 | 25.282 | 1860.2 | 4.2137 | 4.0314 | 0.18228 | 24.1883 | 4.5 | 3.9737 | 0.52627 |  | 22-03-2026 17:50 | 25.025 | 25.609 | 1876.9 | 4.2682 | 4.0314 | 0.23678 | 24.1883 | 4.6 | 3.9737 | 0.62627 |  | 22-03-2026 17:50 | 18.261 | 18.745 | 1400.9 | 3.1242 | 2.9862 | 0.13796 | 17.9173 | 3.4 | 2.9435 | 0.45649 |  | 22-03-2026 17:50 | 18.133 | 18.689 | 1393.3 | 3.1148 | 2.9862 | 0.12862 | 17.9173 | 3.4 | 2.9435 | 0.45649 |  | 22-03-2026 17:50 | 18.144 | 18.626 | 1391.7 | 3.1043 | 2.9862 | 0.11812 | 17.9173 | 3.4 | 2.9435 | 0.45649 |  | 22-03-2026 17:50 | 18.264 | 19.143 | 1400.9 | 3.1905 | 2.9862 | 0.20429 | 17.9173 | 3.4 | 2.9435 | 0.45649 |  | 22-03-2026 17:50 | 17.232 | 17.694 | 1325.6 | 2.949 | 2.841 | 0.10799 | 17.046 | 3.3 | 2.8004 | 0.49962 |  | 22-03-2026 17:50 | 32.5327 | 30.9114 | 1.6213 | 185.4682 | 35.2 | 30.4693 | 4.7307 | -2.6673 | 8 | 97.09%
22-03-2026 17:40 | 85 | 50.51 | 30.918 | 31.526 | 1871.5 | 5.2543 | 5.0282 | 0.22612 | 30.1693 | 4.5 | 4.9563 | -0.45631 |  | 22-03-2026 17:40 | 30.769 | 31.381 | 1884.6 | 5.2302 | 5.0282 | 0.20195 | 30.1693 | 4.7 | 4.9563 | -0.25631 |  | 22-03-2026 17:40 | 30.152 | 30.749 | 1855.7 | 5.1248 | 5.0282 | 0.09662 | 30.1693 | 4.7 | 4.9563 | -0.25631 |  | 22-03-2026 17:40 | 30.639 | 31.252 | 1872.3 | 5.2087 | 5.0282 | 0.18045 | 30.1693 | 4.7 | 4.9563 | -0.25631 |  | 22-03-2026 17:40 | 22.496 | 23.042 | 1397.5 | 3.8403 | 3.7246 | 0.11573 | 22.3476 | 3.5 | 3.6713 | -0.17134 |  | 22-03-2026 17:40 | 22.34 | 22.88 | 1389.9 | 3.8133 | 3.7246 | 0.088731 | 22.3476 | 3.5 | 3.6713 | -0.17134 |  | 22-03-2026 17:40 | 22.184 | 22.756 | 1388.3 | 3.7927 | 3.7246 | 0.068064 | 22.3476 | 3.4 | 3.6713 | -0.27134 |  | 22-03-2026 17:40 | 22.407 | 23.373 | 1397.5 | 3.8955 | 3.7246 | 0.1709 | 22.3476 | 3.6 | 3.6713 | -0.071341 |  | 22-03-2026 17:40 | 21.341 | 21.87 | 1322.3 | 3.645 | 3.5435 | 0.1015 | 21.261 | 3.2 | 3.4928 | -0.29283 |  | 22-03-2026 17:40 | 39.8048 | 38.5548 | 1.2501 | 231.3286 | 35.8 | 38.0034 | -2.2034 | 4.0048 | 9 | 98.49%
22-03-2026 17:30 | 174 | 51.09 | 0 | 0 | 1867 | 0 | 10.2701 | -10.2701 | 61.6206 | 0 | 10.1232 | -10.1232 |  | 22-03-2026 17:30 | 0 | 0 | 1879.9 | 0 | 10.2701 | -10.2701 | 61.6206 | 0 | 10.1232 | -10.1232 |  | 22-03-2026 17:30 | 0 | 0 | 1851 | 0 | 10.2701 | -10.2701 | 61.6206 | 0 | 10.1232 | -10.1232 |  | 22-03-2026 17:30 | 0 | 0 | 1867.6 | 0 | 10.2701 | -10.2701 | 61.6206 | 0 | 10.1232 | -10.1232 |  | 22-03-2026 17:30 | 0 | 0 | 1394 | 0 | 7.6075 | -7.6075 | 45.6449 | 0 | 7.4987 | -7.4987 |  | 22-03-2026 17:30 | 0 | 0 | 1386.4 | 0 | 7.6075 | -7.6075 | 45.6449 | 0 | 7.4987 | -7.4987 |  | 22-03-2026 17:30 | 0 | 0 | 1384.9 | 0 | 7.6075 | -7.6075 | 45.6449 | 0 | 7.4987 | -7.4987 |  | 22-03-2026 17:30 | 0 | 0 | 1393.9 | 0 | 7.6075 | -7.6075 | 45.6449 | 0 | 7.4987 | -7.4987 |  | 22-03-2026 17:30 | 0 | 0 | 1319.1 | 0 | 7.2376 | -7.2376 | 43.4255 | 0 | 7.1341 | -7.1341 |  | 22-03-2026 17:30 | 0 | 78.7479 | -78.7479 | 472.4876 | 0 | 77.6218 | -77.6218 | 0
22-03-2026 17:20 | 273 | 51.09 | 0 | 0 | 1867 | 0 | 16.1134 | -16.1134 | 96.6806 | 0 | 15.883 | -15.883 |  | 22-03-2026 17:20 | 0 | 0 | 1879.9 | 0 | 16.1134 | -16.1134 | 96.6806 | 0 | 15.883 | -15.883 |  | 22-03-2026 17:20 | 0 | 0 | 1851 | 0 | 16.1134 | -16.1134 | 96.6806 | 0 | 15.883 | -15.883 |  | 22-03-2026 17:20 | 0 | 0 | 1867.6 | 0 | 16.1134 | -16.1134 | 96.6806 | 0 | 15.883 | -15.883 |  | 22-03-2026 17:20 | 0 | 0 | 1394 | 0 | 11.9359 | -11.9359 | 71.6153 | 0 | 11.7652 | -11.7652 |  | 22-03-2026 17:20 | 0 | 0 | 1386.4 | 0 | 11.9359 | -11.9359 | 71.6153 | 0 | 11.7652 | -11.7652 |  | 22-03-2026 17:20 | 0 | 0 | 1384.9 | 0 | 11.9359 | -11.9359 | 71.6153 | 0 | 11.7652 | -11.7652 |  | 22-03-2026 17:20 | 0 | 0 | 1393.9 | 0 | 11.9359 | -11.9359 | 71.6153 | 0 | 11.7652 | -11.7652 |  | 22-03-2026 17:20 | 0 | 0 | 1319.1 | 0 | 11.3555 | -11.3555 | 68.1331 | 0 | 11.1931 | -11.1931 |  | 22-03-2026 17:20 | 0 | 123.5528 | -123.5528 | 741.3168 | 0 | 121.786 | -121.786 | 0
22-03-2026 17:10 | 248 | 50.8 | 0 | 0 | 1867 | 0 | 14.6542 | -14.6542 | 87.9252 | 0 | 14.4446 | -14.4446 |  | 22-03-2026 17:10 | 0 | 0 | 1879.9 | 0 | 14.6542 | -14.6542 | 87.9252 | 0 | 14.4446 | -14.4446 |  | 22-03-2026 17:10 | 0 | 0 | 1851 | 0 | 14.6542 | -14.6542 | 87.9252 | 0 | 14.4446 | -14.4446 |  | 22-03-2026 17:10 | 0 | 0 | 1867.6 | 0 | 14.6542 | -14.6542 | 87.9252 | 0 | 14.4446 | -14.4446 |  | 22-03-2026 17:10 | 0 | 0 | 1394 | 0 | 10.855 | -10.855 | 65.1298 | 0 | 10.6997 | -10.6997 |  | 22-03-2026 17:10 | 0 | 0 | 1386.4 | 0 | 10.855 | -10.855 | 65.1298 | 0 | 10.6997 | -10.6997 |  | 22-03-2026 17:10 | 0 | 0 | 1384.9 | 0 | 10.855 | -10.855 | 65.1298 | 0 | 10.6997 | -10.6997 |  | 22-03-2026 17:10 | 0 | 0 | 1393.9 | 0 | 10.855 | -10.855 | 65.1298 | 0 | 10.6997 | -10.6997 |  | 22-03-2026 17:10 | 0 | 0 | 1319.1 | 0 | 10.3272 | -10.3272 | 61.9629 | 0 | 10.1795 | -10.1795 |  | 22-03-2026 17:10 | 0 | 112.3638 | -112.3638 | 674.1829 | 0 | 110.757 | -110.757 | 0
22-03-2026 17:00 | 302 | 50.8 | 0 | 0 | 1867 | 0 | 17.845 | -17.845 | 107.0702 | 0 | 17.5899 | -17.5899 |  | 22-03-2026 17:00 | 0 | 0 | 1879.9 | 0 | 17.845 | -17.845 | 107.0702 | 0 | 17.5899 | -17.5899 |  | 22-03-2026 17:00 | 0 | 0 | 1851 | 0 | 17.845 | -17.845 | 107.0702 | 0 | 17.5899 | -17.5899 |  | 22-03-2026 17:00 | 0 | 0 | 1867.6 | 0 | 17.845 | -17.845 | 107.0702 | 0 | 17.5899 | -17.5899 |  | 22-03-2026 17:00 | 0 | 0 | 1394 | 0 | 13.2185 | -13.2185 | 79.3113 | 0 | 13.0295 | -13.0295 |  | 22-03-2026 17:00 | 0 | 0 | 1386.4 | 0 | 13.2185 | -13.2185 | 79.3113 | 0 | 13.0295 | -13.0295 |  | 22-03-2026 17:00 | 0 | 0 | 1384.9 | 0 | 13.2185 | -13.2185 | 79.3113 | 0 | 13.0295 | -13.0295 |  | 22-03-2026 17:00 | 0 | 0 | 1393.9 | 0 | 13.2185 | -13.2185 | 79.3113 | 0 | 13.0295 | -13.0295 |  | 22-03-2026 17:00 | 0 | 0 | 1319.1 | 0 | 12.5758 | -12.5758 | 75.4548 | 0 | 12.396 | -12.396 |  | 22-03-2026 17:00 | 0 | 136.8301 | -136.8301 | 820.9808 | 0 | 134.8735 | -134.8735 | 0
22-03-2026 16:50 | 362 | 50.51 | 0 | 0 | 1867 | 0 | 21.4143 | -21.4143 | 128.4856 | 0 | 21.108 | -21.108 |  | 22-03-2026 16:50 | 0 | 0 | 1879.9 | 0 | 21.4143 | -21.4143 | 128.4856 | 0 | 21.108 | -21.108 |  | 22-03-2026 16:50 | 0 | 0 | 1851 | 0 | 21.4143 | -21.4143 | 128.4856 | 0 | 21.108 | -21.108 |  | 22-03-2026 16:50 | 0 | 0 | 1867.6 | 0 | 21.4143 | -21.4143 | 128.4856 | 0 | 21.108 | -21.108 |  | 22-03-2026 16:50 | 0 | 0 | 1394 | 0 | 15.8624 | -15.8624 | 95.1745 | 0 | 15.6356 | -15.6356 |  | 22-03-2026 16:50 | 0 | 0 | 1386.4 | 0 | 15.8624 | -15.8624 | 95.1745 | 0 | 15.6356 | -15.6356 |  | 22-03-2026 16:50 | 0 | 0 | 1384.9 | 0 | 15.8624 | -15.8624 | 95.1745 | 0 | 15.6356 | -15.6356 |  | 22-03-2026 16:50 | 0 | 0 | 1393.9 | 0 | 15.8624 | -15.8624 | 95.1745 | 0 | 15.6356 | -15.6356 |  | 22-03-2026 16:50 | 0 | 0 | 1319.1 | 0 | 15.0911 | -15.0911 | 90.5468 | 0 | 14.8753 | -14.8753 |  | 22-03-2026 16:50 | 0 | 164.1979 | -164.1979 | 985.1875 | 0 | 161.8499 | -161.8499 | 0
22-03-2026 16:40 | 257 | 51.09 | 0 | 0 | 1867 | 0 | 15.1691 | -15.1691 | 91.0144 | 0 | 14.9521 | -14.9521 |  | 22-03-2026 16:40 | 0 | 0 | 1879.9 | 0 | 15.1691 | -15.1691 | 91.0144 | 0 | 14.9521 | -14.9521 |  | 22-03-2026 16:40 | 0 | 0 | 1851 | 0 | 15.1691 | -15.1691 | 91.0144 | 0 | 14.9521 | -14.9521 |  | 22-03-2026 16:40 | 0 | 0 | 1867.6 | 0 | 15.1691 | -15.1691 | 91.0144 | 0 | 14.9521 | -14.9521 |  | 22-03-2026 16:40 | 0 | 0 | 1394 | 0 | 11.2363 | -11.2363 | 67.4181 | 0 | 11.0757 | -11.0757 |  | 22-03-2026 16:40 | 0 | 0 | 1386.4 | 0 | 11.2363 | -11.2363 | 67.4181 | 0 | 11.0757 | -11.0757 |  | 22-03-2026 16:40 | 0 | 0 | 1384.9 | 0 | 11.2363 | -11.2363 | 67.4181 | 0 | 11.0757 | -11.0757 |  | 22-03-2026 16:40 | 0 | 0 | 1393.9 | 0 | 11.2363 | -11.2363 | 67.4181 | 0 | 11.0757 | -11.0757 |  | 22-03-2026 16:40 | 0 | 0 | 1319.1 | 0 | 10.69 | -10.69 | 64.1399 | 0 | 10.5371 | -10.5371 |  | 22-03-2026 16:40 | 0 | 116.3116 | -116.3116 | 697.8697 | 0 | 114.6484 | -114.6484 | 0
22-03-2026 16:30 | 507 | 50.8 | 0 | 0 | 1867 | 0 | 29.9584 | -29.9584 | 179.7503 | 0 | 29.53 | -29.53 |  | 22-03-2026 16:30 | 0 | 0 | 1879.9 | 0 | 29.9584 | -29.9584 | 179.7503 | 0 | 29.53 | -29.53 |  | 22-03-2026 16:30 | 0 | 0 | 1851 | 0 | 29.9584 | -29.9584 | 179.7503 | 0 | 29.53 | -29.53 |  | 22-03-2026 16:30 | 0 | 0 | 1867.6 | 0 | 29.9584 | -29.9584 | 179.7503 | 0 | 29.53 | -29.53 |  | 22-03-2026 16:30 | 0 | 0 | 1394 | 0 | 22.1914 | -22.1914 | 133.1484 | 0 | 21.8741 | -21.8741 |  | 22-03-2026 16:30 | 0 | 0 | 1386.4 | 0 | 22.1914 | -22.1914 | 133.1484 | 0 | 21.8741 | -21.8741 |  | 22-03-2026 16:30 | 0 | 0 | 1384.9 | 0 | 22.1914 | -22.1914 | 133.1484 | 0 | 21.8741 | -21.8741 |  | 22-03-2026 16:30 | 0 | 0 | 1393.9 | 0 | 22.1914 | -22.1914 | 133.1484 | 0 | 21.8741 | -21.8741 |  | 22-03-2026 16:30 | 0 | 0 | 1319.1 | 0 | 21.1124 | -21.1124 | 126.6742 | 0 | 20.8105 | -20.8105 |  | 22-03-2026 16:30 | 0 | 229.7115 | -229.7115 | 1378.269 | 0 | 226.4266 | -226.4266 | 0
22-03-2026 16:20 | 253 | 50.51 | 0 | 0 | 1867 | 0 | 14.9663 | -14.9663 | 89.798 | 0 | 14.7523 | -14.7523 |  | 22-03-2026 16:20 | 0 | 0 | 1879.9 | 0 | 14.9663 | -14.9663 | 89.798 | 0 | 14.7523 | -14.7523 |  | 22-03-2026 16:20 | 0 | 0 | 1851 | 0 | 14.9663 | -14.9663 | 89.798 | 0 | 14.7523 | -14.7523 |  | 22-03-2026 16:20 | 0 | 0 | 1867.6 | 0 | 14.9663 | -14.9663 | 89.798 | 0 | 14.7523 | -14.7523 |  | 22-03-2026 16:20 | 0 | 0 | 1394 | 0 | 11.0862 | -11.0862 | 66.517 | 0 | 10.9276 | -10.9276 |  | 22-03-2026 16:20 | 0 | 0 | 1386.4 | 0 | 11.0862 | -11.0862 | 66.517 | 0 | 10.9276 | -10.9276 |  | 22-03-2026 16:20 | 0 | 0 | 1384.9 | 0 | 11.0862 | -11.0862 | 66.517 | 0 | 10.9276 | -10.9276 |  | 22-03-2026 16:20 | 0 | 0 | 1393.9 | 0 | 11.0862 | -11.0862 | 66.517 | 0 | 10.9276 | -10.9276 |  | 22-03-2026 16:20 | 0 | 0 | 1319.1 | 0 | 10.5471 | -10.5471 | 63.2827 | 0 | 10.3963 | -10.3963 |  | 22-03-2026 16:20 | 0 | 114.7571 | -114.7571 | 688.5427 | 0 | 113.1161 | -113.1161 | 0
22-03-2026 16:10 | 391 | 50.8 |  |  |  | 0 | 23.104 | -23.104 | 138.624 | 0 | 22.7736 | -22.7736 |  | 22-03-2026 16:10 | 0 | 0 | 1879.9 | 0 | 23.104 | -23.104 | 138.624 | 0 | 22.7736 | -22.7736 |  | 22-03-2026 16:10 | 0 | 0 | 1851 | 0 | 23.104 | -23.104 | 138.624 | 0 | 22.7736 | -22.7736 |  | 22-03-2026 16:10 | 0 | 0 | 1867.6 | 0 | 23.104 | -23.104 | 138.624 | 0 | 22.7736 | -22.7736 |  | 22-03-2026 16:10 | 0 | 0 | 1394 | 0 | 17.1141 | -17.1141 | 102.6845 | 0 | 16.8693 | -16.8693 |  | 22-03-2026 16:10 | 0 | 0 | 1386.4 | 0 | 17.1141 | -17.1141 | 102.6845 | 0 | 16.8693 | -16.8693 |  | 22-03-2026 16:10 | 0 | 0 | 1384.9 | 0 | 17.1141 | -17.1141 | 102.6845 | 0 | 16.8693 | -16.8693 |  | 22-03-2026 16:10 | 0 | 0 | 1393.9 | 0 | 17.1141 | -17.1141 | 102.6845 | 0 | 16.8693 | -16.8693 |  | 22-03-2026 16:10 | 0 | 0 | 1319.1 | 0 | 16.2819 | -16.2819 | 97.6915 | 0 | 16.0491 | -16.0491 |  | 22-03-2026 16:10 | 0 | 177.1542 | -177.1542 | 1062.9254 | 0 | 174.6209 | -174.6209 | 0
22-03-2026 16:00 | 612 | 50.51 | 0 | 0 | 1867 | 0 | 36.2031 | -36.2031 | 217.2188 | 0 | 35.6854 | -35.6854 |  | 22-03-2026 16:00 | 0 | 0 | 1879.9 | 0 | 36.2031 | -36.2031 | 217.2188 | 0 | 35.6854 | -35.6854 |  | 22-03-2026 16:00 | 0 | 0 | 1851 | 0 | 36.2031 | -36.2031 | 217.2188 | 0 | 35.6854 | -35.6854 |  | 22-03-2026 16:00 | 0 | 0 | 1867.6 | 0 | 36.2031 | -36.2031 | 217.2188 | 0 | 35.6854 | -35.6854 |  | 22-03-2026 16:00 | 0 | 0 | 1394 | 0 | 26.8171 | -26.8171 | 160.9028 | 0 | 26.4337 | -26.4337 |  | 22-03-2026 16:00 | 0 | 0 | 1386.4 | 0 | 26.8171 | -26.8171 | 160.9028 | 0 | 26.4337 | -26.4337 |  | 22-03-2026 16:00 | 0 | 0 | 1384.9 | 0 | 26.8171 | -26.8171 | 160.9028 | 0 | 26.4337 | -26.4337 |  | 22-03-2026 16:00 | 0 | 0 | 1393.9 | 0 | 26.8171 | -26.8171 | 160.9028 | 0 | 26.4337 | -26.4337 |  | 22-03-2026 16:00 | 0 | 0 | 1319.1 | 0 | 25.5132 | -25.5132 | 153.0791 | 0 | 25.1483 | -25.1483 |  | 22-03-2026 16:00 | 0 | 277.5943 | -277.5943 | 1665.5657 | 0 | 273.6247 | -273.6247 | 0
22-03-2026 15:50 | 353 | 50.23 | 0 | 0 | 1867 | 0 | 20.9043 | -20.9043 | 125.4261 | 0 | 20.6054 | -20.6054 |  | 22-03-2026 15:50 | 0 | 0 | 1879.9 | 0 | 20.9043 | -20.9043 | 125.4261 | 0 | 20.6054 | -20.6054 |  | 22-03-2026 15:50 | 0 | 0 | 1851 | 0 | 20.9043 | -20.9043 | 125.4261 | 0 | 20.6054 | -20.6054 |  | 22-03-2026 15:50 | 0 | 0 | 1867.6 | 0 | 20.9043 | -20.9043 | 125.4261 | 0 | 20.6054 | -20.6054 |  | 22-03-2026 15:50 | 0 | 0 | 1394 | 0 | 15.4847 | -15.4847 | 92.9082 | 0 | 15.2633 | -15.2633 |  | 22-03-2026 15:50 | 0 | 0 | 1386.4 | 0 | 15.4847 | -15.4847 | 92.9082 | 0 | 15.2633 | -15.2633 |  | 22-03-2026 15:50 | 0 | 0 | 1384.9 | 0 | 15.4847 | -15.4847 | 92.9082 | 0 | 15.2633 | -15.2633 |  | 22-03-2026 15:50 | 0 | 0 | 1393.9 | 0 | 15.4847 | -15.4847 | 92.9082 | 0 | 15.2633 | -15.2633 |  | 22-03-2026 15:50 | 0 | 0 | 1319.1 | 0 | 14.7318 | -14.7318 | 88.3906 | 0 | 14.5211 | -14.5211 |  | 22-03-2026 15:50 | 0 | 160.2879 | -160.2879 | 961.7277 | 0 | 157.9958 | -157.9958 | 0
22-03-2026 15:40 | 431 | 51.09 | 0 | 0 | 1867 | 0 | 25.4392 | -25.4392 | 152.635 | 0 | 25.0754 | -25.0754 |  | 22-03-2026 15:40 | 0 | 0 | 1879.9 | 0 | 25.4392 | -25.4392 | 152.635 | 0 | 25.0754 | -25.0754 |  | 22-03-2026 15:40 | 0 | 0 | 1851 | 0 | 25.4392 | -25.4392 | 152.635 | 0 | 25.0754 | -25.0754 |  | 22-03-2026 15:40 | 0 | 0 | 1867.6 | 0 | 25.4392 | -25.4392 | 152.635 | 0 | 25.0754 | -25.0754 |  | 22-03-2026 15:40 | 0 | 0 | 1394 | 0 | 18.8438 | -18.8438 | 113.063 | 0 | 18.5744 | -18.5744 |  | 22-03-2026 15:40 | 0 | 0 | 1386.4 | 0 | 18.8438 | -18.8438 | 113.063 | 0 | 18.5744 | -18.5744 |  | 22-03-2026 15:40 | 0 | 0 | 1384.9 | 0 | 18.8438 | -18.8438 | 113.063 | 0 | 18.5744 | -18.5744 |  | 22-03-2026 15:40 | 0 | 0 | 1393.9 | 0 | 18.8438 | -18.8438 | 113.063 | 0 | 18.5744 | -18.5744 |  | 22-03-2026 15:40 | 0 | 0 | 1319.1 | 0 | 17.9276 | -17.9276 | 107.5654 | 0 | 17.6712 | -17.6712 |  | 22-03-2026 15:40 | 0 | 195.0596 | -195.0596 | 1170.3573 | 0 | 192.2702 | -192.2702 | 0
22-03-2026 15:30 | 565 | 50.51 | 0 | 0 | 1867 | 0 | 33.4228 | -33.4228 | 200.537 | 0 | 32.9449 | -32.9449 |  | 22-03-2026 15:30 | 0 | 0 | 1879.9 | 0 | 33.4228 | -33.4228 | 200.537 | 0 | 32.9449 | -32.9449 |  | 22-03-2026 15:30 | 0 | 0 | 1851 | 0 | 33.4228 | -33.4228 | 200.537 | 0 | 32.9449 | -32.9449 |  | 22-03-2026 15:30 | 0 | 0 | 1867.6 | 0 | 33.4228 | -33.4228 | 200.537 | 0 | 32.9449 | -32.9449 |  | 22-03-2026 15:30 | 0 | 0 | 1394 | 0 | 24.7577 | -24.7577 | 148.5459 | 0 | 24.4036 | -24.4036 |  | 22-03-2026 15:30 | 0 | 0 | 1386.4 | 0 | 24.7577 | -24.7577 | 148.5459 | 0 | 24.4036 | -24.4036 |  | 22-03-2026 15:30 | 0 | 0 | 1384.9 | 0 | 24.7577 | -24.7577 | 148.5459 | 0 | 24.4036 | -24.4036 |  | 22-03-2026 15:30 | 0 | 0 | 1393.9 | 0 | 24.7577 | -24.7577 | 148.5459 | 0 | 24.4036 | -24.4036 |  | 22-03-2026 15:30 | 0 | 0 | 1319.1 | 0 | 23.5538 | -23.5538 | 141.323 | 0 | 23.217 | -23.217 |  | 22-03-2026 15:30 | 0 | 256.2758 | -256.2758 | 1537.6546 | 0 | 252.611 | -252.611 | 0
22-03-2026 15:20 | 655 | 51.09 | 0 | 0 | 1867 | 0 | 38.6605 | -38.6605 | 231.9627 | 0 | 38.1076 | -38.1076 |  | 22-03-2026 15:20 | 0 | 0 | 1879.9 | 0 | 38.6605 | -38.6605 | 231.9627 | 0 | 38.1076 | -38.1076 |  | 22-03-2026 15:20 | 0 | 0 | 1851 | 0 | 38.6605 | -38.6605 | 231.9627 | 0 | 38.1076 | -38.1076 |  | 22-03-2026 15:20 | 0 | 0 | 1867.6 | 0 | 38.6605 | -38.6605 | 231.9627 | 0 | 38.1076 | -38.1076 |  | 22-03-2026 15:20 | 0 | 0 | 1394 | 0 | 28.6374 | -28.6374 | 171.8242 | 0 | 28.2279 | -28.2279 |  | 22-03-2026 15:20 | 0 | 0 | 1386.4 | 0 | 28.6374 | -28.6374 | 171.8242 | 0 | 28.2279 | -28.2279 |  | 22-03-2026 15:20 | 0 | 0 | 1384.9 | 0 | 28.6374 | -28.6374 | 171.8242 | 0 | 28.2279 | -28.2279 |  | 22-03-2026 15:20 | 0 | 0 | 1393.9 | 0 | 28.6374 | -28.6374 | 171.8242 | 0 | 28.2279 | -28.2279 |  | 22-03-2026 15:20 | 0 | 0 | 1319.1 | 0 | 27.2449 | -27.2449 | 163.4695 | 0 | 26.8553 | -26.8553 |  | 22-03-2026 15:20 | 0 | 296.4362 | -296.4362 | 1778.6173 | 0 | 292.1972 | -292.1972 | 0
22-03-2026 15:10 | 755 | 52.81 | 0 | 0 | 1867 | 0 | 44.2676 | -44.2676 | 265.6055 | 13.3 | 43.6346 | -30.3346 |  | 22-03-2026 15:10 | 0 | 0 | 1879.9 | 0 | 44.2676 | -44.2676 | 265.6055 | 14.1 | 43.6346 | -29.5346 |  | 22-03-2026 15:10 | 0 | 0 | 1851 | 0 | 44.2676 | -44.2676 | 265.6055 | 13.1 | 43.6346 | -30.5346 |  | 22-03-2026 15:10 | 0 | 0 | 1867.6 | 0 | 44.2676 | -44.2676 | 265.6055 | 13.7 | 43.6346 | -29.9346 |  | 22-03-2026 15:10 | 0 | 0 | 1394 | 0 | 32.7908 | -32.7908 | 196.7448 | 10.2 | 32.3219 | -22.1219 |  | 22-03-2026 15:10 | 0 | 0 | 1386.4 | 0 | 32.7908 | -32.7908 | 196.7448 | 9.9 | 32.3219 | -22.4219 |  | 22-03-2026 15:10 | 0 | 0 | 1384.9 | 0 | 32.7908 | -32.7908 | 196.7448 | 10 | 32.3219 | -22.3219 |  | 22-03-2026 15:10 | 0 | 0 | 1393.9 | 0 | 32.7908 | -32.7908 | 196.7448 | 9.8 | 32.3219 | -22.5219 |  | 22-03-2026 15:10 | 0 | 0 | 1319.1 | 0 | 31.1964 | -31.1964 | 187.1783 | 9.8 | 30.7503 | -20.9503 |  | 22-03-2026 15:10 | 0 | 339.4299 | -339.4299 | 2036.5797 | 103.9 | 334.5761 | -230.6761 | -103.9
22-03-2026 15:00 | 848 | 51.37 | 287.395 | 291.642 | 1853.7 | 48.607 | 49.998 | -1.391 | 299.9882 | 48.4 | 49.2831 | -0.88305 | 0.98544 | 22-03-2026 15:00 | 303.143 | 308.229 | 1865.8 | 51.3715 | 49.998 | 1.3735 | 299.9882 | 49.1 | 49.2831 | -0.18305 | 0.9835 | 22-03-2026 15:00 | 285.395 | 294.71 | 1837.9 | 49.1183 | 49.998 | -0.87969 | 299.9882 | 48.3 | 49.2831 | -0.98305 | 0.96839 | 22-03-2026 15:00 | 289.08 | 293.84 | 1853.9 | 48.9733 | 49.998 | -1.0247 | 299.9882 | 48.1 | 49.2831 | -1.1831 | 0.9838 | 22-03-2026 15:00 | 213.589 | 216.798 | 1383.8 | 36.133 | 37.0356 | -0.90257 | 222.2134 | 36.6 | 36.506 | 0.094034 | 0.9852 | 22-03-2026 15:00 | 210.049 | 214.195 | 1376.5 | 35.6992 | 37.0356 | -1.3364 | 222.2134 | 36.1 | 36.506 | -0.40597 | 0.98064 | 22-03-2026 15:00 | 211.491 | 214.863 | 1374.9 | 35.8105 | 37.0356 | -1.2251 | 222.2134 | 36.1 | 36.506 | -0.40597 | 0.98431 | 22-03-2026 15:00 | 210.203 | 215.71 | 1384.1 | 35.9517 | 37.0356 | -1.0839 | 222.2134 | 36.3 | 36.506 | -0.20597 | 0.97447 | 22-03-2026 15:00 | 204.672 | 209.669 | 1309.3 | 34.9448 | 35.2348 | -0.28993 | 211.4086 | 33.7 | 34.7309 | -1.0309 | 0.97617 | 22-03-2026 15:00 | 376.6093 | 383.3692 | -6.7598 | 2300.215 | 372.7 | 377.887 | -5.187 | 3.9093
22-03-2026 14:50 | 855 | 51.09 | 299.016 | 290.048 | 1805.3 | 48.3413 | 50.4652 | -2.1238 | 302.791 | 95.3 | 49.7435 | 45.5565 | 1.0309 | 22-03-2026 14:50 | 243.572 | 248.683 | 1816.7 | 41.4472 | 50.4652 | -9.018 | 302.791 | 48.4 | 49.7435 | -1.3435 | 0.97945 | 22-03-2026 14:50 | 290.368 | 298.994 | 1789.6 | 49.8323 | 50.4652 | -0.63284 | 302.791 | 47.6 | 49.7435 | -2.1435 | 0.97115 | 22-03-2026 14:50 | 278.461 | 297.458 | 1805.8 | 49.5763 | 50.4652 | -0.88884 | 302.791 | 48.1 | 49.7435 | -1.6435 | 0.93614 | 22-03-2026 14:50 | 206.928 | 210.015 | 1347.2 | 35.0025 | 37.3816 | -2.3791 | 224.2896 | 35.4 | 36.8471 | -1.4471 | 0.9853 | 22-03-2026 14:50 | 209.284 | 212.385 | 1340.4 | 35.3975 | 37.3816 | -1.9841 | 224.2896 | 35 | 36.8471 | -1.8471 | 0.9854 | 22-03-2026 14:50 | 207.829 | 214.264 | 1338.8 | 35.7107 | 37.3816 | -1.6709 | 224.2896 | 34.8 | 36.8471 | -2.0471 | 0.96997 | 22-03-2026 14:50 | 210.816 | 220.19 | 1347.8 | 36.6983 | 37.3816 | -0.68327 | 224.2896 | 35.5 | 36.8471 | -1.3471 | 0.95743 | 22-03-2026 14:50 | 199.719 | 203.123 | 1275.6 | 33.8538 | 35.564 | -1.7101 | 213.3838 | 33.6 | 35.0554 | -1.4554 | 0.98324 | 22-03-2026 14:50 | 365.86 | 386.9511 | -21.0911 | 2321.7065 | 413.7 | 381.4177 | 32.2823 | -47.84
22-03-2026 14:40 | 830 | 51.09 |  |  |  | 0 | 48.9896 | -48.9896 | 293.9375 | 0 | 48.289 | -48.289 |  | 22-03-2026 14:40 | 270.852 | 273.167 | 1768.3 | 45.5278 | 48.9896 | -3.4617 | 293.9375 | 47.6 | 48.289 | -0.68903 | 0.99153 | 22-03-2026 14:40 | 281.89 | 289.475 | 1742 | 48.2458 | 48.9896 | -0.74375 | 293.9375 | 47.3 | 48.289 | -0.98903 | 0.9738 | 22-03-2026 14:40 | 285.113 | 289.837 | 1757.7 | 48.3062 | 48.9896 | -0.68341 | 293.9375 | 47.8 | 48.289 | -0.48903 | 0.9837 | 22-03-2026 14:40 | 214.982 | 218.189 | 1311.8 | 36.3648 | 36.2886 | 0.076255 | 217.7315 | 36.4 | 35.7697 | 0.63035 | 0.9853 | 22-03-2026 14:40 | 211.335 | 214.731 | 1305.4 | 35.7885 | 36.2886 | -0.50008 | 217.7315 | 35.9 | 35.7697 | 0.13035 | 0.98418 | 22-03-2026 14:40 | 215.1 | 220.966 | 1304 | 36.8277 | 36.2886 | 0.53909 | 217.7315 | 36 | 35.7697 | 0.23035 | 0.97345 | 22-03-2026 14:40 | 212.356 | 219.071 | 1312.3 | 36.5118 | 36.2886 | 0.22325 | 217.7315 | 35.6 | 35.7697 | -0.16965 | 0.96935 | 22-03-2026 14:40 | 200.209 | 203.196 | 1242 | 33.866 | 34.5241 | -0.65809 | 207.1445 | 33.8 | 34.0304 | -0.23039 | 0.9853 | 22-03-2026 14:40 | 321.4387 | 375.6367 | -54.1981 | 2253.8204 | 320.4 | 370.2651 | -49.8651 | 1.0387
22-03-2026 14:30 | 928 | 51.09 | 308.448 | 313.162 | 1710 | 52.1937 | 54.7739 | -2.5802 | 328.6434 | 51.5 | 53.9906 | -2.4906 | 0.98495 | 22-03-2026 14:30 | 311.973 | 317.336 | 1720.7 | 52.8893 | 54.7739 | -1.8846 | 328.6434 | 52.1 | 53.9906 | -1.8906 | 0.9831 | 22-03-2026 14:30 | 306.361 | 314.985 | 1694.7 | 52.4975 | 54.7739 | -2.2764 | 328.6434 | 53.4 | 53.9906 | -0.59063 | 0.97262 | 22-03-2026 14:30 | 310.394 | 315.762 | 1709.9 | 52.627 | 54.7739 | -2.1469 | 328.6434 | 52.7 | 53.9906 | -1.2906 | 0.983 | 22-03-2026 14:30 | 231.806 | 235.456 | 1275.4 | 39.2427 | 40.5733 | -1.3306 | 243.4395 | 38.7 | 39.9931 | -1.2931 | 0.9845 | 22-03-2026 14:30 | 229.319 | 233.608 | 1269.5 | 38.9347 | 40.5733 | -1.6386 | 243.4395 | 38.2 | 39.9931 | -1.7931 | 0.98164 | 22-03-2026 14:30 | 228.894 | 232.907 | 1268 | 38.8178 | 40.5733 | -1.7554 | 243.4395 | 38.3 | 39.9931 | -1.6931 | 0.98277 | 22-03-2026 14:30 | 229.276 | 236.369 | 1276.7 | 39.3948 | 40.5733 | -1.1784 | 243.4395 | 38.4 | 39.9931 | -1.5931 | 0.96999 | 22-03-2026 14:30 | 217.304 | 220.636 | 1208.2 | 36.7727 | 38.6004 | -1.8278 | 231.6026 | 36.2 | 38.0484 | -1.8484 | 0.9849 | 22-03-2026 14:30 | 403.3702 | 419.989 | -16.6188 | 2519.9341 | 399.5 | 413.9832 | -14.4832 | 3.8702
22-03-2026 14:20 | 942 | 51.09 | 313.729 | 319.057 | 1658.5 | 53.1762 | 55.6002 | -2.4241 | 333.6013 | 54.7 | 54.8051 | -0.10514 | 0.9833 | 22-03-2026 14:20 | 318.485 | 323.96 | 1668.6 | 53.9933 | 55.6002 | -1.6069 | 333.6013 | 57.8 | 54.8051 | 2.9949 | 0.9831 | 22-03-2026 14:20 | 312.49 | 321.238 | 1641.3 | 53.5397 | 55.6002 | -2.0606 | 333.6013 | 53 | 54.8051 | -1.8051 | 0.97277 | 22-03-2026 14:20 | 316.284 | 321.721 | 1657.2 | 53.6202 | 55.6002 | -1.9801 | 333.6013 | 54.9 | 54.8051 | 0.09486 | 0.9831 | 22-03-2026 14:20 | 235.685 | 239.371 | 1236.7 | 39.8952 | 41.1854 | -1.2902 | 247.1121 | 41.1 | 40.5964 | 0.5036 | 0.9846 | 22-03-2026 14:20 | 233.501 | 237.67 | 1231.3 | 39.6117 | 41.1854 | -1.5737 | 247.1121 | 40.6 | 40.5964 | 0.0036 | 0.98246 | 22-03-2026 14:20 | 233.317 | 237.769 | 1229.7 | 39.6282 | 41.1854 | -1.5572 | 247.1121 | 40.6 | 40.5964 | 0.0036 | 0.98128 | 22-03-2026 14:20 | 233.877 | 241.148 | 1238.3 | 40.1913 | 41.1854 | -0.99402 | 247.1121 | 40.8 | 40.5964 | 0.2036 | 0.96985 | 22-03-2026 14:20 | 221.237 | 224.471 | 1172 | 37.4118 | 39.1828 | -1.7709 | 235.0966 | 38.5 | 38.6224 | -0.12245 | 0.98559 | 22-03-2026 14:20 | 411.0675 | 426.3251 | -15.2576 | 2557.9503 | 422 | 420.2286 | 1.7714 | -10.9325
22-03-2026 14:10 | 1022 | 50.23 | 347.965 | 353.228 | 1603.8 | 58.8713 | 60.5219 | -1.6506 | 363.1316 | 32.6 | 59.6565 | -27.0565 | 0.9851 | 22-03-2026 14:10 | 333.783 | 339.279 | 1610.8 | 56.5465 | 60.5219 | -3.9754 | 363.1316 | 31.8 | 59.6565 | -27.8565 | 0.9838 | 22-03-2026 14:10 | 347.442 | 357.152 | 1588.3 | 59.5253 | 60.5219 | -0.99659 | 363.1316 | 31.4 | 59.6565 | -28.2565 | 0.97281 | 22-03-2026 14:10 | 345.657 | 351.028 | 1602.3 | 58.5047 | 60.5219 | -2.0173 | 363.1316 | 31.5 | 59.6565 | -28.1565 | 0.9847 | 22-03-2026 14:10 | 264.81 | 268.87 | 1195.6 | 44.8117 | 44.8311 | -0.01939 | 268.9863 | 23.7 | 44.19 | -20.49 | 0.9849 | 22-03-2026 14:10 | 259.57 | 263.84 | 1190.7 | 43.9733 | 44.8311 | -0.85772 | 268.9863 | 23.4 | 44.19 | -20.79 | 0.98382 | 22-03-2026 14:10 | 260.45 | 265.643 | 1189.1 | 44.2738 | 44.8311 | -0.55722 | 268.9863 | 23.6 | 44.19 | -20.59 | 0.98045 | 22-03-2026 14:10 | 260.52 | 268.553 | 1197.5 | 44.7588 | 44.8311 | -0.072223 | 268.9863 | 23.7 | 44.19 | -20.49 | 0.97009 | 22-03-2026 14:10 | 245.172 | 248.906 | 1133.5 | 41.4843 | 42.6512 | -1.1669 | 255.9072 | 22.7 | 42.0413 | -19.3413 | 0.985 | 22-03-2026 14:10 | 452.7498 | 464.0631 | -11.3133 | 2784.3788 | 244.4 | 457.427 | -213.027 | 208.3498
22-03-2026 14:00 | 504 | 49.94 | 172.31 | 174.703 | 1571.2 | 29.1172 | 29.8797 | -0.76249 | 179.2779 | 35.4 | 29.4524 | 5.9476 | 0.9863 | 22-03-2026 14:00 | 171.655 | 174.092 | 1579 | 29.0153 | 29.8797 | -0.86432 | 179.2779 | 35.2 | 29.4524 | 5.7476 | 0.986 | 22-03-2026 14:00 | 173.767 | 176.163 | 1556.9 | 29.3605 | 29.8797 | -0.51916 | 179.2779 | 35 | 29.4524 | 5.5476 | 0.9864 | 22-03-2026 14:00 | 180.921 | 183.471 | 1570.8 | 30.5785 | 29.8797 | 0.69884 | 179.2779 | 35.3 | 29.4524 | 5.8476 | 0.9861 | 22-03-2026 14:00 | 128.006 | 129.447 | 1171.9 | 21.5745 | 22.1331 | -0.55858 | 132.7985 | 26.4 | 21.8166 | 4.5834 | 0.98887 | 22-03-2026 14:00 | 132.577 | 134.391 | 1167.3 | 22.3985 | 22.1331 | 0.26542 | 132.7985 | 26.1 | 21.8166 | 4.2834 | 0.9865 | 22-03-2026 14:00 | 130.045 | 131.785 | 1165.5 | 21.9642 | 22.1331 | -0.16891 | 132.7985 | 26.4 | 21.8166 | 4.5834 | 0.9868 | 22-03-2026 14:00 | 130.111 | 132.357 | 1173.8 | 22.0595 | 22.1331 | -0.07358 | 132.7985 | 26.5 | 21.8166 | 4.6834 | 0.98303 | 22-03-2026 14:00 | 129.437 | 131.208 | 1110.8 | 21.868 | 21.0569 | 0.81112 | 126.3413 | 24.8 | 20.7558 | 4.0442 | 0.9865 | 22-03-2026 14:00 | 227.9362 | 229.1078 | -1.1717 | 1374.647 | 271.1 | 225.8316 | 45.2684 | -43.1638
22-03-2026 13:50 | 721 | 49.94 | 248.43 | 251.048 | 1535.8 | 41.8413 | 42.7445 | -0.90318 | 256.4671 | 43.9 | 42.1333 | 1.7667 | 0.98957 | 22-03-2026 13:50 | 261.232 | 265.372 | 1543.8 | 44.2287 | 42.7445 | 1.4842 | 256.4671 | 44.4 | 42.1333 | 2.2667 | 0.9844 | 22-03-2026 13:50 | 258.83 | 266.78 | 1521.9 | 44.4633 | 42.7445 | 1.7188 | 256.4671 | 44.2 | 42.1333 | 2.0667 | 0.9702 | 22-03-2026 13:50 | 259.886 | 261.866 | 1535.5 | 43.6443 | 42.7445 | 0.89982 | 256.4671 | 44.8 | 42.1333 | 2.6667 | 0.99244 | 22-03-2026 13:50 | 196.84 | 199.675 | 1145.5 | 33.2792 | 31.6626 | 1.6166 | 189.9756 | 33.8 | 31.2098 | 2.5902 | 0.9858 | 22-03-2026 13:50 | 195.214 | 198.301 | 1141.2 | 33.0502 | 31.6626 | 1.3876 | 189.9756 | 33.4 | 31.2098 | 2.1902 | 0.98443 | 22-03-2026 13:50 | 190.031 | 193.357 | 1139.1 | 32.2262 | 31.6626 | 0.56357 | 189.9756 | 32.9 | 31.2098 | 1.6902 | 0.9828 | 22-03-2026 13:50 | 193.253 | 199.936 | 1147.3 | 33.3227 | 31.6626 | 1.6601 | 189.9756 | 33.2 | 31.2098 | 1.9902 | 0.96657 | 22-03-2026 13:50 | 182.847 | 185.5 | 1086 | 30.9167 | 30.123 | 0.79362 | 180.7383 | 31.4 | 29.6923 | 1.7077 | 0.9857 | 22-03-2026 13:50 | 336.9725 | 327.7515 | 9.221 | 1966.5089 | 342 | 323.0646 | 18.9354 | -5.0275
22-03-2026 13:40 | 703 | 50.23 | 241.606 | 245.385 | 1491.9 | 40.8975 | 41.631 | -0.73353 | 249.7862 | 43.6 | 41.0357 | 2.5643 | 0.9846 | 22-03-2026 13:40 | 255.799 | 259.826 | 1499.4 | 43.3043 | 41.631 | 1.6733 | 249.7862 | 100 | 41.0357 | 58.9643 | 0.9845 | 22-03-2026 13:40 | 239.313 | 246.703 | 1477.7 | 41.1172 | 41.631 | -0.51386 | 249.7862 | 43.3 | 41.0357 | 2.2643 | 0.97004 | 22-03-2026 13:40 | 234.743 | 238.39 | 1490.7 | 39.7317 | 41.631 | -1.8994 | 249.7862 | 43.6 | 41.0357 | 2.5643 | 0.9847 | 22-03-2026 13:40 | 177.907 | 180.506 | 1111.7 | 30.0843 | 30.8378 | -0.75347 | 185.0268 | 32.2 | 30.3968 | 1.8032 | 0.9856 | 22-03-2026 13:40 | 179.744 | 182.389 | 1107.8 | 30.3982 | 30.8378 | -0.43963 | 185.0268 | 31.8 | 30.3968 | 1.4032 | 0.9855 | 22-03-2026 13:40 | 172.675 | 175.198 | 1106.2 | 29.1997 | 30.8378 | -1.6381 | 185.0268 | 31.7 | 30.3968 | 1.3032 | 0.9856 | 22-03-2026 13:40 | 171.516 | 176.034 | 1114.1 | 29.339 | 30.8378 | -1.4988 | 185.0268 | 31.8 | 30.3968 | 1.4032 | 0.97433 | 22-03-2026 13:40 | 163.943 | 166.321 | 1054.6 | 27.7202 | 29.3383 | -1.6182 | 176.0301 | 30.1 | 28.9188 | 1.1812 | 0.9857 | 22-03-2026 13:40 | 311.792 | 319.2137 | -7.4217 | 1915.2821 | 388.1 | 314.6489 | 73.4511 | -76.308
22-03-2026 13:30 | 872 | 50.8 | 297.871 | 302.93 | 1448.3 | 50.4883 | 51.5261 | -1.0377 | 309.1564 | 56.6 | 50.7892 | 5.8108 | 0.9833 |  |  |  |  | 0 | 51.5261 | -51.5261 | 309.1564 | 0 | 50.7892 | -50.7892 |  | 22-03-2026 13:30 | 288.701 | 296.998 | 1434.4 | 49.4997 | 51.5261 | -2.0264 | 309.1564 | 54.7 | 50.7892 | 3.9108 | 0.97206 | 22-03-2026 13:30 | 288.035 | 292.986 | 1447.1 | 48.831 | 51.5261 | -2.6951 | 309.1564 | 55.2 | 50.7892 | 4.4108 | 0.9831 | 22-03-2026 13:30 | 219.808 | 223.246 | 1079.5 | 37.2077 | 38.1675 | -0.95979 | 229.0047 | 41.4 | 37.6217 | 3.7783 | 0.9846 | 22-03-2026 13:30 | 215.551 | 220.036 | 1076 | 36.6727 | 38.1675 | -1.4948 | 229.0047 | 40.8 | 37.6217 | 3.1783 | 0.97962 | 22-03-2026 13:30 | 218.952 | 223.482 | 1074.5 | 37.247 | 38.1675 | -0.92045 | 229.0047 | 40.8 | 37.6217 | 3.1783 | 0.97973 | 22-03-2026 13:30 | 220.248 | 227.066 | 1082.3 | 37.8443 | 38.1675 | -0.32312 | 229.0047 | 41 | 37.6217 | 3.3783 | 0.96997 | 22-03-2026 13:30 | 208.002 | 211.234 | 1024.5 | 35.2057 | 36.3116 | -1.1059 | 217.8696 | 39.3 | 35.7923 | 3.5077 | 0.9847 | 22-03-2026 13:30 | 332.9963 | 395.0857 | -62.0893 | 2370.514 | 369.8 | 389.4359 | -19.6359 | -36.8037
22-03-2026 13:20 | 1039 | 50.23 | 341.687 | 347.773 | 1391.7 | 57.9622 | 61.5287 | -3.5665 | 369.1719 | 55.2 | 60.6488 | -5.4488 | 0.9825 | 22-03-2026 13:20 | 340.278 | 349.747 | 1399.4 | 58.2912 | 61.5287 | -3.2375 | 369.1719 | 57.8 | 60.6488 | -2.8488 | 0.97293 | 22-03-2026 13:20 | 339.546 | 349.354 | 1379.7 | 58.2257 | 61.5287 | -3.303 | 369.1719 | 56.3 | 60.6488 | -4.3488 | 0.97193 | 22-03-2026 13:20 | 343.333 | 349.52 | 1391.9 | 58.2533 | 61.5287 | -3.2753 | 369.1719 | 56.9 | 60.6488 | -3.7488 | 0.9823 | 22-03-2026 13:20 | 256.693 | 260.92 | 1038.1 | 43.4867 | 45.5768 | -2.0901 | 273.4607 | 42.6 | 44.925 | -2.325 | 0.9838 | 22-03-2026 13:20 | 253.71 | 258.761 | 1035.2 | 43.1268 | 45.5768 | -2.4499 | 273.4607 | 42.1 | 44.925 | -2.825 | 0.98048 | 22-03-2026 13:20 | 253.145 | 258.433 | 1033.7 | 43.0722 | 45.5768 | -2.5046 | 273.4607 | 42.1 | 44.925 | -2.825 | 0.97954 | 22-03-2026 13:20 | 254.341 | 261.91 | 1041.3 | 43.6517 | 45.5768 | -1.9251 | 273.4607 | 42.3 | 44.925 | -2.625 | 0.9711 | 22-03-2026 13:20 | 241.675 | 245.555 | 985.2 | 40.9258 | 43.3607 | -2.4348 | 260.164 | 39.5 | 42.7406 | -3.2406 | 0.9842 | 22-03-2026 13:20 | 446.9955 | 471.7824 | -24.7869 | 2830.6943 | 434.8 | 465.0359 | -30.2359 | 12.1955
22-03-2026 13:10 | 1026 | 50.23 | 339.544 | 345.451 | 1336.5 | 57.5752 | 60.7588 | -3.1836 | 364.5528 | 55 | 59.89 | -4.89 | 0.9829 | 22-03-2026 13:10 | 343.35 | 349.466 | 1341.6 | 58.2443 | 60.7588 | -2.5145 | 364.5528 | 113.9 | 59.89 | 54.01 | 0.9825 | 22-03-2026 13:10 | 337.379 | 347.458 | 1323.4 | 57.9097 | 60.7588 | -2.8491 | 364.5528 | 54.8 | 59.89 | -5.09 | 0.97099 | 22-03-2026 13:10 | 340.152 | 346.246 | 1335 | 57.7077 | 60.7588 | -3.0511 | 364.5528 | 56.1 | 59.89 | -3.79 | 0.9824 | 22-03-2026 13:10 | 255.579 | 259.735 | 995.5 | 43.2892 | 45.0065 | -1.7174 | 270.0391 | 42.1 | 44.3629 | -2.2629 | 0.984 | 22-03-2026 13:10 | 251.734 | 256.554 | 993.1 | 42.759 | 45.0065 | -2.2475 | 270.0391 | 41.5 | 44.3629 | -2.8629 | 0.98121 | 22-03-2026 13:10 | 252.001 | 256.944 | 991.6 | 42.824 | 45.0065 | -2.1825 | 270.0391 | 41.6 | 44.3629 | -2.7629 | 0.98076 | 22-03-2026 13:10 | 253.128 | 260.776 | 999 | 43.4627 | 45.0065 | -1.5439 | 270.0391 | 41.9 | 44.3629 | -2.4629 | 0.97067 | 22-03-2026 13:10 | 239.22 | 243.085 | 945.7 | 40.5142 | 42.8181 | -2.304 | 256.9088 | 39.5 | 42.2058 | -2.7058 | 0.9841 | 22-03-2026 13:10 | 444.2858 | 465.8794 | -21.5936 | 2795.2765 | 486.4 | 459.2173 | 27.1827 | -42.1142
22-03-2026 13:00 | 1022 | 49.94 | 333.922 | 339.801 | 1281.5 | 56.6335 | 60.5893 | -3.9558 | 363.5358 | 59.4 | 59.7229 | -0.32288 | 0.9827 |  |  |  |  | 0 | 60.5893 | -60.5893 | 363.5358 | 0 | 59.7229 | -59.7229 |  | 22-03-2026 13:00 | 331.547 | 341.301 | 1268.6 | 56.8835 | 60.5893 | -3.7058 | 363.5358 | 56.4 | 59.7229 | -3.3229 | 0.97142 | 22-03-2026 13:00 | 337.259 | 343.402 | 1278.9 | 57.2337 | 60.5893 | -3.3556 | 363.5358 | 56.1 | 59.7229 | -3.6229 | 0.98211 | 22-03-2026 13:00 | 251.12 | 255.203 | 953.4 | 42.5338 | 44.881 | -2.3471 | 269.2858 | 42.2 | 44.2392 | -2.0392 | 0.984 | 22-03-2026 13:00 | 249.029 | 253.709 | 951.6 | 42.2848 | 44.881 | -2.5961 | 269.2858 | 41.7 | 44.2392 | -2.5392 | 0.98155 | 22-03-2026 13:00 | 247.977 | 252.942 | 950 | 42.157 | 44.881 | -2.724 | 269.2858 | 42.3 | 44.2392 | -1.9392 | 0.98037 | 22-03-2026 13:00 | 249.821 | 257.626 | 957.1 | 42.9377 | 44.881 | -1.9433 | 269.2858 | 42 | 44.2392 | -2.2392 | 0.9697 | 22-03-2026 13:00 | 237.196 | 241.053 | 906.2 | 40.1755 | 42.6987 | -2.5232 | 256.1921 | 39.7 | 42.0881 | -2.3881 | 0.984 | 22-03-2026 13:00 | 380.8395 | 464.5798 | -83.7403 | 2787.4786 | 379.8 | 457.9363 | -78.1363 | 1.0395
22-03-2026 12:50 | 1040 | 50.23 | 340.657 | 346.689 | 1222.1 | 57.7815 | 61.5879 | -3.8064 | 369.5272 | 54.6 | 60.7072 | -6.1072 | 0.9826 | 22-03-2026 12:50 | 343.57 | 349.512 | 1227.7 | 58.252 | 61.5879 | -3.3359 | 369.5272 | 54.5 | 60.7072 | -6.2072 | 0.983 | 22-03-2026 12:50 | 337.073 | 346.856 | 1212.2 | 57.8093 | 61.5879 | -3.7785 | 369.5272 | 56.3 | 60.7072 | -4.4072 | 0.9718 | 22-03-2026 12:50 | 342.292 | 348.495 | 1222.8 | 58.0825 | 61.5879 | -3.5054 | 369.5272 | 56.5 | 60.7072 | -4.2072 | 0.9822 | 22-03-2026 12:50 | 254.764 | 258.933 | 911.2 | 43.1555 | 45.6206 | -2.4651 | 273.7239 | 42.7 | 44.9683 | -2.2683 | 0.9839 | 22-03-2026 12:50 | 252.347 | 257.031 | 909.9 | 42.8385 | 45.6206 | -2.7821 | 273.7239 | 42.1 | 44.9683 | -2.8683 | 0.98178 | 22-03-2026 12:50 | 251.718 | 256.892 | 907.7 | 42.8153 | 45.6206 | -2.8053 | 273.7239 | 41.6 | 44.9683 | -3.3683 | 0.97986 | 22-03-2026 12:50 | 252.669 | 260.134 | 915.1 | 43.3557 | 45.6206 | -2.265 | 273.7239 | 42.2 | 44.9683 | -2.7683 | 0.9713 | 22-03-2026 12:50 | 239.927 | 243.828 | 866.5 | 40.638 | 43.4024 | -2.7644 | 260.4144 | 40.7 | 42.7817 | -2.0817 | 0.984 | 22-03-2026 12:50 | 444.7283 | 472.2365 | -27.5081 | 2833.4187 | 431.2 | 465.4835 | -34.2835 | 13.5283
22-03-2026 12:40 | 1042 | 50.23 | 344.557 | 350.494 | 1167.5 | 58.4157 | 61.7063 | -3.2906 | 370.2378 | 57.9 | 60.8239 | -2.9239 | 0.98306 | 22-03-2026 12:40 | 342.172 | 347.877 | 1173.2 | 57.9795 | 61.7063 | -3.7268 | 370.2378 | 57.8 | 60.8239 | -3.0239 | 0.9836 | 22-03-2026 12:40 | 340.535 | 350.421 | 1155.9 | 58.4035 | 61.7063 | -3.3028 | 370.2378 | 58 | 60.8239 | -2.8239 | 0.97179 | 22-03-2026 12:40 | 341.508 | 347.308 | 1166.3 | 57.8847 | 61.7063 | -3.8216 | 370.2378 | 57.3 | 60.8239 | -3.5239 | 0.9833 | 22-03-2026 12:40 | 257.523 | 261.684 | 868.5 | 43.614 | 45.7084 | -2.0944 | 274.2503 | 43.4 | 45.0547 | -1.6547 | 0.9841 | 22-03-2026 12:40 | 255.564 | 260.419 | 867.8 | 43.4032 | 45.7084 | -2.3052 | 274.2503 | 43.1 | 45.0547 | -1.9547 | 0.98136 | 22-03-2026 12:40 | 254.794 | 260.166 | 866.1 | 43.361 | 45.7084 | -2.3474 | 274.2503 | 43 | 45.0547 | -2.0547 | 0.97935 | 22-03-2026 12:40 | 256.447 | 264.002 | 872.9 | 44.0003 | 45.7084 | -1.708 | 274.2503 | 43.3 | 45.0547 | -1.7547 | 0.97138 | 22-03-2026 12:40 | 243.175 | 247.104 | 825.8 | 41.184 | 43.4859 | -2.3019 | 260.9152 | 40.8 | 42.864 | -2.064 | 0.9841 | 22-03-2026 12:40 | 448.2458 | 473.1446 | -24.8988 | 2838.8676 | 444.6 | 466.3786 | -21.7786 | 3.6458
22-03-2026 12:30 | 1049 | 49.65 | 347.356 | 353.471 | 1109.6 | 58.9118 | 62.2592 | -3.3473 | 373.555 | 58.2 | 61.3689 | -3.1689 | 0.9827 | 22-03-2026 12:30 | 340.428 | 345.963 | 1115.4 | 57.6605 | 62.2592 | -4.5987 | 373.555 | 57.7 | 61.3689 | -3.6689 | 0.984 | 22-03-2026 12:30 | 344.883 | 354.915 | 1097.9 | 59.1525 | 62.2592 | -3.1067 | 373.555 | 57.2 | 61.3689 | -4.1689 | 0.97173 | 22-03-2026 12:30 | 342.16 | 347.512 | 1109 | 57.9187 | 62.2592 | -4.3405 | 373.555 | 57.4 | 61.3689 | -3.9689 | 0.9846 | 22-03-2026 12:30 | 261.38 | 265.603 | 825.1 | 44.2672 | 46.1179 | -1.8507 | 276.7074 | 44.1 | 45.4584 | -1.3584 | 0.9841 | 22-03-2026 12:30 | 258.311 | 263.224 | 824.7 | 43.8707 | 46.1179 | -2.2472 | 276.7074 | 44.2 | 45.4584 | -1.2584 | 0.98134 | 22-03-2026 12:30 | 259.158 | 264.288 | 823.1 | 44.048 | 46.1179 | -2.0699 | 276.7074 | 44.3 | 45.4584 | -1.1584 | 0.98059 | 22-03-2026 12:30 | 261.132 | 269.27 | 829.6 | 44.8783 | 46.1179 | -1.2396 | 276.7074 | 44.5 | 45.4584 | -0.95841 | 0.96978 | 22-03-2026 12:30 | 245.784 | 249.755 | 785 | 41.6258 | 43.8755 | -2.2496 | 263.2528 | 41.5 | 43.248 | -1.748 | 0.9841 | 22-03-2026 12:30 | 452.3335 | 477.3837 | -25.0502 | 2864.3022 | 449.1 | 470.5571 | -21.4571 | 3.2335
22-03-2026 12:20 | 1083 | 49.94 | 352.114 | 357.785 | 1051.4 | 59.6308 | 64.2057 | -4.5749 | 385.2342 | 53.7 | 63.2876 | -9.5876 | 0.98415 | 22-03-2026 12:20 | 351.043 | 356.57 | 1057.7 | 59.4283 | 64.2057 | -4.7774 | 385.2342 | 53.8 | 63.2876 | -9.4876 | 0.9845 | 22-03-2026 12:20 | 351.469 | 361.837 | 1040.7 | 60.3062 | 64.2057 | -3.8995 | 385.2342 | 53.4 | 63.2876 | -9.8876 | 0.97135 | 22-03-2026 12:20 | 349.721 | 355.299 | 1051.6 | 59.2165 | 64.2057 | -4.9892 | 385.2342 | 53.6 | 63.2876 | -9.6876 | 0.9843 | 22-03-2026 12:20 | 273.035 | 277.418 | 781 | 46.2363 | 47.5598 | -1.3234 | 285.3586 | 40.8 | 46.8797 | -6.0797 | 0.9842 | 22-03-2026 12:20 | 270.681 | 275.765 | 780.5 | 45.9608 | 47.5598 | -1.5989 | 285.3586 | 39.7 | 46.8797 | -7.1797 | 0.98156 | 22-03-2026 12:20 | 271.066 | 276.387 | 778.8 | 46.0645 | 47.5598 | -1.4953 | 285.3586 | 39.8 | 46.8797 | -7.0797 | 0.98075 | 22-03-2026 12:20 | 272.542 | 280.73 | 785.1 | 46.7883 | 47.5598 | -0.77144 | 285.3586 | 40 | 46.8797 | -6.8797 | 0.97083 | 22-03-2026 12:20 | 257.305 | 261.409 | 743.5 | 43.5682 | 45.2472 | -1.6791 | 271.4834 | 37.8 | 44.6002 | -6.8002 | 0.9843 | 22-03-2026 12:20 | 467.2 | 492.3091 | -25.1091 | 2953.8546 | 412.6 | 485.2691 | -72.6691 | 54.6
22-03-2026 12:10 | 834 | 50.23 | 290.238 | 294.897 | 997.7 | 49.1495 | 49.3887 | -0.23923 | 296.3324 | 49.3 | 48.6825 | 0.61752 | 0.9842 | 22-03-2026 12:10 | 316.206 | 321.478 | 1003.9 | 53.5797 | 49.3887 | 4.1909 | 296.3324 | 49.8 | 48.6825 | 1.1175 | 0.9836 | 22-03-2026 12:10 | 282.24 | 289.457 | 987.3 | 48.2428 | 49.3887 | -1.1459 | 296.3324 | 49 | 48.6825 | 0.31752 | 0.97507 | 22-03-2026 12:10 | 290.714 | 295.471 | 998 | 49.2452 | 49.3887 | -0.14357 | 296.3324 | 49.5 | 48.6825 | 0.81752 | 0.9839 | 22-03-2026 12:10 | 212.103 | 215.246 | 740.2 | 35.8743 | 36.5842 | -0.70991 | 219.5055 | 36.9 | 36.0611 | 0.83891 | 0.9854 | 22-03-2026 12:10 | 215.15 | 218.733 | 740.8 | 36.4555 | 36.5842 | -0.12875 | 219.5055 | 36.6 | 36.0611 | 0.53891 | 0.98362 | 22-03-2026 12:10 | 214.285 | 218.879 | 739 | 36.4798 | 36.5842 | -0.10441 | 219.5055 | 36.6 | 36.0611 | 0.53891 | 0.97901 | 22-03-2026 12:10 | 221.158 | 227.687 | 745.1 | 37.9478 | 36.5842 | 1.3636 | 219.5055 | 36.9 | 36.0611 | 0.83891 | 0.97132 | 22-03-2026 12:10 | 208.464 | 211.574 | 705.7 | 35.2623 | 34.8054 | 0.45695 | 208.8323 | 35.3 | 34.3077 | 0.99234 | 0.9853 | 22-03-2026 12:10 | 382.237 | 378.6973 | 3.5397 | 2272.1838 | 379.9 | 373.2819 | 6.6181 | 2.337
22-03-2026 12:00 | 754 | 49.65 | 267.813 | 271.891 | 948.4 | 45.3152 | 44.7506 | 0.56454 | 268.5038 | 41.1 | 44.1107 | -3.0107 | 0.985 | 22-03-2026 12:00 | 266.418 | 271.584 | 954.1 | 45.264 | 44.7506 | 0.51337 | 268.5038 | 41.2 | 44.1107 | -2.9107 | 0.98098 | 22-03-2026 12:00 | 258.93 | 262.822 | 938.3 | 43.8037 | 44.7506 | -0.94696 | 268.5038 | 40.7 | 44.1107 | -3.4107 | 0.98519 | 22-03-2026 12:00 | 265.768 | 269.87 | 948.5 | 44.9783 | 44.7506 | 0.22771 | 268.5038 | 40.9 | 44.1107 | -3.2107 | 0.9848 | 22-03-2026 12:00 | 189.201 | 191.887 | 703.3 | 31.9812 | 33.1486 | -1.1674 | 198.8917 | 30.6 | 32.6746 | -2.0746 | 0.986 | 22-03-2026 12:00 | 196.52 | 199.27 | 704.2 | 33.2117 | 33.1486 | 0.063054 | 198.8917 | 30.3 | 32.6746 | -2.3746 | 0.9862 | 22-03-2026 12:00 | 188.608 | 191.273 | 702.4 | 31.8788 | 33.1486 | -1.2698 | 198.8917 | 30.2 | 32.6746 | -2.4746 | 0.98607 | 22-03-2026 12:00 | 192.561 | 197.785 | 708.2 | 32.9642 | 33.1486 | -0.18445 | 198.8917 | 30.8 | 32.6746 | -1.8746 | 0.97359 | 22-03-2026 12:00 | 182.811 | 185.444 | 670.4 | 30.9073 | 31.5368 | -0.62947 | 189.2208 | 28.7 | 31.0858 | -2.3858 | 0.9858 | 22-03-2026 12:00 | 340.3043 | 343.1338 | -2.8294 | 2058.8026 | 314.5 | 338.2269 | -23.7269 | 25.8043
22-03-2026 11:50 | 621 | 49.65 | 229.156 | 224.536 | 907.3 | 37.4227 | 36.8569 | 0.56572 | 221.1417 | 42.3 | 36.3299 | 5.9701 | 1.0206 | 22-03-2026 11:50 | 237.716 | 222.301 | 912.9 | 37.0502 | 36.8569 | 0.19322 | 221.1417 | 41.9 | 36.3299 | 5.5701 | 1.0693 | 22-03-2026 11:50 | 223.189 | 229.493 | 897.6 | 38.2488 | 36.8569 | 1.3919 | 221.1417 | 41.1 | 36.3299 | 4.7701 | 0.97253 | 22-03-2026 11:50 | 218.701 | 220.185 | 907.6 | 36.6975 | 36.8569 | -0.15945 | 221.1417 | 41.4 | 36.3299 | 5.0701 | 0.99326 | 22-03-2026 11:50 | 170.37 | 172.754 | 672.7 | 28.7923 | 27.3014 | 1.4909 | 163.8087 | 30.8 | 26.911 | 3.889 | 0.9862 | 22-03-2026 11:50 | 165.629 | 168.399 | 673.9 | 28.0665 | 27.3014 | 0.76506 | 163.8087 | 30.5 | 26.911 | 3.589 | 0.98355 | 22-03-2026 11:50 | 170.166 | 173.663 | 672.2 | 28.9438 | 27.3014 | 1.6424 | 163.8087 | 30.5 | 26.911 | 3.589 | 0.97986 | 22-03-2026 11:50 | 160.792 | 166.426 | 677.4 | 27.7377 | 27.3014 | 0.43622 | 163.8087 | 30.5 | 26.911 | 3.589 | 0.96615 | 22-03-2026 11:50 | 151.351 | 153.484 | 641.7 | 25.5807 | 25.9739 | -0.39328 | 155.8437 | 28.9 | 25.6025 | 3.2975 | 0.9861 | 22-03-2026 11:50 | 288.5402 | 282.6075 | 5.9327 | 1695.6451 | 317.9 | 278.5662 | 39.3338 | -29.3598
22-03-2026 11:40 | 868 | 49.94 | 275.083 | 279.556 | 865 | 46.5927 | 51.4594 | -4.8667 | 308.7565 | 54.5 | 50.7235 | 3.7765 | 0.984 | 22-03-2026 11:40 | 332.745 | 294.608 | 871 | 49.1013 | 51.4594 | -2.3581 | 308.7565 | 55.6 | 50.7235 | 4.8765 | 1.1294 | 22-03-2026 11:40 | 290.193 | 298.591 | 856.5 | 49.7652 | 51.4594 | -1.6942 | 308.7565 | 54.8 | 50.7235 | 4.0765 | 0.97187 | 22-03-2026 11:40 | 297.103 | 302.057 | 866.2 | 50.3428 | 51.4594 | -1.1166 | 308.7565 | 55 | 50.7235 | 4.2765 | 0.9836 | 22-03-2026 11:40 | 215.271 | 218.461 | 641.9 | 36.4102 | 38.1181 | -1.7079 | 228.7085 | 41.4 | 37.573 | 3.827 | 0.9854 | 22-03-2026 11:40 | 214.561 | 217.762 | 643.4 | 36.2937 | 38.1181 | -1.8244 | 228.7085 | 40.8 | 37.573 | 3.227 | 0.9853 | 22-03-2026 11:40 | 208.948 | 212.773 | 641.7 | 35.4622 | 38.1181 | -2.6559 | 228.7085 | 40.7 | 37.573 | 3.127 | 0.98202 | 22-03-2026 11:40 | 221.959 | 228.47 | 646.9 | 38.0783 | 38.1181 | -0.039749 | 228.7085 | 40.5 | 37.573 | 2.927 | 0.9715 | 22-03-2026 11:40 | 215.025 | 218.233 | 612.8 | 36.3722 | 36.2646 | 0.10753 | 217.5878 | 38.2 | 35.746 | 2.454 | 0.9853 | 22-03-2026 11:40 | 378.4185 | 394.5746 | -16.1561 | 2367.4476 | 421.5 | 388.9322 | 32.5678 | -43.0815
22-03-2026 11:30 | 974 | 49.65 | 326.967 | 332.419 | 810.5 | 55.4032 | 57.8078 | -2.4047 | 346.847 | 47.5 | 56.9812 | -9.4812 | 0.9836 | 22-03-2026 11:30 | 334.589 | 340.202 | 815.4 | 56.7003 | 57.8078 | -1.1075 | 346.847 | 48 | 56.9812 | -8.9812 | 0.9835 | 22-03-2026 11:30 | 329.702 | 339.964 | 801.7 | 56.6607 | 57.8078 | -1.1472 | 346.847 | 46.5 | 56.9812 | -10.4812 | 0.96981 | 22-03-2026 11:30 | 337.879 | 343.548 | 811.2 | 57.258 | 57.8078 | -0.54984 | 346.847 | 46.9 | 56.9812 | -10.0812 | 0.9835 | 22-03-2026 11:30 | 253.09 | 256.996 | 600.5 | 42.8327 | 42.8206 | 0.012045 | 256.9237 | 35 | 42.2083 | -7.2083 | 0.9848 | 22-03-2026 11:30 | 250.725 | 256.731 | 602.6 | 42.7885 | 42.8206 | -0.032122 | 256.9237 | 34.7 | 42.2083 | -7.5083 | 0.97661 | 22-03-2026 11:30 | 254.158 | 258.605 | 601 | 43.1008 | 42.8206 | 0.28021 | 256.9237 | 34.8 | 42.2083 | -7.4083 | 0.9828 | 22-03-2026 11:30 | 258.513 | 265.873 | 606.4 | 44.3122 | 42.8206 | 1.4915 | 256.9237 | 34.9 | 42.2083 | -7.3083 | 0.97232 | 22-03-2026 11:30 | 239.556 | 243.253 | 574.6 | 40.5422 | 40.7385 | -0.19635 | 244.4311 | 33 | 40.156 | -7.156 | 0.9848 | 22-03-2026 11:30 | 439.5985 | 443.2524 | -3.6539 | 2659.5142 | 361.3 | 436.9139 | -75.6139 | 78.2985
22-03-2026 11:20 | 647 | 49.65 | 223.747 | 231.604 | 763 | 38.6007 | 38.4001 | 0.20059 | 230.4004 | 35.3 | 37.851 | -2.551 | 0.96608 | 22-03-2026 11:20 | 230.524 | 233.94 | 767.4 | 38.99 | 38.4001 | 0.58993 | 230.4004 | 34.1 | 37.851 | -3.751 | 0.9854 | 22-03-2026 11:20 | 227.914 | 234.045 | 755.2 | 39.0075 | 38.4001 | 0.60743 | 230.4004 | 34.4 | 37.851 | -3.451 | 0.9738 | 22-03-2026 11:20 | 229.81 | 233.239 | 764.3 | 38.8732 | 38.4001 | 0.47309 | 230.4004 | 34.8 | 37.851 | -3.051 | 0.9853 | 22-03-2026 11:20 | 172.72 | 175.119 | 565.5 | 29.1865 | 28.4445 | 0.742 | 170.667 | 25.9 | 28.0377 | -2.1377 | 0.9863 | 22-03-2026 11:20 | 169.625 | 172.234 | 567.9 | 28.7057 | 28.4445 | 0.26117 | 170.667 | 25.7 | 28.0377 | -2.3377 | 0.98485 | 22-03-2026 11:20 | 170.815 | 173.275 | 566.2 | 28.8792 | 28.4445 | 0.43467 | 170.667 | 25.7 | 28.0377 | -2.3377 | 0.9858 | 22-03-2026 11:20 | 169.939 | 174.736 | 571.5 | 29.1227 | 28.4445 | 0.67817 | 170.667 | 25.8 | 28.0377 | -2.2377 | 0.97255 | 22-03-2026 11:20 | 161.085 | 163.323 | 541.6 | 27.2205 | 27.0614 | 0.15908 | 162.3685 | 24.4 | 26.6744 | -2.2744 | 0.9863 | 22-03-2026 11:20 | 298.5858 | 294.4397 | 4.1461 | 1766.6383 | 266.1 | 290.2292 | -24.1292 | 32.4858
22-03-2026 11:10 | 683 | 49.65 | 236.644 | 237.572 | 727.7 | 39.5953 | 40.5367 | -0.94138 | 243.2203 | 41.6 | 39.957 | 1.643 | 0.99609 | 22-03-2026 11:10 | 227.812 | 244.518 | 733.3 | 40.753 | 40.5367 | 0.21629 | 243.2203 | 42.6 | 39.957 | 2.643 | 0.93168 | 22-03-2026 11:10 | 237.589 | 243.09 | 720.8 | 40.515 | 40.5367 | -0.021709 | 243.2203 | 42.3 | 39.957 | 2.343 | 0.97737 | 22-03-2026 11:10 | 237.473 | 241.114 | 729.5 | 40.1857 | 40.5367 | -0.35104 | 243.2203 | 42.8 | 39.957 | 2.843 | 0.9849 | 22-03-2026 11:10 | 177.126 | 179.677 | 539.6 | 29.9462 | 30.0272 | -0.081025 | 180.1631 | 32.5 | 29.5978 | 2.9022 | 0.9858 | 22-03-2026 11:10 | 173.86 | 176.471 | 542.2 | 29.4118 | 30.0272 | -0.61536 | 180.1631 | 32.3 | 29.5978 | 2.7022 | 0.9852 | 22-03-2026 11:10 | 176.057 | 179.183 | 540.5 | 29.8638 | 30.0272 | -0.16336 | 180.1631 | 32.1 | 29.5978 | 2.5022 | 0.98255 | 22-03-2026 11:10 | 175.928 | 181.289 | 545.7 | 30.2148 | 30.0272 | 0.18764 | 180.1631 | 32.4 | 29.5978 | 2.8022 | 0.97043 | 22-03-2026 11:10 | 166.935 | 169.288 | 517.2 | 28.2147 | 28.5672 | -0.35249 | 171.4029 | 30.7 | 28.1586 | 2.5414 | 0.9861 | 22-03-2026 11:10 | 308.7003 | 310.8228 | -2.1224 | 1864.9365 | 329.3 | 306.378 | 22.922 | -20.5997
22-03-2026 11:00 | 838 | 49.65 | 289.08 | 293.751 | 686.1 | 48.9585 | 49.7361 | -0.77761 | 298.4166 | 48.8 | 49.0249 | -0.22488 | 0.9841 | 22-03-2026 11:00 | 290.82 | 295.639 | 690.7 | 49.2732 | 49.7361 | -0.46294 | 298.4166 | 102.7 | 49.0249 | 53.6751 | 0.9837 | 22-03-2026 11:00 | 286.884 | 294.803 | 678.5 | 49.1338 | 49.7361 | -0.60227 | 298.4166 | 48.5 | 49.0249 | -0.52488 | 0.97314 | 22-03-2026 11:00 | 288.64 | 293.363 | 686.7 | 48.8938 | 49.7361 | -0.84227 | 298.4166 | 49.8 | 49.0249 | 0.77512 | 0.9839 | 22-03-2026 11:00 | 214.789 | 217.795 | 507.1 | 36.2992 | 36.8416 | -0.54239 | 221.0494 | 36.5 | 36.3147 | 0.18527 | 0.9862 | 22-03-2026 11:00 | 212.539 | 216.16 | 509.9 | 36.0267 | 36.8416 | -0.81489 | 221.0494 | 36.3 | 36.3147 | -0.014727 | 0.98325 | 22-03-2026 11:00 | 213.173 | 216.831 | 508.4 | 36.1385 | 36.8416 | -0.70306 | 221.0494 | 36.4 | 36.3147 | 0.085273 | 0.98313 | 22-03-2026 11:00 | 214.523 | 220.732 | 513.3 | 36.7887 | 36.8416 | -0.052895 | 221.0494 | 36.6 | 36.3147 | 0.28527 | 0.97187 | 22-03-2026 11:00 | 202.64 | 205.663 | 486.5 | 34.2772 | 35.0502 | -0.77302 | 210.3011 | 34.5 | 34.549 | -0.048965 | 0.9853 | 22-03-2026 11:00 | 375.7895 | 381.3609 | -5.5714 | 2288.1652 | 430.1 | 375.9074 | 54.1926 | -54.3105
22-03-2026 10:50 | 930 | 49.94 | 314.042 | 319.062 | 637.3 | 53.177 | 55.1351 | -1.9581 | 330.8105 | 53.4 | 54.3467 | -0.94665 | 0.98427 |  |  |  |  | 0 | 55.1351 | -55.1351 | 330.8105 | 0 | 54.3467 | -54.3467 |  | 22-03-2026 10:50 | 310.711 | 319.248 | 630 | 53.208 | 55.1351 | -1.9271 | 330.8105 | 52.2 | 54.3467 | -2.1467 | 0.97326 | 22-03-2026 10:50 | 316.133 | 321.502 | 636.9 | 53.5837 | 55.1351 | -1.5514 | 330.8105 | 52.9 | 54.3467 | -1.4467 | 0.9833 | 22-03-2026 10:50 | 236.066 | 239.69 | 470.6 | 39.9483 | 40.8408 | -0.89247 | 245.0448 | 39.5 | 40.2568 | -0.75678 | 0.98488 | 22-03-2026 10:50 | 234.264 | 238.457 | 473.6 | 39.7428 | 40.8408 | -1.098 | 245.0448 | 39.2 | 40.2568 | -1.0568 | 0.98242 | 22-03-2026 10:50 | 234.281 | 238.336 | 472 | 39.7227 | 40.8408 | -1.1181 | 245.0448 | 39.1 | 40.2568 | -1.1568 | 0.98299 | 22-03-2026 10:50 | 235.785 | 242.943 | 476.7 | 40.4905 | 40.8408 | -0.3503 | 245.0448 | 39.5 | 40.2568 | -0.75678 | 0.97054 | 22-03-2026 10:50 | 223.194 | 226.57 | 452 | 37.7617 | 38.855 | -1.0933 | 233.1298 | 37.4 | 38.2993 | -0.89934 | 0.9851 | 22-03-2026 10:50 | 357.6347 | 422.7585 | -65.1238 | 2536.551 | 353.2 | 416.7131 | -63.5131 | 4.4347
22-03-2026 10:40 | 924 | 50.23 | 313.768 | 319.331 | 583.9 | 53.2218 | 54.7185 | -1.4966 | 328.3107 | 51.9 | 53.936 | -2.036 | 0.98258 | 22-03-2026 10:40 | 317.525 | 322.918 | 588 | 53.8197 | 54.7185 | -0.89879 | 328.3107 | 52.3 | 53.936 | -1.636 | 0.9833 | 22-03-2026 10:40 | 311.361 | 320.068 | 577.8 | 53.3447 | 54.7185 | -1.3738 | 328.3107 | 50.8 | 53.936 | -3.136 | 0.9728 | 22-03-2026 10:40 | 315.073 | 320.424 | 584 | 53.404 | 54.7185 | -1.3145 | 328.3107 | 50.6 | 53.936 | -3.336 | 0.9833 | 22-03-2026 10:40 | 234.733 | 238.332 | 431.1 | 39.722 | 40.5322 | -0.81019 | 243.1931 | 38.2 | 39.9526 | -1.7526 | 0.9849 | 22-03-2026 10:40 | 233.468 | 237.886 | 434.4 | 39.6477 | 40.5322 | -0.88452 | 243.1931 | 38 | 39.9526 | -1.9526 | 0.98143 | 22-03-2026 10:40 | 233.015 | 237.15 | 432.9 | 39.525 | 40.5322 | -1.0072 | 243.1931 | 38 | 39.9526 | -1.9526 | 0.98256 | 22-03-2026 10:40 | 234.465 | 241.323 | 437.2 | 40.2205 | 40.5322 | -0.31169 | 243.1931 | 38.2 | 39.9526 | -1.7526 | 0.97158 | 22-03-2026 10:40 | 222.3 | 225.674 | 414.6 | 37.6123 | 38.5614 | -0.94902 | 231.3681 | 36.2 | 38.0099 | -1.8099 | 0.98505 | 22-03-2026 10:40 | 410.5177 | 419.5639 | -9.0463 | 2517.3835 | 394.2 | 413.5642 | -19.3642 | 16.3177
22-03-2026 10:30 | 876 | 49.94 | 299.3 | 304.136 | 532 | 50.6893 | 51.9337 | -1.2444 | 311.6021 | 47.5 | 51.191 | -3.691 | 0.9841 | 22-03-2026 10:30 | 302.156 | 307.132 | 535.7 | 51.1887 | 51.9337 | -0.74502 | 311.6021 | 49.4 | 51.191 | -1.791 | 0.9838 | 22-03-2026 10:30 | 297.616 | 305.542 | 527 | 50.9237 | 51.9337 | -1.01 | 311.6021 | 48.5 | 51.191 | -2.691 | 0.97406 | 22-03-2026 10:30 | 300.915 | 305.87 | 533.4 | 50.9783 | 51.9337 | -0.95536 | 311.6021 | 49.7 | 51.191 | -1.491 | 0.9838 | 22-03-2026 10:30 | 224.09 | 227.41 | 392.9 | 37.9017 | 38.4694 | -0.56773 | 230.8164 | 36.9 | 37.9193 | -1.0193 | 0.9854 | 22-03-2026 10:30 | 222.811 | 226.553 | 396.4 | 37.7588 | 38.4694 | -0.71057 | 230.8164 | 36.4 | 37.9193 | -1.5193 | 0.98348 | 22-03-2026 10:30 | 222.848 | 226.712 | 394.9 | 37.7853 | 38.4694 | -0.68407 | 230.8164 | 36.3 | 37.9193 | -1.6193 | 0.98296 | 22-03-2026 10:30 | 224.262 | 230.808 | 399 | 38.468 | 38.4694 | -0.0014006 | 230.8164 | 36.6 | 37.9193 | -1.3193 | 0.97164 | 22-03-2026 10:30 | 212.535 | 215.706 | 378.4 | 35.951 | 36.5989 | -0.64787 | 219.5932 | 34.7 | 36.0755 | -1.3755 | 0.9853 | 22-03-2026 10:30 | 391.6448 | 398.2112 | -6.5664 | 2389.2674 | 376 | 392.5168 | -16.5168 | 15.6448
22-03-2026 10:20 | 838 | 49.94 | 288.877 | 293.455 | 484.5 | 48.9092 | 49.6809 | -0.77169 | 298.0852 | 47.2 | 48.9704 | -1.7704 | 0.9844 | 22-03-2026 10:20 | 291.151 | 295.84 | 486.3 | 49.3067 | 49.6809 | -0.37419 | 298.0852 | 48.2 | 48.9704 | -0.77042 | 0.98415 | 22-03-2026 10:20 | 286.116 | 293.647 | 478.5 | 48.9412 | 49.6809 | -0.73969 | 298.0852 | 47.3 | 48.9704 | -1.6704 | 0.97435 | 22-03-2026 10:20 | 289.321 | 293.966 | 483.7 | 48.9943 | 49.6809 | -0.68653 | 298.0852 | 47.3 | 48.9704 | -1.6704 | 0.9842 | 22-03-2026 10:20 | 215.397 | 218.522 | 356 | 36.4203 | 36.8006 | -0.3803 | 220.8038 | 34.8 | 36.2744 | -1.4744 | 0.9857 | 22-03-2026 10:20 | 214.291 | 217.879 | 360 | 36.3132 | 36.8006 | -0.48747 | 220.8038 | 35.1 | 36.2744 | -1.1744 | 0.98353 | 22-03-2026 10:20 | 214.552 | 218.312 | 358.6 | 36.3853 | 36.8006 | -0.4153 | 220.8038 | 35.1 | 36.2744 | -1.1744 | 0.98278 | 22-03-2026 10:20 | 215.778 | 222.073 | 362.4 | 37.0122 | 36.8006 | 0.21153 | 220.8038 | 35.3 | 36.2744 | -0.97439 | 0.97165 | 22-03-2026 10:20 | 204.465 | 207.431 | 343.7 | 34.5718 | 35.0112 | -0.43941 | 210.0675 | 33.4 | 34.5106 | -1.1106 | 0.9857 | 22-03-2026 10:20 | 376.8542 | 380.9372 | -4.0831 | 2285.6234 | 363.7 | 375.4898 | -11.7898 | 13.1542
22-03-2026 10:10 | 805 | 49.65 | 279.229 | 283.568 | 437.3 | 47.2613 | 47.7775 | -0.51619 | 286.6652 | 46.1 | 47.0943 | -0.99431 | 0.9847 | 22-03-2026 10:10 | 281.23 | 285.629 | 438.1 | 47.6048 | 47.7775 | -0.17269 | 286.6652 | 45.2 | 47.0943 | -1.8943 | 0.9846 | 22-03-2026 10:10 | 276.783 | 283.768 | 431.2 | 47.2947 | 47.7775 | -0.48286 | 286.6652 | 44.6 | 47.0943 | -2.4943 | 0.97538 | 22-03-2026 10:10 | 279.86 | 284.237 | 436.4 | 47.3728 | 47.7775 | -0.40469 | 286.6652 | 45.6 | 47.0943 | -1.4943 | 0.9846 | 22-03-2026 10:10 | 207.912 | 210.907 | 321.2 | 35.1512 | 35.3908 | -0.23959 | 212.3446 | 33.8 | 34.8847 | -1.0847 | 0.9858 | 22-03-2026 10:10 | 207.302 | 210.314 | 324.9 | 35.0523 | 35.3908 | -0.33843 | 212.3446 | 33.7 | 34.8847 | -1.1847 | 0.98568 | 22-03-2026 10:10 | 206.996 | 210.482 | 323.5 | 35.0803 | 35.3908 | -0.31043 | 212.3446 | 33.7 | 34.8847 | -1.1847 | 0.98344 | 22-03-2026 10:10 | 208.137 | 214.164 | 327.1 | 35.694 | 35.3908 | 0.30324 | 212.3446 | 33.9 | 34.8847 | -0.98467 | 0.97186 | 22-03-2026 10:10 | 197.385 | 200.208 | 310.3 | 33.368 | 33.6699 | -0.30193 | 202.0196 | 32.1 | 33.1884 | -1.0884 | 0.9859 | 22-03-2026 10:10 | 363.8795 | 366.3431 | -2.4636 | 2198.0584 | 348.7 | 361.1044 | -12.4044 | 15.1795
22-03-2026 10:00 | 722 | 49.65 | 250.571 | 254.232 | 391.2 | 42.372 | 42.8514 | -0.4794 | 257.1084 | 41.9 | 42.2386 | -0.33862 | 0.9856 | 22-03-2026 10:00 | 254.721 | 265.676 | 392.9 | 44.2793 | 42.8514 | 1.4279 | 257.1084 | 43.5 | 42.2386 | 1.2614 | 0.95877 | 22-03-2026 10:00 | 248.91 | 257.693 | 386.6 | 42.9488 | 42.8514 | 0.097437 | 257.1084 | 41.6 | 42.2386 | -0.63862 | 0.96592 | 22-03-2026 10:00 | 255.649 | 259.489 | 390.8 | 43.2482 | 42.8514 | 0.39677 | 257.1084 | 41.7 | 42.2386 | -0.53862 | 0.9852 | 22-03-2026 10:00 | 188.091 | 190.684 | 287.4 | 31.7807 | 31.7418 | 0.038892 | 190.4507 | 31 | 31.2879 | -0.28787 | 0.9864 | 22-03-2026 10:00 | 188.553 | 191.191 | 291.2 | 31.8652 | 31.7418 | 0.12339 | 190.4507 | 31 | 31.2879 | -0.28787 | 0.9862 | 22-03-2026 10:00 | 188.269 | 191.205 | 289.8 | 31.8675 | 31.7418 | 0.12572 | 190.4507 | 30.9 | 31.2879 | -0.38787 | 0.98464 | 22-03-2026 10:00 | 189.977 | 195.668 | 293.2 | 32.6113 | 31.7418 | 0.86956 | 190.4507 | 31.1 | 31.2879 | -0.18787 | 0.97092 | 22-03-2026 10:00 | 180.057 | 182.335 | 278.2 | 30.3892 | 30.1984 | 0.1908 | 181.1902 | 29.5 | 29.7665 | -0.26653 | 0.98751 | 22-03-2026 10:00 | 331.3622 | 328.5711 | 2.7911 | 1971.4263 | 322.2 | 323.8725 | -1.6725 | 9.1622
22-03-2026 09:50 | 672 | 49.65 | 240.177 | 243.686 | 349.3 | 40.6143 | 39.8838 | 0.73049 | 239.3031 | 39.4 | 39.3135 | 0.086491 |  | 22-03-2026 09:50 | 244.908 | 252.174 | 349.4 | 42.029 | 39.8838 | 2.1452 | 239.3031 | 38.2 | 39.3135 | -1.1135 |  | 22-03-2026 09:50 | 235.994 | 241.526 | 345 | 40.2543 | 39.8838 | 0.37049 | 239.3031 | 39.5 | 39.3135 | 0.18649 |  | 22-03-2026 09:50 | 234.116 | 238.297 | 349.1 | 39.7162 | 39.8838 | -0.16768 | 239.3031 | 40.8 | 39.3135 | 1.4865 |  | 22-03-2026 09:50 | 176.179 | 179.174 | 256.4 | 29.8623 | 29.5436 | 0.31874 | 177.2615 | 29.7 | 29.1211 | 0.57888 |  | 22-03-2026 09:50 | 171.642 | 174.287 | 260.2 | 29.0478 | 29.5436 | -0.49576 | 177.2615 | 29.8 | 29.1211 | 0.67888 |  | 22-03-2026 09:50 | 176.756 | 179.202 | 258.9 | 29.867 | 29.5436 | 0.32341 | 177.2615 | 29.6 | 29.1211 | 0.47888 |  | 22-03-2026 09:50 | 173.802 | 179.599 | 262.1 | 29.9332 | 29.5436 | 0.38958 | 177.2615 | 29.9 | 29.1211 | 0.77888 |  | 22-03-2026 09:50 | 162.793 | 165.038 | 248.7 | 27.5063 | 28.1071 | -0.60073 | 168.6424 | 28.4 | 27.7051 | 0.69486 |  | 22-03-2026 09:50 | 308.8305 | 305.8168 | 3.0137 | 1834.901 | 305.3 | 301.4436 | 3.8564 | 3.5305
22-03-2026 09:40 | 688 | 50.23 | 240.878 | 244.422 | 309.9 | 40.737 | 40.7427 | -0.0057448 | 244.4565 | 38.8 | 40.1601 | -1.3601 |  | 22-03-2026 09:40 | 243.31 | 246.965 | 311.2 | 41.1608 | 40.7427 | 0.41809 | 244.4565 | 39.1 | 40.1601 | -1.0601 |  | 22-03-2026 09:40 | 238.567 | 244.047 | 305.5 | 40.6745 | 40.7427 | -0.068245 | 244.4565 | 37.9 | 40.1601 | -2.2601 |  | 22-03-2026 09:40 | 241.679 | 245.285 | 308.3 | 40.8808 | 40.7427 | 0.13809 | 244.4565 | 37.8 | 40.1601 | -2.3601 |  | 22-03-2026 09:40 | 179.471 | 181.945 | 226.7 | 30.3242 | 30.1798 | 0.14436 | 181.0789 | 28.8 | 29.7482 | -0.94824 |  | 22-03-2026 09:40 | 179.973 | 182.436 | 230.4 | 30.406 | 30.1798 | 0.22619 | 181.0789 | 29 | 29.7482 | -0.74824 |  | 22-03-2026 09:40 | 179.569 | 182.047 | 229.3 | 30.3412 | 30.1798 | 0.16136 | 181.0789 | 28.9 | 29.7482 | -0.84824 |  | 22-03-2026 09:40 | 180.781 | 185.914 | 232.2 | 30.9857 | 30.1798 | 0.80586 | 181.0789 | 29 | 29.7482 | -0.74824 |  | 22-03-2026 09:40 | 171.532 | 173.879 | 220.3 | 28.9798 | 28.7124 | 0.26748 | 172.2741 | 27.6 | 28.3018 | -0.70177 |  | 22-03-2026 09:40 | 314.49 | 312.4026 | 2.0874 | 1874.4155 | 296.9 | 307.9352 | -11.0352 | 17.59
22-03-2026 09:30 | 635 | 49.94 | 224.496 | 227.637 | 271.1 | 37.9395 | 37.646 | 0.2935 | 225.876 | 35.6 | 37.1077 | -1.5077 |  | 22-03-2026 09:30 | 225.044 | 228.309 | 272.1 | 38.0515 | 37.646 | 0.4055 | 225.876 | 36.8 | 37.1077 | -0.30766 |  | 22-03-2026 09:30 | 221.771 | 226.475 | 267.6 | 37.7458 | 37.646 | 0.099836 | 225.876 | 35.7 | 37.1077 | -1.4077 |  | 22-03-2026 09:30 | 224.236 | 227.415 | 270.5 | 37.9025 | 37.646 | 0.2565 | 225.876 | 36.7 | 37.1077 | -0.40766 |  | 22-03-2026 09:30 | 165.883 | 168.119 | 197.9 | 28.0198 | 27.8859 | 0.13391 | 167.3155 | 26.6 | 27.4872 | -0.88716 |  | 22-03-2026 09:30 | 166.935 | 169.151 | 201.4 | 28.1918 | 27.8859 | 0.30591 | 167.3155 | 26.9 | 27.4872 | -0.58716 |  | 22-03-2026 09:30 | 166.041 | 168.304 | 200.4 | 28.0507 | 27.8859 | 0.16474 | 167.3155 | 26.8 | 27.4872 | -0.68716 |  | 22-03-2026 09:30 | 167.51 | 172.208 | 203.2 | 28.7013 | 27.8859 | 0.81541 | 167.3155 | 27 | 27.4872 | -0.48716 |  | 22-03-2026 09:30 | 158.861 | 161.002 | 192.7 | 26.8337 | 26.53 | 0.30366 | 159.18 | 25.6 | 26.1506 | -0.55062 |  | 22-03-2026 09:30 | 291.4367 | 288.6577 | 2.779 | 1731.9461 | 277.7 | 284.5299 | -6.8299 | 13.7367
22-03-2026 09:20 | 594 | 49.65 | 211.289 | 214.159 | 235.5 | 35.6932 | 35.2545 | 0.43869 | 211.5268 | 34.5 | 34.7503 | -0.25033 |  | 22-03-2026 09:20 | 212.29 | 215.239 | 235.3 | 35.8732 | 35.2545 | 0.61869 | 211.5268 | 34.1 | 34.7503 | -0.65033 |  | 22-03-2026 09:20 | 208.864 | 213.058 | 231.9 | 35.5097 | 35.2545 | 0.25519 | 211.5268 | 34 | 34.7503 | -0.75033 |  | 22-03-2026 09:20 | 211.796 | 214.738 | 233.8 | 35.7897 | 35.2545 | 0.53519 | 211.5268 | 33.8 | 34.7503 | -0.95033 |  | 22-03-2026 09:20 | 151.998 | 153.844 | 171.3 | 25.6407 | 26.1144 | -0.47376 | 156.6865 | 25 | 25.741 | -0.74099 |  | 22-03-2026 09:20 | 157.334 | 159.39 | 174.5 | 26.565 | 26.1144 | 0.45058 | 156.6865 | 25.2 | 25.741 | -0.54099 |  | 22-03-2026 09:20 | 156.585 | 158.631 | 173.6 | 26.4385 | 26.1144 | 0.32408 | 156.6865 | 25 | 25.741 | -0.74099 |  | 22-03-2026 09:20 | 157.869 | 162.216 | 176.2 | 27.036 | 26.1144 | 0.92158 | 156.6865 | 25.8 | 25.741 | 0.059012 |  | 22-03-2026 09:20 | 149.717 | 151.658 | 167.1 | 25.2763 | 24.8446 | 0.43169 | 149.0678 | 24.4 | 24.4894 | -0.089362 |  | 22-03-2026 09:20 | 273.8222 | 270.3202 | 3.5019 | 1621.9214 | 261.8 | 266.4547 | -4.6547 | 12.0222
22-03-2026 09:10 | 553 | 49.36 | 197.536 | 200.127 | 201 | 33.3545 | 32.8575 | 0.49696 | 197.1453 | 33.2 | 32.3877 | 0.81232 |  | 22-03-2026 09:10 | 0 | 0 | 201.2 | 0 | 32.8575 | -32.8575 | 197.1453 | 61.9 | 32.3877 | 29.5123 |  | 22-03-2026 09:10 | 195.391 | 199.117 | 197.9 | 33.1862 | 32.8575 | 0.32862 | 197.1453 | 31.3 | 32.3877 | -1.0877 |  | 22-03-2026 09:10 | 196.652 | 199.283 | 200 | 33.2138 | 32.8575 | 0.35629 | 197.1453 | 31.7 | 32.3877 | -0.68768 |  | 22-03-2026 09:10 | 146.014 | 147.892 | 146.3 | 24.6487 | 24.3389 | 0.30975 | 146.0335 | 23.2 | 23.9909 | -0.79087 |  | 22-03-2026 09:10 | 147.315 | 149.18 | 149.3 | 24.8633 | 24.3389 | 0.52441 | 146.0335 | 23.7 | 23.9909 | -0.29087 |  | 22-03-2026 09:10 | 146.465 | 148.319 | 148.6 | 24.7198 | 24.3389 | 0.38091 | 146.0335 | 23.5 | 23.9909 | -0.49087 |  | 22-03-2026 09:10 | 147.707 | 151.87 | 150.4 | 25.3117 | 24.3389 | 0.97275 | 146.0335 | 23.3 | 23.9909 | -0.69087 |  | 22-03-2026 09:10 | 140.118 | 141.906 | 142.7 | 23.651 | 23.1555 | 0.49553 | 138.9328 | 22.4 | 22.8243 | -0.42434 |  | 22-03-2026 09:10 | 222.949 | 251.9413 | -28.9923 | 1511.6479 | 274.2 | 248.3386 | 25.8614 | -51.251
22-03-2026 09:00 | 510 | 49.36 | 181.506 | 183.822 | 167.8 | 30.637 | 30.3026 | 0.33438 | 181.8157 | 27.2 | 29.8693 | -2.6693 | [5 empty] | 0 | 30.3026 | -30.3026 | 181.8157 | 0 | 29.8693 | -29.8693 |  | 22-03-2026 09:00 | 179.867 | 183.464 | 166.6 | 30.5773 | 30.3026 | 0.27472 | 181.8157 | 28.4 | 29.8693 | -1.4693 |  | 22-03-2026 09:00 | 182.621 | 184.97 | 168.3 | 30.8283 | 30.3026 | 0.52572 | 181.8157 | 29 | 29.8693 | -0.86929 |  | 22-03-2026 09:00 | 132.724 | 134.268 | 123.1 | 22.378 | 22.4464 | -0.068382 | 134.6783 | 21.5 | 22.1254 | -0.6254 |  | 22-03-2026 09:00 | 135.899 | 137.577 | 125.6 | 22.9295 | 22.4464 | 0.48312 | 134.6783 | 21.8 | 22.1254 | -0.3254 |  | 22-03-2026 09:00 | 135.046 | 136.721 | 125.1 | 22.7868 | 22.4464 | 0.34045 | 134.6783 | 21.7 | 22.1254 | -0.4254 |  | 22-03-2026 09:00 | 136.807 | 140.672 | 127.1 | 23.4453 | 22.4464 | 0.99895 | 134.6783 | 21.9 | 22.1254 | -0.2254 |  | 22-03-2026 09:00 | 129.424 | 131.022 | 120.3 | 21.837 | 21.355 | 0.48205 | 128.1297 | 20.5 | 21.0496 | -0.54958 |  | 22-03-2026 09:00 | 205.4193 | 232.3509 | -26.9316 | 1394.1057 | 192 | 229.0283 | -37.0283 | 13.4193
22-03-2026 08:50 | 458 | 48.79 | 164.864 | 166.866 | 140.6 | 27.811 | 27.2723 | 0.53871 | 163.6337 | 24.9 | 26.8823 | -1.9823 |  | 22-03-2026 08:50 | 160.127 | 162.184 | 139.3 | 27.0307 | 27.2723 | -0.24162 | 163.6337 | 24.3 | 26.8823 | -2.5823 |  | 22-03-2026 08:50 | 161.206 | 166.4 | 138.2 | 27.7333 | 27.2723 | 0.46105 | 163.6337 | 24.7 | 26.8823 | -2.1823 |  | 22-03-2026 08:50 | 161.784 | 163.782 | 139.3 | 27.297 | 27.2723 | 0.024713 | 163.6337 | 24.8 | 26.8823 | -2.0823 |  | 22-03-2026 08:50 | 120.474 | 121.925 | 101.6 | 20.3208 | 20.2017 | 0.11914 | 121.2102 | 18.3 | 19.9128 | -1.6128 |  | 22-03-2026 08:50 | 121.736 | 123.19 | 103.8 | 20.5317 | 20.2017 | 0.32997 | 121.2102 | 18.5 | 19.9128 | -1.4128 |  | 22-03-2026 08:50 | 121.616 | 123.081 | 103.4 | 20.5135 | 20.2017 | 0.31181 | 121.2102 | 18.5 | 19.9128 | -1.4128 |  | 22-03-2026 08:50 | 122.754 | 126.285 | 105.2 | 21.0475 | 20.2017 | 0.84581 | 121.2102 | 18.7 | 19.9128 | -1.2128 |  | 22-03-2026 08:50 | 116.339 | 117.764 | 99.8 | 19.6273 | 19.2194 | 0.40792 | 115.3165 | 17.8 | 18.9446 | -1.1446 |  | 22-03-2026 08:50 | 211.9128 | 209.1153 | 2.7975 | 1254.692 | 190.5 | 206.125 | -15.625 | 21.4128
22-03-2026 08:40 | 404 | 47.35 | 143.703 | 145.639 | 115.7 | 24.2732 | 24.189 | 0.084131 | 145.1342 | 24.1 | 23.8431 | 0.25687 |  | 22-03-2026 08:40 | 142.508 | 144.311 | 115 | 24.0518 | 24.189 | -0.1372 | 145.1342 | 23.8 | 23.8431 | -0.043133 |  | 22-03-2026 08:40 | 142.426 | 144.73 | 113.5 | 24.1217 | 24.189 | -0.067369 | 145.1342 | 23.8 | 23.8431 | -0.043133 |  | 22-03-2026 08:40 | 142.221 | 143.963 | 114.5 | 23.9938 | 24.189 | -0.1952 | 145.1342 | 23.8 | 23.8431 | -0.043133 |  | 22-03-2026 08:40 | 104.465 | 105.712 | 83.3 | 17.6187 | 17.9178 | -0.29914 | 107.5068 | 17.3 | 17.6616 | -0.36158 |  | 22-03-2026 08:40 | 106.924 | 108.179 | 85.3 | 18.0298 | 17.9178 | 0.11203 | 107.5068 | 17.7 | 17.6616 | 0.03842 |  | 22-03-2026 08:40 | 106.631 | 107.893 | 84.9 | 17.9822 | 17.9178 | 0.064362 | 107.5068 | 17.6 | 17.6616 | -0.06158 |  | 22-03-2026 08:40 | 108.82 | 111.806 | 86.5 | 18.6343 | 17.9178 | 0.71653 | 107.5068 | 18.1 | 17.6616 | 0.43842 |  | 22-03-2026 08:40 | 103.257 | 104.373 | 82 | 17.3955 | 17.0466 | 0.34893 | 102.2794 | 17.2 | 16.8028 | 0.39719 |  | 22-03-2026 08:40 | 186.101 | 185.4739 | 0.62707 | 1112.8436 | 183.4 | 182.8217 | 0.57834 | 2.701
22-03-2026 08:30 | 384 | 44.2 | 134.114 | 135.661 | 91.6 | 22.6102 | 23.2666 | -0.65639 | 139.5993 | 38.8 | 22.9338 | 15.8662 |  | 22-03-2026 08:30 | 136.027 | 137.651 | 91.2 | 22.9418 | 23.2666 | -0.32472 | 139.5993 | 21.3 | 22.9338 | -1.6338 |  | 22-03-2026 08:30 | 133.752 | 135.732 | 89.7 | 22.622 | 23.2666 | -0.64455 | 139.5993 | 20.7 | 22.9338 | -2.2338 |  | 22-03-2026 08:30 | 135.56 | 137.165 | 90.7 | 22.8608 | 23.2666 | -0.40572 | 139.5993 | 21 | 22.9338 | -1.9338 |  | 22-03-2026 08:30 | 99.286 | 100.431 | 66 | 16.7385 | 17.2345 | -0.49598 | 103.4069 | 15.4 | 16.988 | -1.588 |  | 22-03-2026 08:30 | 100.019 | 101.059 | 67.6 | 16.8432 | 17.2345 | -0.39132 | 103.4069 | 15.6 | 16.988 | -1.388 |  | 22-03-2026 08:30 | 100.693 | 101.854 | 67.3 | 16.9757 | 17.2345 | -0.25882 | 103.4069 | 15.5 | 16.988 | -1.488 |  | 22-03-2026 08:30 | 101.393 | 104.486 | 68.4 | 17.4143 | 17.2345 | 0.17985 | 103.4069 | 15.8 | 16.988 | -1.188 |  | 22-03-2026 08:30 | 96.519 | 97.642 | 64.8 | 16.2737 | 16.3965 | -0.12281 | 98.3789 | 15 | 16.162 | -1.162 |  | 22-03-2026 08:30 | 175.2802 | 178.4006 | -3.1205 | 1070.4037 | 179.1 | 175.8495 | 3.2505 | -3.8198
22-03-2026 08:20 | 334 | 39.03 |  |  |  | 0 | 20.6296 | -20.6296 | 123.7777 | 0 | 20.3346 | -20.3346 |  | 22-03-2026 08:20 | 114.705 | 117.64 | 69.9 | 19.6067 | 20.6296 | -1.023 | 123.7777 | 17.6 | 20.3346 | -2.7346 |  | 22-03-2026 08:20 | 114.373 | 115.827 | 69 | 19.3045 | 20.6296 | -1.3251 | 123.7777 | 17.7 | 20.3346 | -2.6346 |  | 22-03-2026 08:20 | 116.141 | 117.48 | 69.7 | 19.58 | 20.6296 | -1.0496 | 123.7777 | 18 | 20.3346 | -2.3346 |  | 22-03-2026 08:20 | 84.793 | 85.762 | 50.6 | 14.2937 | 15.2812 | -0.98754 | 91.6872 | 13.1 | 15.0627 | -1.9627 |  | 22-03-2026 08:20 | 85.941 | 86.906 | 52 | 14.4843 | 15.2812 | -0.79687 | 91.6872 | 13.4 | 15.0627 | -1.6627 |  | 22-03-2026 08:20 | 86.274 | 87.269 | 51.8 | 14.5448 | 15.2812 | -0.73637 | 91.6872 | 13.4 | 15.0627 | -1.6627 |  | 22-03-2026 08:20 | 87.283 | 89.567 | 52.6 | 14.9278 | 15.2812 | -0.35337 | 91.6872 | 13.4 | 15.0627 | -1.6627 |  | 22-03-2026 08:20 | 83.233 | 84.21 | 49.8 | 14.035 | 14.5382 | -0.50317 | 87.229 | 12.7 | 14.3303 | -1.6303 |  | 22-03-2026 08:20 | 130.7768 | 158.1815 | -27.4046 | 949.0889 | 119.3 | 155.9195 | -36.6195 | 11.4768
22-03-2026 08:10 | 288 | 36.16 | 98.686 | 99.753 | 52.8 | 16.6255 | 17.9763 | -1.3508 | 107.858 | 15.2 | 17.7193 | -2.5193 |  | 22-03-2026 08:10 | 97.32 | 98.818 | 52.3 | 16.4697 | 17.9763 | -1.5067 | 107.858 | 15.5 | 17.7193 | -2.2193 |  | 22-03-2026 08:10 | 96.785 | 97.975 | 51.3 | 16.3292 | 17.9763 | -1.6472 | 107.858 | 14.6 | 17.7193 | -3.1193 |  | 22-03-2026 08:10 | 98.03 | 99.12 | 51.7 | 16.52 | 17.9763 | -1.4563 | 107.858 | 14.8 | 17.7193 | -2.9193 |  | 22-03-2026 08:10 | 71.543 | 72.397 | 37.5 | 12.0662 | 13.3158 | -1.2496 | 79.8948 | 10.8 | 13.1254 | -2.3254 |  | 22-03-2026 08:10 | 73.287 | 74.14 | 38.6 | 12.3567 | 13.3158 | -0.95913 | 79.8948 | 11 | 13.1254 | -2.1254 |  | 22-03-2026 08:10 | 72.128 | 72.982 | 38.4 | 12.1637 | 13.3158 | -1.1521 | 79.8948 | 11.1 | 13.1254 | -2.0254 |  | 22-03-2026 08:10 | 74.155 | 76.202 | 39.2 | 12.7003 | 13.3158 | -0.61547 | 79.8948 | 11.4 | 13.1254 | -1.7254 |  | 22-03-2026 08:10 | 70.394 | 71.242 | 37.1 | 11.8737 | 12.6683 | -0.79467 | 76.01 | 10.8 | 12.4872 | -1.6872 |  | 22-03-2026 08:10 | 127.1048 | 137.8369 | -10.732 | 827.0211 | 115.2 | 135.8658 | -20.6658 | 11.9048
22-03-2026 08:00 | 245 | 29.85 | 81.745 | 82.646 | 37.6 | 13.7743 | 15.6438 | -1.8695 | 93.8629 | 12.4 | 15.4201 | -3.0201 |  | 22-03-2026 08:00 | 79.965 | 80.871 | 36.8 | 13.4785 | 15.6438 | -2.1653 | 93.8629 | 12 | 15.4201 | -3.4201 |  | 22-03-2026 08:00 | 80.587 | 81.483 | 36.7 | 13.5805 | 15.6438 | -2.0633 | 93.8629 | 12.1 | 15.4201 | -3.3201 |  | 22-03-2026 08:00 | 81.806 | 82.611 | 36.9 | 13.7685 | 15.6438 | -1.8753 | 93.8629 | 12.5 | 15.4201 | -2.9201 |  | 22-03-2026 08:00 | 59.275 | 60.019 | 26.7 | 10.0032 | 11.588 | -1.5849 | 69.5281 | 9.1 | 11.4223 | -2.3223 |  | 22-03-2026 08:00 | 61.054 | 61.789 | 27.6 | 10.2982 | 11.588 | -1.2899 | 69.5281 | 9.4 | 11.4223 | -2.0223 |  | 22-03-2026 08:00 | 60.572 | 61.32 | 27.3 | 10.22 | 11.588 | -1.368 | 69.5281 | 9.2 | 11.4223 | -2.2223 |  | 22-03-2026 08:00 | 61.5 | 63.448 | 27.8 | 10.5747 | 11.588 | -1.0134 | 69.5281 | 9.3 | 11.4223 | -2.1223 |  | 22-03-2026 08:00 | 58.598 | 59.34 | 26.3 | 9.89 | 11.0246 | -1.1346 | 66.1474 | 8.9 | 10.8669 | -1.9669 |  | 22-03-2026 08:00 | 105.5878 | 119.9519 | -14.3641 | 719.7116 | 94.9 | 118.2366 | -23.3366 | 10.6878
22-03-2026 07:50 | 204 | 23.25 | 67.065 | 67.811 | 25.2 | 11.3018 | 13.332 | -2.0301 | 79.9918 | 9.8 | 13.1413 | -3.3413 |  | 22-03-2026 07:50 | 66.576 | 67.357 | 24.8 | 11.2262 | 13.332 | -2.1058 | 79.9918 | 9.8 | 13.1413 | -3.3413 |  | 22-03-2026 07:50 | 65.439 | 66.214 | 24.6 | 11.0357 | 13.332 | -2.2963 | 79.9918 | 9.7 | 13.1413 | -3.4413 |  | 22-03-2026 07:50 | 66.07 | 66.852 | 24.4 | 11.142 | 13.332 | -2.19 | 79.9918 | 9.6 | 13.1413 | -3.5413 |  | 22-03-2026 07:50 | 47.882 | 48.557 | 17.6 | 8.0928 | 9.8755 | -1.7827 | 59.2532 | 6.9 | 9.7343 | -2.8343 |  | 22-03-2026 07:50 | 49.453 | 50 | 18.2 | 8.3333 | 9.8755 | -1.5422 | 59.2532 | 7.1 | 9.7343 | -2.6343 |  | 22-03-2026 07:50 | 49.243 | 49.927 | 18.1 | 8.3212 | 9.8755 | -1.5544 | 59.2532 | 7.1 | 9.7343 | -2.6343 |  | 22-03-2026 07:50 | 50.166 | 51.593 | 18.5 | 8.5988 | 9.8755 | -1.2767 | 59.2532 | 7.4 | 9.7343 | -2.3343 |  | 22-03-2026 07:50 | 47.698 | 48.361 | 17.4 | 8.0602 | 9.3953 | -1.3352 | 56.3721 | 7 | 9.261 | -2.261 |  | 22-03-2026 07:50 | 86.112 | 102.2254 | -16.1134 | 613.3522 | 74.4 | 100.7635 | -26.3635 | 11.712
22-03-2026 07:40 | 161 | 16.93 | 51.521 | 52.189 | 15.4 | 8.6982 | 10.7531 | -2.055 | 64.5188 | 7.4 | 10.5994 | -3.1994 |  | 22-03-2026 07:40 | 50.613 | 51.28 | 15 | 8.5467 | 10.7531 | -2.2065 | 64.5188 | 7.3 | 10.5994 | -3.2994 |  | 22-03-2026 07:40 | 50.109 | 50.764 | 14.9 | 8.4607 | 10.7531 | -2.2925 | 64.5188 | 7.2 | 10.5994 | -3.3994 |  | 22-03-2026 07:40 | 50.644 | 51.316 | 14.8 | 8.5527 | 10.7531 | -2.2005 | 64.5188 | 7.3 | 10.5994 | -3.2994 |  | 22-03-2026 07:40 | 36.605 | 37.162 | 10.7 | 6.1937 | 7.9653 | -1.7716 | 47.7917 | 5.3 | 7.8514 | -2.5514 |  | 22-03-2026 07:40 | 37.941 | 38.503 | 11.1 | 6.4172 | 7.9653 | -1.5481 | 47.7917 | 5.5 | 7.8514 | -2.3514 |  | 22-03-2026 07:40 | 37.63 | 38.344 | 11 | 6.3907 | 7.9653 | -1.5746 | 47.7917 | 5.5 | 7.8514 | -2.3514 |  | 22-03-2026 07:40 | 38.454 | 39.524 | 11.1 | 6.5873 | 7.9653 | -1.3779 | 47.7917 | 5.4 | 7.8514 | -2.4514 |  | 22-03-2026 07:40 | 36.307 | 37.03 | 10.4 | 6.1717 | 7.578 | -1.4063 | 45.4679 | 5.2 | 7.4696 | -2.2696 |  | 22-03-2026 07:40 | 66.0187 | 82.4516 | -16.4329 | 494.7096 | 56.1 | 81.2725 | -25.1725 | 9.9187
22-03-2026 07:30 | 122 | 17.22 | 38.363 | 38.924 | 8 | 6.4873 | 8.1403 | -1.653 | 48.8417 | 4.9 | 8.0239 | -3.1239 |  | 22-03-2026 07:30 | 36.349 | 36.895 | 7.7 | 6.1492 | 8.1403 | -1.9911 | 48.8417 | 4.8 | 8.0239 | -3.2239 |  | 22-03-2026 07:30 | 36.829 | 37.386 | 7.7 | 6.231 | 8.1403 | -1.9093 | 48.8417 | 4.7 | 8.0239 | -3.3239 |  | 22-03-2026 07:30 | 36.728 | 37.295 | 7.5 | 6.2158 | 8.1403 | -1.9245 | 48.8417 | 4.6 | 8.0239 | -3.4239 |  | 22-03-2026 07:30 | 26.665 | 27.143 | 5.4 | 4.5238 | 6.0298 | -1.506 | 36.1791 | 3.3 | 5.9436 | -2.6436 |  | 22-03-2026 07:30 | 27.655 | 28.119 | 5.6 | 4.6865 | 6.0298 | -1.3433 | 36.1791 | 3.5 | 5.9436 | -2.4436 |  | 22-03-2026 07:30 | 27.467 | 27.93 | 5.5 | 4.655 | 6.0298 | -1.3748 | 36.1791 | 3.4 | 5.9436 | -2.5436 |  | 22-03-2026 07:30 | 28.06 | 29.065 | 5.7 | 4.8442 | 6.0298 | -1.1857 | 36.1791 | 3.6 | 5.9436 | -2.3436 |  | 22-03-2026 07:30 | 26.22 | 26.695 | 5.2 | 4.4492 | 5.7366 | -1.2875 | 34.4199 | 3.3 | 5.6546 | -2.3546 |  | 22-03-2026 07:30 | 48.242 | 62.4172 | -14.1752 | 374.5031 | 36.1 | 61.5246 | -25.4246 | 12.142
22-03-2026 07:20 | 53 | 14.92 | 18.214 | 18.622 | 3.1 | 3.1037 | 3.5641 | -0.4604 | 21.3844 | 1.8 | 3.5131 | -1.7131 |  | 22-03-2026 07:20 | 15.226 | 15.78 | 2.9 | 2.63 | 3.5641 | -0.93407 | 21.3844 | 1.6 | 3.5131 | -1.9131 |  | 22-03-2026 07:20 | 17.758 | 18.167 | 3 | 3.0278 | 3.5641 | -0.53623 | 21.3844 | 1.7 | 3.5131 | -1.8131 |  | 22-03-2026 07:20 | 17.129 | 17.954 | 2.9 | 2.9923 | 3.5641 | -0.57173 | 21.3844 | 1.7 | 3.5131 | -1.8131 |  | 22-03-2026 07:20 | 12.706 | 13.344 | 2.1 | 2.224 | 2.6401 | -0.41605 | 15.8403 | 1.3 | 2.6023 | -1.3023 |  | 22-03-2026 07:20 | 13.091 | 13.456 | 2.1 | 2.2427 | 2.6401 | -0.39738 | 15.8403 | 1.3 | 2.6023 | -1.3023 |  | 22-03-2026 07:20 | 13.048 | 13.424 | 2.1 | 2.2373 | 2.6401 | -0.40272 | 15.8403 | 1.3 | 2.6023 | -1.3023 |  | 22-03-2026 07:20 | 13.351 | 14.321 | 2.1 | 2.3868 | 2.6401 | -0.25322 | 15.8403 | 1.3 | 2.6023 | -1.3023 |  | 22-03-2026 07:20 | 12.091 | 12.459 | 1.9 | 2.0765 | 2.5117 | -0.43518 | 15.0701 | 1.1 | 2.4758 | -1.3758 |  | 22-03-2026 07:20 | 22.9212 | 27.3282 | -4.407 | 163.9689 | 13.1 | 26.9374 | -13.8374 | 9.8212
22-03-2026 07:10 | 17 | 14.35 | 6.248 | 6.51 | 1.3 | 1.085 | 1.1454 | -0.060395 | 6.8724 | 0.8 | 1.129 | -0.32902 |  | 22-03-2026 07:10 | 6.066 | 6.741 | 1.3 | 1.1235 | 1.1454 | -0.021895 | 6.8724 | 0.8 | 1.129 | -0.32902 |  | 22-03-2026 07:10 | 6.166 | 6.43 | 1.3 | 1.0717 | 1.1454 | -0.073728 | 6.8724 | 0.8 | 1.129 | -0.32902 |  | 22-03-2026 07:10 | 6.135 | 6.894 | 1.2 | 1.149 | 1.1454 | 0.0036055 | 6.8724 | 0.8 | 1.129 | -0.32902 |  | 22-03-2026 07:10 | 4.334 | 4.996 | 0.8 | 0.83267 | 0.84844 | -0.015774 | 5.0906 | 0.5 | 0.83631 | -0.33631 |  | 22-03-2026 07:10 | 4.327 | 4.526 | 0.8 | 0.75433 | 0.84844 | -0.094107 | 5.0906 | 0.5 | 0.83631 | -0.33631 |  | 22-03-2026 07:10 | 4.328 | 4.53 | 0.8 | 0.755 | 0.84844 | -0.09344 | 5.0906 | 0.5 | 0.83631 | -0.33631 |  | 22-03-2026 07:10 | 4.448 | 4.969 | 0.8 | 0.82817 | 0.84844 | -0.020274 | 5.0906 | 0.5 | 0.83631 | -0.33631 |  | 22-03-2026 07:10 | 4.093 | 4.282 | 0.8 | 0.71367 | 0.80719 | -0.093519 | 4.8431 | 0.6 | 0.79564 | -0.19564 |  | 22-03-2026 07:10 | 8.313 | 8.7825 | -0.46953 | 52.6952 | 5.8 | 8.6569 | -2.8569 | 2.513
22-03-2026 07:00 | 11 | 14.92 | 4.041 | 4.233 | 0.5 | 0.7055 | 0.73971 | -0.034212 | 4.4383 | 0.5 | 0.72913 | -0.22913 |  | 22-03-2026 07:00 | 3.926 | 4.548 | 0.5 | 0.758 | 0.73971 | 0.018288 | 4.4383 | 0.5 | 0.72913 | -0.22913 |  | 22-03-2026 07:00 | 3.929 | 4.113 | 0.5 | 0.6855 | 0.73971 | -0.054212 | 4.4383 | 0.5 | 0.72913 | -0.22913 |  | 22-03-2026 07:00 | 3.837 | 4.56 | 0.4 | 0.76 | 0.73971 | 0.020288 | 4.4383 | 0.4 | 0.72913 | -0.32913 |  | 22-03-2026 07:00 | 2.71 | 3.325 | 0.3 | 0.55417 | 0.54793 | 0.0062317 | 3.2876 | 0.3 | 0.5401 | -0.2401 |  | 22-03-2026 07:00 | 2.743 | 2.878 | 0.3 | 0.47967 | 0.54793 | -0.068268 | 3.2876 | 0.3 | 0.5401 | -0.2401 |  | 22-03-2026 07:00 | 2.752 | 2.888 | 0.3 | 0.48133 | 0.54793 | -0.066602 | 3.2876 | 0.3 | 0.5401 | -0.2401 |  | 22-03-2026 07:00 | 2.807 | 3.403 | 0.3 | 0.56717 | 0.54793 | 0.019232 | 3.2876 | 0.3 | 0.5401 | -0.2401 |  | 22-03-2026 07:00 | 2.548 | 2.676 | 0.2 | 0.446 | 0.52129 | -0.075292 | 3.1278 | 0.2 | 0.51384 | -0.31384 |  | 22-03-2026 07:00 | 5.4373 | 5.6719 | -0.23455 | 34.0313 | 3.3 | 5.5908 | -2.2908 | 2.1373
[110 empty] | Total: - | 14589.0357 | 18029.3926 | -3440.357 |  | 14483.5 | 17771.5723 | -3288.0723 | 105.5357
Sum:- | 39577 |  | 11004.346 |  | 78110.5 |  |  |  |  | 1885.3 | 2317.723 | -432.423 | 0.98678 |  | 10150.546 |  | 78755.8 |  |  |  |  | 1898.5 | 2317.723 | -419.223 | 0.98901 |  | 11321.963 |  | 81051.2 |  |  |  |  | 1869.2 | 2317.723 | -448.523 | 0.97309 |  | 11413.596 |  | 81803.6 |  |  |  |  | 1886 | 2317.723 | -431.723 | 0.98289 |  | 8506.149 |  | 60940 |  |  |  |  | 1407.4 | 1716.8319 | -309.4319 | 0.98522 |  | 8480.991 |  | 60760 |  |  |  |  | 1399.8 | 1716.8319 | -317.0319 | 0.98306 |  | 8468.499 |  | 60665.1 |  |  |  |  | 1398.2 | 1716.8319 | -318.6319 | 0.98158 |  | 8525.279 |  | 61106 |  |  |  |  | 1407.4 | 1716.8319 | -309.4319 | 0.9709 |  | 8081.608 |  | 57839.9 |  |  |  |  | 1331.7 | 1633.3529 | -301.6529 | 0.98488

## 23 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual | Inverter No. | Efficiency
23-03-2026 19:00 | 0 | 37.31 | 0.08 | 0.094 | 1768.4 | 0.015667 | 0 | 0.015667 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0 | 0.258 | 1793.8 | 0.043 | 0 | 0.043 | 0 | 0.1 | 0 | 0.1 |  | 23-03-2026 19:00 | 0.05 | 0.088 | 1761.4 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.003 | 0.311 | 1778.7 | 0.051833 | 0 | 0.051833 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.061 | 0.064 | 1336.5 | 0.010667 | 0 | 0.010667 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.077 | 0.081 | 1324.2 | 0.0135 | 0 | 0.0135 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.093 | 0.098 | 1319.2 | 0.016333 | 0 | 0.016333 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.073 | 0.088 | 1328.2 | 0.014667 | 0 | 0.014667 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.096 | 0.101 | 1258.3 | 0.016833 | 0 | 0.016833 | 0 | 0 | 0 | 0 |  | 23-03-2026 19:00 | 0.19717 | 0 | 0.19717 | 0 | 0.1 | 0 | 0.1 | 0.097167 | 1 | 97.06%
23-03-2026 18:50 | 4 | 38.46 | 0.842 | 0.893 | 1768.4 | 0.14883 | 0.24758 | -0.098746 | 1.4855 | 0.3 | 0.24404 | 0.055961 |  | 23-03-2026 18:50 | 1.193 | 1.537 | 1793.7 | 0.25617 | 0.24758 | 0.008587 | 1.4855 | 0.3 | 0.24404 | 0.055961 |  | 23-03-2026 18:50 | 0.932 | 0.98 | 1761.4 | 0.16333 | 0.24758 | -0.084246 | 1.4855 | 0.3 | 0.24404 | 0.055961 |  | 23-03-2026 18:50 | 0.934 | 1.337 | 1778.7 | 0.22283 | 0.24758 | -0.024746 | 1.4855 | 0.4 | 0.24404 | 0.15596 |  | 23-03-2026 18:50 | 0.559 | 0.601 | 1336.5 | 0.10017 | 0.18339 | -0.083226 | 1.1004 | 0.2 | 0.18077 | 0.01923 |  | 23-03-2026 18:50 | 0.499 | 0.449 | 1324.2 | 0.074833 | 0.18339 | -0.10856 | 1.1004 | 0.2 | 0.18077 | 0.01923 |  | 23-03-2026 18:50 | 0.509 | 0.535 | 1319.2 | 0.089167 | 0.18339 | -0.094226 | 1.1004 | 0.2 | 0.18077 | 0.01923 |  | 23-03-2026 18:50 | 0.663 | 0.737 | 1328.2 | 0.12283 | 0.18339 | -0.060559 | 1.1004 | 0.2 | 0.18077 | 0.01923 |  | 23-03-2026 18:50 | 0.451 | 0.474 | 1258.3 | 0.079 | 0.17448 | -0.095475 | 1.0469 | 0.2 | 0.17198 | 0.02802 |  | 23-03-2026 18:50 | 1.2572 | 1.8984 | -0.6412 | 11.3902 | 2.3 | 1.8712 | 0.42878 | -1.0428 | 2 | 98.78%
23-03-2026 18:40 | 4 | 41.04 | 2.546 | 2.677 | 1768.1 | 0.44617 | 0.24523 | 0.20093 | 1.4714 | 1 | 0.24173 | 0.75827 |  | 23-03-2026 18:40 | 2.732 | 3.053 | 1793.4 | 0.50883 | 0.24523 | 0.2636 | 1.4714 | 1 | 0.24173 | 0.75827 |  | 23-03-2026 18:40 | 2.54 | 2.671 | 1761.1 | 0.44517 | 0.24523 | 0.19993 | 1.4714 | 1 | 0.24173 | 0.75827 |  | 23-03-2026 18:40 | 2.584 | 3.018 | 1778.3 | 0.503 | 0.24523 | 0.25777 | 1.4714 | 0.9 | 0.24173 | 0.65827 |  | 23-03-2026 18:40 | 1.626 | 1.878 | 1336.3 | 0.313 | 0.18165 | 0.13135 | 1.0899 | 0.7 | 0.17906 | 0.52094 |  | 23-03-2026 18:40 | 1.747 | 1.837 | 1324 | 0.30617 | 0.18165 | 0.12451 | 1.0899 | 0.7 | 0.17906 | 0.52094 |  | 23-03-2026 18:40 | 1.73 | 1.819 | 1319 | 0.30317 | 0.18165 | 0.12151 | 1.0899 | 0.7 | 0.17906 | 0.52094 |  | 23-03-2026 18:40 | 1.696 | 2.004 | 1328 | 0.334 | 0.18165 | 0.15235 | 1.0899 | 0.7 | 0.17906 | 0.52094 |  | 23-03-2026 18:40 | 1.629 | 1.713 | 1258.1 | 0.2855 | 0.17282 | 0.11268 | 1.0369 | 0.6 | 0.17035 | 0.42965 |  | 23-03-2026 18:40 | 3.445 | 1.8804 | 1.5646 | 11.2822 | 7.3 | 1.8535 | 5.4465 | -3.855 | 3 | 97.48%
23-03-2026 18:30 | 22 | 43.62 | 9.504 | 9.867 | 1767.1 | 1.6445 | 1.3359 | 0.30862 | 8.0153 | 2.1 | 1.3168 | 0.78322 |  | 23-03-2026 18:30 | 10.024 | 10.464 | 1792.4 | 1.744 | 1.3359 | 0.40812 | 8.0153 | 2.2 | 1.3168 | 0.88322 |  | 23-03-2026 18:30 | 9.688 | 10.061 | 1760.1 | 1.6768 | 1.3359 | 0.34095 | 8.0153 | 2.2 | 1.3168 | 0.88322 |  | 23-03-2026 18:30 | 9.75 | 10.138 | 1777.4 | 1.6897 | 1.3359 | 0.35379 | 8.0153 | 2.2 | 1.3168 | 0.88322 |  | 23-03-2026 18:30 | 7.093 | 7.453 | 1335.6 | 1.2422 | 0.98954 | 0.25263 | 5.9372 | 1.6 | 0.97539 | 0.62461 |  | 23-03-2026 18:30 | 6.921 | 7.218 | 1323.3 | 1.203 | 0.98954 | 0.21346 | 5.9372 | 1.6 | 0.97539 | 0.62461 |  | 23-03-2026 18:30 | 6.672 | 6.965 | 1318.3 | 1.1608 | 0.98954 | 0.17129 | 5.9372 | 1.5 | 0.97539 | 0.52461 |  | 23-03-2026 18:30 | 6.488 | 6.827 | 1327.3 | 1.1378 | 0.98954 | 0.14829 | 5.9372 | 1.4 | 0.97539 | 0.42461 |  | 23-03-2026 18:30 | 6.096 | 6.374 | 1257.5 | 1.0623 | 0.94143 | 0.12091 | 5.6486 | 1.3 | 0.92796 | 0.37204 |  | 23-03-2026 18:30 | 12.5612 | 10.2431 | 2.3181 | 61.4587 | 16.1 | 10.0966 | 6.0034 | -3.5388 | 4 | 98.29%
23-03-2026 18:20 | 37 | 45.92 | 15.99 | 16.417 | 1765 | 2.7362 | 2.2274 | 0.50881 | 13.3642 | 3.5 | 2.1955 | 1.3045 |  | 23-03-2026 18:20 | 17.308 | 17.092 | 1790.2 | 2.8487 | 2.2274 | 0.62131 | 13.3642 | 3.6 | 2.1955 | 1.4045 |  | 23-03-2026 18:20 | 16.463 | 16.896 | 1757.9 | 2.816 | 2.2274 | 0.58864 | 13.3642 | 3.4 | 2.1955 | 1.2045 |  | 23-03-2026 18:20 | 16.444 | 16.878 | 1775.2 | 2.813 | 2.2274 | 0.58564 | 13.3642 | 3.4 | 2.1955 | 1.2045 |  | 23-03-2026 18:20 | 12.233 | 12.637 | 1334 | 2.1062 | 1.6499 | 0.45627 | 9.8994 | 2.6 | 1.6263 | 0.9737 |  | 23-03-2026 18:20 | 11.724 | 12.112 | 1321.7 | 2.0187 | 1.6499 | 0.36877 | 9.8994 | 2.4 | 1.6263 | 0.7737 |  | 23-03-2026 18:20 | 11.388 | 11.782 | 1316.8 | 1.9637 | 1.6499 | 0.31377 | 9.8994 | 2.4 | 1.6263 | 0.7737 |  | 23-03-2026 18:20 | 9.68 | 10.151 | 1325.9 | 1.6918 | 1.6499 | 0.041936 | 9.8994 | 1.9 | 1.6263 | 0.2737 |  | 23-03-2026 18:20 | 9.864 | 10.226 | 1256.2 | 1.7043 | 1.5697 | 0.13466 | 9.418 | 2.1 | 1.5472 | 0.55277 |  | 23-03-2026 18:20 | 20.6985 | 17.0787 | 3.6198 | 102.4722 | 25.3 | 16.8345 | 8.4655 | -4.6015 | 5 | 98.23%
23-03-2026 18:10 | 49 | 47.93 | 25.279 | 25.318 | 1761.5 | 4.2197 | 2.9274 | 1.2923 | 17.5641 | 4.8 | 2.8855 | 1.9145 |  | 23-03-2026 18:10 | 25.508 | 26.06 | 1786.6 | 4.3433 | 2.9274 | 1.416 | 17.5641 | 5.1 | 2.8855 | 2.2145 |  | 23-03-2026 18:10 | 25.105 | 25.644 | 1754.5 | 4.274 | 2.9274 | 1.3466 | 17.5641 | 5 | 2.8855 | 2.1145 |  | 23-03-2026 18:10 | 24.932 | 25.469 | 1771.8 | 4.2448 | 2.9274 | 1.3175 | 17.5641 | 5 | 2.8855 | 2.1145 |  | 23-03-2026 18:10 | 18.757 | 19.216 | 1331.4 | 3.2027 | 2.1684 | 1.0343 | 13.0105 | 3.8 | 2.1374 | 1.6626 |  | 23-03-2026 18:10 | 17.928 | 18.384 | 1319.3 | 3.064 | 2.1684 | 0.89559 | 13.0105 | 3.6 | 2.1374 | 1.4626 |  | 23-03-2026 18:10 | 17.658 | 18.093 | 1314.4 | 3.0155 | 2.1684 | 0.84709 | 13.0105 | 3.6 | 2.1374 | 1.4626 |  | 23-03-2026 18:10 | 13.79 | 14.261 | 1324 | 2.3768 | 2.1684 | 0.20842 | 13.0105 | 2.9 | 2.1374 | 0.7626 |  | 23-03-2026 18:10 | 15.932 | 16.354 | 1254.1 | 2.7257 | 2.063 | 0.66269 | 12.3779 | 3.3 | 2.0335 | 1.2665 |  | 23-03-2026 18:10 | 31.4665 | 22.4461 | 9.0204 | 134.6764 | 37.1 | 22.1251 | 14.9749 | -5.6335 | 6 | 98.08%
23-03-2026 18:00 | 62 | 49.94 | 35.041 | 35.662 | 1756.7 | 5.9437 | 3.6757 | 2.268 | 22.054 | 7.2 | 3.6231 | 3.5769 |  | 23-03-2026 18:00 | 36.109 | 36.748 | 1781.5 | 6.1247 | 3.6757 | 2.449 | 22.054 | 7 | 3.6231 | 3.3769 |  | 23-03-2026 18:00 | 35.697 | 36.322 | 1749.5 | 6.0537 | 3.6757 | 2.378 | 22.054 | 7.1 | 3.6231 | 3.4769 |  | 23-03-2026 18:00 | 35.033 | 35.661 | 1766.8 | 5.9435 | 3.6757 | 2.2678 | 22.054 | 7 | 3.6231 | 3.3769 |  | 23-03-2026 18:00 | 26.762 | 27.308 | 1327.6 | 4.5513 | 2.7227 | 1.8286 | 16.3363 | 5.2 | 2.6838 | 2.5162 |  | 23-03-2026 18:00 | 25.629 | 26.168 | 1315.7 | 4.3613 | 2.7227 | 1.6386 | 16.3363 | 5 | 2.6838 | 2.3162 |  | 23-03-2026 18:00 | 25.712 | 26.253 | 1310.8 | 4.3755 | 2.7227 | 1.6528 | 16.3363 | 5.1 | 2.6838 | 2.4162 |  | 23-03-2026 18:00 | 22.865 | 23.642 | 1321.1 | 3.9403 | 2.7227 | 1.2176 | 16.3363 | 4.8 | 2.6838 | 2.1162 |  | 23-03-2026 18:00 | 23.938 | 24.465 | 1250.8 | 4.0775 | 2.5903 | 1.4872 | 15.542 | 4.8 | 2.5533 | 2.2467 |  | 23-03-2026 18:00 | 45.3715 | 28.1839 | 17.1876 | 169.1034 | 53.2 | 27.7809 | 25.4191 | -7.8285 | 7 | 97.65%
23-03-2026 17:50 | 153 | 50.8 | 49.436 | 49.684 | 1749.5 | 8.2807 | 9.0407 | -0.76003 | 54.2442 | 9.3 | 8.9114 | 0.38859 |  | 23-03-2026 17:50 | 50.252 | 51.043 | 1774.5 | 8.5072 | 9.0407 | -0.53353 | 54.2442 | 9.8 | 8.9114 | 0.88859 |  | 23-03-2026 17:50 | 48.892 | 49.657 | 1742.4 | 8.2762 | 9.0407 | -0.76453 | 54.2442 | 9.6 | 8.9114 | 0.68859 |  | 23-03-2026 17:50 | 48.257 | 49.017 | 1759.8 | 8.1695 | 9.0407 | -0.8712 | 54.2442 | 9.5 | 8.9114 | 0.58859 |  | 23-03-2026 17:50 | 36.89 | 37.536 | 1322.4 | 6.256 | 6.6968 | -0.44081 | 40.1809 | 7.2 | 6.601 | 0.59895 |  | 23-03-2026 17:50 | 35.451 | 36.071 | 1310.7 | 6.0118 | 6.6968 | -0.68498 | 40.1809 | 6.9 | 6.601 | 0.29895 |  | 23-03-2026 17:50 | 35.476 | 36.097 | 1305.7 | 6.0162 | 6.6968 | -0.68065 | 40.1809 | 6.8 | 6.601 | 0.19895 |  | 23-03-2026 17:50 | 35.026 | 36.007 | 1316.3 | 6.0012 | 6.6968 | -0.69565 | 40.1809 | 6.8 | 6.601 | 0.19895 |  | 23-03-2026 17:50 | 33.26 | 33.856 | 1246 | 5.6427 | 6.3712 | -0.72852 | 38.2271 | 6.5 | 6.2801 | 0.21992 |  | 23-03-2026 17:50 | 63.1613 | 69.3212 | -6.1599 | 415.9273 | 72.4 | 68.3299 | 4.0701 | -9.2387 | 8 | 96.68%
23-03-2026 17:40 | 199 | 51.37 | 63.719 | 64.571 | 1740.2 | 10.7618 | 11.733 | -0.97119 | 70.3982 | 12.1 | 11.5652 | 0.53476 |  | 23-03-2026 17:40 | 65.431 | 66.333 | 1764.7 | 11.0555 | 11.733 | -0.67753 | 70.3982 | 13.1 | 11.5652 | 1.5348 |  | 23-03-2026 17:40 | 63.771 | 64.644 | 1732.8 | 10.774 | 11.733 | -0.95903 | 70.3982 | 12.1 | 11.5652 | 0.53476 |  | 23-03-2026 17:40 | 63.678 | 64.556 | 1750.3 | 10.7593 | 11.733 | -0.97369 | 70.3982 | 12.2 | 11.5652 | 0.63476 |  | 23-03-2026 17:40 | 47.265 | 48.024 | 1315.2 | 8.004 | 8.6911 | -0.68713 | 52.1468 | 9.1 | 8.5668 | 0.53315 |  | 23-03-2026 17:40 | 46.075 | 46.805 | 1303.8 | 7.8008 | 8.6911 | -0.8903 | 52.1468 | 8.9 | 8.5668 | 0.33315 |  | 23-03-2026 17:40 | 46.184 | 46.931 | 1298.9 | 7.8218 | 8.6911 | -0.8693 | 52.1468 | 8.9 | 8.5668 | 0.33315 |  | 23-03-2026 17:40 | 45.883 | 47.197 | 1309.5 | 7.8662 | 8.6911 | -0.82496 | 52.1468 | 8.9 | 8.5668 | 0.33315 |  | 23-03-2026 17:40 | 43.497 | 44.213 | 1239.5 | 7.3688 | 8.2685 | -0.8997 | 49.6112 | 8.3 | 8.1503 | 0.14971 |  | 23-03-2026 17:40 | 82.2123 | 89.9652 | -7.7528 | 539.791 | 93.6 | 88.6787 | 4.9213 | -11.3877 | 9 | 98.19%
23-03-2026 17:30 | 250 | 51.95 | 82.317 | 83.367 | 1728.1 | 13.8945 | 14.707 | -0.81252 | 88.2421 | 14.8 | 14.4967 | 0.30329 |  | 23-03-2026 17:30 | 83.783 | 84.878 | 1751.6 | 14.1463 | 14.707 | -0.56069 | 88.2421 | 14.2 | 14.4967 | -0.29671 |  | 23-03-2026 17:30 | 82.368 | 83.463 | 1720.7 | 13.9105 | 14.707 | -0.79652 | 88.2421 | 15 | 14.4967 | 0.50329 |  | 23-03-2026 17:30 | 81.875 | 82.902 | 1738.1 | 13.817 | 14.707 | -0.89002 | 88.2421 | 14.8 | 14.4967 | 0.30329 |  | 23-03-2026 17:30 | 61.734 | 62.579 | 1306.1 | 10.4298 | 10.8941 | -0.46426 | 65.3645 | 11.4 | 10.7383 | 0.6617 |  | 23-03-2026 17:30 | 59.598 | 60.432 | 1294.9 | 10.072 | 10.8941 | -0.82209 | 65.3645 | 10.9 | 10.7383 | 0.1617 |  | 23-03-2026 17:30 | 59.826 | 60.688 | 1290 | 10.1147 | 10.8941 | -0.77942 | 65.3645 | 11 | 10.7383 | 0.2617 |  | 23-03-2026 17:30 | 59.452 | 61.007 | 1300.6 | 10.1678 | 10.8941 | -0.72626 | 65.3645 | 10.9 | 10.7383 | 0.1617 |  | 23-03-2026 17:30 | 56.061 | 56.895 | 1231.2 | 9.4825 | 10.3644 | -0.88188 | 62.1863 | 10.3 | 10.2162 | 0.083835 |  | 23-03-2026 17:30 | 106.0352 | 112.7688 | -6.7336 | 676.6128 | 113.3 | 111.1562 | 2.1438 | -7.2648
23-03-2026 17:20 | 293 | 51.66 | 98.35 | 99.545 | 1713.3 | 16.5908 | 17.2559 | -0.66511 | 103.5357 | 17.7 | 17.0092 | 0.69082 |  | 23-03-2026 17:20 | 100.122 | 100.519 | 1737.4 | 16.7532 | 17.2559 | -0.50278 | 103.5357 | 17.7 | 17.0092 | 0.69082 |  | 23-03-2026 17:20 | 98.635 | 100.247 | 1705.7 | 16.7078 | 17.2559 | -0.54811 | 103.5357 | 17.6 | 17.0092 | 0.59082 |  | 23-03-2026 17:20 | 97.921 | 99.14 | 1723.3 | 16.5233 | 17.2559 | -0.73261 | 103.5357 | 17.5 | 17.0092 | 0.49082 |  | 23-03-2026 17:20 | 74.072 | 75.04 | 1294.7 | 12.5067 | 12.7822 | -0.27551 | 76.6931 | 13 | 12.5994 | 0.4006 |  | 23-03-2026 17:20 | 71.59 | 72.518 | 1284 | 12.0863 | 12.7822 | -0.69585 | 76.6931 | 12.6 | 12.5994 | 0.00060455 |  | 23-03-2026 17:20 | 72.017 | 72.965 | 1279 | 12.1608 | 12.7822 | -0.62135 | 76.6931 | 12.9 | 12.5994 | 0.3006 |  | 23-03-2026 17:20 | 71.795 | 73.802 | 1289.7 | 12.3003 | 12.7822 | -0.48185 | 76.6931 | 12.8 | 12.5994 | 0.2006 |  | 23-03-2026 17:20 | 67.475 | 68.385 | 1220.9 | 11.3975 | 12.1607 | -0.76316 | 72.964 | 12 | 11.9868 | 0.013236 |  | 23-03-2026 17:20 | 127.0268 | 132.3132 | -5.2863 | 793.879 | 133.8 | 130.4211 | 3.3789 | -6.7732
23-03-2026 17:10 | 324 | 51.09 | 111.418 | 112.278 | 1695.6 | 18.713 | 19.1236 | -0.41064 | 114.7419 | 10.3 | 18.8502 | -8.5502 |  | 23-03-2026 17:10 | 112.65 | 114.041 | 1719.7 | 19.0068 | 19.1236 | -0.11681 | 114.7419 | 11.9 | 18.8502 | -6.9502 |  | 23-03-2026 17:10 | 110.776 | 112.761 | 1688.1 | 18.7935 | 19.1236 | -0.33014 | 114.7419 | 11.2 | 18.8502 | -7.6502 |  | 23-03-2026 17:10 | 110.917 | 112.298 | 1705.8 | 18.7163 | 19.1236 | -0.40731 | 114.7419 | 12.3 | 18.8502 | -6.5502 |  | 23-03-2026 17:10 | 83.744 | 84.813 | 1281.7 | 14.1355 | 14.1657 | -0.030162 | 84.994 | 8.8 | 13.9631 | -5.1631 |  | 23-03-2026 17:10 | 81.576 | 82.609 | 1271.4 | 13.7682 | 14.1657 | -0.3975 | 84.994 | 9.7 | 13.9631 | -4.2631 |  | 23-03-2026 17:10 | 81.883 | 82.928 | 1266.1 | 13.8213 | 14.1657 | -0.34433 | 84.994 | 9.2 | 13.9631 | -4.7631 |  | 23-03-2026 17:10 | 82.081 | 84.202 | 1276.9 | 14.0337 | 14.1657 | -0.132 | 84.994 | 10.5 | 13.9631 | -3.4631 |  | 23-03-2026 17:10 | 77.31 | 78.328 | 1208.9 | 13.0547 | 13.4769 | -0.42221 | 80.8612 | 10.1 | 13.2842 | -3.1842 |  | 23-03-2026 17:10 | 144.043 | 146.6341 | -2.5911 | 879.8046 | 94 | 144.5372 | -50.5372 | 50.043
23-03-2026 17:00 | 369 | 51.66 | 120.686 | 124.502 | 1685.3 | 20.7503 | 21.7319 | -0.98156 | 130.3913 | 13.9 | 21.4211 | -7.5211 |  | 23-03-2026 17:00 | 126.645 | 128.295 | 1707.8 | 21.3825 | 21.7319 | -0.34939 | 130.3913 | 15.3 | 21.4211 | -6.1211 |  | 23-03-2026 17:00 | 126.659 | 129.263 | 1676.9 | 21.5438 | 21.7319 | -0.18806 | 130.3913 | 14.9 | 21.4211 | -6.5211 |  | 23-03-2026 17:00 | 125.697 | 127.262 | 1693.5 | 21.2103 | 21.7319 | -0.52156 | 130.3913 | 16.6 | 21.4211 | -4.8211 |  | 23-03-2026 17:00 | 95.485 | 96.674 | 1272.9 | 16.1123 | 16.0977 | 0.014638 | 96.5862 | 11.7 | 15.8675 | -4.1675 |  | 23-03-2026 17:00 | 93.469 | 94.599 | 1261.7 | 15.7665 | 16.0977 | -0.3312 | 96.5862 | 12.9 | 15.8675 | -2.9675 |  | 23-03-2026 17:00 | 93.731 | 94.879 | 1256.9 | 15.8132 | 16.0977 | -0.28453 | 96.5862 | 12.5 | 15.8675 | -3.3675 |  | 23-03-2026 17:00 | 94.194 | 96.693 | 1266.4 | 16.1155 | 16.0977 | 0.017805 | 96.5862 | 13.8 | 15.8675 | -2.0675 |  | 23-03-2026 17:00 | 89.004 | 90.14 | 1198.8 | 15.0233 | 15.315 | -0.29163 | 91.8898 | 13.4 | 15.096 | -1.696 |  | 23-03-2026 17:00 | 163.7178 | 166.6333 | -2.9155 | 999.7998 | 125 | 164.2504 | -39.2504 | 38.7178
23-03-2026 16:50 | 415 | 52.23 | 141.38 | 143.184 | 1671.4 | 23.864 | 24.3872 | -0.52323 | 146.3234 | 55.3 | 24.0385 | 31.2615 |  | 23-03-2026 16:50 | 143.3 | 145.202 | 1692.5 | 24.2003 | 24.3872 | -0.1869 | 146.3234 | 26.1 | 24.0385 | 2.0615 |  | 23-03-2026 16:50 | 141.644 | 144.553 | 1662 | 24.0922 | 24.3872 | -0.29507 | 146.3234 | 25.3 | 24.0385 | 1.2615 |  | 23-03-2026 16:50 | 141.686 | 143.581 | 1676.9 | 23.9302 | 24.3872 | -0.45707 | 146.3234 | 25.5 | 24.0385 | 1.4615 |  | 23-03-2026 16:50 | 106.295 | 107.673 | 1261.2 | 17.9455 | 18.0646 | -0.11912 | 108.3877 | 19 | 17.8063 | 1.1937 |  | 23-03-2026 16:50 | 104.3 | 105.601 | 1248.8 | 17.6002 | 18.0646 | -0.46445 | 108.3877 | 18.6 | 17.8063 | 0.79371 |  | 23-03-2026 16:50 | 104.508 | 105.842 | 1244.4 | 17.6403 | 18.0646 | -0.42429 | 108.3877 | 18.6 | 17.8063 | 0.79371 |  | 23-03-2026 16:50 | 104.509 | 107.573 | 1252.6 | 17.9288 | 18.0646 | -0.13579 | 108.3877 | 18.6 | 17.8063 | 0.79371 |  | 23-03-2026 16:50 | 98.743 | 100.023 | 1185.4 | 16.6705 | 17.1862 | -0.51575 | 103.1175 | 17.7 | 16.9405 | 0.75952 |  | 23-03-2026 16:50 | 183.872 | 186.9937 | -3.1217 | 1121.962 | 224.7 | 184.3197 | 40.3803 | -40.828
23-03-2026 16:40 | 502 | 51.95 | 171.499 | 173.793 | 1646 | 28.9655 | 29.5317 | -0.56619 | 177.1902 | 0 | 29.1094 | -29.1094 |  | 23-03-2026 16:40 | 0 | 177.23 | 1666.4 | 29.5383 | 29.5317 | 0.0066387 | 177.1902 | 29.8 | 29.1094 | 0.69061 |  | 23-03-2026 16:40 | 170.966 | 174.646 | 1636.7 | 29.1077 | 29.5317 | -0.42403 | 177.1902 | 30.3 | 29.1094 | 1.1906 |  | 23-03-2026 16:40 | 172.201 | 174.558 | 1651.4 | 29.093 | 29.5317 | -0.43869 | 177.1902 | 30.4 | 29.1094 | 1.2906 |  | 23-03-2026 16:40 | 127.83 | 129.487 | 1242.2 | 21.5812 | 21.8753 | -0.29416 | 131.252 | 22.7 | 21.5625 | 1.1375 |  | 23-03-2026 16:40 | 125.713 | 127.356 | 1230.2 | 21.226 | 21.8753 | -0.64933 | 131.252 | 22.3 | 21.5625 | 0.73749 |  | 23-03-2026 16:40 | 125.09 | 127.041 | 1225.8 | 21.1735 | 21.8753 | -0.70183 | 131.252 | 22.2 | 21.5625 | 0.63749 |  | 23-03-2026 16:40 | 125.323 | 128.924 | 1234 | 21.4873 | 21.8753 | -0.388 | 131.252 | 22.3 | 21.5625 | 0.73749 |  | 23-03-2026 16:40 | 118.918 | 120.484 | 1167.7 | 20.0807 | 20.8117 | -0.731 | 124.87 | 21 | 20.5141 | 0.48594 |  | 23-03-2026 16:40 | 222.2532 | 226.4398 | -4.1866 | 1358.6386 | 201 | 223.2017 | -22.2017 | 21.2532
23-03-2026 16:30 | 536 | 51.66 | 183.739 | 186.235 | 1616.1 | 31.0392 | 31.5672 | -0.52802 | 189.4031 | 32.8 | 31.1158 | 1.6842 |  | 23-03-2026 16:30 | 188.652 | 189.97 | 1636.6 | 31.6617 | 31.5672 | 0.094479 | 189.4031 | 33.2 | 31.1158 | 2.0842 |  | 23-03-2026 16:30 | 183.855 | 187.779 | 1606.4 | 31.2965 | 31.5672 | -0.27069 | 189.4031 | 32.2 | 31.1158 | 1.0842 |  | 23-03-2026 16:30 | 184.567 | 187.15 | 1621 | 31.1917 | 31.5672 | -0.37552 | 189.4031 | 32.4 | 31.1158 | 1.2842 |  | 23-03-2026 16:30 | 137.432 | 139.242 | 1219.5 | 23.207 | 23.3831 | -0.1761 | 140.2986 | 24.2 | 23.0487 | 1.1513 |  | 23-03-2026 16:30 | 134.695 | 136.572 | 1207.9 | 22.762 | 23.3831 | -0.6211 | 140.2986 | 23.8 | 23.0487 | 0.75128 |  | 23-03-2026 16:30 | 134.356 | 136.161 | 1203.6 | 22.6935 | 23.3831 | -0.6896 | 140.2986 | 24.1 | 23.0487 | 1.0513 |  | 23-03-2026 16:30 | 134.585 | 138.207 | 1211.7 | 23.0345 | 23.3831 | -0.3486 | 140.2986 | 24.1 | 23.0487 | 1.0513 |  | 23-03-2026 16:30 | 127.362 | 129.053 | 1146.7 | 21.5088 | 22.2461 | -0.73729 | 133.4768 | 22.9 | 21.928 | 0.97199 |  | 23-03-2026 16:30 | 238.3948 | 242.0473 | -3.6524 | 1452.2837 | 249.7 | 238.586 | 11.114 | -11.3052
23-03-2026 16:20 | 602 | 51.95 | 205.775 | 208.771 | 1583.3 | 34.7952 | 35.4145 | -0.61934 | 212.487 | 34.6 | 34.9081 | -0.30808 |  | 23-03-2026 16:20 | 208.196 | 211.195 | 1603.4 | 35.1992 | 35.4145 | -0.21534 | 212.487 | 36.2 | 34.9081 | 1.2919 |  | 23-03-2026 16:20 | 205.402 | 210.138 | 1574.2 | 35.023 | 35.4145 | -0.3915 | 212.487 | 34.7 | 34.9081 | -0.20808 |  | 23-03-2026 16:20 | 206.078 | 209.046 | 1588.6 | 34.841 | 35.4145 | -0.5735 | 212.487 | 35.4 | 34.9081 | 0.49192 |  | 23-03-2026 16:20 | 154.391 | 156.488 | 1195.3 | 26.0813 | 26.233 | -0.15163 | 157.3978 | 26.5 | 25.8578 | 0.64217 |  | 23-03-2026 16:20 | 151.38 | 153.523 | 1184.1 | 25.5872 | 26.233 | -0.6458 | 157.3978 | 26 | 25.8578 | 0.14217 |  | 23-03-2026 16:20 | 151.609 | 154.134 | 1179.5 | 25.689 | 26.233 | -0.54396 | 157.3978 | 25.6 | 25.8578 | -0.25783 |  | 23-03-2026 16:20 | 151.83 | 156.037 | 1187.6 | 26.0062 | 26.233 | -0.2268 | 157.3978 | 25.7 | 25.8578 | -0.15783 |  | 23-03-2026 16:20 | 143.408 | 145.385 | 1123.8 | 24.2308 | 24.9574 | -0.72658 | 149.7445 | 24.3 | 24.6005 | -0.30053 |  | 23-03-2026 16:20 | 267.4528 | 271.5473 | -4.0945 | 1629.2837 | 269 | 267.6642 | 1.3358 | -1.5472
23-03-2026 16:10 | 625 | 51.66 | 212.383 | 215.021 | 1548.7 | 35.8368 | 36.8088 | -0.97192 | 220.8525 | 37.2 | 36.2824 | 0.91761 |  | 23-03-2026 16:10 | 215.473 | 218.643 | 1567.2 | 36.4405 | 36.8088 | -0.36825 | 220.8525 | 78.5 | 36.2824 | 42.2176 |  | 23-03-2026 16:10 | 212.123 | 216.951 | 1539.5 | 36.1585 | 36.8088 | -0.65025 | 220.8525 | 36.6 | 36.2824 | 0.31761 |  | 23-03-2026 16:10 | 214.191 | 217.307 | 1553.2 | 36.2178 | 36.8088 | -0.59092 | 220.8525 | 36.9 | 36.2824 | 0.61761 |  | 23-03-2026 16:10 | 160.107 | 162.349 | 1168.8 | 27.0582 | 27.2657 | -0.20758 | 163.5945 | 27.6 | 26.8758 | 0.72416 |  | 23-03-2026 16:10 | 157.541 | 159.729 | 1158.1 | 26.6215 | 27.2657 | -0.64424 | 163.5945 | 27.1 | 26.8758 | 0.22416 |  | 23-03-2026 16:10 | 157.607 | 159.82 | 1153.9 | 26.6367 | 27.2657 | -0.62908 | 163.5945 | 27.2 | 26.8758 | 0.32416 |  | 23-03-2026 16:10 | 157.836 | 162.19 | 1161.9 | 27.0317 | 27.2657 | -0.23408 | 163.5945 | 27.1 | 26.8758 | 0.22416 |  | 23-03-2026 16:10 | 149.089 | 151.145 | 1099.5 | 25.1908 | 25.94 | -0.74914 | 155.6399 | 25.7 | 25.569 | 0.13096 |  | 23-03-2026 16:10 | 277.1925 | 282.238 | -5.0455 | 1693.4278 | 323.9 | 278.202 | 45.698 | -46.7075
23-03-2026 16:00 | 679 | 51.66 | 231.341 | 234.195 | 1511.5 | 39.0325 | 39.989 | -0.95653 | 239.9342 | 40.1 | 39.4172 | 0.68281 | [5 empty] | 0 | 39.989 | -39.989 | 239.9342 | 0 | 39.4172 | -39.4172 |  | 23-03-2026 16:00 | 230.048 | 235.127 | 1502.9 | 39.1878 | 39.989 | -0.8012 | 239.9342 | 40 | 39.4172 | 0.58281 |  | 23-03-2026 16:00 | 231.872 | 235.379 | 1516.3 | 39.2298 | 39.989 | -0.7592 | 239.9342 | 39.7 | 39.4172 | 0.28281 |  | 23-03-2026 16:00 | 172.698 | 175.132 | 1141.2 | 29.1887 | 29.6215 | -0.43284 | 177.729 | 29.7 | 29.1979 | 0.50208 |  | 23-03-2026 16:00 | 170.223 | 172.797 | 1131 | 28.7995 | 29.6215 | -0.822 | 177.729 | 29.2 | 29.1979 | 0.0020836 |  | 23-03-2026 16:00 | 169.236 | 172.009 | 1126.7 | 28.6682 | 29.6215 | -0.95334 | 177.729 | 29.1 | 29.1979 | -0.097916 |  | 23-03-2026 16:00 | 169.237 | 174.047 | 1134.8 | 29.0078 | 29.6215 | -0.61367 | 177.729 | 29.3 | 29.1979 | 0.10208 |  | 23-03-2026 16:00 | 160.269 | 162.545 | 1073.8 | 27.0908 | 28.1812 | -1.0904 | 169.0872 | 27.9 | 27.7782 | 0.1218 |  | 23-03-2026 16:00 | 260.2052 | 306.6233 | -46.4182 | 1839.74 | 265 | 302.2386 | -37.2386 | -4.7948
23-03-2026 15:50 | 733 | 51.09 | 250.291 | 253.114 | 1471.4 | 42.1857 | 43.2643 | -1.0786 | 259.5858 | 41.7 | 42.6456 | -0.94561 |  | 23-03-2026 15:50 | 253.309 | 257.245 | 1488.7 | 42.8742 | 43.2643 | -0.39013 | 259.5858 | 41.1 | 42.6456 | -1.5456 |  | 23-03-2026 15:50 | 248.873 | 255.031 | 1462.9 | 42.5052 | 43.2643 | -0.75913 | 259.5858 | 42 | 42.6456 | -0.64561 |  | 23-03-2026 15:50 | 249.96 | 253.792 | 1476.6 | 42.2987 | 43.2643 | -0.96563 | 259.5858 | 42.5 | 42.6456 | -0.14561 |  | 23-03-2026 15:50 | 187.137 | 189.794 | 1111.5 | 31.6323 | 32.0476 | -0.41529 | 192.2857 | 31.7 | 31.5893 | 0.11066 |  | 23-03-2026 15:50 | 183.274 | 186.132 | 1101.8 | 31.022 | 32.0476 | -1.0256 | 192.2857 | 31.2 | 31.5893 | -0.38934 |  | 23-03-2026 15:50 | 183.499 | 186.599 | 1097.6 | 31.0998 | 32.0476 | -0.94779 | 192.2857 | 31.2 | 31.5893 | -0.38934 |  | 23-03-2026 15:50 | 183.32 | 188.558 | 1105.5 | 31.4263 | 32.0476 | -0.62129 | 192.2857 | 31.7 | 31.5893 | 0.11066 |  | 23-03-2026 15:50 | 173.894 | 176.345 | 1045.9 | 29.3908 | 30.4893 | -1.0985 | 182.9361 | 29.8 | 30.0533 | -0.25335 |  | 23-03-2026 15:50 | 324.435 | 331.737 | -7.302 | 1990.4221 | 322.9 | 326.9932 | -4.0932 | 1.535
23-03-2026 15:40 | 757 | 52.23 | 229.574 | 232.364 | 1429.7 | 38.7273 | 44.4847 | -5.7573 | 266.908 | 41.3 | 43.8485 | -2.5485 |  | 23-03-2026 15:40 | 253.252 | 257.135 | 1447.6 | 42.8558 | 44.4847 | -1.6288 | 266.908 | 42.1 | 43.8485 | -1.7485 |  | 23-03-2026 15:40 | 240.777 | 246.237 | 1420.9 | 41.0395 | 44.4847 | -3.4452 | 266.908 | 41.3 | 43.8485 | -2.5485 |  | 23-03-2026 15:40 | 256.439 | 260.45 | 1434.1 | 43.4083 | 44.4847 | -1.0763 | 266.908 | 42.2 | 43.8485 | -1.6485 |  | 23-03-2026 15:40 | 195.066 | 197.896 | 1079.8 | 32.9827 | 32.9516 | 0.031062 | 197.7096 | 31.3 | 32.4804 | -1.1804 |  | 23-03-2026 15:40 | 191.854 | 195.042 | 1070.6 | 32.507 | 32.9516 | -0.44461 | 197.7096 | 31.3 | 32.4804 | -1.1804 |  | 23-03-2026 15:40 | 193.156 | 196.694 | 1066.4 | 32.7823 | 32.9516 | -0.16927 | 197.7096 | 31.3 | 32.4804 | -1.1804 |  | 23-03-2026 15:40 | 193.02 | 198.452 | 1073.8 | 33.0753 | 32.9516 | 0.12373 | 197.7096 | 31.3 | 32.4804 | -1.1804 |  | 23-03-2026 15:40 | 180.392 | 183.009 | 1016.1 | 30.5015 | 31.3494 | -0.84787 | 188.0962 | 29.8 | 30.9011 | -1.1011 |  | 23-03-2026 15:40 | 327.8798 | 341.0945 | -13.2146 | 2046.5668 | 321.9 | 336.2168 | -14.3168 | 5.9798
23-03-2026 15:30 | 807 | 54.53 | 251.878 | 255.949 | 1388.4 | 42.6582 | 47.0009 | -4.3428 | 282.0055 | 41.3 | 46.3288 | -5.0288 |  | 23-03-2026 15:30 | 224.029 | 230.816 | 1405.5 | 38.4693 | 47.0009 | -8.5316 | 282.0055 | 43.6 | 46.3288 | -2.7288 |  | 23-03-2026 15:30 | 277.96 | 284.551 | 1379.6 | 47.4252 | 47.0009 | 0.42425 | 282.0055 | 41.8 | 46.3288 | -4.5288 |  | 23-03-2026 15:30 | 282.127 | 286.958 | 1391.9 | 47.8263 | 47.0009 | 0.82542 | 282.0055 | 43.3 | 46.3288 | -3.0288 |  | 23-03-2026 15:30 | 209.848 | 212.936 | 1048.5 | 35.4893 | 34.8155 | 0.67384 | 208.893 | 32.5 | 34.3176 | -1.8176 |  | 23-03-2026 15:30 | 205.909 | 208.96 | 1039.3 | 34.8267 | 34.8155 | 0.011172 | 208.893 | 31.8 | 34.3176 | -2.5176 |  | 23-03-2026 15:30 | 207.075 | 210.574 | 1035.1 | 35.0957 | 34.8155 | 0.28017 | 208.893 | 31.9 | 34.3176 | -2.4176 |  | 23-03-2026 15:30 | 197.817 | 202.952 | 1042.5 | 33.8253 | 34.8155 | -0.99016 | 208.893 | 31.4 | 34.3176 | -2.9176 |  | 23-03-2026 15:30 | 188.588 | 191.285 | 986.3 | 31.8808 | 33.1226 | -1.2418 | 198.7358 | 29 | 32.649 | -3.649 |  | 23-03-2026 15:30 | 347.4968 | 360.3883 | -12.8914 | 2162.3297 | 326.6 | 355.2347 | -28.6347 | 20.8968
23-03-2026 15:20 | 835 | 52.23 | 282.793 | 287.333 | 1347.1 | 47.8888 | 49.0683 | -1.1795 | 294.4098 | 47.3 | 48.3666 | -1.0666 |  | 23-03-2026 15:20 | 285.446 | 290.117 | 1361.9 | 48.3528 | 49.0683 | -0.71546 | 294.4098 | 49.8 | 48.3666 | 1.4334 |  | 23-03-2026 15:20 | 281.725 | 289.444 | 1337.8 | 48.2407 | 49.0683 | -0.82763 | 294.4098 | 47.1 | 48.3666 | -1.2666 |  | 23-03-2026 15:20 | 282.642 | 287.267 | 1348.6 | 47.8778 | 49.0683 | -1.1905 | 294.4098 | 46.7 | 48.3666 | -1.6666 |  | 23-03-2026 15:20 | 212.895 | 216.071 | 1016 | 36.0118 | 36.3469 | -0.33505 | 218.0813 | 35.2 | 35.8271 | -0.62712 |  | 23-03-2026 15:20 | 208.592 | 212.23 | 1007.5 | 35.3717 | 36.3469 | -0.97522 | 218.0813 | 34.4 | 35.8271 | -1.4271 |  | 23-03-2026 15:20 | 209.478 | 213.618 | 1003.2 | 35.603 | 36.3469 | -0.74388 | 218.0813 | 34.5 | 35.8271 | -1.3271 |  | 23-03-2026 15:20 | 210.184 | 216.187 | 1011.1 | 36.0312 | 36.3469 | -0.31572 | 218.0813 | 34.5 | 35.8271 | -1.3271 |  | 23-03-2026 15:20 | 198.755 | 201.7 | 957.3 | 33.6167 | 34.5796 | -0.96289 | 207.4773 | 33.1 | 34.0851 | -0.98507 |  | 23-03-2026 15:20 | 368.9945 | 376.2403 | -7.2458 | 2257.4415 | 362.6 | 370.86 | -8.26 | 6.3945
23-03-2026 15:10 | 835 | 51.66 | 280.743 | 285.222 | 1299.8 | 47.537 | 49.1765 | -1.6395 | 295.059 | 47.3 | 48.4733 | -1.1733 |  | 23-03-2026 15:10 | 284.795 | 289.485 | 1312.1 | 48.2475 | 49.1765 | -0.929 | 295.059 | 47.3 | 48.4733 | -1.1733 |  | 23-03-2026 15:10 | 280.373 | 287.819 | 1290.7 | 47.9698 | 49.1765 | -1.2067 | 295.059 | 47.2 | 48.4733 | -1.2733 |  | 23-03-2026 15:10 | 281.785 | 286.355 | 1301.9 | 47.7258 | 49.1765 | -1.4507 | 295.059 | 47.5 | 48.4733 | -0.97327 |  | 23-03-2026 15:10 | 212.275 | 215.465 | 980.8 | 35.9108 | 36.427 | -0.5162 | 218.5622 | 35.6 | 35.9061 | -0.30613 |  | 23-03-2026 15:10 | 208.166 | 211.957 | 973.1 | 35.3262 | 36.427 | -1.1009 | 218.5622 | 35 | 35.9061 | -0.90613 |  | 23-03-2026 15:10 | 208.786 | 212.734 | 968.7 | 35.4557 | 36.427 | -0.97137 | 218.5622 | 35 | 35.9061 | -0.90613 |  | 23-03-2026 15:10 | 209.218 | 215.454 | 976.6 | 35.909 | 36.427 | -0.51803 | 218.5622 | 35.1 | 35.9061 | -0.80613 |  | 23-03-2026 15:10 | 197.326 | 200.25 | 924.2 | 33.375 | 34.6558 | -1.2808 | 207.9349 | 32.8 | 34.1602 | -1.3602 |  | 23-03-2026 15:10 | 367.4568 | 377.0699 | -9.6131 | 2262.4196 | 362.8 | 371.6778 | -8.8778 | 4.6568
23-03-2026 15:00 | 859 | 51.95 | 284.533 | 289.16 | 1252.5 | 48.1933 | 50.5333 | -2.34 | 303.1999 | 48.6 | 49.8107 | -1.2107 | 0.984 | 23-03-2026 15:00 | 293.451 | 296.21 | 1264.8 | 49.3683 | 50.5333 | -1.165 | 303.1999 | 48.8 | 49.8107 | -1.0107 | 0.99069 | 23-03-2026 15:00 | 284.975 | 292.539 | 1243.5 | 48.7565 | 50.5333 | -1.7768 | 303.1999 | 49 | 49.8107 | -0.81069 | 0.97414 | 23-03-2026 15:00 | 287.317 | 292.078 | 1254.4 | 48.6797 | 50.5333 | -1.8537 | 303.1999 | 50.3 | 49.8107 | 0.48931 | 0.9837 | 23-03-2026 15:00 | 214.861 | 218.089 | 945.2 | 36.3482 | 37.4321 | -1.0839 | 224.5925 | 37.4 | 36.8968 | 0.50319 | 0.9852 | 23-03-2026 15:00 | 211.043 | 214.634 | 938.1 | 35.7723 | 37.4321 | -1.6598 | 224.5925 | 37.1 | 36.8968 | 0.20319 | 0.98327 | 23-03-2026 15:00 | 211.183 | 215.297 | 933.7 | 35.8828 | 37.4321 | -1.5493 | 224.5925 | 36.8 | 36.8968 | -0.096809 | 0.98089 | 23-03-2026 15:00 | 211.671 | 217.799 | 941.5 | 36.2998 | 37.4321 | -1.1323 | 224.5925 | 37 | 36.8968 | 0.10319 | 0.97186 | 23-03-2026 15:00 | 199.975 | 203 | 891.4 | 33.8333 | 35.612 | -1.7787 | 213.672 | 35.1 | 35.1027 | -0.0027437 | 0.9851 | 23-03-2026 15:00 | 373.1343 | 387.4736 | -14.3393 | 2324.8417 | 380.1 | 381.9327 | -1.8327 | -6.9657
23-03-2026 14:50 | 945 | 51.66 | 313.97 | 319.27 | 1203.9 | 53.2117 | 55.6548 | -2.4432 | 333.929 | 54.5 | 54.859 | -0.35897 | 0.9834 | 23-03-2026 14:50 | 319.339 | 324.763 | 1216 | 54.1272 | 55.6548 | -1.5277 | 333.929 | 54.5 | 54.859 | -0.35897 | 0.9833 | 23-03-2026 14:50 | 311.694 | 320.366 | 1194.5 | 53.3943 | 55.6548 | -2.2605 | 333.929 | 52.7 | 54.859 | -2.159 | 0.97293 | 23-03-2026 14:50 | 315.883 | 321.281 | 1204.1 | 53.5468 | 55.6548 | -2.108 | 333.929 | 52.6 | 54.859 | -2.259 | 0.9832 | 23-03-2026 14:50 | 235.02 | 238.696 | 907.8 | 39.7827 | 41.2258 | -1.4431 | 247.3548 | 39.2 | 40.6363 | -1.4363 | 0.9846 | 23-03-2026 14:50 | 232.906 | 236.793 | 901 | 39.4655 | 41.2258 | -1.7603 | 247.3548 | 38.6 | 40.6363 | -2.0363 | 0.98358 | 23-03-2026 14:50 | 231.563 | 235.884 | 896.9 | 39.314 | 41.2258 | -1.9118 | 247.3548 | 38.7 | 40.6363 | -1.9363 | 0.98168 | 23-03-2026 14:50 | 232.567 | 239.182 | 904.5 | 39.8637 | 41.2258 | -1.3621 | 247.3548 | 39.4 | 40.6363 | -1.2363 | 0.97234 | 23-03-2026 14:50 | 221.056 | 224.422 | 856.3 | 37.4037 | 39.2212 | -1.8176 | 235.3275 | 37.2 | 38.6604 | -1.4604 | 0.985 | 23-03-2026 14:50 | 410.1095 | 426.7438 | -16.6343 | 2560.4629 | 407.4 | 420.6414 | -13.2414 | 2.7095
23-03-2026 14:40 | 930 | 51.09 | 314.106 | 319.278 | 1149.4 | 53.213 | 54.8919 | -1.6789 | 329.3516 | 45.1 | 54.107 | -9.007 | 0.9838 | 23-03-2026 14:40 | 320.194 | 325.533 | 1161.5 | 54.2555 | 54.8919 | -0.63644 | 329.3516 | 45.6 | 54.107 | -8.507 | 0.9836 | 23-03-2026 14:40 | 314.052 | 322.464 | 1141.8 | 53.744 | 54.8919 | -1.1479 | 329.3516 | 47.1 | 54.107 | -7.007 | 0.97391 | 23-03-2026 14:40 | 318.014 | 323.284 | 1151.5 | 53.8807 | 54.8919 | -1.0113 | 329.3516 | 46.9 | 54.107 | -7.207 | 0.9837 | 23-03-2026 14:40 | 237.209 | 240.821 | 868.6 | 40.1368 | 40.6607 | -0.52386 | 243.9642 | 36.1 | 40.0792 | -3.9792 | 0.985 | 23-03-2026 14:40 | 235.307 | 239.385 | 862.4 | 39.8975 | 40.6607 | -0.7632 | 243.9642 | 35.3 | 40.0792 | -4.7792 | 0.98296 | 23-03-2026 14:40 | 234.368 | 238.881 | 858.2 | 39.8135 | 40.6607 | -0.8472 | 243.9642 | 35.7 | 40.0792 | -4.3792 | 0.98111 | 23-03-2026 14:40 | 236.391 | 243.322 | 865.1 | 40.5537 | 40.6607 | -0.10703 | 243.9642 | 35.5 | 40.0792 | -4.5792 | 0.97152 | 23-03-2026 14:40 | 222.886 | 226.188 | 819.1 | 37.698 | 38.6836 | -0.98562 | 232.1017 | 33.1 | 38.1304 | -5.0304 | 0.9854 | 23-03-2026 14:40 | 413.1927 | 420.8942 | -7.7015 | 2525.365 | 360.4 | 414.8754 | -54.4754 | 52.7927
23-03-2026 14:30 | 226 | 50.51 | 82.183 | 83.384 | 1104.3 | 13.8973 | 13.3691 | 0.5282 | 80.2148 | 34.7 | 13.178 | 21.522 | 0.9856 | 23-03-2026 14:30 | 106.47 | 80.901 | 1115.9 | 13.4835 | 13.3691 | 0.11437 | 80.2148 | 34.1 | 13.178 | 20.922 | 1.3161 | 23-03-2026 14:30 | 77.746 | 79.358 | 1094.7 | 13.2263 | 13.3691 | -0.1428 | 80.2148 | 32.6 | 13.178 | 19.422 | 0.97969 | 23-03-2026 14:30 | 76.68 | 77.848 | 1104.6 | 12.9747 | 13.3691 | -0.39447 | 80.2148 | 32.3 | 13.178 | 19.122 | 0.985 | 23-03-2026 14:30 | 57.647 | 58.608 | 832.5 | 9.768 | 9.9031 | -0.13506 | 59.4184 | 23.6 | 9.7614 | 13.8386 | 0.9836 | 23-03-2026 14:30 | 55.95 | 56.9 | 827.1 | 9.4833 | 9.9031 | -0.41973 | 59.4184 | 23.2 | 9.7614 | 13.4386 | 0.9833 | 23-03-2026 14:30 | 56.42 | 57.378 | 822.5 | 9.563 | 9.9031 | -0.34006 | 59.4184 | 22.3 | 9.7614 | 12.5386 | 0.9833 | 23-03-2026 14:30 | 56.149 | 57.98 | 829.6 | 9.6633 | 9.9031 | -0.23973 | 59.4184 | 21.4 | 9.7614 | 11.6386 | 0.96842 | 23-03-2026 14:30 | 52.581 | 53.501 | 786 | 8.9168 | 9.4215 | -0.5047 | 56.5292 | 20.8 | 9.2868 | 11.5132 | 0.9828 | 23-03-2026 14:30 | 100.9763 | 102.5103 | -1.534 | 615.0618 | 245 | 101.0444 | 143.9556 | -144.0237
23-03-2026 14:20 | 890 | 51.37 | 306.702 | 316.282 | 1069.6 | 52.7137 | 52.4743 | 0.23932 | 314.8461 | 44.2 | 51.724 | -7.524 | 0.96971 | 23-03-2026 14:20 | 294.945 | 299.832 | 1081.8 | 49.972 | 52.4743 | -2.5023 | 314.8461 | 46.3 | 51.724 | -5.424 | 0.9837 | 23-03-2026 14:20 | 332.607 | 341.934 | 1062.1 | 56.989 | 52.4743 | 4.5147 | 314.8461 | 43.7 | 51.724 | -8.024 | 0.97272 | 23-03-2026 14:20 | 333.372 | 339.206 | 1072.3 | 56.5343 | 52.4743 | 4.06 | 314.8461 | 44.9 | 51.724 | -6.824 | 0.9828 | 23-03-2026 14:20 | 250.461 | 254.378 | 808.9 | 42.3963 | 38.8699 | 3.5264 | 233.2193 | 31.8 | 38.314 | -6.514 | 0.9846 | 23-03-2026 14:20 | 246.676 | 251.591 | 803.9 | 41.9318 | 38.8699 | 3.0619 | 233.2193 | 32.4 | 38.314 | -5.914 | 0.98046 | 23-03-2026 14:20 | 249.509 | 254.54 | 800.2 | 42.4233 | 38.8699 | 3.5534 | 233.2193 | 31.7 | 38.314 | -6.614 | 0.98023 | 23-03-2026 14:20 | 249.724 | 257.123 | 808.2 | 42.8538 | 38.8699 | 3.9839 | 233.2193 | 33.1 | 38.314 | -5.214 | 0.97122 | 23-03-2026 14:20 | 235.343 | 239 | 765.2 | 39.8333 | 36.9799 | 2.8535 | 221.8793 | 32.2 | 36.4511 | -4.2511 | 0.9847 | 23-03-2026 14:20 | 425.6477 | 402.3568 | 23.2909 | 2414.1407 | 340.3 | 396.6031 | -56.3031 | 85.3477
23-03-2026 14:10 | 1025 | 51.95 | 336.68 | 342.677 | 1025.4 | 57.1128 | 60.2988 | -3.1859 | 361.7927 | 55.2 | 59.4365 | -4.2365 | 0.9825 | 23-03-2026 14:10 | 341.707 | 347.829 | 1035.5 | 57.9715 | 60.2988 | -2.3273 | 361.7927 | 57.6 | 59.4365 | -1.8365 | 0.9824 | 23-03-2026 14:10 | 333.568 | 343.671 | 1018.4 | 57.2785 | 60.2988 | -3.0203 | 361.7927 | 55.6 | 59.4365 | -3.8365 | 0.9706 | 23-03-2026 14:10 | 337.485 | 343.566 | 1027.4 | 57.261 | 60.2988 | -3.0378 | 361.7927 | 56.2 | 59.4365 | -3.2365 | 0.9823 | 23-03-2026 14:10 | 251.823 | 255.964 | 777.1 | 42.6607 | 44.6658 | -2.0051 | 267.9946 | 42 | 44.027 | -2.027 | 0.98382 | 23-03-2026 14:10 | 248.575 | 253.316 | 771.5 | 42.2193 | 44.6658 | -2.4464 | 267.9946 | 41.5 | 44.027 | -2.527 | 0.98128 | 23-03-2026 14:10 | 247.641 | 253.108 | 768.5 | 42.1847 | 44.6658 | -2.4811 | 267.9946 | 41.4 | 44.027 | -2.627 | 0.9784 | 23-03-2026 14:10 | 248.828 | 256.344 | 775.1 | 42.724 | 44.6658 | -1.9418 | 267.9946 | 41 | 44.027 | -3.027 | 0.97068 | 23-03-2026 14:10 | 235.477 | 239.306 | 733 | 39.8843 | 42.4939 | -2.6096 | 254.9636 | 38.8 | 41.8863 | -3.0863 | 0.984 | 23-03-2026 14:10 | 439.2968 | 462.3521 | -23.0553 | 2774.1126 | 429.3 | 455.7405 | -26.4405 | 9.9968
23-03-2026 14:00 | 1023 | 51.95 | 336.788 | 342.647 | 970.2 | 57.1078 | 60.1811 | -3.0733 | 361.0867 | 55.6 | 59.3205 | -3.7205 | 0.9829 | 23-03-2026 14:00 | 339.011 | 346.878 | 977.9 | 57.813 | 60.1811 | -2.3681 | 361.0867 | 57.9 | 59.3205 | -1.4205 | 0.97732 | 23-03-2026 14:00 | 334.539 | 344.518 | 962.8 | 57.4197 | 60.1811 | -2.7615 | 361.0867 | 56.2 | 59.3205 | -3.1205 | 0.97103 | 23-03-2026 14:00 | 337.725 | 343.775 | 971.2 | 57.2958 | 60.1811 | -2.8853 | 361.0867 | 56.5 | 59.3205 | -2.8205 | 0.9824 | 23-03-2026 14:00 | 251.923 | 256.045 | 735.1 | 42.6742 | 44.5786 | -1.9044 | 267.4717 | 42.3 | 43.9411 | -1.6411 | 0.9839 | 23-03-2026 14:00 | 249.728 | 254.29 | 730 | 42.3817 | 44.5786 | -2.1969 | 267.4717 | 41.8 | 43.9411 | -2.1411 | 0.98206 | 23-03-2026 14:00 | 248.701 | 254.036 | 727.1 | 42.3393 | 44.5786 | -2.2393 | 267.4717 | 41.8 | 43.9411 | -2.1411 | 0.979 | 23-03-2026 14:00 | 250.426 | 257.855 | 734.1 | 42.9758 | 44.5786 | -1.6028 | 267.4717 | 42 | 43.9411 | -1.9411 | 0.97119 | 23-03-2026 14:00 | 237.525 | 241.314 | 694.2 | 40.219 | 42.411 | -2.192 | 254.4662 | 39.8 | 41.8045 | -2.0045 | 0.9843 | 23-03-2026 14:00 | 440.2263 | 461.45 | -21.2236 | 2768.6997 | 433.9 | 454.8512 | -20.9512 | 6.3263
23-03-2026 13:50 | 1023 | 51.95 | 338.138 | 344.126 | 914.6 | 57.3543 | 60.1811 | -2.8268 | 361.0867 | 56.5 | 59.3205 | -2.8205 | 0.9826 | 23-03-2026 13:50 | 342.231 | 348.362 | 920 | 58.0603 | 60.1811 | -2.1208 | 361.0867 | 55.6 | 59.3205 | -3.7205 | 0.9824 | 23-03-2026 13:50 | 336.375 | 346.2 | 906.6 | 57.7 | 60.1811 | -2.4811 | 361.0867 | 54.6 | 59.3205 | -4.7205 | 0.97162 | 23-03-2026 13:50 | 336.965 | 343.037 | 914.7 | 57.1728 | 60.1811 | -3.0083 | 361.0867 | 55 | 59.3205 | -4.3205 | 0.9823 | 23-03-2026 13:50 | 253.554 | 257.677 | 692.8 | 42.9462 | 44.5786 | -1.6324 | 267.4717 | 41.1 | 43.9411 | -2.8411 | 0.984 | 23-03-2026 13:50 | 249.492 | 254.092 | 688.2 | 42.3487 | 44.5786 | -2.2299 | 267.4717 | 40.5 | 43.9411 | -3.4411 | 0.9819 | 23-03-2026 13:50 | 250.665 | 255.672 | 685.3 | 42.612 | 44.5786 | -1.9666 | 267.4717 | 40.4 | 43.9411 | -3.5411 | 0.98042 | 23-03-2026 13:50 | 251.906 | 259.276 | 692.1 | 43.2127 | 44.5786 | -1.3659 | 267.4717 | 40.6 | 43.9411 | -3.3411 | 0.97157 | 23-03-2026 13:50 | 236.946 | 240.75 | 654.4 | 40.125 | 42.411 | -2.286 | 254.4662 | 38.4 | 41.8045 | -3.4045 | 0.9842 | 23-03-2026 13:50 | 441.532 | 461.45 | -19.918 | 2768.6997 | 422.7 | 454.8512 | -32.1512 | 18.832
23-03-2026 13:40 | 1013 | 52.23 | 334.911 | 340.738 | 858.1 | 56.7897 | 59.5284 | -2.7387 | 357.1702 | 56.3 | 58.6771 | -2.3771 | 0.9829 | 23-03-2026 13:40 | 337.478 | 343.454 | 864.4 | 57.2423 | 59.5284 | -2.286 | 357.1702 | 55.5 | 58.6771 | -3.1771 | 0.9826 | 23-03-2026 13:40 | 330.889 | 340.435 | 852 | 56.7392 | 59.5284 | -2.7892 | 357.1702 | 55.8 | 58.6771 | -2.8771 | 0.97196 | 23-03-2026 13:40 | 334.865 | 340.795 | 859.7 | 56.7992 | 59.5284 | -2.7292 | 357.1702 | 56.2 | 58.6771 | -2.4771 | 0.9826 | 23-03-2026 13:40 | 249.755 | 253.816 | 651.7 | 42.3027 | 44.0951 | -1.7924 | 264.5705 | 42 | 43.4645 | -1.4645 | 0.984 | 23-03-2026 13:40 | 246.568 | 251.563 | 647.7 | 41.9272 | 44.0951 | -2.1679 | 264.5705 | 41.5 | 43.4645 | -1.9645 | 0.98014 | 23-03-2026 13:40 | 246.657 | 251.668 | 644.9 | 41.9447 | 44.0951 | -2.1504 | 264.5705 | 41.4 | 43.4645 | -2.0645 | 0.98009 | 23-03-2026 13:40 | 247.466 | 254.909 | 651.5 | 42.4848 | 44.0951 | -1.6102 | 264.5705 | 41.6 | 43.4645 | -1.8645 | 0.9708 | 23-03-2026 13:40 | 234.058 | 237.816 | 616 | 39.636 | 41.951 | -2.315 | 251.706 | 39.9 | 41.3511 | -1.4511 | 0.9842 | 23-03-2026 13:40 | 435.8657 | 456.4448 | -20.5791 | 2738.6686 | 430.2 | 449.9176 | -19.7176 | 5.6657
23-03-2026 13:30 | 1034 | 51.37 | 340.957 | 346.924 | 801.8 | 57.8207 | 60.9646 | -3.1439 | 365.7874 | 55.7 | 60.0928 | -4.3928 | 0.9828 | 23-03-2026 13:30 | 346.685 | 352.896 | 808.9 | 58.816 | 60.9646 | -2.1486 | 365.7874 | 56.3 | 60.0928 | -3.7928 | 0.9824 | 23-03-2026 13:30 | 340.285 | 350.453 | 796.2 | 58.4088 | 60.9646 | -2.5557 | 365.7874 | 56 | 60.0928 | -4.0928 | 0.97099 | 23-03-2026 13:30 | 343.157 | 349.269 | 803.5 | 58.2115 | 60.9646 | -2.7531 | 365.7874 | 56.4 | 60.0928 | -3.6928 | 0.9825 | 23-03-2026 13:30 | 256.584 | 260.73 | 609.7 | 43.455 | 45.1589 | -1.7039 | 270.9537 | 42.4 | 44.5132 | -2.1132 | 0.9841 | 23-03-2026 13:30 | 253.492 | 258.389 | 606.2 | 43.0648 | 45.1589 | -2.0941 | 270.9537 | 41.9 | 44.5132 | -2.6132 | 0.98105 | 23-03-2026 13:30 | 252.633 | 258.174 | 603.5 | 43.029 | 45.1589 | -2.1299 | 270.9537 | 41.8 | 44.5132 | -2.7132 | 0.97854 | 23-03-2026 13:30 | 254 | 261.759 | 609.9 | 43.6265 | 45.1589 | -1.5324 | 270.9537 | 42 | 44.5132 | -2.5132 | 0.97036 | 23-03-2026 13:30 | 240.606 | 244.469 | 576.1 | 40.7448 | 42.9631 | -2.2183 | 257.7788 | 40.4 | 42.3488 | -1.9488 | 0.9842 | 23-03-2026 13:30 | 447.1772 | 467.4572 | -20.28 | 2804.7432 | 432.9 | 460.7726 | -27.8726 | 14.2772
23-03-2026 13:20 | 1046 | 52.23 | 343.451 | 349.568 | 746.1 | 58.2613 | 61.4676 | -3.2063 | 368.8055 | 56.1 | 60.5886 | -4.4886 | 0.9825 | 23-03-2026 13:20 | 341.565 | 347.119 | 752.6 | 57.8532 | 61.4676 | -3.6144 | 368.8055 | 56.3 | 60.5886 | -4.2886 | 0.984 | 23-03-2026 13:20 | 339.54 | 349.731 | 740.2 | 58.2885 | 61.4676 | -3.1791 | 368.8055 | 55.8 | 60.5886 | -4.7886 | 0.97086 | 23-03-2026 13:20 | 341.012 | 346.804 | 747.1 | 57.8007 | 61.4676 | -3.6669 | 368.8055 | 56.7 | 60.5886 | -3.8886 | 0.9833 | 23-03-2026 13:20 | 256.476 | 260.673 | 567.3 | 43.4455 | 45.5315 | -2.086 | 273.1893 | 43.7 | 44.8804 | -1.1804 | 0.9839 | 23-03-2026 13:20 | 253.644 | 258.551 | 564.3 | 43.0918 | 45.5315 | -2.4397 | 273.1893 | 43.2 | 44.8804 | -1.6804 | 0.98102 | 23-03-2026 13:20 | 252.434 | 258.895 | 561.7 | 43.1492 | 45.5315 | -2.3824 | 273.1893 | 43.8 | 44.8804 | -1.0804 | 0.97504 | 23-03-2026 13:20 | 254.285 | 262.45 | 567.9 | 43.7417 | 45.5315 | -1.7899 | 273.1893 | 43.6 | 44.8804 | -1.2804 | 0.96889 | 23-03-2026 13:20 | 233.866 | 238.981 | 535.7 | 39.8302 | 43.3176 | -3.4875 | 259.9058 | 40 | 42.6982 | -2.6982 | 0.9786 | 23-03-2026 13:20 | 445.462 | 471.3141 | -25.8521 | 2827.8848 | 439.2 | 464.5743 | -25.3743 | 6.262
23-03-2026 13:10 | 1056 | 52.52 | 331.815 | 337.039 | 690 | 56.1732 | 61.9856 | -5.8124 | 371.9136 | 57.3 | 61.0992 | -3.7992 | 0.9845 | 23-03-2026 13:10 | 335.753 | 341.143 | 696.3 | 56.8572 | 61.9856 | -5.1284 | 371.9136 | 56.6 | 61.0992 | -4.4992 | 0.9842 | 23-03-2026 13:10 | 340.122 | 350.016 | 684.4 | 58.336 | 61.9856 | -3.6496 | 371.9136 | 56.1 | 61.0992 | -4.9992 | 0.97173 | 23-03-2026 13:10 | 339.364 | 344.882 | 690.4 | 57.4803 | 61.9856 | -4.5053 | 371.9136 | 55.2 | 61.0992 | -5.8992 | 0.984 | 23-03-2026 13:10 | 263.365 | 267.756 | 523.6 | 44.626 | 45.9153 | -1.2893 | 275.4916 | 42.2 | 45.2587 | -3.0587 | 0.9836 | 23-03-2026 13:10 | 258.204 | 263.553 | 521.1 | 43.9255 | 45.9153 | -1.9898 | 275.4916 | 42.4 | 45.2587 | -2.8587 | 0.9797 | 23-03-2026 13:10 | 259.832 | 265.733 | 517.9 | 44.2888 | 45.9153 | -1.6264 | 275.4916 | 41.7 | 45.2587 | -3.5587 | 0.97779 | 23-03-2026 13:10 | 261.086 | 268.991 | 524.3 | 44.8318 | 45.9153 | -1.0834 | 275.4916 | 42.3 | 45.2587 | -2.9587 | 0.97061 | 23-03-2026 13:10 | 245.978 | 249.978 | 495.7 | 41.663 | 43.6827 | -2.0197 | 262.0961 | 40.2 | 43.058 | -2.858 | 0.984 | 23-03-2026 13:10 | 448.1818 | 475.2862 | -27.1043 | 2851.7171 | 434 | 468.4896 | -34.4896 | 14.1818
23-03-2026 13:00 | 1108 | 55.68 | 352.296 | 358.024 | 632.7 | 59.6707 | 64.2419 | -4.5713 | 385.4516 | 57 | 63.3233 | -6.3233 | 0.984 | 23-03-2026 13:00 | 352.266 | 357.958 | 639.7 | 59.6597 | 64.2419 | -4.5823 | 385.4516 | 57.6 | 63.3233 | -5.7233 | 0.9841 | 23-03-2026 13:00 | 352.193 | 362.36 | 628.3 | 60.3933 | 64.2419 | -3.8486 | 385.4516 | 56.8 | 63.3233 | -6.5233 | 0.97194 | 23-03-2026 13:00 | 352.105 | 357.691 | 635.2 | 59.6152 | 64.2419 | -4.6268 | 385.4516 | 57.7 | 63.3233 | -5.6233 | 0.98438 | 23-03-2026 13:00 | 274.239 | 278.512 | 481.4 | 46.4187 | 47.5866 | -1.168 | 285.5197 | 44.9 | 46.9061 | -2.0061 | 0.98466 | 23-03-2026 13:00 | 271.596 | 277.262 | 478.7 | 46.2103 | 47.5866 | -1.3763 | 285.5197 | 44.3 | 46.9061 | -2.6061 | 0.97956 | 23-03-2026 13:00 | 271.229 | 276.954 | 476.2 | 46.159 | 47.5866 | -1.4276 | 285.5197 | 44.2 | 46.9061 | -2.7061 | 0.97933 | 23-03-2026 13:00 | 273.024 | 281.424 | 482 | 46.904 | 47.5866 | -0.68262 | 285.5197 | 44.7 | 46.9061 | -2.2061 | 0.97015 | 23-03-2026 13:00 | 258.691 | 262.897 | 455.5 | 43.8162 | 45.2728 | -1.4566 | 271.6367 | 42.8 | 44.6254 | -1.8254 | 0.984 | 23-03-2026 13:00 | 468.847 | 492.587 | -23.74 | 2955.5222 | 450 | 485.543 | -35.543 | 18.847
23-03-2026 12:50 | 798 | 52.81 | 246.635 | 354.575 | 575.7 | 59.0958 | 46.7888 | 12.307 | 280.7327 | 40 | 46.1197 | -6.1197 | 0.69558 | 23-03-2026 12:50 | 265.508 | 272.764 | 582.1 | 45.4607 | 46.7888 | -1.3281 | 280.7327 | 42 | 46.1197 | -4.1197 | 0.9734 | 23-03-2026 12:50 | 257.665 | 274.796 | 571.5 | 45.7993 | 46.7888 | -0.98945 | 280.7327 | 40.3 | 46.1197 | -5.8197 | 0.93766 | 23-03-2026 12:50 | 272.921 | 277.246 | 577.5 | 46.2077 | 46.7888 | -0.58112 | 280.7327 | 40.9 | 46.1197 | -5.2197 | 0.9844 | 23-03-2026 12:50 | 174.137 | 177.554 | 436.5 | 29.5923 | 34.6584 | -5.066 | 207.9502 | 31 | 34.1627 | -3.1627 | 0.98076 | 23-03-2026 12:50 | 180.971 | 183.559 | 434.4 | 30.5932 | 34.6584 | -4.0652 | 207.9502 | 30.9 | 34.1627 | -3.2627 | 0.9859 | 23-03-2026 12:50 | 192.752 | 200.803 | 432 | 33.4672 | 34.6584 | -1.1912 | 207.9502 | 30.7 | 34.1627 | -3.4627 | 0.95991 | 23-03-2026 12:50 | 214.951 | 227.041 | 437.3 | 37.8402 | 34.6584 | 3.1818 | 207.9502 | 31.6 | 34.1627 | -2.5627 | 0.94675 | 23-03-2026 12:50 | 187.098 | 190.382 | 412.7 | 31.7303 | 32.9731 | -1.2428 | 197.8388 | 29.5 | 32.5016 | -3.0016 | 0.98275 | 23-03-2026 12:50 | 359.7867 | 358.7617 | 1.025 | 2152.5703 | 316.9 | 353.6314 | -36.7314 | 42.8867
23-03-2026 12:40 | 1121 | 55.68 | 352.696 | 357.854 | 535.7 | 59.6423 | 64.9957 | -5.3533 | 389.9741 | 46.6 | 64.0662 | -17.4662 | 0.98559 | 23-03-2026 12:40 | 267.649 | 314.953 | 540.1 | 52.4922 | 64.9957 | -12.5035 | 389.9741 | 46 | 64.0662 | -18.0662 | 0.84981 | 23-03-2026 12:40 | 352.449 | 362.06 | 531.2 | 60.3433 | 64.9957 | -4.6523 | 389.9741 | 46.2 | 64.0662 | -17.8662 | 0.97345 | 23-03-2026 12:40 | 352.637 | 357.898 | 536.6 | 59.6497 | 64.9957 | -5.346 | 389.9741 | 46.6 | 64.0662 | -17.4662 | 0.9853 | 23-03-2026 12:40 | 317.63 | 323.123 | 405.5 | 53.8538 | 48.1449 | 5.7089 | 288.8697 | 36.4 | 47.4565 | -11.0565 | 0.983 | 23-03-2026 12:40 | 301.587 | 316.426 | 403.5 | 52.7377 | 48.1449 | 4.5927 | 288.8697 | 36.8 | 47.4565 | -10.6565 | 0.9531 | 23-03-2026 12:40 | 313.125 | 322.393 | 401.3 | 53.7322 | 48.1449 | 5.5872 | 288.8697 | 35.9 | 47.4565 | -11.5565 | 0.97125 | 23-03-2026 12:40 | 232.692 | 244.772 | 405.7 | 40.7953 | 48.1449 | -7.3496 | 288.8697 | 35.4 | 47.4565 | -12.0565 | 0.95065 | 23-03-2026 12:40 | 208.349 | 228.27 | 383.2 | 38.045 | 45.804 | -7.759 | 274.8237 | 33.7 | 45.149 | -11.449 | 0.91273 | 23-03-2026 12:40 | 471.2915 | 498.3665 | -27.075 | 2990.1989 | 363.6 | 491.2398 | -127.6398 | 107.6915
23-03-2026 12:30 | 1290 | 52.52 | 352.729 | 357.919 | 489.1 | 59.6532 | 75.7211 | -16.0679 | 454.3263 | 51 | 74.6382 | -23.6382 | 0.9855 | 23-03-2026 12:30 | 351.009 | 357.884 | 494.1 | 59.6473 | 75.7211 | -16.0737 | 454.3263 | 50.7 | 74.6382 | -23.9382 | 0.98079 | 23-03-2026 12:30 | 350.903 | 334.776 | 485 | 55.796 | 75.7211 | -19.9251 | 454.3263 | 49.5 | 74.6382 | -25.1382 | 1.0482 | 23-03-2026 12:30 | 352.445 | 357.889 | 490 | 59.6482 | 75.7211 | -16.0729 | 454.3263 | 49.3 | 74.6382 | -25.3382 | 0.98479 | 23-03-2026 12:30 | 200.31 | 203.34 | 369.1 | 33.89 | 56.0897 | -22.1997 | 336.538 | 39.3 | 55.2876 | -15.9876 | 0.9851 | 23-03-2026 12:30 | 330.872 | 338.977 | 366.7 | 56.4962 | 56.0897 | 0.4065 | 336.538 | 38 | 55.2876 | -17.2876 | 0.97609 | 23-03-2026 12:30 | 191.885 | 197.27 | 365.4 | 32.8783 | 56.0897 | -23.2113 | 336.538 | 38.2 | 55.2876 | -17.0876 | 0.9727 | 23-03-2026 12:30 | 194.136 | 199.342 | 370.3 | 33.2237 | 56.0897 | -22.866 | 336.538 | 37.9 | 55.2876 | -17.3876 | 0.97388 | 23-03-2026 12:30 | 252.099 | 251.829 | 349.5 | 41.9715 | 53.3624 | -11.3909 | 320.1742 | 36.5 | 52.5993 | -16.0993 | 1.0011 | 23-03-2026 12:30 | 433.2043 | 580.6053 | -147.4009 | 3483.6316 | 390.4 | 572.3026 | -181.9026 | 42.8043
23-03-2026 12:20 | 838 | 52.23 | 347.774 | 354.113 | 438.1 | 59.0188 | 49.2446 | 9.7742 | 295.4675 | 57.4 | 48.5404 | 8.8596 | 0.9821 | 23-03-2026 12:20 | 319.824 | 356.771 | 443.4 | 59.4618 | 49.2446 | 10.2172 | 295.4675 | 57.3 | 48.5404 | 8.7596 | 0.89644 | 23-03-2026 12:20 | 265.806 | 270.265 | 435.5 | 45.0442 | 49.2446 | -4.2004 | 295.4675 | 56.8 | 48.5404 | 8.2596 | 0.9835 | 23-03-2026 12:20 | 291.433 | 296.564 | 440.7 | 49.4273 | 49.2446 | 0.18275 | 295.4675 | 57 | 48.5404 | 8.4596 | 0.9827 | 23-03-2026 12:20 | 208.078 | 221.523 | 329.8 | 36.9205 | 36.4775 | 0.44303 | 218.8648 | 44 | 35.9558 | 8.0442 | 0.93931 | 23-03-2026 12:20 | 203.825 | 206.929 | 328.7 | 34.4882 | 36.4775 | -1.9893 | 218.8648 | 43.8 | 35.9558 | 7.8442 | 0.985 | 23-03-2026 12:20 | 221.265 | 236.58 | 327.2 | 39.43 | 36.4775 | 2.9525 | 218.8648 | 43.5 | 35.9558 | 7.5442 | 0.93527 | 23-03-2026 12:20 | 204.824 | 223.696 | 332.4 | 37.2827 | 36.4775 | 0.8052 | 218.8648 | 43.8 | 35.9558 | 7.8442 | 0.91564 | 23-03-2026 12:20 | 186.973 | 189.782 | 313 | 31.6303 | 34.7038 | -3.0735 | 208.2228 | 41.3 | 34.2075 | 7.0925 | 0.9852 | 23-03-2026 12:20 | 392.7038 | 377.592 | 15.1118 | 2265.5521 | 444.9 | 372.1925 | 72.7075 | -52.1962
23-03-2026 12:10 | 962 | 52.23 | 324.831 | 334.092 | 380.7 | 55.682 | 56.5314 | -0.84937 | 339.1882 | 56 | 55.723 | 0.27703 | 0.97228 | 23-03-2026 12:10 | 316.657 | 322.166 | 386.1 | 53.6943 | 56.5314 | -2.837 | 339.1882 | 56 | 55.723 | 0.27703 | 0.9829 | 23-03-2026 12:10 | 341.845 | 353.461 | 378.7 | 58.9102 | 56.5314 | 2.3788 | 339.1882 | 55.5 | 55.723 | -0.22297 | 0.96714 | 23-03-2026 12:10 | 324.439 | 333.723 | 383.7 | 55.6205 | 56.5314 | -0.91087 | 339.1882 | 56.9 | 55.723 | 1.177 | 0.97218 | 23-03-2026 12:10 | 241.808 | 245.59 | 285.8 | 40.9317 | 41.8751 | -0.94342 | 251.2505 | 41.9 | 41.2763 | 0.62372 | 0.9846 | 23-03-2026 12:10 | 247.122 | 251.089 | 284.9 | 41.8482 | 41.8751 | -0.026925 | 251.2505 | 41.6 | 41.2763 | 0.32372 | 0.9842 | 23-03-2026 12:10 | 229.443 | 235.102 | 283.7 | 39.1837 | 41.8751 | -2.6914 | 251.2505 | 41.6 | 41.2763 | 0.32372 | 0.97593 | 23-03-2026 12:10 | 235.56 | 242.173 | 288.6 | 40.3622 | 41.8751 | -1.5129 | 251.2505 | 42 | 41.2763 | 0.72372 | 0.97269 | 23-03-2026 12:10 | 223.761 | 227.192 | 271.7 | 37.8653 | 39.839 | -1.9736 | 239.0338 | 39.7 | 39.2693 | 0.43073 | 0.9849 | 23-03-2026 12:10 | 424.098 | 433.4648 | -9.3668 | 2600.7889 | 431.2 | 427.2663 | 3.9337 | -7.102
23-03-2026 12:00 | 1020 | 51.66 | 336.966 | 341.421 | 324.7 | 56.9035 | 60.0719 | -3.1684 | 360.4313 | 56.3 | 59.2129 | -2.9129 | 0.98695 | 23-03-2026 12:00 | 344.009 | 350.101 | 330.1 | 58.3502 | 60.0719 | -1.7217 | 360.4313 | 57.4 | 59.2129 | -1.8129 | 0.9826 | 23-03-2026 12:00 | 334.649 | 344.252 | 323.2 | 57.3753 | 60.0719 | -2.6966 | 360.4313 | 56.1 | 59.2129 | -3.1129 | 0.9721 | 23-03-2026 12:00 | 338.899 | 344.9 | 326.8 | 57.4833 | 60.0719 | -2.5886 | 360.4313 | 56.1 | 59.2129 | -3.1129 | 0.9826 | 23-03-2026 12:00 | 252.118 | 256.015 | 243.9 | 42.6692 | 44.4977 | -1.8285 | 266.9862 | 41.6 | 43.8614 | -2.2614 | 0.98478 | 23-03-2026 12:00 | 249.859 | 254.762 | 243.3 | 42.4603 | 44.4977 | -2.0374 | 266.9862 | 41.4 | 43.8614 | -2.4614 | 0.98075 | 23-03-2026 12:00 | 250.496 | 255.502 | 242.1 | 42.5837 | 44.4977 | -1.914 | 266.9862 | 41.2 | 43.8614 | -2.6614 | 0.98041 | 23-03-2026 12:00 | 252.914 | 260.692 | 246.6 | 43.4487 | 44.4977 | -1.049 | 266.9862 | 41.5 | 43.8614 | -2.3614 | 0.97016 | 23-03-2026 12:00 | 239.152 | 242.864 | 232 | 40.4773 | 42.334 | -1.8567 | 254.0043 | 39.4 | 41.7287 | -2.3287 | 0.98472 | 23-03-2026 12:00 | 441.7515 | 460.6124 | -18.8609 | 2763.6742 | 431 | 454.0256 | -23.0256 | 10.7515
23-03-2026 11:50 | 1002 | 51.95 | 332.663 | 338.451 | 268.4 | 56.4085 | 58.9457 | -2.5372 | 353.6744 | 55.2 | 58.1028 | -2.9028 | 0.9829 | 23-03-2026 11:50 | 338.038 | 343.954 | 272.7 | 57.3257 | 58.9457 | -1.6201 | 353.6744 | 56 | 58.1028 | -2.1028 | 0.9828 | 23-03-2026 11:50 | 331.309 | 340.78 | 267.1 | 56.7967 | 58.9457 | -2.1491 | 353.6744 | 54.7 | 58.1028 | -3.4028 | 0.97221 | 23-03-2026 11:50 | 335.566 | 341.508 | 270.7 | 56.918 | 58.9457 | -2.0277 | 353.6744 | 55.6 | 58.1028 | -2.5028 | 0.9826 | 23-03-2026 11:50 | 249.42 | 253.424 | 202.3 | 42.2373 | 43.6635 | -1.4262 | 261.981 | 41.2 | 43.0391 | -1.8391 | 0.9842 | 23-03-2026 11:50 | 247.687 | 252.409 | 201.9 | 42.0682 | 43.6635 | -1.5953 | 261.981 | 41.1 | 43.0391 | -1.9391 | 0.98129 | 23-03-2026 11:50 | 247.693 | 252.821 | 200.9 | 42.1368 | 43.6635 | -1.5267 | 261.981 | 40.9 | 43.0391 | -2.1391 | 0.97972 | 23-03-2026 11:50 | 249.377 | 256.938 | 205.1 | 42.823 | 43.6635 | -0.84051 | 261.981 | 41.2 | 43.0391 | -1.8391 | 0.97057 | 23-03-2026 11:50 | 236.826 | 240.579 | 192.6 | 40.0965 | 41.5404 | -1.4439 | 249.2425 | 39.7 | 40.9464 | -1.2464 | 0.9844 | 23-03-2026 11:50 | 436.8107 | 451.9774 | -15.1667 | 2711.8643 | 425.6 | 445.5141 | -19.9141 | 11.2107
23-03-2026 11:40 | 1010 | 51.95 | 332.355 | 338.103 | 213.2 | 56.3505 | 59.4164 | -3.0659 | 356.4981 | 56.5 | 58.5667 | -2.0667 | 0.983 | 23-03-2026 11:40 | 339.662 | 345.606 | 216.7 | 57.601 | 59.4164 | -1.8154 | 356.4981 | 57.2 | 58.5667 | -1.3667 |  | 23-03-2026 11:40 | 330.756 | 340.342 | 212.4 | 56.7237 | 59.4164 | -2.6927 | 356.4981 | 55.1 | 58.5667 | -3.4667 | 0.97183 | 23-03-2026 11:40 | 338.361 | 344.318 | 215.1 | 57.3863 | 59.4164 | -2.03 | 356.4981 | 55.9 | 58.5667 | -2.6667 | 0.9827 | 23-03-2026 11:40 | 249.714 | 253.671 | 161.1 | 42.2785 | 44.0121 | -1.7336 | 264.0727 | 41.6 | 43.3827 | -1.7827 | 0.9844 | 23-03-2026 11:40 | 250.253 | 254.718 | 160.8 | 42.453 | 44.0121 | -1.5591 | 264.0727 | 41.3 | 43.3827 | -2.0827 | 0.98247 | 23-03-2026 11:40 | 248.946 | 253.951 | 160 | 42.3252 | 44.0121 | -1.687 | 264.0727 | 41.2 | 43.3827 | -2.1827 | 0.98029 | 23-03-2026 11:40 | 251.517 | 259.158 | 163.9 | 43.193 | 44.0121 | -0.81912 | 264.0727 | 41.4 | 43.3827 | -1.9827 | 0.97052 | 23-03-2026 11:40 | 238.923 | 242.674 | 152.9 | 40.4457 | 41.8721 | -1.4264 | 251.2325 | 38.9 | 41.2733 | -2.3733 | 0.98454 | 23-03-2026 11:40 | 438.7568 | 455.586 | -16.8291 | 2733.5159 | 429.1 | 449.0711 | -19.9711 | 9.6568
23-03-2026 11:30 | 989 | 51.95 | 331.137 | 336.891 | 156.7 | 56.1485 | 58.181 | -2.0325 | 349.0858 | 53.1 | 57.349 | -4.249 | 0.98292 | 23-03-2026 11:30 | 337.647 | 343.486 | 159.5 | 57.2477 | 58.181 | -0.9333 | 349.0858 | 55.4 | 57.349 | -1.949 | 0.983 | 23-03-2026 11:30 | 327.922 | 337.004 | 157.3 | 56.1673 | 58.181 | -2.0136 | 349.0858 | 55 | 57.349 | -2.349 | 0.97305 | 23-03-2026 11:30 | 334.202 | 339.982 | 159.2 | 56.6637 | 58.181 | -1.5173 | 349.0858 | 55.7 | 57.349 | -1.649 | 0.983 | 23-03-2026 11:30 | 247.575 | 251.473 | 119.5 | 41.9122 | 43.097 | -1.1848 | 258.5821 | 41.5 | 42.4807 | -0.98073 | 0.9845 | 23-03-2026 11:30 | 247.536 | 251.688 | 119.5 | 41.948 | 43.097 | -1.149 | 258.5821 | 41.4 | 42.4807 | -1.0807 | 0.9835 | 23-03-2026 11:30 | 246.493 | 251.167 | 118.8 | 41.8612 | 43.097 | -1.2358 | 258.5821 | 41.3 | 42.4807 | -1.1807 | 0.98139 | 23-03-2026 11:30 | 248.319 | 255.859 | 122.5 | 42.6432 | 43.097 | -0.45385 | 258.5821 | 41.6 | 42.4807 | -0.88073 | 0.97053 | 23-03-2026 11:30 | 236.486 | 240.16 | 114 | 40.0267 | 41.0015 | -0.9748 | 246.0088 | 39.4 | 40.4151 | -1.0151 | 0.9847 | 23-03-2026 11:30 | 434.6183 | 446.1134 | -11.4951 | 2676.6804 | 424.4 | 439.734 | -15.334 | 10.2183
23-03-2026 11:20 | 941 | 54.24 | 319.485 | 324.779 | 103.6 | 54.1298 | 54.8673 | -0.73749 | 329.2039 | 52.9 | 54.0827 | -1.1827 | 0.9837 | 23-03-2026 11:20 | 324.54 | 330.018 | 104.1 | 55.003 | 54.8673 | 0.13568 | 329.2039 | 54.1 | 54.0827 | 0.01728 | 0.9834 | 23-03-2026 11:20 | 318.229 | 326.311 | 102.3 | 54.3852 | 54.8673 | -0.48216 | 329.2039 | 52.6 | 54.0827 | -1.4827 | 0.97523 | 23-03-2026 11:20 | 322.868 | 328.318 | 103.5 | 54.7197 | 54.8673 | -0.14766 | 329.2039 | 53.1 | 54.0827 | -0.98272 | 0.9834 | 23-03-2026 11:20 | 240.267 | 243.951 | 78 | 40.6585 | 40.6425 | 0.016039 | 243.8548 | 39.3 | 40.0613 | -0.76127 | 0.9849 | 23-03-2026 11:20 | 238.929 | 243.028 | 78.1 | 40.5047 | 40.6425 | -0.13779 | 243.8548 | 39.3 | 40.0613 | -0.76127 | 0.98313 | 23-03-2026 11:20 | 239.287 | 243.816 | 77.5 | 40.636 | 40.6425 | -0.0064613 | 243.8548 | 39.1 | 40.0613 | -0.96127 | 0.98142 | 23-03-2026 11:20 | 239.939 | 247.184 | 80.9 | 41.1973 | 40.6425 | 0.55487 | 243.8548 | 39.4 | 40.0613 | -0.66127 | 0.97069 | 23-03-2026 11:20 | 225.66 | 229.073 | 74.6 | 38.1788 | 38.6663 | -0.48743 | 231.9976 | 37.4 | 38.1133 | -0.71334 | 0.9851 | 23-03-2026 11:20 | 419.413 | 420.7054 | -1.2924 | 2524.2324 | 407.2 | 414.6893 | -7.4893 | 12.213
23-03-2026 11:10 | 947 | 54.53 | 316.542 | 321.951 | 50.7 | 53.6585 | 55.1547 | -1.4962 | 330.9284 | 37.8 | 54.366 | -16.566 | 0.9832 | 23-03-2026 11:10 | 321.264 | 325.018 | 50 | 54.1697 | 55.1547 | -0.98507 | 330.9284 | 36.9 | 54.366 | -17.466 | 0.98845 | 23-03-2026 11:10 | 313.549 | 321.102 | 49.7 | 53.517 | 55.1547 | -1.6377 | 330.9284 | 36.8 | 54.366 | -17.566 | 0.97648 | 23-03-2026 11:10 | 317 | 322.482 | 50.4 | 53.747 | 55.1547 | -1.4077 | 330.9284 | 37.4 | 54.366 | -16.966 | 0.983 | 23-03-2026 11:10 | 234.085 | 237.795 | 38.7 | 39.6325 | 40.8554 | -1.2229 | 245.1321 | 29.3 | 40.2711 | -10.9711 | 0.9844 | 23-03-2026 11:10 | 233.469 | 237.145 | 38.8 | 39.5242 | 40.8554 | -1.3312 | 245.1321 | 29.4 | 40.2711 | -10.8711 | 0.9845 | 23-03-2026 11:10 | 231.558 | 235.595 | 38.4 | 39.2658 | 40.8554 | -1.5895 | 245.1321 | 29.1 | 40.2711 | -11.1711 | 0.98286 | 23-03-2026 11:10 | 231.828 | 238.831 | 41.5 | 39.8052 | 40.8554 | -1.0502 | 245.1321 | 32.1 | 40.2711 | -8.1711 | 0.97068 | 23-03-2026 11:10 | 220.874 | 224.283 | 37.2 | 37.3805 | 38.8688 | -1.4883 | 233.2129 | 28.4 | 38.313 | -9.913 | 0.9848 | 23-03-2026 11:10 | 410.7003 | 422.9092 | -12.2088 | 2537.455 | 297.2 | 416.8616 | -119.6616 | 113.5003
23-03-2026 11:00 | 926 | 54.24 | 0 | 0 | 12.9 | 0 | 53.9927 | -53.9927 | 323.9563 | 0 | 53.2206 | -53.2206 |  | 23-03-2026 11:00 | 0 | 0 | 13.1 | 0 | 53.9927 | -53.9927 | 323.9563 | 0 | 53.2206 | -53.2206 |  | 23-03-2026 11:00 | 0 | 0 | 12.9 | 0 | 53.9927 | -53.9927 | 323.9563 | 0 | 53.2206 | -53.2206 |  | 23-03-2026 11:00 | 0 | 0 | 13 | 0 | 53.9927 | -53.9927 | 323.9563 | 0 | 53.2206 | -53.2206 |  | 23-03-2026 11:00 | 0 | 0 | 9.4 | 0 | 39.9946 | -39.9946 | 239.9676 | 0 | 39.4227 | -39.4227 |  | 23-03-2026 11:00 | 0 | 0 | 9.4 | 0 | 39.9946 | -39.9946 | 239.9676 | 0 | 39.4227 | -39.4227 |  | 23-03-2026 11:00 | 0 | 0 | 9.3 | 0 | 39.9946 | -39.9946 | 239.9676 | 0 | 39.4227 | -39.4227 |  | 23-03-2026 11:00 | 0 | 0 | 9.4 | 0 | 39.9946 | -39.9946 | 239.9676 | 0 | 39.4227 | -39.4227 |  | 23-03-2026 11:00 | 0 | 0 | 8.8 | 0 | 38.0499 | -38.0499 | 228.2995 | 0 | 37.5058 | -37.5058 |  | 23-03-2026 11:00 | 0 | 413.9992 | -413.9992 | 2483.9949 | 0 | 408.079 | -408.079 | 0
23-03-2026 10:50 | 916 | 53.96 | 0 | 0 | 12.9 | 0 | 53.4679 | -53.4679 | 320.8077 | 0 | 52.7034 | -52.7034 |  | 23-03-2026 10:50 | 0 | 0 | 13.1 | 0 | 53.4679 | -53.4679 | 320.8077 | 0 | 52.7034 | -52.7034 |  | 23-03-2026 10:50 | 0 | 0 | 12.9 | 0 | 53.4679 | -53.4679 | 320.8077 | 0 | 52.7034 | -52.7034 |  | 23-03-2026 10:50 | 0 | 0 | 13 | 0 | 53.4679 | -53.4679 | 320.8077 | 0 | 52.7034 | -52.7034 |  | 23-03-2026 10:50 | 0 | 0 | 9.4 | 0 | 39.6059 | -39.6059 | 237.6353 | 0 | 39.0395 | -39.0395 |  | 23-03-2026 10:50 | 0 | 0 | 9.4 | 0 | 39.6059 | -39.6059 | 237.6353 | 0 | 39.0395 | -39.0395 |  | 23-03-2026 10:50 | 0 | 0 | 9.3 | 0 | 39.6059 | -39.6059 | 237.6353 | 0 | 39.0395 | -39.0395 |  | 23-03-2026 10:50 | 0 | 0 | 9.4 | 0 | 39.6059 | -39.6059 | 237.6353 | 0 | 39.0395 | -39.0395 |  | 23-03-2026 10:50 | 0 | 0 | 8.8 | 0 | 37.6801 | -37.6801 | 226.0806 | 0 | 37.1413 | -37.1413 |  | 23-03-2026 10:50 | 0 | 409.9754 | -409.9754 | 2459.8525 | 0 | 404.1128 | -404.1128 | 0
23-03-2026 10:40 | 749 | 53.96 | 0 | 0 | 12.9 | 0 | 43.72 | -43.72 | 262.3198 | 0 | 43.0948 | -43.0948 |  | 23-03-2026 10:40 | 0 | 0 | 13.1 | 0 | 43.72 | -43.72 | 262.3198 | 0 | 43.0948 | -43.0948 |  | 23-03-2026 10:40 | 0 | 0 | 12.9 | 0 | 43.72 | -43.72 | 262.3198 | 0 | 43.0948 | -43.0948 |  | 23-03-2026 10:40 | 0 | 0 | 13 | 0 | 43.72 | -43.72 | 262.3198 | 0 | 43.0948 | -43.0948 |  | 23-03-2026 10:40 | 0 | 0 | 9.4 | 0 | 32.3852 | -32.3852 | 194.311 | 0 | 31.9221 | -31.9221 |  | 23-03-2026 10:40 | 0 | 0 | 9.4 | 0 | 32.3852 | -32.3852 | 194.311 | 0 | 31.9221 | -31.9221 |  | 23-03-2026 10:40 | 0 | 0 | 9.3 | 0 | 32.3852 | -32.3852 | 194.311 | 0 | 31.9221 | -31.9221 |  | 23-03-2026 10:40 | 0 | 0 | 9.4 | 0 | 32.3852 | -32.3852 | 194.311 | 0 | 31.9221 | -31.9221 |  | 23-03-2026 10:40 | 0 | 0 | 8.8 | 0 | 30.8105 | -30.8105 | 184.8628 | 0 | 30.3699 | -30.3699 |  | 23-03-2026 10:40 | 0 | 335.231 | -335.231 | 2011.3859 | 0 | 330.4372 | -330.4372 | 0
23-03-2026 10:30 | 612 | 53.67 | 0 | 0 | 12.9 | 0 | 35.7635 | -35.7635 | 214.5808 | 0 | 35.2521 | -35.2521 |  | 23-03-2026 10:30 | 0 | 0 | 13.1 | 0 | 35.7635 | -35.7635 | 214.5808 | 0 | 35.2521 | -35.2521 |  | 23-03-2026 10:30 | 0 | 0 | 12.9 | 0 | 35.7635 | -35.7635 | 214.5808 | 0 | 35.2521 | -35.2521 |  | 23-03-2026 10:30 | 0 | 0 | 13 | 0 | 35.7635 | -35.7635 | 214.5808 | 0 | 35.2521 | -35.2521 |  | 23-03-2026 10:30 | 0 | 0 | 9.4 | 0 | 26.4915 | -26.4915 | 158.9488 | 0 | 26.1126 | -26.1126 |  | 23-03-2026 10:30 | 0 | 0 | 9.4 | 0 | 26.4915 | -26.4915 | 158.9488 | 0 | 26.1126 | -26.1126 |  | 23-03-2026 10:30 | 0 | 0 | 9.3 | 0 | 26.4915 | -26.4915 | 158.9488 | 0 | 26.1126 | -26.1126 |  | 23-03-2026 10:30 | 0 | 0 | 9.4 | 0 | 26.4915 | -26.4915 | 158.9488 | 0 | 26.1126 | -26.1126 |  | 23-03-2026 10:30 | 0 | 0 | 8.8 | 0 | 25.2033 | -25.2033 | 151.2201 | 0 | 24.8429 | -24.8429 |  | 23-03-2026 10:30 | 0 | 274.2231 | -274.2231 | 1645.3385 | 0 | 270.3017 | -270.3017 | 0
23-03-2026 10:20 | 765 | 53.38 | 0 | 0 | 12.9 | 0 | 44.7548 | -44.7548 | 268.5287 | 0 | 44.1148 | -44.1148 | [5 empty] | 0 | 44.7548 | -44.7548 | 268.5287 | 0 | 44.1148 | -44.1148 |  | 23-03-2026 10:20 | 0 | 0 | 12.9 | 0 | 44.7548 | -44.7548 | 268.5287 | 0 | 44.1148 | -44.1148 |  | 23-03-2026 10:20 | 0 | 0 | 13 | 0 | 44.7548 | -44.7548 | 268.5287 | 0 | 44.1148 | -44.1148 |  | 23-03-2026 10:20 | 0 | 0 | 9.4 | 0 | 33.1517 | -33.1517 | 198.9101 | 0 | 32.6776 | -32.6776 |  | 23-03-2026 10:20 | 0 | 0 | 9.4 | 0 | 33.1517 | -33.1517 | 198.9101 | 0 | 32.6776 | -32.6776 |  | 23-03-2026 10:20 | 0 | 0 | 9.3 | 0 | 33.1517 | -33.1517 | 198.9101 | 0 | 32.6776 | -32.6776 |  | 23-03-2026 10:20 | 0 | 0 | 9.4 | 0 | 33.1517 | -33.1517 | 198.9101 | 0 | 32.6776 | -32.6776 |  | 23-03-2026 10:20 | 0 | 0 | 8.8 | 0 | 31.5397 | -31.5397 | 189.2383 | 0 | 31.0887 | -31.0887 |  | 23-03-2026 10:20 | 0 | 343.1656 | -343.1656 | 2058.9935 | 0 | 338.2583 | -338.2583 | 0
23-03-2026 10:10 | 785 | 52.81 | 0 | 0 | 12.9 | 0 | 46.0266 | -46.0266 | 276.1594 | 0 | 45.3684 | -45.3684 |  | 23-03-2026 10:10 | 0 | 0 | 13.1 | 0 | 46.0266 | -46.0266 | 276.1594 | 0 | 45.3684 | -45.3684 |  | 23-03-2026 10:10 | 0 | 0 | 12.9 | 0 | 46.0266 | -46.0266 | 276.1594 | 0 | 45.3684 | -45.3684 |  | 23-03-2026 10:10 | 0 | 0 | 13 | 0 | 46.0266 | -46.0266 | 276.1594 | 0 | 45.3684 | -45.3684 |  | 23-03-2026 10:10 | 0 | 0 | 9.4 | 0 | 34.0937 | -34.0937 | 204.5625 | 0 | 33.6062 | -33.6062 |  | 23-03-2026 10:10 | 0 | 0 | 9.4 | 0 | 34.0937 | -34.0937 | 204.5625 | 0 | 33.6062 | -33.6062 |  | 23-03-2026 10:10 | 0 | 0 | 9.3 | 0 | 34.0937 | -34.0937 | 204.5625 | 0 | 33.6062 | -33.6062 |  | 23-03-2026 10:10 | 0 | 0 | 9.4 | 0 | 34.0937 | -34.0937 | 204.5625 | 0 | 33.6062 | -33.6062 |  | 23-03-2026 10:10 | 0 | 0 | 8.8 | 0 | 32.436 | -32.436 | 194.6159 | 0 | 31.9721 | -31.9721 |  | 23-03-2026 10:10 | 0 | 352.9172 | -352.9172 | 2117.5033 | 0 | 347.8705 | -347.8705 | 0
23-03-2026 10:00 | 558 | 53.96 | 0 | 0 | 12.9 | 0 | 32.5711 | -32.5711 | 195.4265 | 0 | 32.1053 | -32.1053 |  | 23-03-2026 10:00 | 0 | 0 | 13.1 | 0 | 32.5711 | -32.5711 | 195.4265 | 0 | 32.1053 | -32.1053 |  | 23-03-2026 10:00 | 0 | 0 | 12.9 | 0 | 32.5711 | -32.5711 | 195.4265 | 0 | 32.1053 | -32.1053 |  | 23-03-2026 10:00 | 0 | 0 | 13 | 0 | 32.5711 | -32.5711 | 195.4265 | 0 | 32.1053 | -32.1053 |  | 23-03-2026 10:00 | 0 | 0 | 9.4 | 0 | 24.1267 | -24.1267 | 144.7604 | 0 | 23.7817 | -23.7817 |  | 23-03-2026 10:00 | 0 | 0 | 9.4 | 0 | 24.1267 | -24.1267 | 144.7604 | 0 | 23.7817 | -23.7817 |  | 23-03-2026 10:00 | 0 | 0 | 9.3 | 0 | 24.1267 | -24.1267 | 144.7604 | 0 | 23.7817 | -23.7817 |  | 23-03-2026 10:00 | 0 | 0 | 9.4 | 0 | 24.1267 | -24.1267 | 144.7604 | 0 | 23.7817 | -23.7817 |  | 23-03-2026 10:00 | 0 | 0 | 8.8 | 0 | 22.9536 | -22.9536 | 137.7216 | 0 | 22.6254 | -22.6254 |  | 23-03-2026 10:00 | 0 | 249.7448 | -249.7448 | 1498.4691 | 0 | 246.1735 | -246.1735 | 0
23-03-2026 09:50 | 639 | 53.96 | 0 | 0 | 12.9 | 0 | 37.2991 | -37.2991 | 223.7949 | 0 | 36.7658 | -36.7658 |  | 23-03-2026 09:50 | 0 | 0 | 13.1 | 0 | 37.2991 | -37.2991 | 223.7949 | 0 | 36.7658 | -36.7658 |  | 23-03-2026 09:50 | 0 | 0 | 12.9 | 0 | 37.2991 | -37.2991 | 223.7949 | 0 | 36.7658 | -36.7658 |  | 23-03-2026 09:50 | 0 | 0 | 13 | 0 | 37.2991 | -37.2991 | 223.7949 | 0 | 36.7658 | -36.7658 |  | 23-03-2026 09:50 | 0 | 0 | 9.4 | 0 | 27.629 | -27.629 | 165.774 | 0 | 27.2339 | -27.2339 |  | 23-03-2026 09:50 | 0 | 0 | 9.4 | 0 | 27.629 | -27.629 | 165.774 | 0 | 27.2339 | -27.2339 |  | 23-03-2026 09:50 | 0 | 0 | 9.3 | 0 | 27.629 | -27.629 | 165.774 | 0 | 27.2339 | -27.2339 |  | 23-03-2026 09:50 | 0 | 0 | 9.4 | 0 | 27.629 | -27.629 | 165.774 | 0 | 27.2339 | -27.2339 |  | 23-03-2026 09:50 | 0 | 0 | 8.8 | 0 | 26.2856 | -26.2856 | 157.7134 | 0 | 25.9097 | -25.9097 |  | 23-03-2026 09:50 | 0 | 285.9981 | -285.9981 | 1715.9888 | 0 | 281.9084 | -281.9084 | 0
23-03-2026 09:40 | 735 | 54.24 | 0 | 0 | 12.9 | 0 | 42.856 | -42.856 | 257.1359 | 0 | 42.2431 | -42.2431 |  | 23-03-2026 09:40 | 0 | 0 | 13.1 | 0 | 42.856 | -42.856 | 257.1359 | 0 | 42.2431 | -42.2431 |  | 23-03-2026 09:40 | 0 | 0 | 12.9 | 0 | 42.856 | -42.856 | 257.1359 | 0 | 42.2431 | -42.2431 |  | 23-03-2026 09:40 | 0 | 0 | 13 | 0 | 42.856 | -42.856 | 257.1359 | 0 | 42.2431 | -42.2431 |  | 23-03-2026 09:40 | 0 | 0 | 9.4 | 0 | 31.7452 | -31.7452 | 190.471 | 0 | 31.2912 | -31.2912 |  | 23-03-2026 09:40 | 0 | 0 | 9.4 | 0 | 31.7452 | -31.7452 | 190.471 | 0 | 31.2912 | -31.2912 |  | 23-03-2026 09:40 | 0 | 0 | 9.3 | 0 | 31.7452 | -31.7452 | 190.471 | 0 | 31.2912 | -31.2912 |  | 23-03-2026 09:40 | 0 | 0 | 9.4 | 0 | 31.7452 | -31.7452 | 190.471 | 0 | 31.2912 | -31.2912 |  | 23-03-2026 09:40 | 0 | 0 | 8.8 | 0 | 30.2016 | -30.2016 | 181.2096 | 0 | 29.7697 | -29.7697 |  | 23-03-2026 09:40 | 0 | 328.6062 | -328.6062 | 1971.6374 | 0 | 323.9072 | -323.9072 | 0
23-03-2026 09:30 | 628 | 53.67 | 0 | 0 | 12.9 | 0 | 36.6985 | -36.6985 | 220.1908 | 0 | 36.1737 | -36.1737 |  | 23-03-2026 09:30 | 0 | 0 | 13.1 | 0 | 36.6985 | -36.6985 | 220.1908 | 0 | 36.1737 | -36.1737 |  | 23-03-2026 09:30 | 0 | 0 | 12.9 | 0 | 36.6985 | -36.6985 | 220.1908 | 0 | 36.1737 | -36.1737 |  | 23-03-2026 09:30 | 0 | 0 | 13 | 0 | 36.6985 | -36.6985 | 220.1908 | 0 | 36.1737 | -36.1737 |  | 23-03-2026 09:30 | 0 | 0 | 9.4 | 0 | 27.184 | -27.184 | 163.1043 | 0 | 26.7953 | -26.7953 |  | 23-03-2026 09:30 | 0 | 0 | 9.4 | 0 | 27.184 | -27.184 | 163.1043 | 0 | 26.7953 | -26.7953 |  | 23-03-2026 09:30 | 0 | 0 | 9.3 | 0 | 27.184 | -27.184 | 163.1043 | 0 | 26.7953 | -26.7953 |  | 23-03-2026 09:30 | 0 | 0 | 9.4 | 0 | 27.184 | -27.184 | 163.1043 | 0 | 26.7953 | -26.7953 |  | 23-03-2026 09:30 | 0 | 0 | 8.8 | 0 | 25.8623 | -25.8623 | 155.1735 | 0 | 25.4924 | -25.4924 |  | 23-03-2026 09:30 | 0 | 281.3923 | -281.3923 | 1688.3539 | 0 | 277.3684 | -277.3684 | 0
23-03-2026 09:20 | 558 | 53.09 | 0 | 0 | 12.9 | 0 | 32.6814 | -32.6814 | 196.0887 | 0 | 32.2141 | -32.2141 |  | 23-03-2026 09:20 | 0 | 0 | 13.1 | 0 | 32.6814 | -32.6814 | 196.0887 | 0 | 32.2141 | -32.2141 |  | 23-03-2026 09:20 | 0 | 0 | 12.9 | 0 | 32.6814 | -32.6814 | 196.0887 | 0 | 32.2141 | -32.2141 |  | 23-03-2026 09:20 | 0 | 0 | 13 | 0 | 32.6814 | -32.6814 | 196.0887 | 0 | 32.2141 | -32.2141 |  | 23-03-2026 09:20 | 0 | 0 | 9.4 | 0 | 24.2085 | -24.2085 | 145.2509 | 0 | 23.8623 | -23.8623 |  | 23-03-2026 09:20 | 0 | 0 | 9.4 | 0 | 24.2085 | -24.2085 | 145.2509 | 0 | 23.8623 | -23.8623 |  | 23-03-2026 09:20 | 0 | 0 | 9.3 | 0 | 24.2085 | -24.2085 | 145.2509 | 0 | 23.8623 | -23.8623 |  | 23-03-2026 09:20 | 0 | 0 | 9.4 | 0 | 24.2085 | -24.2085 | 145.2509 | 0 | 23.8623 | -23.8623 |  | 23-03-2026 09:20 | 0 | 0 | 8.8 | 0 | 23.0314 | -23.0314 | 138.1882 | 0 | 22.702 | -22.702 |  | 23-03-2026 09:20 | 0 | 250.5911 | -250.5911 | 1503.5466 | 0 | 247.0076 | -247.0076 | 0
23-03-2026 09:10 | 561 | 53.67 | 0 | 0 | 12.9 | 0 | 32.7832 | -32.7832 | 196.6991 | 0 | 32.3144 | -32.3144 |  | 23-03-2026 09:10 | 0 | 0 | 13.1 | 0 | 32.7832 | -32.7832 | 196.6991 | 0 | 32.3144 | -32.3144 |  | 23-03-2026 09:10 | 0 | 0 | 12.9 | 0 | 32.7832 | -32.7832 | 196.6991 | 0 | 32.3144 | -32.3144 |  | 23-03-2026 09:10 | 0 | 0 | 13 | 0 | 32.7832 | -32.7832 | 196.6991 | 0 | 32.3144 | -32.3144 |  | 23-03-2026 09:10 | 0 | 0 | 9.4 | 0 | 24.2838 | -24.2838 | 145.703 | 0 | 23.9366 | -23.9366 |  | 23-03-2026 09:10 | 0 | 0 | 9.4 | 0 | 24.2838 | -24.2838 | 145.703 | 0 | 23.9366 | -23.9366 |  | 23-03-2026 09:10 | 0 | 0 | 9.3 | 0 | 24.2838 | -24.2838 | 145.703 | 0 | 23.9366 | -23.9366 |  | 23-03-2026 09:10 | 0 | 0 | 9.4 | 0 | 24.2838 | -24.2838 | 145.703 | 0 | 23.9366 | -23.9366 |  | 23-03-2026 09:10 | 0 | 0 | 8.8 | 0 | 23.1031 | -23.1031 | 138.6184 | 0 | 22.7727 | -22.7727 |  | 23-03-2026 09:10 | 0 | 251.3712 | -251.3712 | 1508.227 | 0 | 247.7766 | -247.7766 | 0
23-03-2026 09:00 | 324 | 52.81 | 0 | 0 | 12.9 | 0 | 18.997 | -18.997 | 113.9817 | 0 | 18.7253 | -18.7253 |  | 23-03-2026 09:00 | 0 | 0 | 13.1 | 0 | 18.997 | -18.997 | 113.9817 | 0 | 18.7253 | -18.7253 |  | 23-03-2026 09:00 | 0 | 0 | 12.9 | 0 | 18.997 | -18.997 | 113.9817 | 0 | 18.7253 | -18.7253 |  | 23-03-2026 09:00 | 0 | 0 | 13 | 0 | 18.997 | -18.997 | 113.9817 | 0 | 18.7253 | -18.7253 |  | 23-03-2026 09:00 | 0 | 0 | 9.4 | 0 | 14.0718 | -14.0718 | 84.4309 | 0 | 13.8706 | -13.8706 |  | 23-03-2026 09:00 | 0 | 0 | 9.4 | 0 | 14.0718 | -14.0718 | 84.4309 | 0 | 13.8706 | -13.8706 |  | 23-03-2026 09:00 | 0 | 0 | 9.3 | 0 | 14.0718 | -14.0718 | 84.4309 | 0 | 13.8706 | -13.8706 |  | 23-03-2026 09:00 | 0 | 0 | 9.4 | 0 | 14.0718 | -14.0718 | 84.4309 | 0 | 13.8706 | -13.8706 |  | 23-03-2026 09:00 | 0 | 0 | 8.8 | 0 | 13.3876 | -13.3876 | 80.3255 | 0 | 13.1961 | -13.1961 |  | 23-03-2026 09:00 | 0 | 145.6627 | -145.6627 | 873.9759 | 0 | 143.5797 | -143.5797 | 0
23-03-2026 08:50 | 405 | 52.23 | 0 | 0 | 12.9 | 0 | 23.7996 | -23.7996 | 142.7975 | 0 | 23.4593 | -23.4593 |  | 23-03-2026 08:50 | 0 | 0 | 13.1 | 0 | 23.7996 | -23.7996 | 142.7975 | 0 | 23.4593 | -23.4593 |  | 23-03-2026 08:50 | 0 | 0 | 12.9 | 0 | 23.7996 | -23.7996 | 142.7975 | 0 | 23.4593 | -23.4593 |  | 23-03-2026 08:50 | 0 | 0 | 13 | 0 | 23.7996 | -23.7996 | 142.7975 | 0 | 23.4593 | -23.4593 |  | 23-03-2026 08:50 | 0 | 0 | 9.4 | 0 | 17.6293 | -17.6293 | 105.776 | 0 | 17.3772 | -17.3772 |  | 23-03-2026 08:50 | 0 | 0 | 9.4 | 0 | 17.6293 | -17.6293 | 105.776 | 0 | 17.3772 | -17.3772 |  | 23-03-2026 08:50 | 0 | 0 | 9.3 | 0 | 17.6293 | -17.6293 | 105.776 | 0 | 17.3772 | -17.3772 |  | 23-03-2026 08:50 | 0 | 0 | 9.4 | 0 | 17.6293 | -17.6293 | 105.776 | 0 | 17.3772 | -17.3772 |  | 23-03-2026 08:50 | 0 | 0 | 8.8 | 0 | 16.7721 | -16.7721 | 100.6327 | 0 | 16.5323 | -16.5323 |  | 23-03-2026 08:50 | 0 | 182.4878 | -182.4878 | 1094.9267 | 0 | 179.8782 | -179.8782 | 0
23-03-2026 08:40 | 205 | 48.79 | 0 | 0 | 12.9 | 0 | 12.207 | -12.207 | 73.2422 | 0 | 12.0325 | -12.0325 |  | 23-03-2026 08:40 | 0 | 0 | 13.1 | 0 | 12.207 | -12.207 | 73.2422 | 0 | 12.0325 | -12.0325 |  | 23-03-2026 08:40 | 0 | 0 | 12.9 | 0 | 12.207 | -12.207 | 73.2422 | 0 | 12.0325 | -12.0325 |  | 23-03-2026 08:40 | 0 | 0 | 13 | 0 | 12.207 | -12.207 | 73.2422 | 0 | 12.0325 | -12.0325 |  | 23-03-2026 08:40 | 0 | 0 | 9.4 | 0 | 9.0422 | -9.0422 | 54.2535 | 0 | 8.9129 | -8.9129 |  | 23-03-2026 08:40 | 0 | 0 | 9.4 | 0 | 9.0422 | -9.0422 | 54.2535 | 0 | 8.9129 | -8.9129 |  | 23-03-2026 08:40 | 0 | 0 | 9.3 | 0 | 9.0422 | -9.0422 | 54.2535 | 0 | 8.9129 | -8.9129 |  | 23-03-2026 08:40 | 0 | 0 | 9.4 | 0 | 9.0422 | -9.0422 | 54.2535 | 0 | 8.9129 | -8.9129 |  | 23-03-2026 08:40 | 0 | 0 | 8.8 | 0 | 8.6026 | -8.6026 | 51.6154 | 0 | 8.4796 | -8.4796 |  | 23-03-2026 08:40 | 0 | 93.5997 | -93.5997 | 561.598 | 0 | 92.2612 | -92.2612 | 0
23-03-2026 08:30 | 355 | 45.35 | 0 | 0 | 12.9 | 0 | 21.4166 | -21.4166 | 128.4998 | 0 | 21.1104 | -21.1104 |  | 23-03-2026 08:30 | 0 | 0 | 13.1 | 0 | 21.4166 | -21.4166 | 128.4998 | 0 | 21.1104 | -21.1104 |  | 23-03-2026 08:30 | 0 | 0 | 12.9 | 0 | 21.4166 | -21.4166 | 128.4998 | 0 | 21.1104 | -21.1104 |  | 23-03-2026 08:30 | 0 | 0 | 13 | 0 | 21.4166 | -21.4166 | 128.4998 | 0 | 21.1104 | -21.1104 |  | 23-03-2026 08:30 | 0 | 0 | 9.4 | 0 | 15.8642 | -15.8642 | 95.185 | 0 | 15.6373 | -15.6373 |  | 23-03-2026 08:30 | 0 | 0 | 9.4 | 0 | 15.8642 | -15.8642 | 95.185 | 0 | 15.6373 | -15.6373 |  | 23-03-2026 08:30 | 0 | 0 | 9.3 | 0 | 15.8642 | -15.8642 | 95.185 | 0 | 15.6373 | -15.6373 |  | 23-03-2026 08:30 | 0 | 0 | 9.4 | 0 | 15.8642 | -15.8642 | 95.185 | 0 | 15.6373 | -15.6373 |  | 23-03-2026 08:30 | 0 | 0 | 8.8 | 0 | 15.0928 | -15.0928 | 90.5568 | 0 | 14.877 | -14.877 |  | 23-03-2026 08:30 | 0 | 164.216 | -164.216 | 985.296 | 0 | 161.8677 | -161.8677 | 0
23-03-2026 08:20 | 137 | 37.31 | 0 | 0 | 12.9 | 0 | 8.5154 | -8.5154 | 51.0925 | 0 | 8.3937 | -8.3937 |  | 23-03-2026 08:20 | 0 | 0 | 13.1 | 0 | 8.5154 | -8.5154 | 51.0925 | 0 | 8.3937 | -8.3937 |  | 23-03-2026 08:20 | 0 | 0 | 12.9 | 0 | 8.5154 | -8.5154 | 51.0925 | 0 | 8.3937 | -8.3937 |  | 23-03-2026 08:20 | 0 | 0 | 13 | 0 | 8.5154 | -8.5154 | 51.0925 | 0 | 8.3937 | -8.3937 |  | 23-03-2026 08:20 | 0 | 0 | 9.4 | 0 | 6.3077 | -6.3077 | 37.8463 | 0 | 6.2175 | -6.2175 |  | 23-03-2026 08:20 | 0 | 0 | 9.4 | 0 | 6.3077 | -6.3077 | 37.8463 | 0 | 6.2175 | -6.2175 |  | 23-03-2026 08:20 | 0 | 0 | 9.3 | 0 | 6.3077 | -6.3077 | 37.8463 | 0 | 6.2175 | -6.2175 |  | 23-03-2026 08:20 | 0 | 0 | 9.4 | 0 | 6.3077 | -6.3077 | 37.8463 | 0 | 6.2175 | -6.2175 |  | 23-03-2026 08:20 | 0 | 0 | 8.8 | 0 | 6.001 | -6.001 | 36.0061 | 0 | 5.9152 | -5.9152 |  | 23-03-2026 08:20 | 0 | 65.2936 | -65.2936 | 391.7615 | 0 | 64.3599 | -64.3599 | 0
23-03-2026 08:10 | 107 | 32.43 | 0 | 0 | 12.9 | 0 | 6.7694 | -6.7694 | 40.6166 | 0 | 6.6726 | -6.6726 |  | 23-03-2026 08:10 | 0 | 0 | 13.1 | 0 | 6.7694 | -6.7694 | 40.6166 | 0 | 6.6726 | -6.6726 |  | 23-03-2026 08:10 | 0 | 0 | 12.9 | 0 | 6.7694 | -6.7694 | 40.6166 | 0 | 6.6726 | -6.6726 |  | 23-03-2026 08:10 | 0 | 0 | 13 | 0 | 6.7694 | -6.7694 | 40.6166 | 0 | 6.6726 | -6.6726 |  | 23-03-2026 08:10 | 0 | 0 | 9.4 | 0 | 5.0144 | -5.0144 | 30.0864 | 0 | 4.9427 | -4.9427 |  | 23-03-2026 08:10 | 0 | 0 | 9.4 | 0 | 5.0144 | -5.0144 | 30.0864 | 0 | 4.9427 | -4.9427 |  | 23-03-2026 08:10 | 0 | 0 | 9.3 | 0 | 5.0144 | -5.0144 | 30.0864 | 0 | 4.9427 | -4.9427 |  | 23-03-2026 08:10 | 0 | 0 | 9.4 | 0 | 5.0144 | -5.0144 | 30.0864 | 0 | 4.9427 | -4.9427 |  | 23-03-2026 08:10 | 0 | 0 | 8.8 | 0 | 4.7706 | -4.7706 | 28.6235 | 0 | 4.7024 | -4.7024 |  | 23-03-2026 08:10 | 0 | 51.9059 | -51.9059 | 311.4357 | 0 | 51.1637 | -51.1637 | 0
23-03-2026 08:00 | 104 | 32.43 | 0 | 0 | 12.9 | 0 | 6.5796 | -6.5796 | 39.4779 | 0 | 6.4856 | -6.4856 |  | 23-03-2026 08:00 | 0 | 0 | 13.1 | 0 | 6.5796 | -6.5796 | 39.4779 | 0 | 6.4856 | -6.4856 |  | 23-03-2026 08:00 | 0 | 0 | 12.9 | 0 | 6.5796 | -6.5796 | 39.4779 | 0 | 6.4856 | -6.4856 |  | 23-03-2026 08:00 | 0 | 0 | 13 | 0 | 6.5796 | -6.5796 | 39.4779 | 0 | 6.4856 | -6.4856 |  | 23-03-2026 08:00 | 0 | 0 | 9.4 | 0 | 4.8738 | -4.8738 | 29.2429 | 0 | 4.8041 | -4.8041 |  | 23-03-2026 08:00 | 0 | 0 | 9.4 | 0 | 4.8738 | -4.8738 | 29.2429 | 0 | 4.8041 | -4.8041 |  | 23-03-2026 08:00 | 0 | 0 | 9.3 | 0 | 4.8738 | -4.8738 | 29.2429 | 0 | 4.8041 | -4.8041 |  | 23-03-2026 08:00 | 0 | 0 | 9.4 | 0 | 4.8738 | -4.8738 | 29.2429 | 0 | 4.8041 | -4.8041 |  | 23-03-2026 08:00 | 0 | 0 | 8.8 | 0 | 4.6368 | -4.6368 | 27.821 | 0 | 4.5705 | -4.5705 |  | 23-03-2026 08:00 | 0 | 50.4506 | -50.4506 | 302.7038 | 0 | 49.7292 | -49.7292 | 0
23-03-2026 07:50 | 106 | 30.42 | 0 | 0 | 12.9 | 0 | 6.7546 | -6.7546 | 40.5277 | 1.5 | 6.658 | -5.158 |  | 23-03-2026 07:50 | 0 | 0 | 13.1 | 0 | 6.7546 | -6.7546 | 40.5277 | 1.5 | 6.658 | -5.158 |  | 23-03-2026 07:50 | 0 | 0 | 12.9 | 0 | 6.7546 | -6.7546 | 40.5277 | 1.7 | 6.658 | -4.958 |  | 23-03-2026 07:50 | 0 | 0 | 13 | 0 | 6.7546 | -6.7546 | 40.5277 | 1.5 | 6.658 | -5.158 |  | 23-03-2026 07:50 | 0 | 0 | 9.4 | 0 | 5.0034 | -5.0034 | 30.0205 | 1.1 | 4.9319 | -3.8319 |  | 23-03-2026 07:50 | 0 | 0 | 9.4 | 0 | 5.0034 | -5.0034 | 30.0205 | 0 | 4.9319 | -4.9319 |  | 23-03-2026 07:50 | 0 | 0 | 9.3 | 0 | 5.0034 | -5.0034 | 30.0205 | 1.1 | 4.9319 | -3.8319 |  | 23-03-2026 07:50 | 0 | 0 | 9.4 | 0 | 5.0034 | -5.0034 | 30.0205 | 1.1 | 4.9319 | -3.8319 |  | 23-03-2026 07:50 | 0 | 0 | 8.8 | 0 | 4.7601 | -4.7601 | 28.5608 | 0 | 4.6921 | -4.6921 |  | 23-03-2026 07:50 | 0 | 51.7922 | -51.7922 | 310.7535 | 9.5 | 51.0516 | -41.5516 | -9.5
23-03-2026 07:40 | 72 | 28.99 | 25.736 | 26.275 | 11.4 | 4.3792 | 4.6114 | -0.23228 | 27.6687 | 4.5 | 4.5455 | -0.045502 |  | 23-03-2026 07:40 | 25.609 | 26.772 | 11.6 | 4.462 | 4.6114 | -0.14945 | 27.6687 | 4.6 | 4.5455 | 0.054498 |  | 23-03-2026 07:40 | 25.644 | 26.197 | 11.2 | 4.3662 | 4.6114 | -0.24528 | 27.6687 | 4.3 | 4.5455 | -0.2455 |  | 23-03-2026 07:40 | 26.079 | 26.611 | 11.5 | 4.4352 | 4.6114 | -0.17628 | 27.6687 | 4.5 | 4.5455 | -0.045502 |  | 23-03-2026 07:40 | 19.101 | 19.698 | 8.3 | 3.283 | 3.4159 | -0.13289 | 20.4953 | 3.4 | 3.367 | 0.032961 |  | 23-03-2026 07:40 | 18.978 | 19.441 | 8.2 | 3.2402 | 3.4159 | -0.17572 | 20.4953 | 3.3 | 3.367 | -0.067039 |  | 23-03-2026 07:40 | 18.939 | 19.405 | 8.2 | 3.2342 | 3.4159 | -0.18172 | 20.4953 | 3.3 | 3.367 | -0.067039 |  | 23-03-2026 07:40 | 19.065 | 19.74 | 8.3 | 3.29 | 3.4159 | -0.12589 | 20.4953 | 3.3 | 3.367 | -0.067039 |  | 23-03-2026 07:40 | 17.997 | 18.451 | 7.8 | 3.0752 | 3.2498 | -0.17463 | 19.4988 | 3.1 | 3.2033 | -0.10332 |  | 23-03-2026 07:40 | 33.765 | 35.3591 | -1.5941 | 212.1547 | 34.3 | 34.8535 | -0.55348 | -0.535
23-03-2026 07:30 | 71 | 27.84 | 25.252 | 25.788 | 6.9 | 4.298 | 4.566 | -0.26796 | 27.3958 | 3.1 | 4.5007 | -1.4007 |  | 23-03-2026 07:30 | 26.138 | 26.795 | 7 | 4.4658 | 4.566 | -0.10013 | 27.3958 | 3.1 | 4.5007 | -1.4007 |  | 23-03-2026 07:30 | 25.917 | 26.47 | 6.9 | 4.4117 | 4.566 | -0.15429 | 27.3958 | 3.1 | 4.5007 | -1.4007 |  | 23-03-2026 07:30 | 26.031 | 26.687 | 7 | 4.4478 | 4.566 | -0.11813 | 27.3958 | 3.2 | 4.5007 | -1.3007 |  | 23-03-2026 07:30 | 18.845 | 19.333 | 4.9 | 3.2222 | 3.3822 | -0.16003 | 20.2932 | 2.2 | 3.3338 | -1.1338 |  | 23-03-2026 07:30 | 18.894 | 19.336 | 4.9 | 3.2227 | 3.3822 | -0.15953 | 20.2932 | 2.2 | 3.3338 | -1.1338 |  | 23-03-2026 07:30 | 18.808 | 19.272 | 4.9 | 3.212 | 3.3822 | -0.17019 | 20.2932 | 2.3 | 3.3338 | -1.0338 |  | 23-03-2026 07:30 | 18.91 | 19.737 | 5 | 3.2895 | 3.3822 | -0.092693 | 20.2932 | 2.3 | 3.3338 | -1.0338 |  | 23-03-2026 07:30 | 17.937 | 18.391 | 4.7 | 3.0652 | 3.2177 | -0.15257 | 19.3064 | 2.2 | 3.1717 | -0.97172 |  | 23-03-2026 07:30 | 33.6348 | 35.0104 | -1.3755 | 210.0621 | 23.7 | 34.5097 | -10.8097 | 9.9348
23-03-2026 07:20 | 36 | 26.69 | 12.251 | 12.652 | 3.8 | 2.1087 | 2.3245 | -0.21588 | 13.9473 | 1.9 | 2.2913 | -0.39131 |  | 23-03-2026 07:20 | 12.173 | 13.192 | 3.9 | 2.1987 | 2.3245 | -0.12588 | 13.9473 | 1.9 | 2.2913 | -0.39131 |  | 23-03-2026 07:20 | 12.281 | 12.691 | 3.8 | 2.1152 | 2.3245 | -0.20938 | 13.9473 | 1.9 | 2.2913 | -0.39131 |  | 23-03-2026 07:20 | 12.452 | 13.155 | 3.8 | 2.1925 | 2.3245 | -0.13205 | 13.9473 | 1.8 | 2.2913 | -0.49131 |  | 23-03-2026 07:20 | 8.992 | 9.622 | 2.7 | 1.6037 | 1.7219 | -0.11822 | 10.3313 | 1.4 | 1.6973 | -0.29726 |  | 23-03-2026 07:20 | 8.844 | 9.188 | 2.7 | 1.5313 | 1.7219 | -0.19055 | 10.3313 | 1.4 | 1.6973 | -0.29726 |  | 23-03-2026 07:20 | 8.845 | 9.195 | 2.6 | 1.5325 | 1.7219 | -0.18939 | 10.3313 | 1.3 | 1.6973 | -0.39726 |  | 23-03-2026 07:20 | 8.914 | 9.464 | 2.7 | 1.5773 | 1.7219 | -0.14455 | 10.3313 | 1.3 | 1.6973 | -0.39726 |  | 23-03-2026 07:20 | 8.395 | 8.733 | 2.5 | 1.4555 | 1.6382 | -0.18266 | 9.829 | 1.3 | 1.6147 | -0.31474 |  | 23-03-2026 07:20 | 16.3153 | 17.8239 | -1.5086 | 106.9434 | 14.2 | 17.569 | -3.369 | 2.1153
23-03-2026 07:10 | 29 | 25.83 | 9.814 | 10.182 | 1.9 | 1.697 | 1.8782 | -0.18122 | 11.2693 | 1.2 | 1.8514 | -0.65136 |  | 23-03-2026 07:10 | 10.15 | 10.636 | 2 | 1.7727 | 1.8782 | -0.10555 | 11.2693 | 1.3 | 1.8514 | -0.55136 |  | 23-03-2026 07:10 | 9.874 | 10.251 | 1.9 | 1.7085 | 1.8782 | -0.16972 | 11.2693 | 1.2 | 1.8514 | -0.65136 |  | 23-03-2026 07:10 | 9.99 | 10.973 | 2 | 1.8288 | 1.8782 | -0.049388 | 11.2693 | 1.3 | 1.8514 | -0.55136 |  | 23-03-2026 07:10 | 7.169 | 7.77 | 1.3 | 1.295 | 1.3913 | -0.096275 | 8.3477 | 0.8 | 1.3714 | -0.57138 |  | 23-03-2026 07:10 | 7.196 | 7.498 | 1.3 | 1.2497 | 1.3913 | -0.14161 | 8.3477 | 0.8 | 1.3714 | -0.57138 |  | 23-03-2026 07:10 | 7.128 | 7.465 | 1.3 | 1.2442 | 1.3913 | -0.14711 | 8.3477 | 0.8 | 1.3714 | -0.57138 |  | 23-03-2026 07:10 | 7.184 | 7.774 | 1.4 | 1.2957 | 1.3913 | -0.095609 | 8.3477 | 0.9 | 1.3714 | -0.47138 |  | 23-03-2026 07:10 | 6.759 | 7.054 | 1.2 | 1.1757 | 1.3236 | -0.14796 | 7.9418 | 0.8 | 1.3047 | -0.5047 |  | 23-03-2026 07:10 | 13.2672 | 14.4016 | -1.1344 | 86.4097 | 9.1 | 14.1957 | -5.0957 | 4.1672
23-03-2026 07:00 | 17 | 24.68 | 5.919 | 6.184 | 0.7 | 1.0307 | 1.1055 | -0.074804 | 6.6328 | 0.7 | 1.0897 | -0.38966 |  | 23-03-2026 07:00 | 6.057 | 6.506 | 0.7 | 1.0843 | 1.1055 | -0.021138 | 6.6328 | 0.7 | 1.0897 | -0.38966 |  | 23-03-2026 07:00 | 5.883 | 6.15 | 0.7 | 1.025 | 1.1055 | -0.080471 | 6.6328 | 0.7 | 1.0897 | -0.38966 |  | 23-03-2026 07:00 | 6.002 | 6.789 | 0.7 | 1.1315 | 1.1055 | 0.026029 | 6.6328 | 0.7 | 1.0897 | -0.38966 |  | 23-03-2026 07:00 | 4.206 | 4.681 | 0.5 | 0.78017 | 0.81887 | -0.038701 | 4.9132 | 0.5 | 0.80716 | -0.30716 |  | 23-03-2026 07:00 | 4.207 | 4.41 | 0.5 | 0.735 | 0.81887 | -0.083867 | 4.9132 | 0.5 | 0.80716 | -0.30716 |  | 23-03-2026 07:00 | 4.191 | 4.394 | 0.5 | 0.73233 | 0.81887 | -0.086534 | 4.9132 | 0.5 | 0.80716 | -0.30716 |  | 23-03-2026 07:00 | 4.271 | 4.739 | 0.5 | 0.78983 | 0.81887 | -0.029034 | 4.9132 | 0.5 | 0.80716 | -0.30716 |  | 23-03-2026 07:00 | 3.98 | 4.176 | 0.4 | 0.696 | 0.77905 | -0.083051 | 4.6743 | 0.4 | 0.76791 | -0.36791 |  | 23-03-2026 07:00 | 8.0048 | 8.4764 | -0.47157 | 50.8584 | 5.2 | 8.3552 | -3.1552 | 2.8048
[110 empty] | Total: - | 14044.5985 | 19190.4946 | -5145.8961 |  | 13666.5 | 18916.0706 | -5249.5706 | 378.0985
Sum:- | 42588 |  | 10745.919 |  | 55418.5 |  |  |  |  | 1768.4 | 2466.9855 | -698.5855 | 0.97062 |  | 10365.238 |  | 54557.5 |  |  |  |  | 1793.8 | 2466.9855 | -673.1855 | 0.98784 |  | 10728.588 |  | 55108 |  |  |  |  | 1761.4 | 2466.9855 | -705.5855 | 0.97479 |  | 10836.842 |  | 55633.5 |  |  |  |  | 1778.7 | 2466.9855 | -688.2855 | 0.98287 |  | 8068.627 |  | 41873.3 |  |  |  |  | 1336.5 | 1827.3967 | -490.8967 | 0.98229 |  | 8097.341 |  | 41537.7 |  |  |  |  | 1323 | 1827.3967 | -504.3967 | 0.98084 |  | 7980.968 |  | 41366.6 |  |  |  |  | 1319.2 | 1827.3967 | -508.1967 | 0.97654 |  | 7922.489 |  | 41720.7 |  |  |  |  | 1328.2 | 1827.3967 | -499.1967 | 0.96677 |  | 7527.614 |  | 39469.9 |  |  |  |  | 1257.3 | 1738.5416 | -481.2416 | 0.98189

## 24 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual | Inverter No. | Efficiency
24-03-2026 19:00 | 0 | 38.46 | 0 | 0 | 2122.9 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 24-03-2026 19:00 | 0 | 0 | 2135.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 2088.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 2113.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 1577.3 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 24-03-2026 19:00 | 0 | 0 | 1572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 1560.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 1570.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 1491.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24-03-2026 19:00 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | -0.2 | 1 | 98.85%
24-03-2026 18:50 | 0 | 39.89 | 0.762 | 0.801 | 2122.8 | 0.1335 | 0 | 0.1335 | 0 | 0.3 | 0 | 0.3 |  | 24-03-2026 18:50 | 0.876 | 1.268 | 2135.3 | 0.21133 | 0 | 0.21133 | 0 | 0.4 | 0 | 0.4 |  | 24-03-2026 18:50 | 0.811 | 0.853 | 2088.2 | 0.14217 | 0 | 0.14217 | 0 | 0.4 | 0 | 0.4 |  | 24-03-2026 18:50 | 0.811 | 1.146 | 2113.3 | 0.191 | 0 | 0.191 | 0 | 0.3 | 0 | 0.3 |  | 24-03-2026 18:50 | 0.394 | 0.535 | 1577.2 | 0.089167 | 0 | 0.089167 | 0 | 0.2 | 0 | 0.2 |  | 24-03-2026 18:50 | 0.431 | 0.453 | 1572 | 0.0755 | 0 | 0.0755 | 0 | 0.2 | 0 | 0.2 |  | 24-03-2026 18:50 | 0.374 | 0.393 | 1560.6 | 0.0655 | 0 | 0.0655 | 0 | 0.2 | 0 | 0.2 |  | 24-03-2026 18:50 | 0.513 | 0.777 | 1570.8 | 0.1295 | 0 | 0.1295 | 0 | 0.2 | 0 | 0.2 |  | 24-03-2026 18:50 | 0.349 | 0.367 | 1491.2 | 0.061167 | 0 | 0.061167 | 0 | 0.3 | 0 | 0.3 |  | 24-03-2026 18:50 | 1.0988 | 0 | 1.0988 | 0 | 2.5 | 0 | 2.5 | -1.4012 | 2 | 97.95%
24-03-2026 18:40 | 5 | 42.19 | 3.32 | 3.491 | 2122.5 | 0.58183 | 0.30523 | 0.2766 | 1.8314 | 0.9 | 0.30087 | 0.59913 |  | 24-03-2026 18:40 | 3.686 | 3.99 | 2134.9 | 0.665 | 0.30523 | 0.35977 | 1.8314 | 0.9 | 0.30087 | 0.59913 |  | 24-03-2026 18:40 | 3.419 | 3.595 | 2087.8 | 0.59917 | 0.30523 | 0.29393 | 1.8314 | 0.8 | 0.30087 | 0.49913 |  | 24-03-2026 18:40 | 3.525 | 3.888 | 2113 | 0.648 | 0.30523 | 0.34277 | 1.8314 | 0.9 | 0.30087 | 0.59913 |  | 24-03-2026 18:40 | 2.48 | 2.608 | 1577 | 0.43467 | 0.2261 | 0.20857 | 1.3566 | 0.6 | 0.22287 | 0.37713 |  | 24-03-2026 18:40 | 2.374 | 2.515 | 1571.8 | 0.41917 | 0.2261 | 0.19307 | 1.3566 | 0.6 | 0.22287 | 0.37713 |  | 24-03-2026 18:40 | 2.408 | 2.532 | 1560.4 | 0.422 | 0.2261 | 0.1959 | 1.3566 | 0.6 | 0.22287 | 0.37713 |  | 24-03-2026 18:40 | 2.508 | 2.686 | 1570.6 | 0.44767 | 0.2261 | 0.22157 | 1.3566 | 0.6 | 0.22287 | 0.37713 |  | 24-03-2026 18:40 | 2.269 | 2.386 | 1490.9 | 0.39767 | 0.21511 | 0.18256 | 1.2906 | 0.5 | 0.21203 | 0.28797 |  | 24-03-2026 18:40 | 4.6152 | 2.3404 | 2.2747 | 14.0427 | 6.4 | 2.307 | 4.093 | -1.7848 | 3 | 97.37%
24-03-2026 18:30 | 18 | 45.35 | 7.441 | 7.767 | 2121.6 | 1.2945 | 1.0859 | 0.20859 | 6.5155 | 1.8 | 1.0704 | 0.72961 |  | 24-03-2026 18:30 | 7.863 | 7.856 | 2134 | 1.3093 | 1.0859 | 0.22342 | 6.5155 | 1.9 | 1.0704 | 0.82961 |  | 24-03-2026 18:30 | 7.172 | 7.496 | 2087 | 1.2493 | 1.0859 | 0.16342 | 6.5155 | 1.9 | 1.0704 | 0.82961 |  | 24-03-2026 18:30 | 7.254 | 7.581 | 2112.1 | 1.2635 | 1.0859 | 0.17759 | 6.5155 | 1.9 | 1.0704 | 0.82961 |  | 24-03-2026 18:30 | 5.192 | 5.445 | 1576.4 | 0.9075 | 0.80438 | 0.10312 | 4.8263 | 1.4 | 0.79288 | 0.60712 |  | 24-03-2026 18:30 | 5.136 | 5.383 | 1571.2 | 0.89717 | 0.80438 | 0.092786 | 4.8263 | 1.4 | 0.79288 | 0.60712 |  | 24-03-2026 18:30 | 5.133 | 5.382 | 1559.8 | 0.897 | 0.80438 | 0.09262 | 4.8263 | 1.4 | 0.79288 | 0.60712 |  | 24-03-2026 18:30 | 5.199 | 5.532 | 1570 | 0.922 | 0.80438 | 0.11762 | 4.8263 | 1.4 | 0.79288 | 0.60712 |  | 24-03-2026 18:30 | 4.836 | 5.073 | 1490.4 | 0.8455 | 0.76527 | 0.080232 | 4.5916 | 1.3 | 0.75433 | 0.54567 |  | 24-03-2026 18:30 | 9.5858 | 8.3264 | 1.2594 | 49.9587 | 14.4 | 8.2074 | 6.1926 | -4.8142 | 4 | 98.41%
24-03-2026 18:20 | 49 | 47.64 | 18.767 | 19.254 | 2119.8 | 3.209 | 2.9306 | 0.27841 | 17.5835 | 4.5 | 2.8887 | 1.6113 |  | 24-03-2026 18:20 | 22.774 | 23.315 | 2132.1 | 3.8858 | 2.9306 | 0.95525 | 17.5835 | 4.6 | 2.8887 | 1.7113 |  | 24-03-2026 18:20 | 19.289 | 19.784 | 2085.1 | 3.2973 | 2.9306 | 0.36675 | 17.5835 | 4.5 | 2.8887 | 1.6113 |  | 24-03-2026 18:20 | 19.416 | 19.916 | 2110.2 | 3.3193 | 2.9306 | 0.38875 | 17.5835 | 4.6 | 2.8887 | 1.7113 |  | 24-03-2026 18:20 | 14.159 | 14.592 | 1575 | 2.432 | 2.1708 | 0.26119 | 13.0248 | 3.3 | 2.1398 | 1.1602 |  | 24-03-2026 18:20 | 13.916 | 14.345 | 1569.8 | 2.3908 | 2.1708 | 0.22003 | 13.0248 | 3.3 | 2.1398 | 1.1602 |  | 24-03-2026 18:20 | 13.68 | 14.11 | 1558.4 | 2.3517 | 2.1708 | 0.18086 | 13.0248 | 3.2 | 2.1398 | 1.0602 |  | 24-03-2026 18:20 | 12.94 | 13.538 | 1568.6 | 2.2563 | 2.1708 | 0.085527 | 13.0248 | 3.1 | 2.1398 | 0.96024 |  | 24-03-2026 18:20 | 12.574 | 13 | 1489.1 | 2.1667 | 2.0653 | 0.10141 | 12.3915 | 3 | 2.0357 | 0.96428 |  | 24-03-2026 18:20 | 25.309 | 22.4708 | 2.8382 | 134.825 | 34.1 | 22.1495 | 11.9505 | -8.791 | 5 | 98.2%
24-03-2026 18:10 | 92 | 49.65 | 40.043 | 40.495 | 2115.3 | 6.7492 | 5.4603 | 1.2889 | 32.7617 | 6.9 | 5.3822 | 1.5178 |  | 24-03-2026 18:10 | 40.222 | 40.934 | 2127.5 | 6.8223 | 5.4603 | 1.362 | 32.7617 | 6.9 | 5.3822 | 1.5178 |  | 24-03-2026 18:10 | 39.355 | 40.143 | 2080.6 | 6.6905 | 5.4603 | 1.2302 | 32.7617 | 6.8 | 5.3822 | 1.4178 |  | 24-03-2026 18:10 | 39.95 | 40.649 | 2105.6 | 6.7748 | 5.4603 | 1.3145 | 32.7617 | 6.8 | 5.3822 | 1.4178 |  | 24-03-2026 18:10 | 29.722 | 30.304 | 1571.7 | 5.0507 | 4.0447 | 1.006 | 24.2679 | 5.1 | 3.9868 | 1.1132 |  | 24-03-2026 18:10 | 28.789 | 29.362 | 1566.5 | 4.8937 | 4.0447 | 0.84901 | 24.2679 | 4.9 | 3.9868 | 0.91318 |  | 24-03-2026 18:10 | 28.553 | 29.124 | 1555.2 | 4.854 | 4.0447 | 0.80934 | 24.2679 | 4.9 | 3.9868 | 0.91318 |  | 24-03-2026 18:10 | 25.175 | 25.933 | 1565.5 | 4.3222 | 4.0447 | 0.27751 | 24.2679 | 4.6 | 3.9868 | 0.61318 |  | 24-03-2026 18:10 | 26.202 | 26.808 | 1486.1 | 4.468 | 3.848 | 0.62001 | 23.0879 | 4.6 | 3.793 | 0.80703 |  | 24-03-2026 18:10 | 50.6253 | 41.8678 | 8.7576 | 251.2067 | 51.5 | 41.2691 | 10.2309 | -0.87467 | 6 | 98.26%
24-03-2026 18:00 | 103 | 49.65 | 40.023 | 40.736 | 2108.4 | 6.7893 | 6.1131 | 0.67618 | 36.6789 | 7.6 | 6.0257 | 1.5743 |  | 24-03-2026 18:00 | 40.603 | 41.335 | 2120.6 | 6.8892 | 6.1131 | 0.77602 | 36.6789 | 7.7 | 6.0257 | 1.6743 |  | 24-03-2026 18:00 | 40.143 | 40.878 | 2073.8 | 6.813 | 6.1131 | 0.69985 | 36.6789 | 7.4 | 6.0257 | 1.3743 |  | 24-03-2026 18:00 | 40.331 | 41.058 | 2098.8 | 6.843 | 6.1131 | 0.72985 | 36.6789 | 7.3 | 6.0257 | 1.2743 |  | 24-03-2026 18:00 | 29.786 | 30.388 | 1566.6 | 5.0647 | 4.5283 | 0.53641 | 27.1696 | 5.4 | 4.4635 | 0.9365 |  | 24-03-2026 18:00 | 29.324 | 29.913 | 1561.6 | 4.9855 | 4.5283 | 0.45724 | 27.1696 | 5.2 | 4.4635 | 0.7365 |  | 24-03-2026 18:00 | 29.107 | 29.692 | 1550.3 | 4.9487 | 4.5283 | 0.42041 | 27.1696 | 5.3 | 4.4635 | 0.8365 |  | 24-03-2026 18:00 | 28.751 | 29.386 | 1560.9 | 4.8977 | 4.5283 | 0.36941 | 27.1696 | 5.1 | 4.4635 | 0.6365 |  | 24-03-2026 18:00 | 27.568 | 28.156 | 1481.5 | 4.6927 | 4.3081 | 0.38459 | 25.8485 | 4.9 | 4.2465 | 0.65353 |  | 24-03-2026 18:00 | 51.9237 | 46.8737 | 5.05 | 281.2423 | 55.9 | 46.2034 | 9.6966 | -3.9763 | 7 | 98.14%
24-03-2026 17:50 | 129 | 49.94 | 45.4 | 46.148 | 2100.8 | 7.6913 | 7.6478 | 0.043564 | 45.8866 | 5.4 | 7.5384 | -2.1384 |  | 24-03-2026 17:50 | 39.217 | 43.561 | 2112.9 | 7.2602 | 7.6478 | -0.3876 | 45.8866 | 5.3 | 7.5384 | -2.2384 |  | 24-03-2026 17:50 | 43.896 | 44.651 | 2066.4 | 7.4418 | 7.6478 | -0.20594 | 45.8866 | 5.5 | 7.5384 | -2.0384 |  | 24-03-2026 17:50 | 44.362 | 45.125 | 2091.5 | 7.5208 | 7.6478 | -0.12694 | 45.8866 | 5.6 | 7.5384 | -1.9384 |  | 24-03-2026 17:50 | 32.57 | 33.184 | 1561.2 | 5.5307 | 5.665 | -0.13435 | 33.9901 | 4.1 | 5.584 | -1.484 |  | 24-03-2026 17:50 | 31.978 | 32.571 | 1556.4 | 5.4285 | 5.665 | -0.23651 | 33.9901 | 4.1 | 5.584 | -1.484 |  | 24-03-2026 17:50 | 31.274 | 31.863 | 1545 | 5.3105 | 5.665 | -0.35451 | 33.9901 | 4 | 5.584 | -1.584 |  | 24-03-2026 17:50 | 31.098 | 31.991 | 1555.8 | 5.3318 | 5.665 | -0.33318 | 33.9901 | 4.1 | 5.584 | -1.484 |  | 24-03-2026 17:50 | 29.645 | 30.165 | 1476.6 | 5.0275 | 5.3896 | -0.36206 | 32.3374 | 3.9 | 5.3125 | -1.4125 |  | 24-03-2026 17:50 | 56.5432 | 58.6407 | -2.0975 | 351.8442 | 42 | 57.8021 | -15.8021 | 14.5432 | 8 | 97.04%
24-03-2026 17:40 | 104 | 49.94 | 0 | 0 | 2095.4 | 0 | 6.1656 | -6.1656 | 36.9939 | 0.1 | 6.0775 | -5.9775 |  | 24-03-2026 17:40 | 0 | 0 | 2107.6 | 0 | 6.1656 | -6.1656 | 36.9939 | 0.3 | 6.0775 | -5.7775 |  | 24-03-2026 17:40 | 0 | 0 | 2060.9 | 0 | 6.1656 | -6.1656 | 36.9939 | 0.1 | 6.0775 | -5.9775 |  | 24-03-2026 17:40 | 0 | 0 | 2085.9 | 0 | 6.1656 | -6.1656 | 36.9939 | 0 | 6.0775 | -6.0775 |  | 24-03-2026 17:40 | 0 | 0 | 1557.1 | 0 | 4.5671 | -4.5671 | 27.4029 | 0 | 4.5018 | -4.5018 |  | 24-03-2026 17:40 | 0 | 0 | 1552.3 | 0 | 4.5671 | -4.5671 | 27.4029 | 0 | 4.5018 | -4.5018 |  | 24-03-2026 17:40 | 0 | 0 | 1541 | 0 | 4.5671 | -4.5671 | 27.4029 | 0 | 4.5018 | -4.5018 |  | 24-03-2026 17:40 | 0 | 0 | 1551.7 | 0 | 4.5671 | -4.5671 | 27.4029 | 0.1 | 4.5018 | -4.4018 |  | 24-03-2026 17:40 | 0 | 0 | 1472.7 | 0 | 4.3451 | -4.3451 | 26.0704 | 0 | 4.2829 | -4.2829 |  | 24-03-2026 17:40 | 0 | 47.2762 | -47.2762 | 283.6573 | 0.6 | 46.6002 | -46.0002 | -0.6 | 9 | 98.52%
24-03-2026 17:30 | 255 | 49.36 | 86.608 | 87.731 | 2095.3 | 14.6218 | 15.1513 | -0.52947 | 90.9078 | 16.7 | 14.9346 | 1.7654 |  | 24-03-2026 17:30 | 85.857 | 87.005 | 2107.3 | 14.5008 | 15.1513 | -0.65047 | 90.9078 | 16.4 | 14.9346 | 1.4654 |  | 24-03-2026 17:30 | 87.233 | 88.721 | 2060.8 | 14.7868 | 15.1513 | -0.36447 | 90.9078 | 16.5 | 14.9346 | 1.5654 |  | 24-03-2026 17:30 | 87.35 | 88.501 | 2085.9 | 14.7502 | 15.1513 | -0.40114 | 90.9078 | 16.5 | 14.9346 | 1.5654 |  | 24-03-2026 17:30 | 0 | 0 | 1557.1 | 0 | 11.2232 | -11.2232 | 67.3391 | 12.4 | 11.0627 | 1.3373 |  | 24-03-2026 17:30 | 0 | 0 | 1552.3 | 0 | 11.2232 | -11.2232 | 67.3391 | 12.4 | 11.0627 | 1.3373 |  | 24-03-2026 17:30 | 63.63 | 0 | 1541 | 0 | 11.2232 | -11.2232 | 67.3391 | 12.3 | 11.0627 | 1.2373 |  | 24-03-2026 17:30 | 63.711 | 65.444 | 1551.6 | 10.9073 | 11.2232 | -0.31586 | 67.3391 | 12.2 | 11.0627 | 1.1373 |  | 24-03-2026 17:30 | 60.021 | 60.879 | 1472.7 | 10.1465 | 10.6775 | -0.53098 | 64.0649 | 11.5 | 10.5248 | 0.97521 |  | 24-03-2026 17:30 | 79.7135 | 116.1755 | -36.462 | 697.0528 | 126.9 | 114.5142 | 12.3858 | -47.1865
24-03-2026 17:20 | 241 | 49.65 | 92.537 | 86.932 | 2078.6 | 14.4887 | 14.3036 | 0.18508 | 85.8215 | 18.9 | 14.099 | 4.801 |  | 24-03-2026 17:20 | 85.813 | 86.987 | 2090.9 | 14.4978 | 14.3036 | 0.19425 | 85.8215 | 31.9 | 14.099 | 17.801 |  | 24-03-2026 17:20 | 84.066 | 85.301 | 2044.3 | 14.2168 | 14.3036 | -0.086749 | 85.8215 | 19 | 14.099 | 4.901 |  | 24-03-2026 17:20 | 85.041 | 86.187 | 2069.4 | 14.3645 | 14.3036 | 0.060918 | 85.8215 | 19.1 | 14.099 | 5.001 |  | 24-03-2026 17:20 | 63.812 | 64.169 | 1544.7 | 10.6948 | 10.5952 | 0.099587 | 63.5715 | 14.3 | 10.4437 | 3.8563 |  | 24-03-2026 17:20 | 63.37 | 63.886 | 1539.9 | 10.6477 | 10.5952 | 0.05242 | 63.5715 | 13.7 | 10.4437 | 3.2563 |  | 24-03-2026 17:20 | 62.588 | 63.483 | 1528.7 | 10.5805 | 10.5952 | -0.014746 | 63.5715 | 13.8 | 10.4437 | 3.3563 |  | 24-03-2026 17:20 | 62.579 | 64.556 | 1539.4 | 10.7593 | 10.5952 | 0.16409 | 63.5715 | 14 | 10.4437 | 3.5563 |  | 24-03-2026 17:20 | 59.08 | 60.04 | 1461.2 | 10.0067 | 10.0801 | -0.073398 | 60.4804 | 13.3 | 9.9359 | 3.3641 |  | 24-03-2026 17:20 | 110.2568 | 109.6754 | 0.58145 | 658.0523 | 158 | 108.107 | 49.893 | -47.7432
24-03-2026 17:10 | 301 | 49.65 | 105.985 | 107.272 | 2059.7 | 17.8787 | 17.8646 | 0.014026 | 107.1878 | 12.6 | 17.6092 | -5.0092 | [5 empty] | 0 | 17.8646 | -17.8646 | 107.1878 | 0 | 17.6092 | -17.6092 |  | 24-03-2026 17:10 | 106.847 | 108.571 | 2025.3 | 18.0952 | 17.8646 | 0.23053 | 107.1878 | 12.6 | 17.6092 | -5.0092 |  | 24-03-2026 17:10 | 106.731 | 108.082 | 2050.3 | 18.0137 | 17.8646 | 0.14903 | 107.1878 | 12.6 | 17.6092 | -5.0092 |  | 24-03-2026 17:10 | 80.8 | 81.873 | 1530.4 | 13.6455 | 13.2331 | 0.41243 | 79.3984 | 9.6 | 13.0438 | -3.4438 |  | 24-03-2026 17:10 | 78.968 | 80 | 1526.2 | 13.3333 | 13.2331 | 0.10027 | 79.3984 | 9.4 | 13.0438 | -3.6438 |  | 24-03-2026 17:10 | 79.581 | 80.605 | 1514.9 | 13.4342 | 13.2331 | 0.2011 | 79.3984 | 9.4 | 13.0438 | -3.6438 |  | 24-03-2026 17:10 | 78.966 | 81.084 | 1525.4 | 13.514 | 13.2331 | 0.28093 | 79.3984 | 9.3 | 13.0438 | -3.7438 |  | 24-03-2026 17:10 | 74.064 | 75.055 | 1447.9 | 12.5092 | 12.5896 | -0.080458 | 75.5377 | 8.7 | 12.4096 | -3.7096 |  | 24-03-2026 17:10 | 120.4237 | 136.9805 | -16.5568 | 821.8827 | 84.2 | 135.0216 | -50.8216 | 36.2237
24-03-2026 17:00 | 222 | 49.94 | 80.133 | 81.205 | 2047.1 | 13.5342 | 13.1613 | 0.37289 | 78.9677 | 15.2 | 12.9731 | 2.2269 |  | 24-03-2026 17:00 | 80.94 | 81.823 | 2059 | 13.6372 | 13.1613 | 0.47589 | 78.9677 | 15.7 | 12.9731 | 2.7269 |  | 24-03-2026 17:00 | 79.615 | 81.294 | 2012.7 | 13.549 | 13.1613 | 0.38772 | 78.9677 | 14.7 | 12.9731 | 1.7269 |  | 24-03-2026 17:00 | 79.951 | 81.07 | 2037.7 | 13.5117 | 13.1613 | 0.35039 | 78.9677 | 14.9 | 12.9731 | 1.9269 |  | 24-03-2026 17:00 | 59.273 | 60.176 | 1520.8 | 10.0293 | 9.7491 | 0.28024 | 58.4946 | 10.8 | 9.6097 | 1.1903 |  | 24-03-2026 17:00 | 58.647 | 59.552 | 1516.8 | 9.9253 | 9.7491 | 0.17624 | 58.4946 | 10.8 | 9.6097 | 1.1903 |  | 24-03-2026 17:00 | 58.388 | 59.301 | 1505.5 | 9.8835 | 9.7491 | 0.13441 | 58.4946 | 10.8 | 9.6097 | 1.1903 |  | 24-03-2026 17:00 | 58.486 | 60.393 | 1516.1 | 10.0655 | 9.7491 | 0.31641 | 58.4946 | 10.7 | 9.6097 | 1.0903 |  | 24-03-2026 17:00 | 55.458 | 56.348 | 1439.2 | 9.3913 | 9.2751 | 0.11628 | 55.6503 | 10.3 | 9.1424 | 1.1576 |  | 24-03-2026 17:00 | 103.527 | 100.9165 | 2.6105 | 605.4993 | 113.9 | 99.4734 | 14.4266 | -10.373
24-03-2026 16:50 | 270 | 49.65 | 91.374 | 93.728 | 2031.9 | 15.6213 | 16.0248 | -0.40343 | 96.1486 | 31 | 15.7956 | 15.2044 |  | 24-03-2026 16:50 | 90.362 | 91.483 | 2043.3 | 15.2472 | 16.0248 | -0.77759 | 96.1486 | 13.2 | 15.7956 | -2.5956 |  | 24-03-2026 16:50 | 94.376 | 96.309 | 1998 | 16.0515 | 16.0248 | 0.02674 | 96.1486 | 13 | 15.7956 | -2.7956 |  | 24-03-2026 16:50 | 97.376 | 98.659 | 2022.8 | 16.4432 | 16.0248 | 0.41841 | 96.1486 | 13.2 | 15.7956 | -2.5956 |  | 24-03-2026 16:50 | 70.939 | 71.924 | 1510 | 11.9873 | 11.8702 | 0.11714 | 71.2212 | 9.7 | 11.7004 | -2.0004 |  | 24-03-2026 16:50 | 71.988 | 72.988 | 1506 | 12.1647 | 11.8702 | 0.29447 | 71.2212 | 9.8 | 11.7004 | -1.9004 |  | 24-03-2026 16:50 | 69.052 | 70.025 | 1494.7 | 11.6708 | 11.8702 | -0.19936 | 71.2212 | 9.4 | 11.7004 | -2.3004 |  | 24-03-2026 16:50 | 70.194 | 72.577 | 1505.4 | 12.0962 | 11.8702 | 0.22597 | 71.2212 | 9.5 | 11.7004 | -2.2004 |  | 24-03-2026 16:50 | 67.692 | 68.66 | 1428.9 | 11.4433 | 11.293 | 0.15031 | 67.7581 | 9 | 11.1315 | -2.1315 |  | 24-03-2026 16:50 | 122.7255 | 122.8728 | -0.14733 | 737.237 | 117.8 | 121.1158 | -3.3158 | 4.9255
24-03-2026 16:40 | 239 | 50.23 | 85.177 | 85.507 | 2018.7 | 14.2512 | 14.1534 | 0.0978 | 84.9202 | 0 | 13.951 | -13.951 |  | 24-03-2026 16:40 | 85.263 | 86.456 | 2030.1 | 14.4093 | 14.1534 | 0.25597 | 84.9202 | 18.2 | 13.951 | 4.249 |  | 24-03-2026 16:40 | 81.634 | 83.21 | 1985 | 13.8683 | 14.1534 | -0.28503 | 84.9202 | 17.9 | 13.951 | 3.949 |  | 24-03-2026 16:40 | 83.041 | 84.22 | 2009.6 | 14.0367 | 14.1534 | -0.1167 | 84.9202 | 18 | 13.951 | 4.049 |  | 24-03-2026 16:40 | 59.554 | 60.485 | 1500.3 | 10.0808 | 10.484 | -0.40314 | 62.9039 | 13.3 | 10.3341 | 2.9659 |  | 24-03-2026 16:40 | 60.572 | 61.469 | 1496.2 | 10.2448 | 10.484 | -0.23914 | 62.9039 | 13.1 | 10.3341 | 2.7659 |  | 24-03-2026 16:40 | 58.681 | 59.617 | 1485.3 | 9.9362 | 10.484 | -0.54781 | 62.9039 | 13 | 10.3341 | 2.6659 |  | 24-03-2026 16:40 | 59.11 | 60.931 | 1495.9 | 10.1552 | 10.484 | -0.32881 | 62.9039 | 13 | 10.3341 | 2.6659 |  | 24-03-2026 16:40 | 56.732 | 57.643 | 1419.9 | 9.6072 | 9.9742 | -0.36704 | 59.8452 | 12.4 | 9.8316 | 2.5684 |  | 24-03-2026 16:40 | 106.5897 | 108.5236 | -1.9339 | 651.1414 | 118.9 | 106.9717 | 11.9283 | -12.3103
24-03-2026 16:30 | 358 | 51.09 | 127.681 | 129.428 | 2000.9 | 21.5713 | 21.1304 | 0.44089 | 126.7827 | 34.4 | 20.8283 | 13.5717 |  | 24-03-2026 16:30 | 154.775 | 154.381 | 2011.9 | 25.7302 | 21.1304 | 4.5997 | 126.7827 | 33.9 | 20.8283 | 13.0717 |  | 24-03-2026 16:30 | 124.953 | 128.314 | 1967.1 | 21.3857 | 21.1304 | 0.25522 | 126.7827 | 33.5 | 20.8283 | 12.6717 |  | 24-03-2026 16:30 | 123.523 | 124.978 | 1991.6 | 20.8297 | 21.1304 | -0.30078 | 126.7827 | 33.9 | 20.8283 | 13.0717 |  | 24-03-2026 16:30 | 101.325 | 103.16 | 1487 | 17.1933 | 15.6522 | 1.5412 | 93.9131 | 24.9 | 15.4284 | 9.4716 |  | 24-03-2026 16:30 | 93.806 | 95.492 | 1483.1 | 15.9153 | 15.6522 | 0.26315 | 93.9131 | 24.8 | 15.4284 | 9.3716 |  | 24-03-2026 16:30 | 105.924 | 107.546 | 1472.3 | 17.9243 | 15.6522 | 2.2722 | 93.9131 | 24.6 | 15.4284 | 9.1716 |  | 24-03-2026 16:30 | 104.168 | 107.524 | 1482.9 | 17.9207 | 15.6522 | 2.2685 | 93.9131 | 24.6 | 15.4284 | 9.1716 |  | 24-03-2026 16:30 | 87.531 | 88.959 | 1407.5 | 14.8265 | 14.8911 | -0.064613 | 89.3467 | 23.8 | 14.6782 | 9.1218 |  | 24-03-2026 16:30 | 173.297 | 162.0216 | 11.2754 | 972.1297 | 258.4 | 159.7047 | 98.6953 | -85.103
24-03-2026 16:20 | 641 | 51.09 | 214.588 | 221.126 | 1966.5 | 36.8543 | 37.8341 | -0.97979 | 227.0047 | 33.1 | 37.2931 | -4.1931 |  | 24-03-2026 16:20 | 220.194 | 223.388 | 1978 | 37.2313 | 37.8341 | -0.60279 | 227.0047 | 34.5 | 37.2931 | -2.7931 |  | 24-03-2026 16:20 | 219.928 | 225.093 | 1933.6 | 37.5155 | 37.8341 | -0.31862 | 227.0047 | 33.3 | 37.2931 | -3.9931 |  | 24-03-2026 16:20 | 221.962 | 225.159 | 1957.7 | 37.5265 | 37.8341 | -0.30762 | 227.0047 | 33.6 | 37.2931 | -3.6931 |  | 24-03-2026 16:20 | 165.989 | 168.261 | 1462.1 | 28.0435 | 28.0253 | 0.018224 | 168.1517 | 25.1 | 27.6245 | -2.5245 |  | 24-03-2026 16:20 | 163.281 | 165.53 | 1458.3 | 27.5883 | 28.0253 | -0.43694 | 168.1517 | 24.7 | 27.6245 | -2.9245 |  | 24-03-2026 16:20 | 163.554 | 166.069 | 1447.7 | 27.6782 | 28.0253 | -0.34711 | 168.1517 | 24.6 | 27.6245 | -3.0245 |  | 24-03-2026 16:20 | 162.104 | 165.778 | 1458.3 | 27.6297 | 28.0253 | -0.39561 | 168.1517 | 24.7 | 27.6245 | -2.9245 |  | 24-03-2026 16:20 | 155.006 | 157.111 | 1383.7 | 26.1852 | 26.6626 | -0.47741 | 159.9755 | 23.4 | 26.2813 | -2.8813 |  | 24-03-2026 16:20 | 286.2525 | 290.1002 | -3.8477 | 1740.601 | 257 | 285.9517 | -28.9517 | 29.2525
24-03-2026 16:10 | 665 | 50.8 | 233.726 | 237.069 | 1933.4 | 39.5115 | 39.2945 | 0.21697 | 235.7672 | 27 | 38.7326 | -11.7326 |  | 24-03-2026 16:10 | 229.968 | 233.281 | 1943.5 | 38.8802 | 39.2945 | -0.41436 | 235.7672 | 26.7 | 38.7326 | -12.0326 |  | 24-03-2026 16:10 | 230.931 | 235.62 | 1900.3 | 39.27 | 39.2945 | -0.024531 | 235.7672 | 27.1 | 38.7326 | -11.6326 |  | 24-03-2026 16:10 | 233.297 | 236.706 | 1924.1 | 39.451 | 39.2945 | 0.15647 | 235.7672 | 27.1 | 38.7326 | -11.6326 |  | 24-03-2026 16:10 | 172 | 174.336 | 1437 | 29.056 | 29.1071 | -0.05106 | 174.6424 | 20.5 | 28.6908 | -8.1908 |  | 24-03-2026 16:10 | 170.714 | 173.033 | 1433.6 | 28.8388 | 29.1071 | -0.26823 | 174.6424 | 20.2 | 28.6908 | -8.4908 |  | 24-03-2026 16:10 | 169.009 | 171.304 | 1423.1 | 28.5507 | 29.1071 | -0.55639 | 174.6424 | 20.3 | 28.6908 | -8.3908 |  | 24-03-2026 16:10 | 170.158 | 174.675 | 1433.6 | 29.1125 | 29.1071 | 0.0054398 | 174.6424 | 20.5 | 28.6908 | -8.1908 |  | 24-03-2026 16:10 | 162.95 | 165.163 | 1360.3 | 27.5272 | 27.6918 | -0.1646 | 166.1506 | 19 | 27.2958 | -8.2958 |  | 24-03-2026 16:10 | 300.1978 | 301.2981 | -1.1003 | 1807.7888 | 208.4 | 296.9896 | -88.5896 | 91.7978
24-03-2026 16:00 | 266 | 50.23 | 91.798 | 92.998 | 1906.4 | 15.4997 | 15.7523 | -0.25262 | 94.5137 | 15.1 | 15.527 | -0.42702 |  | 24-03-2026 16:00 | 91.744 | 93.859 | 1916.8 | 15.6432 | 15.7523 | -0.10912 | 94.5137 | 14.6 | 15.527 | -0.92702 |  | 24-03-2026 16:00 | 94.982 | 96.715 | 1873.2 | 16.1192 | 15.7523 | 0.36688 | 94.5137 | 14.6 | 15.527 | -0.92702 |  | 24-03-2026 16:00 | 94.715 | 95.982 | 1897 | 15.997 | 15.7523 | 0.24472 | 94.5137 | 14.7 | 15.527 | -0.82702 |  | 24-03-2026 16:00 | 72.009 | 72.789 | 1416.5 | 12.1315 | 11.6684 | 0.46314 | 70.0101 | 11 | 11.5015 | -0.5015 |  | 24-03-2026 16:00 | 70.497 | 71.498 | 1413.4 | 11.9163 | 11.6684 | 0.24798 | 70.0101 | 10.7 | 11.5015 | -0.8015 |  | 24-03-2026 16:00 | 71.477 | 72.255 | 1402.8 | 12.0425 | 11.6684 | 0.37414 | 70.0101 | 10.9 | 11.5015 | -0.6015 |  | 24-03-2026 16:00 | 71.443 | 73.548 | 1413.1 | 12.258 | 11.6684 | 0.58964 | 70.0101 | 10.8 | 11.5015 | -0.7015 |  | 24-03-2026 16:00 | 66.274 | 67.229 | 1341.3 | 11.2048 | 11.101 | 0.10384 | 66.606 | 10 | 10.9423 | -0.94225 |  | 24-03-2026 16:00 | 122.8122 | 120.7836 | 2.0286 | 724.7013 | 112.4 | 119.0563 | -6.6563 | 10.4122
24-03-2026 15:50 | 284 | 50.8 | 123.322 | 124.997 | 1891.3 | 20.8328 | 16.7814 | 4.0514 | 100.6885 | 35.6 | 16.5414 | 19.0586 |  | 24-03-2026 15:50 | 100.359 | 100.508 | 1902.2 | 16.7513 | 16.7814 | -0.030091 | 100.6885 | 34.4 | 16.5414 | 17.8586 |  | 24-03-2026 15:50 | 96.168 | 97.782 | 1858.6 | 16.297 | 16.7814 | -0.48442 | 100.6885 | 32.6 | 16.5414 | 16.0586 |  | 24-03-2026 15:50 | 97.083 | 98.572 | 1882.3 | 16.4287 | 16.7814 | -0.35276 | 100.6885 | 33.5 | 16.5414 | 16.9586 |  | 24-03-2026 15:50 | 71.604 | 72.65 | 1405.5 | 12.1083 | 12.4307 | -0.32235 | 74.5841 | 23.3 | 12.2529 | 11.0471 |  | 24-03-2026 15:50 | 70.6 | 71.745 | 1402.7 | 11.9575 | 12.4307 | -0.47318 | 74.5841 | 23.4 | 12.2529 | 11.1471 |  | 24-03-2026 15:50 | 70.022 | 71.052 | 1391.9 | 11.842 | 12.4307 | -0.58868 | 74.5841 | 22 | 12.2529 | 9.7471 |  | 24-03-2026 15:50 | 69.885 | 71.668 | 1402.3 | 11.9447 | 12.4307 | -0.48602 | 74.5841 | 21.5 | 12.2529 | 9.2471 |  | 24-03-2026 15:50 | 66.202 | 67.176 | 1331.3 | 11.196 | 11.8263 | -0.63026 | 70.9575 | 21.3 | 11.6571 | 9.6429 |  | 24-03-2026 15:50 | 129.3583 | 128.6747 | 0.68364 | 772.0481 | 247.6 | 126.8346 | 120.7654 | -118.2417
24-03-2026 15:40 | 750 | 49.65 | 273.265 | 277.229 | 1855.7 | 46.2048 | 44.5132 | 1.6916 | 267.0793 | 16.7 | 43.8767 | -27.1767 |  | 24-03-2026 15:40 | 233.403 | 277.912 | 1867.8 | 46.3187 | 44.5132 | 1.8054 | 267.0793 | 16.2 | 43.8767 | -27.6767 |  | 24-03-2026 15:40 | 277.046 | 283.804 | 1826 | 47.3007 | 44.5132 | 2.7874 | 267.0793 | 17.4 | 43.8767 | -26.4767 |  | 24-03-2026 15:40 | 254.394 | 257.954 | 1848.8 | 42.9923 | 44.5132 | -1.5209 | 267.0793 | 15.1 | 43.8767 | -28.7767 |  | 24-03-2026 15:40 | 208.436 | 211.267 | 1382.2 | 35.2112 | 32.9728 | 2.2384 | 197.8365 | 12.7 | 32.5012 | -19.8012 |  | 24-03-2026 15:40 | 188.571 | 191.626 | 1379.3 | 31.9377 | 32.9728 | -1.0351 | 197.8365 | 11.5 | 32.5012 | -21.0012 |  | 24-03-2026 15:40 | 204.471 | 207.681 | 1369.9 | 34.6135 | 32.9728 | 1.6407 | 197.8365 | 12.3 | 32.5012 | -20.2012 |  | 24-03-2026 15:40 | 200.475 | 206.64 | 1380.8 | 34.44 | 32.9728 | 1.4672 | 197.8365 | 11.6 | 32.5012 | -20.9012 |  | 24-03-2026 15:40 | 162.692 | 166.281 | 1310 | 27.7135 | 31.3695 | -3.656 | 188.217 | 10.5 | 30.9209 | -20.4209 |  | 24-03-2026 15:40 | 346.7323 | 341.3134 | 5.4189 | 2047.8805 | 124 | 336.4326 | -212.4326 | 222.7323
24-03-2026 15:30 | 248 | 49.65 | 89.619 | 90.827 | 1839 | 15.1378 | 14.719 | 0.41879 | 88.3142 | 13.8 | 14.5086 | -0.70856 |  | 24-03-2026 15:30 | 89.655 | 90.882 | 1851.6 | 15.147 | 14.719 | 0.42796 | 88.3142 | 14.1 | 14.5086 | -0.40856 |  | 24-03-2026 15:30 | 88.298 | 90.053 | 1808.6 | 15.0088 | 14.719 | 0.28979 | 88.3142 | 13.6 | 14.5086 | -0.90856 |  | 24-03-2026 15:30 | 88.172 | 89.388 | 1833.7 | 14.898 | 14.719 | 0.17896 | 88.3142 | 13.6 | 14.5086 | -0.90856 |  | 24-03-2026 15:30 | 65.871 | 66.82 | 1369.5 | 11.1367 | 10.903 | 0.23367 | 65.418 | 10.2 | 10.7471 | -0.54708 |  | 24-03-2026 15:30 | 64.562 | 65.505 | 1367.8 | 10.9175 | 10.903 | 0.014508 | 65.418 | 10 | 10.7471 | -0.74708 |  | 24-03-2026 15:30 | 64.591 | 65.521 | 1357.6 | 10.9202 | 10.903 | 0.017175 | 65.418 | 10 | 10.7471 | -0.74708 |  | 24-03-2026 15:30 | 64.408 | 66.279 | 1369.2 | 11.0465 | 10.903 | 0.14351 | 65.418 | 10 | 10.7471 | -0.74708 |  | 24-03-2026 15:30 | 60.834 | 61.735 | 1299.5 | 10.2892 | 10.3728 | -0.08368 | 62.2371 | 9.3 | 10.2245 | -0.92451 |  | 24-03-2026 15:30 | 114.5017 | 112.861 | 1.6407 | 677.1658 | 104.6 | 111.2471 | -6.6471 | 9.9017
24-03-2026 15:20 | 228 | 50.8 | 78.447 | 80.367 | 1825.2 | 13.3945 | 13.4724 | -0.077911 | 80.8345 | 27.2 | 13.2798 | 13.9202 |  | 24-03-2026 15:20 | 77.359 | 78.521 | 1837.5 | 13.0868 | 13.4724 | -0.38558 | 80.8345 | 28.2 | 13.2798 | 14.9202 |  | 24-03-2026 15:20 | 77.756 | 79.07 | 1795 | 13.1783 | 13.4724 | -0.29408 | 80.8345 | 26.2 | 13.2798 | 12.9202 |  | 24-03-2026 15:20 | 78.213 | 79.388 | 1820.1 | 13.2313 | 13.4724 | -0.24108 | 80.8345 | 28.5 | 13.2798 | 15.2202 |  | 24-03-2026 15:20 | 57.348 | 58.316 | 1359.3 | 9.7193 | 9.9796 | -0.26023 | 59.8774 | 19.7 | 9.8369 | 9.8631 |  | 24-03-2026 15:20 | 56.809 | 57.768 | 1357.8 | 9.628 | 9.9796 | -0.35156 | 59.8774 | 20.4 | 9.8369 | 10.5631 |  | 24-03-2026 15:20 | 56.366 | 57.323 | 1347.6 | 9.5538 | 9.9796 | -0.42573 | 59.8774 | 19.2 | 9.8369 | 9.3631 |  | 24-03-2026 15:20 | 56.351 | 58.255 | 1359.2 | 9.7092 | 9.9796 | -0.2704 | 59.8774 | 19.5 | 9.8369 | 9.6631 |  | 24-03-2026 15:20 | 53.579 | 54.511 | 1290.2 | 9.0852 | 9.4943 | -0.40915 | 56.9659 | 19.4 | 9.3585 | 10.0415 |  | 24-03-2026 15:20 | 100.5865 | 103.3022 | -2.7157 | 619.8133 | 208.3 | 101.825 | 106.475 | -107.7135
24-03-2026 15:10 | 650 | 50.8 | 220.826 | 225.093 | 1798 | 37.5155 | 38.4082 | -0.89269 | 230.4491 | 40.6 | 37.859 | 2.741 |  | 24-03-2026 15:10 | 222.82 | 226.167 | 1809.3 | 37.6945 | 38.4082 | -0.71369 | 230.4491 | 39.2 | 37.859 | 1.341 |  | 24-03-2026 15:10 | 224.017 | 230.348 | 1768.8 | 38.3913 | 38.4082 | -0.016855 | 230.4491 | 38 | 37.859 | 0.14105 |  | 24-03-2026 15:10 | 223.742 | 227.103 | 1791.6 | 37.8505 | 38.4082 | -0.55769 | 230.4491 | 37.1 | 37.859 | -0.75895 |  | 24-03-2026 15:10 | 172.733 | 174.973 | 1339.6 | 29.1622 | 28.4505 | 0.71166 | 170.7031 | 26.7 | 28.0437 | -1.3437 |  | 24-03-2026 15:10 | 169.558 | 172.83 | 1337.4 | 28.805 | 28.4505 | 0.35449 | 170.7031 | 26.9 | 28.0437 | -1.1437 |  | 24-03-2026 15:10 | 170.78 | 173.205 | 1328.4 | 28.8675 | 28.4505 | 0.41699 | 170.7031 | 26.4 | 28.0437 | -1.6437 |  | 24-03-2026 15:10 | 170.656 | 175.051 | 1339.7 | 29.1752 | 28.4505 | 0.72466 | 170.7031 | 26.5 | 28.0437 | -1.5437 |  | 24-03-2026 15:10 | 162.338 | 164.626 | 1270.8 | 27.4377 | 27.0671 | 0.37053 | 162.4028 | 25.9 | 26.6801 | -0.78008 |  | 24-03-2026 15:10 | 294.8993 | 294.5019 | 0.3974 | 1767.0116 | 287.3 | 290.2906 | -2.9906 | 7.5993
24-03-2026 15:00 | 683 | 51.09 | 246.817 | 237.54 | 1757.4 | 39.59 | 40.3131 | -0.72311 | 241.8787 | 33.7 | 39.7366 | -6.0366 | 1.0391 | 24-03-2026 15:00 | 237.719 | 241.388 | 1770.1 | 40.2313 | 40.3131 | -0.08178 | 241.8787 | 33.8 | 39.7366 | -5.9366 | 0.9848 | 24-03-2026 15:00 | 235.228 | 241.118 | 1730.8 | 40.1863 | 40.3131 | -0.12678 | 241.8787 | 32 | 39.7366 | -7.7366 | 0.97557 | 24-03-2026 15:00 | 234.671 | 238.293 | 1754.5 | 39.7155 | 40.3131 | -0.59761 | 241.8787 | 32.9 | 39.7366 | -6.8366 | 0.9848 | 24-03-2026 15:00 | 176.32 | 178.86 | 1312.9 | 29.81 | 29.8616 | -0.051565 | 179.1694 | 24.6 | 29.4345 | -4.8345 | 0.9858 | 24-03-2026 15:00 | 173.825 | 176.477 | 1310.5 | 29.4128 | 29.8616 | -0.44873 | 179.1694 | 24.4 | 29.4345 | -5.0345 | 0.98497 | 24-03-2026 15:00 | 174.311 | 177.142 | 1302 | 29.5237 | 29.8616 | -0.3379 | 179.1694 | 24.3 | 29.4345 | -5.1345 | 0.98402 | 24-03-2026 15:00 | 173.823 | 180.537 | 1313.2 | 30.0895 | 29.8616 | 0.22793 | 179.1694 | 24.5 | 29.4345 | -4.9345 | 0.96281 | 24-03-2026 15:00 | 165.033 | 167.342 | 1244.9 | 27.8903 | 28.4096 | -0.51925 | 170.4575 | 22.9 | 28.0033 | -5.1033 | 0.9862 | 24-03-2026 15:00 | 306.4495 | 309.1083 | -2.6588 | 1854.6498 | 253.1 | 304.688 | -51.588 | 53.3495
24-03-2026 14:50 | 814 | 51.09 | 289.237 | 295.051 | 1723.7 | 49.1752 | 48.0452 | 1.13 | 288.2712 | 39.1 | 47.3582 | -8.2582 | 0.98029 | 24-03-2026 14:50 | 290.013 | 294.819 | 1736.3 | 49.1365 | 48.0452 | 1.0913 | 288.2712 | 41.1 | 47.3582 | -6.2582 | 0.9837 | 24-03-2026 14:50 | 269.519 | 276.232 | 1698.8 | 46.0387 | 48.0452 | -2.0065 | 288.2712 | 40.7 | 47.3582 | -6.6582 | 0.9757 | 24-03-2026 14:50 | 274.14 | 278.654 | 1721.6 | 46.4423 | 48.0452 | -1.6029 | 288.2712 | 41.6 | 47.3582 | -5.7582 | 0.9838 | 24-03-2026 14:50 | 200.426 | 203.437 | 1288.3 | 33.9062 | 35.589 | -1.6829 | 213.5342 | 31 | 35.0801 | -4.0801 | 0.9852 | 24-03-2026 14:50 | 201.416 | 204.442 | 1286.1 | 34.0737 | 35.589 | -1.5154 | 213.5342 | 30.7 | 35.0801 | -4.3801 | 0.9852 | 24-03-2026 14:50 | 195.909 | 198.812 | 1277.7 | 33.1353 | 35.589 | -2.4537 | 213.5342 | 31 | 35.0801 | -4.0801 | 0.9854 | 24-03-2026 14:50 | 196.542 | 201.734 | 1288.7 | 33.6223 | 35.589 | -1.9667 | 213.5342 | 31.6 | 35.0801 | -3.4801 | 0.97426 | 24-03-2026 14:50 | 194.8 | 191.927 | 1222 | 31.9878 | 33.8586 | -1.8707 | 203.1514 | 29.7 | 33.3744 | -3.6744 | 1.015 | 24-03-2026 14:50 | 357.518 | 368.3955 | -10.8775 | 2210.3732 | 316.5 | 363.1275 | -46.6275 | 41.018
24-03-2026 14:40 | 933 | 50.8 | 306.459 | 310.914 | 1684.6 | 51.819 | 55.1305 | -3.3115 | 330.7831 | 51.7 | 54.3422 | -2.6422 | 0.98567 | 24-03-2026 14:40 | 311.713 | 317.08 | 1695.2 | 52.8467 | 55.1305 | -2.2839 | 330.7831 | 52.5 | 54.3422 | -1.8422 | 0.98307 | 24-03-2026 14:40 | 304.679 | 312.924 | 1658.1 | 52.154 | 55.1305 | -2.9765 | 330.7831 | 52.2 | 54.3422 | -2.1422 | 0.97365 | 24-03-2026 14:40 | 308.658 | 313.964 | 1680 | 52.3273 | 55.1305 | -2.8032 | 330.7831 | 52.8 | 54.3422 | -1.5422 | 0.9831 | 24-03-2026 14:40 | 231.017 | 234.63 | 1257.3 | 39.105 | 40.8374 | -1.7324 | 245.0245 | 39.5 | 40.2534 | -0.75345 | 0.9846 | 24-03-2026 14:40 | 228.499 | 232.641 | 1255.4 | 38.7735 | 40.8374 | -2.0639 | 245.0245 | 39 | 40.2534 | -1.2534 | 0.9822 | 24-03-2026 14:40 | 227.983 | 232.409 | 1246.7 | 38.7348 | 40.8374 | -2.1026 | 245.0245 | 38.7 | 40.2534 | -1.5534 | 0.98096 | 24-03-2026 14:40 | 229.201 | 235.841 | 1257.1 | 39.3068 | 40.8374 | -1.5306 | 245.0245 | 38.8 | 40.2534 | -1.4534 | 0.97185 | 24-03-2026 14:40 | 217.286 | 220.617 | 1192.3 | 36.7695 | 38.8518 | -2.0823 | 233.1105 | 36.4 | 38.2962 | -1.8962 | 0.9849 | 24-03-2026 14:40 | 401.8367 | 422.7235 | -20.8869 | 2536.3412 | 401.6 | 416.6786 | -15.0786 | 0.23667
24-03-2026 14:30 | 992 | 51.09 | 329.944 | 335.548 | 1632.9 | 55.9247 | 58.5514 | -2.6267 | 351.3084 | 56.5 | 57.7141 | -1.2141 | 0.9833 | 24-03-2026 14:30 | 332.608 | 339.621 | 1642.7 | 56.6035 | 58.5514 | -1.9479 | 351.3084 | 57.9 | 57.7141 | 0.18588 | 0.97935 | 24-03-2026 14:30 | 329.053 | 338.319 | 1605.9 | 56.3865 | 58.5514 | -2.1649 | 351.3084 | 55.4 | 57.7141 | -2.3141 | 0.97261 | 24-03-2026 14:30 | 332.063 | 337.806 | 1627.2 | 56.301 | 58.5514 | -2.2504 | 351.3084 | 56.8 | 57.7141 | -0.91412 | 0.983 | 24-03-2026 14:30 | 249.961 | 253.922 | 1217.8 | 42.3203 | 43.3714 | -1.0511 | 260.2285 | 42.5 | 42.7512 | -0.2512 | 0.9844 | 24-03-2026 14:30 | 245.15 | 249.61 | 1216.4 | 41.6017 | 43.3714 | -1.7697 | 260.2285 | 42 | 42.7512 | -0.7512 | 0.98213 | 24-03-2026 14:30 | 243.706 | 248.068 | 1208 | 41.3447 | 43.3714 | -2.0267 | 260.2285 | 41.9 | 42.7512 | -0.8512 | 0.98242 | 24-03-2026 14:30 | 185.597 | 189.784 | 1218.3 | 31.6307 | 43.3714 | -11.7407 | 260.2285 | 41.9 | 42.7512 | -0.8512 | 0.97794 | 24-03-2026 14:30 | 201.596 | 204.438 | 1155.9 | 34.073 | 41.2625 | -7.1895 | 247.5751 | 39.7 | 40.6725 | -0.97247 | 0.9861 | 24-03-2026 14:30 | 416.186 | 448.9538 | -32.7678 | 2693.7226 | 434.6 | 442.5337 | -7.9337 | -18.414
24-03-2026 14:20 | 1021 | 49.94 | 352.844 | 358.326 | 1576.4 | 59.721 | 60.53 | -0.80902 | 363.1801 | 23.3 | 59.6644 | -36.3644 | 0.9847 | 24-03-2026 14:20 | 352.679 | 358.013 | 1584.8 | 59.6688 | 60.53 | -0.86119 | 363.1801 | 23.2 | 59.6644 | -36.4644 | 0.9851 | 24-03-2026 14:20 | 352.43 | 362.036 | 1550.5 | 60.3393 | 60.53 | -0.19069 | 363.1801 | 23.4 | 59.6644 | -36.2644 | 0.97347 | 24-03-2026 14:20 | 352.626 | 358.032 | 1570.4 | 59.672 | 60.53 | -0.85802 | 363.1801 | 24.3 | 59.6644 | -35.3644 | 0.9849 | 24-03-2026 14:20 | 266.826 | 270.834 | 1175.3 | 45.139 | 44.8371 | 0.30195 | 269.0223 | 17.4 | 44.1959 | -26.7959 | 0.9852 | 24-03-2026 14:20 | 263.22 | 267.832 | 1174.4 | 44.6387 | 44.8371 | -0.19839 | 269.0223 | 17.9 | 44.1959 | -26.2959 | 0.98278 | 24-03-2026 14:20 | 263.317 | 268.097 | 1166.1 | 44.6828 | 44.8371 | -0.15422 | 269.0223 | 17.7 | 44.1959 | -26.4959 | 0.98217 | 24-03-2026 14:20 | 264.351 | 271.835 | 1176.4 | 45.3058 | 44.8371 | 0.46878 | 269.0223 | 18.1 | 44.1959 | -26.0959 | 0.97247 | 24-03-2026 14:20 | 249.748 | 253.478 | 1116.2 | 42.2463 | 42.6569 | -0.41057 | 255.9414 | 17.5 | 42.0469 | -24.5469 | 0.98528 | 24-03-2026 14:20 | 461.4138 | 464.1252 | -2.7114 | 2784.7512 | 182.8 | 457.4882 | -274.6882 | 278.6138
24-03-2026 14:10 | 283 | 50.23 | 98.543 | 99.851 | 1553.1 | 16.6418 | 16.759 | -0.11717 | 100.554 | 30.4 | 16.5194 | 13.8806 | 0.9869 | 24-03-2026 14:10 | 98.788 | 100.13 | 1561.6 | 16.6883 | 16.759 | -0.070674 | 100.554 | 35.3 | 16.5194 | 18.7806 | 0.9866 | 24-03-2026 14:10 | 98.183 | 100.256 | 1527.1 | 16.7093 | 16.759 | -0.049674 | 100.554 | 28.5 | 16.5194 | 11.9806 | 0.97932 | 24-03-2026 14:10 | 97.481 | 98.805 | 1546.1 | 16.4675 | 16.759 | -0.29151 | 100.554 | 32.1 | 16.5194 | 15.5806 | 0.9866 | 24-03-2026 14:10 | 72.738 | 73.801 | 1157.9 | 12.3002 | 12.4141 | -0.11391 | 74.4845 | 22.9 | 12.2366 | 10.6634 | 0.9856 | 24-03-2026 14:10 | 71.44 | 72.484 | 1156.5 | 12.0807 | 12.4141 | -0.33341 | 74.4845 | 23.8 | 12.2366 | 11.5634 | 0.9856 | 24-03-2026 14:10 | 71.512 | 72.557 | 1148.4 | 12.0928 | 12.4141 | -0.32125 | 74.4845 | 22.7 | 12.2366 | 10.4634 | 0.9856 | 24-03-2026 14:10 | 71.237 | 73.058 | 1158.3 | 12.1763 | 12.4141 | -0.23775 | 74.4845 | 23.6 | 12.2366 | 11.3634 | 0.97507 | 24-03-2026 14:10 | 67.131 | 68.133 | 1098.7 | 11.3555 | 11.8105 | -0.45496 | 70.8628 | 23.3 | 11.6416 | 11.6584 | 0.98529 | 24-03-2026 14:10 | 126.5125 | 128.5028 | -1.9903 | 771.0168 | 242.6 | 126.6652 | 115.9348 | -116.0875
24-03-2026 14:00 | 1091 | 49.36 | 352.742 | 338.48 | 1522.7 | 56.4133 | 64.8238 | -8.4105 | 388.943 | 19.9 | 63.8969 | -43.9969 | 1.0421 | 24-03-2026 14:00 | 125.44 | 126.28 | 1526.3 | 21.0467 | 64.8238 | -43.7772 | 388.943 | 15.5 | 63.8969 | -48.3969 | 0.99335 | 24-03-2026 14:00 | 347.859 | 355.579 | 1498.6 | 59.2632 | 64.8238 | -5.5607 | 388.943 | 20.5 | 63.8969 | -43.3969 | 0.97829 | 24-03-2026 14:00 | 352.321 | 357.36 | 1514 | 59.56 | 64.8238 | -5.2638 | 388.943 | 18.5 | 63.8969 | -45.3969 | 0.9859 | 24-03-2026 14:00 | 283.158 | 287.412 | 1135 | 47.902 | 48.0177 | -0.11565 | 288.1059 | 15.1 | 47.331 | -32.231 | 0.9852 | 24-03-2026 14:00 | 282.468 | 287.732 | 1132.7 | 47.9553 | 48.0177 | -0.062319 | 288.1059 | 13.4 | 47.331 | -33.931 | 0.98171 | 24-03-2026 14:00 | 279.118 | 284.287 | 1125.7 | 47.3812 | 48.0177 | -0.63649 | 288.1059 | 14.9 | 47.331 | -32.431 | 0.98182 | 24-03-2026 14:00 | 284.243 | 292.622 | 1134.7 | 48.7703 | 48.0177 | 0.75268 | 288.1059 | 14.5 | 47.331 | -32.831 | 0.97137 | 24-03-2026 14:00 | 246.63 | 251.812 | 1075.4 | 41.9687 | 45.6828 | -3.7142 | 274.0971 | 12.4 | 45.0296 | -32.6296 | 0.97942 | 24-03-2026 14:00 | 430.2607 | 497.0488 | -66.7881 | 2982.2927 | 144.7 | 489.941 | -345.241 | 285.5607
24-03-2026 13:50 | 247 | 49.94 | 85.915 | 87.329 | 1502.8 | 14.5548 | 14.6434 | -0.08857 | 87.8604 | 23.7 | 14.434 | 9.266 | 0.98381 | 24-03-2026 13:50 | 86.485 | 87.731 | 1510.8 | 14.6218 | 14.6434 | -0.02157 | 87.8604 | 22.3 | 14.434 | 7.866 | 0.9858 | 24-03-2026 13:50 | 85.967 | 87.791 | 1478.1 | 14.6318 | 14.6434 | -0.01157 | 87.8604 | 20.8 | 14.434 | 6.366 | 0.97922 | 24-03-2026 13:50 | 86.116 | 87.348 | 1495.5 | 14.558 | 14.6434 | -0.085404 | 87.8604 | 22 | 14.434 | 7.566 | 0.9859 | 24-03-2026 13:50 | 64.459 | 65.434 | 1119.9 | 10.9057 | 10.847 | 0.058701 | 65.0818 | 16.2 | 10.6919 | 5.5081 | 0.9851 | 24-03-2026 13:50 | 63.536 | 64.484 | 1119.3 | 10.7473 | 10.847 | -0.099632 | 65.0818 | 16.7 | 10.6919 | 6.0081 | 0.9853 | 24-03-2026 13:50 | 63.684 | 64.641 | 1110.8 | 10.7735 | 10.847 | -0.073466 | 65.0818 | 16.1 | 10.6919 | 5.4081 | 0.9852 | 24-03-2026 13:50 | 63.991 | 65.73 | 1120.2 | 10.955 | 10.847 | 0.10803 | 65.0818 | 16.5 | 10.6919 | 5.8081 | 0.97354 | 24-03-2026 13:50 | 60.052 | 60.966 | 1063 | 10.161 | 10.3195 | -0.15854 | 61.9173 | 15.8 | 10.172 | 5.628 | 0.98501 | 24-03-2026 13:50 | 111.909 | 112.281 | -0.37202 | 673.6861 | 170.1 | 110.6754 | 59.4246 | -58.191
24-03-2026 13:40 | 1129 | 51.09 | 352.875 | 358.686 | 1479.1 | 59.781 | 66.6376 | -6.8566 | 399.8258 | 57.7 | 65.6847 | -7.9847 | 0.9838 | 24-03-2026 13:40 | 352.716 | 358.488 | 1488.5 | 59.748 | 66.6376 | -6.8896 | 399.8258 | 59.9 | 65.6847 | -5.7847 | 0.9839 | 24-03-2026 13:40 | 343.118 | 351.71 | 1457.3 | 58.6183 | 66.6376 | -8.0193 | 399.8258 | 59.2 | 65.6847 | -6.4847 | 0.97557 | 24-03-2026 13:40 | 352.76 | 359.116 | 1473.5 | 59.8527 | 66.6376 | -6.785 | 399.8258 | 59.2 | 65.6847 | -6.4847 | 0.9823 | 24-03-2026 13:40 | 270.213 | 276.62 | 1103.7 | 46.1033 | 49.3612 | -3.2579 | 296.1673 | 47.8 | 48.6553 | -0.85535 | 0.97684 | 24-03-2026 13:40 | 270.136 | 274.696 | 1102.6 | 45.7827 | 49.3612 | -3.5785 | 296.1673 | 47.2 | 48.6553 | -1.4553 | 0.9834 | 24-03-2026 13:40 | 265.629 | 270.058 | 1094.7 | 45.0097 | 49.3612 | -4.3515 | 296.1673 | 47.3 | 48.6553 | -1.3553 | 0.9836 | 24-03-2026 13:40 | 267.147 | 275.307 | 1103.7 | 45.8845 | 49.3612 | -3.4767 | 296.1673 | 47.7 | 48.6553 | -0.95535 | 0.97036 | 24-03-2026 13:40 | 255.266 | 259.522 | 1047.2 | 43.2537 | 46.9611 | -3.7074 | 281.7665 | 45.6 | 46.2895 | -0.68954 | 0.9836 | 24-03-2026 13:40 | 464.0338 | 510.9565 | -46.9226 | 3065.7388 | 471.6 | 503.6498 | -32.0498 | -7.5662
24-03-2026 13:30 | 1211 | 50.8 | 352.898 | 358.144 | 1421.4 | 59.6907 | 71.5574 | -11.8667 | 429.3445 | 56.5 | 70.5341 | -14.0341 | 0.98535 | 24-03-2026 13:30 | 352.764 | 358.048 | 1428.6 | 59.6747 | 71.5574 | -11.8827 | 429.3445 | 57.1 | 70.5341 | -13.4341 | 0.98524 | 24-03-2026 13:30 | 352.361 | 362.177 | 1398.1 | 60.3628 | 71.5574 | -11.1946 | 429.3445 | 57.2 | 70.5341 | -13.3341 | 0.9729 | 24-03-2026 13:30 | 352.586 | 357.992 | 1414.3 | 59.6653 | 71.5574 | -11.8921 | 429.3445 | 58.6 | 70.5341 | -11.9341 | 0.9849 | 24-03-2026 13:30 | 299.933 | 305.058 | 1055.9 | 50.843 | 53.0055 | -2.1625 | 318.0329 | 45.4 | 52.2475 | -6.8475 | 0.9832 | 24-03-2026 13:30 | 296.453 | 302.427 | 1055.4 | 50.4045 | 53.0055 | -2.601 | 318.0329 | 44.6 | 52.2475 | -7.6475 | 0.98025 | 24-03-2026 13:30 | 296.581 | 302.998 | 1047.4 | 50.4997 | 53.0055 | -2.5058 | 318.0329 | 44.8 | 52.2475 | -7.4475 | 0.97882 | 24-03-2026 13:30 | 298.741 | 307.718 | 1056 | 51.2863 | 53.0055 | -1.7192 | 318.0329 | 44.9 | 52.2475 | -7.3475 | 0.97083 | 24-03-2026 13:30 | 282.75 | 287.464 | 1001.6 | 47.9107 | 50.4282 | -2.5175 | 302.5689 | 41.9 | 49.707 | -7.807 | 0.9836 | 24-03-2026 13:30 | 490.3377 | 548.6798 | -58.3421 | 3292.0785 | 451 | 540.8336 | -89.8336 | 39.3377
24-03-2026 13:20 | 595 | 49.94 | 239.468 | 241.985 | 1364.9 | 40.3308 | 35.2746 | 5.0562 | 211.6476 | 28.5 | 34.7702 | -6.2702 | 0.9896 | 24-03-2026 13:20 | 204.207 | 207.128 | 1371.5 | 34.5213 | 35.2746 | -0.75326 | 211.6476 | 27.6 | 34.7702 | -7.1702 | 0.9859 | 24-03-2026 13:20 | 241.072 | 247.533 | 1340.9 | 41.2555 | 35.2746 | 5.9809 | 211.6476 | 27.4 | 34.7702 | -7.3702 | 0.9739 | 24-03-2026 13:20 | 175.554 | 178.011 | 1355.7 | 29.6685 | 35.2746 | -5.6061 | 211.6476 | 26.1 | 34.7702 | -8.6702 | 0.9862 | 24-03-2026 13:20 | 162.605 | 164.83 | 1010.5 | 27.4717 | 26.1293 | 1.3423 | 156.776 | 20.4 | 25.7557 | -5.3557 | 0.9865 | 24-03-2026 13:20 | 154.001 | 157.023 | 1010.8 | 26.1705 | 26.1293 | 0.04117 | 156.776 | 20.3 | 25.7557 | -5.4557 | 0.98075 | 24-03-2026 13:20 | 161.569 | 166.09 | 1002.6 | 27.6817 | 26.1293 | 1.5523 | 156.776 | 20.1 | 25.7557 | -5.6557 | 0.97278 | 24-03-2026 13:20 | 159.065 | 166.49 | 1011.1 | 27.7483 | 26.1293 | 1.619 | 156.776 | 20.1 | 25.7557 | -5.6557 | 0.9554 | 24-03-2026 13:20 | 148.921 | 150.959 | 959.7 | 25.1598 | 24.8588 | 0.30101 | 149.1529 | 19.1 | 24.5033 | -5.4033 | 0.9865 | 24-03-2026 13:20 | 280.0082 | 270.4745 | 9.5336 | 1622.8472 | 209.6 | 266.6067 | -57.0067 | 70.4082
24-03-2026 13:10 | 610 | 50.51 | 206.869 | 209.998 | 1336.4 | 34.9997 | 36.0848 | -1.0852 | 216.5089 | 43.9 | 35.5688 | 8.3312 | 0.9851 | 24-03-2026 13:10 | 211.435 | 214.611 | 1343.9 | 35.7685 | 36.0848 | -0.31632 | 216.5089 | 46.8 | 35.5688 | 11.2312 | 0.9852 | 24-03-2026 13:10 | 213.045 | 218.715 | 1313.5 | 36.4525 | 36.0848 | 0.36768 | 216.5089 | 43.8 | 35.5688 | 8.2312 | 0.97408 | 24-03-2026 13:10 | 212.133 | 215.363 | 1329.6 | 35.8938 | 36.0848 | -0.19099 | 216.5089 | 44.2 | 35.5688 | 8.6312 | 0.985 | 24-03-2026 13:10 | 156.009 | 158.256 | 990.1 | 26.376 | 26.7295 | -0.3535 | 160.377 | 32.5 | 26.3473 | 6.1527 | 0.9858 | 24-03-2026 13:10 | 154.854 | 157.254 | 990.5 | 26.209 | 26.7295 | -0.5205 | 160.377 | 32.6 | 26.3473 | 6.2527 | 0.98474 | 24-03-2026 13:10 | 155.153 | 158.393 | 982.5 | 26.3988 | 26.7295 | -0.33067 | 160.377 | 32.5 | 26.3473 | 6.1527 | 0.97954 | 24-03-2026 13:10 | 156.36 | 161.224 | 991 | 26.8707 | 26.7295 | 0.14117 | 160.377 | 32.6 | 26.3473 | 6.2527 | 0.96983 | 24-03-2026 13:10 | 147.66 | 149.757 | 940.6 | 24.9595 | 25.4298 | -0.47031 | 152.5789 | 30.8 | 25.0662 | 5.7338 | 0.986 | 24-03-2026 13:10 | 273.9285 | 276.6871 | -2.7586 | 1660.1226 | 339.7 | 272.7305 | 66.9695 | -65.7715
24-03-2026 13:00 | 922 | 50.8 | 294.339 | 299.572 | 1292.5 | 49.9287 | 54.4805 | -4.5519 | 326.8832 | 57.8 | 53.7015 | 4.0985 | 0.98253 | 24-03-2026 13:00 | 299.472 | 269.117 | 1297.1 | 44.8528 | 54.4805 | -9.6277 | 326.8832 | 55.8 | 53.7015 | 2.0985 | 1.1128 | 24-03-2026 13:00 | 314.162 | 324.099 | 1269.7 | 54.0165 | 54.4805 | -0.46404 | 326.8832 | 57 | 53.7015 | 3.2985 | 0.96934 | 24-03-2026 13:00 | 301.208 | 307.812 | 1285.4 | 51.302 | 54.4805 | -3.1785 | 326.8832 | 56.4 | 53.7015 | 2.6985 | 0.97855 | 24-03-2026 13:00 | 219.504 | 241.27 | 957.6 | 40.2117 | 40.356 | -0.14429 | 242.1357 | 43.5 | 39.7789 | 3.7211 | 0.90979 | 24-03-2026 13:00 | 225.978 | 229.559 | 957.9 | 38.2598 | 40.356 | -2.0961 | 242.1357 | 42.1 | 39.7789 | 2.3211 | 0.9844 | 24-03-2026 13:00 | 214.864 | 219.448 | 950 | 36.5747 | 40.356 | -3.7813 | 242.1357 | 43.9 | 39.7789 | 4.1211 | 0.97911 | 24-03-2026 13:00 | 213.161 | 219.354 | 958.4 | 36.559 | 40.356 | -3.797 | 242.1357 | 42.4 | 39.7789 | 2.6211 | 0.97177 | 24-03-2026 13:00 | 201.971 | 205.109 | 909.8 | 34.1848 | 38.3937 | -4.2089 | 230.3622 | 40.2 | 37.8447 | 2.3553 | 0.9847 | 24-03-2026 13:00 | 385.89 | 417.7397 | -31.8497 | 2506.438 | 439.1 | 411.766 | 27.334 | -53.21
24-03-2026 12:50 | 1092 | 52.23 | 352.81 | 358.802 | 1234.7 | 59.8003 | 64.1707 | -4.3704 | 385.0245 | 58.9 | 63.2531 | -4.3531 | 0.9833 | 24-03-2026 12:50 | 343.416 | 349 | 1241.3 | 58.1667 | 64.1707 | -6.0041 | 385.0245 | 57.9 | 63.2531 | -5.3531 | 0.984 | 24-03-2026 12:50 | 350.13 | 362.499 | 1212.7 | 60.4165 | 64.1707 | -3.7542 | 385.0245 | 56.8 | 63.2531 | -6.4531 | 0.96588 | 24-03-2026 12:50 | 348.699 | 354.693 | 1229 | 59.1155 | 64.1707 | -5.0552 | 385.0245 | 58.4 | 63.2531 | -4.8531 | 0.9831 | 24-03-2026 12:50 | 268.956 | 273.496 | 914.1 | 45.5827 | 47.5339 | -1.9512 | 285.2033 | 45.2 | 46.8542 | -1.6542 | 0.9834 | 24-03-2026 12:50 | 263.893 | 270.488 | 915.8 | 45.0813 | 47.5339 | -2.4526 | 285.2033 | 46.1 | 46.8542 | -0.75415 | 0.97562 | 24-03-2026 12:50 | 265.426 | 270.736 | 906.1 | 45.1227 | 47.5339 | -2.4112 | 285.2033 | 43.7 | 46.8542 | -3.1542 | 0.98039 | 24-03-2026 12:50 | 263.281 | 271.14 | 916 | 45.19 | 47.5339 | -2.3439 | 285.2033 | 46.5 | 46.8542 | -0.35415 | 0.97101 | 24-03-2026 12:50 | 249.117 | 253.245 | 869.6 | 42.2075 | 45.2226 | -3.0151 | 271.3356 | 44.3 | 44.5759 | -0.27592 | 0.9837 | 24-03-2026 12:50 | 460.6832 | 492.0411 | -31.358 | 2952.2469 | 457.8 | 485.005 | -27.205 | 2.8832
24-03-2026 12:40 | 1111 | 51.95 | 352.748 | 358.447 | 1175.8 | 59.7412 | 65.358 | -5.6168 | 392.148 | 57.4 | 64.4234 | -7.0234 | 0.9841 | 24-03-2026 12:40 | 349.952 | 355.534 | 1183.4 | 59.2557 | 65.358 | -6.1023 | 392.148 | 57.8 | 64.4234 | -6.6234 | 0.9843 | 24-03-2026 12:40 | 349.251 | 359.084 | 1155.9 | 59.8473 | 65.358 | -5.5107 | 392.148 | 59.1 | 64.4234 | -5.3234 | 0.97262 | 24-03-2026 12:40 | 344.319 | 349.953 | 1170.6 | 58.3255 | 65.358 | -7.0325 | 392.148 | 59 | 64.4234 | -5.4234 | 0.9839 | 24-03-2026 12:40 | 243.843 | 247.707 | 868.9 | 41.2845 | 48.4133 | -7.1288 | 290.48 | 47.1 | 47.721 | -0.62102 | 0.9844 | 24-03-2026 12:40 | 266.158 | 271.03 | 869.7 | 45.1717 | 48.4133 | -3.2417 | 290.48 | 46.8 | 47.721 | -0.92102 | 0.98202 | 24-03-2026 12:40 | 249.856 | 253.816 | 862.4 | 42.3027 | 48.4133 | -6.1107 | 290.48 | 46.8 | 47.721 | -0.92102 | 0.9844 | 24-03-2026 12:40 | 267.917 | 275.617 | 869.5 | 45.9362 | 48.4133 | -2.4772 | 290.48 | 46.4 | 47.721 | -1.321 | 0.97206 | 24-03-2026 12:40 | 257.89 | 262.11 | 825.3 | 43.685 | 46.0593 | -2.3743 | 276.3557 | 44 | 45.4006 | -1.4006 | 0.9839 | 24-03-2026 12:40 | 455.5497 | 501.1446 | -45.5949 | 3006.8674 | 464.4 | 493.9782 | -29.5782 | -8.8503
24-03-2026 12:30 | 1143 | 53.38 | 352.774 | 358.401 | 1118.4 | 59.7335 | 66.8689 | -7.1354 | 401.2134 | 59.3 | 65.9127 | -6.6127 | 0.9843 | 24-03-2026 12:30 | 352.839 | 358.327 | 1125.6 | 59.7212 | 66.8689 | -7.1477 | 401.2134 | 60.8 | 65.9127 | -5.1127 | 0.98468 | 24-03-2026 12:30 | 352.683 | 362.81 | 1096.8 | 60.4683 | 66.8689 | -6.4006 | 401.2134 | 58.1 | 65.9127 | -7.8127 | 0.97209 | 24-03-2026 12:30 | 351.817 | 357.238 | 1111.6 | 59.5397 | 66.8689 | -7.3292 | 401.2134 | 59.2 | 65.9127 | -6.7127 | 0.98483 | 24-03-2026 12:30 | 279.874 | 284.598 | 821.8 | 47.433 | 49.5325 | -2.0995 | 297.1951 | 45.3 | 48.8242 | -3.5242 | 0.9834 | 24-03-2026 12:30 | 276.926 | 282.918 | 822.9 | 47.153 | 49.5325 | -2.3795 | 297.1951 | 44.8 | 48.8242 | -4.0242 | 0.97882 | 24-03-2026 12:30 | 277.394 | 283.187 | 815.6 | 47.1978 | 49.5325 | -2.3347 | 297.1951 | 44.8 | 48.8242 | -4.0242 | 0.97954 | 24-03-2026 12:30 | 278.738 | 287.113 | 823.1 | 47.8522 | 49.5325 | -1.6804 | 297.1951 | 45.8 | 48.8242 | -3.0242 | 0.97083 | 24-03-2026 12:30 | 264.749 | 269.163 | 781.3 | 44.8605 | 47.1241 | -2.2636 | 282.7444 | 43.2 | 46.4502 | -3.2502 | 0.9836 | 24-03-2026 12:30 | 473.9592 | 512.7298 | -38.7706 | 3076.3785 | 461.3 | 505.3977 | -44.0977 | 12.6592
24-03-2026 12:20 | 1090 | 52.23 | 352.701 | 358.317 | 1059.1 | 59.7195 | 64.0532 | -4.3337 | 384.3193 | 38.9 | 63.1373 | -24.2373 | 0.98433 | 24-03-2026 12:20 | 352.867 | 358.459 | 1064.8 | 59.7432 | 64.0532 | -4.3101 | 384.3193 | 34.9 | 63.1373 | -28.2373 | 0.9844 | 24-03-2026 12:20 | 352.959 | 362.581 | 1038.7 | 60.4302 | 64.0532 | -3.6231 | 384.3193 | 36.8 | 63.1373 | -26.3373 | 0.97346 | 24-03-2026 12:20 | 352.454 | 358.112 | 1052.4 | 59.6853 | 64.0532 | -4.3679 | 384.3193 | 32.8 | 63.1373 | -30.3373 | 0.9842 | 24-03-2026 12:20 | 272.675 | 277.109 | 776.5 | 46.1848 | 47.4468 | -1.262 | 284.681 | 26.4 | 46.7683 | -20.3683 | 0.984 | 24-03-2026 12:20 | 260.704 | 265.863 | 778.1 | 44.3105 | 47.4468 | -3.1363 | 284.681 | 24.3 | 46.7683 | -22.4683 | 0.9806 | 24-03-2026 12:20 | 261.422 | 266.344 | 770.8 | 44.3907 | 47.4468 | -3.0562 | 284.681 | 24.7 | 46.7683 | -22.0683 | 0.98152 | 24-03-2026 12:20 | 234.743 | 241.318 | 777.3 | 40.2197 | 47.4468 | -7.2272 | 284.681 | 22.6 | 46.7683 | -24.1683 | 0.97275 | 24-03-2026 12:20 | 201.992 | 204.922 | 738.1 | 34.1537 | 45.1398 | -10.9861 | 270.8387 | 20.9 | 44.4943 | -23.5943 | 0.9857 | 24-03-2026 12:20 | 448.8375 | 491.14 | -42.3025 | 2946.8398 | 262.3 | 484.1167 | -221.8167 | 186.5375
24-03-2026 12:10 | 1033 | 52.52 | 233.249 | 236.849 | 1020.2 | 39.4748 | 60.6355 | -21.1607 | 363.8133 | 51.7 | 59.7685 | -8.0685 | 0.9848 | 24-03-2026 12:10 | 285.52 | 290.281 | 1029.9 | 48.3802 | 60.6355 | -12.2554 | 363.8133 | 53 | 59.7685 | -6.7685 | 0.9836 | 24-03-2026 12:10 | 123.004 | 125.749 | 1001.9 | 20.9582 | 60.6355 | -39.6774 | 363.8133 | 45.2 | 59.7685 | -14.5685 | 0.97817 | 24-03-2026 12:10 | 279.439 | 283.954 | 1019.6 | 47.3257 | 60.6355 | -13.3099 | 363.8133 | 49.7 | 59.7685 | -10.0685 | 0.9841 | 24-03-2026 12:10 | 63.779 | 64.817 | 750.1 | 10.8028 | 44.9152 | -34.1124 | 269.4913 | 31.5 | 44.2729 | -12.7729 | 0.98399 | 24-03-2026 12:10 | 183.376 | 187.073 | 753.8 | 31.1788 | 44.9152 | -13.7364 | 269.4913 | 35.3 | 44.2729 | -8.9729 | 0.98024 | 24-03-2026 12:10 | 65.979 | 66.706 | 746.1 | 11.1177 | 44.9152 | -33.7975 | 269.4913 | 30.6 | 44.2729 | -13.6729 | 0.9891 | 24-03-2026 12:10 | 78.326 | 80.107 | 754.7 | 13.3512 | 44.9152 | -31.564 | 269.4913 | 31.2 | 44.2729 | -13.0729 | 0.97777 | 24-03-2026 12:10 | 100.703 | 102.102 | 717.2 | 17.017 | 42.7313 | -25.7143 | 256.3876 | 32.6 | 42.1202 | -9.5202 | 0.9863 | 24-03-2026 12:10 | 239.6063 | 464.9343 | -225.328 | 2789.6058 | 360.8 | 458.2857 | -97.4857 | -121.1937
24-03-2026 12:00 | 1032 | 51.09 | 286.214 | 290.897 | 968.5 | 48.4828 | 60.9123 | -12.4295 | 365.4741 | 55 | 60.0413 | -5.0413 | 0.9839 | 24-03-2026 12:00 | 337.28 | 347.203 | 976.9 | 57.8672 | 60.9123 | -3.0452 | 365.4741 | 55.7 | 60.0413 | -4.3413 | 0.97142 | 24-03-2026 12:00 | 215.28 | 220.174 | 956.7 | 36.6957 | 60.9123 | -24.2167 | 365.4741 | 53.5 | 60.0413 | -6.5413 | 0.97777 | 24-03-2026 12:00 | 282.673 | 287.328 | 969.9 | 47.888 | 60.9123 | -13.0243 | 365.4741 | 55.1 | 60.0413 | -4.9413 | 0.9838 | 24-03-2026 12:00 | 108.155 | 109.624 | 718.6 | 18.2707 | 45.1203 | -26.8496 | 270.7215 | 39.4 | 44.475 | -5.075 | 0.9866 | 24-03-2026 12:00 | 169.531 | 171.99 | 718.5 | 28.665 | 45.1203 | -16.4553 | 270.7215 | 39.6 | 44.475 | -4.875 | 0.9857 | 24-03-2026 12:00 | 74.533 | 75.722 | 715.5 | 12.6203 | 45.1203 | -32.4999 | 270.7215 | 38.1 | 44.475 | -6.375 | 0.9843 | 24-03-2026 12:00 | 86.129 | 90.051 | 723.5 | 15.0085 | 45.1203 | -30.1118 | 270.7215 | 38.5 | 44.475 | -5.975 | 0.95645 | 24-03-2026 12:00 | 150.685 | 156.003 | 684.6 | 26.0005 | 42.9263 | -16.9258 | 257.558 | 37.6 | 42.3125 | -4.7125 | 0.96591 | 24-03-2026 12:00 | 291.4987 | 467.0567 | -175.5581 | 2802.3405 | 412.5 | 460.3778 | -47.8778 | -121.0013
24-03-2026 11:50 | 1040 | 51.09 | 341.665 | 347.751 | 913.5 | 57.9585 | 61.3845 | -3.426 | 368.3072 | 55.4 | 60.5067 | -5.1067 | 0.9825 | 24-03-2026 11:50 | 314.487 | 319.926 | 921.2 | 53.321 | 61.3845 | -8.0635 | 368.3072 | 108.9 | 60.5067 | 48.3933 | 0.983 | 24-03-2026 11:50 | 340.816 | 351.152 | 903.2 | 58.5253 | 61.3845 | -2.8592 | 368.3072 | 54.4 | 60.5067 | -6.1067 | 0.97057 | 24-03-2026 11:50 | 348.142 | 354.343 | 914.8 | 59.0572 | 61.3845 | -2.3274 | 368.3072 | 55.3 | 60.5067 | -5.2067 | 0.9825 | 24-03-2026 11:50 | 259.962 | 264.243 | 679.2 | 44.0405 | 45.47 | -1.4295 | 272.8202 | 41.2 | 44.8198 | -3.6198 | 0.9838 | 24-03-2026 11:50 | 258.328 | 263.357 | 678.9 | 43.8928 | 45.47 | -1.5772 | 272.8202 | 41.2 | 44.8198 | -3.6198 | 0.9809 | 24-03-2026 11:50 | 258.885 | 264.319 | 677.4 | 44.0532 | 45.47 | -1.4169 | 272.8202 | 41.7 | 44.8198 | -3.1198 | 0.97944 | 24-03-2026 11:50 | 259.278 | 267.515 | 685 | 44.5858 | 45.47 | -0.88419 | 272.8202 | 41.5 | 44.8198 | -3.3198 | 0.96921 | 24-03-2026 11:50 | 245.33 | 249.294 | 647 | 41.549 | 43.2591 | -1.7101 | 259.5546 | 39.2 | 42.6405 | -3.4405 | 0.9841 | 24-03-2026 11:50 | 446.9833 | 470.6773 | -23.694 | 2824.0641 | 478.8 | 463.9467 | 14.8533 | -31.8167
24-03-2026 11:40 | 1003 | 51.09 | 330.213 | 334.585 | 858.1 | 55.7642 | 59.2007 | -3.4365 | 355.204 | 51.7 | 58.3541 | -6.6541 | 0.98693 |  |  |  |  | 0 | 59.2007 | -59.2007 | 355.204 | 0 | 58.3541 | -58.3541 |  | 24-03-2026 11:40 | 329.517 | 338.778 | 848.8 | 56.463 | 59.2007 | -2.7377 | 355.204 | 51.4 | 58.3541 | -6.9541 | 0.97266 | 24-03-2026 11:40 | 340.438 | 346.502 | 859.5 | 57.7503 | 59.2007 | -1.4503 | 355.204 | 52.2 | 58.3541 | -6.1541 | 0.9825 | 24-03-2026 11:40 | 246.475 | 250.432 | 638 | 41.7387 | 43.8523 | -2.1137 | 263.1141 | 38.8 | 43.2253 | -4.4253 | 0.9842 | 24-03-2026 11:40 | 248.968 | 252.913 | 637.7 | 42.1522 | 43.8523 | -1.7002 | 263.1141 | 38.5 | 43.2253 | -4.7253 | 0.9844 | 24-03-2026 11:40 | 250.191 | 254.643 | 635.7 | 42.4405 | 43.8523 | -1.4118 | 263.1141 | 38 | 43.2253 | -5.2253 | 0.98252 | 24-03-2026 11:40 | 253.214 | 260.46 | 643.5 | 43.41 | 43.8523 | -0.44234 | 263.1141 | 38.4 | 43.2253 | -4.8253 | 0.97218 | 24-03-2026 11:40 | 243.756 | 247.644 | 607.8 | 41.274 | 41.7201 | -0.44607 | 250.3204 | 36.4 | 41.1235 | -4.7235 | 0.9843 | 24-03-2026 11:40 | 380.9928 | 453.9321 | -72.9393 | 2723.5925 | 345.4 | 447.4409 | -102.0409 | 35.5928
24-03-2026 11:30 | 987 | 51.37 | 339.085 | 341.774 | 806.4 | 56.9623 | 58.1935 | -1.2311 | 349.1607 | 35.8 | 57.3613 | -21.5613 | 0.99213 | 24-03-2026 11:30 | 342.312 | 348.48 | 812.3 | 58.08 | 58.1935 | -0.11346 | 349.1607 | 36.3 | 57.3613 | -21.0613 | 0.9823 | 24-03-2026 11:30 | 323.383 | 332.38 | 797.4 | 55.3967 | 58.1935 | -2.7968 | 349.1607 | 36.5 | 57.3613 | -20.8613 | 0.97293 | 24-03-2026 11:30 | 326.397 | 332.177 | 807.3 | 55.3628 | 58.1935 | -2.8306 | 349.1607 | 36.9 | 57.3613 | -20.4613 | 0.9826 | 24-03-2026 11:30 | 255.711 | 259.524 | 599.2 | 43.254 | 43.1063 | 0.14774 | 258.6376 | 29.1 | 42.4898 | -13.3898 | 0.98531 | 24-03-2026 11:30 | 255.983 | 260.947 | 599.2 | 43.4912 | 43.1063 | 0.3849 | 258.6376 | 29.1 | 42.4898 | -13.3898 | 0.98098 | 24-03-2026 11:30 | 252.826 | 257.194 | 597.7 | 42.8657 | 43.1063 | -0.2406 | 258.6376 | 29.1 | 42.4898 | -13.3898 | 0.98302 | 24-03-2026 11:30 | 253.702 | 260.992 | 605.1 | 43.4987 | 43.1063 | 0.3924 | 258.6376 | 32.1 | 42.4898 | -10.3898 | 0.97207 | 24-03-2026 11:30 | 244.709 | 248.713 | 571.4 | 41.4522 | 41.0103 | 0.4419 | 246.0616 | 28 | 40.4238 | -12.4238 | 0.9839 | 24-03-2026 11:30 | 440.3635 | 446.2092 | -5.8457 | 2677.2549 | 292.9 | 439.8284 | -146.9284 | 147.4635
24-03-2026 11:20 | 998 | 51.09 | 0 | 0 | 770.6 | 0 | 58.9055 | -58.9055 | 353.4333 | 95.3 | 58.0632 | 37.2368 |  | 24-03-2026 11:20 | 0 | 0 | 776 | 0 | 58.9055 | -58.9055 | 353.4333 | 41.6 | 58.0632 | -16.4632 |  | 24-03-2026 11:20 | 0 | 0 | 760.9 | 0 | 58.9055 | -58.9055 | 353.4333 | 39.1 | 58.0632 | -18.9632 |  | 24-03-2026 11:20 | 0 | 0 | 770.4 | 0 | 58.9055 | -58.9055 | 353.4333 | 39.5 | 58.0632 | -18.5632 |  | 24-03-2026 11:20 | 0 | 0 | 570.1 | 0 | 43.6337 | -43.6337 | 261.8024 | 29.4 | 43.0098 | -13.6098 |  | 24-03-2026 11:20 | 0 | 0 | 570.1 | 0 | 43.6337 | -43.6337 | 261.8024 | 29.1 | 43.0098 | -13.9098 |  | 24-03-2026 11:20 | 0 | 0 | 568.6 | 0 | 43.6337 | -43.6337 | 261.8024 | 29 | 43.0098 | -14.0098 |  | 24-03-2026 11:20 | 0 | 0 | 573 | 0 | 43.6337 | -43.6337 | 261.8024 | 29.8 | 43.0098 | -13.2098 |  | 24-03-2026 11:20 | 0 | 0 | 543.4 | 0 | 41.5121 | -41.5121 | 249.0726 | 28.1 | 40.9185 | -12.8185 |  | 24-03-2026 11:20 | 0 | 451.6692 | -451.6692 | 2710.0153 | 360.9 | 445.2103 | -84.3103 | -360.9
24-03-2026 11:10 | 991 | 51.09 |  |  |  | 0 | 58.4924 | -58.4924 | 350.9543 | 0 | 57.6559 | -57.6559 |  | 24-03-2026 11:10 | 335.373 | 341.277 | 734.4 | 56.8795 | 58.4924 | -1.6129 | 350.9543 | 52.8 | 57.6559 | -4.8559 | 0.9827 | 24-03-2026 11:10 | 328.372 | 337.323 | 721.8 | 56.2205 | 58.4924 | -2.2719 | 350.9543 | 52.5 | 57.6559 | -5.1559 | 0.97346 | 24-03-2026 11:10 | 332.596 | 338.451 | 730.9 | 56.4085 | 58.4924 | -2.0839 | 350.9543 | 53.4 | 57.6559 | -4.2559 | 0.9827 | 24-03-2026 11:10 | 247.676 | 251.652 | 540.7 | 41.942 | 43.3277 | -1.3857 | 259.9661 | 39.7 | 42.7081 | -3.0081 | 0.9842 | 24-03-2026 11:10 | 246.235 | 250.772 | 541 | 41.7953 | 43.3277 | -1.5324 | 259.9661 | 39.3 | 42.7081 | -3.4081 | 0.98191 | 24-03-2026 11:10 | 245.658 | 250.993 | 539.6 | 41.8322 | 43.3277 | -1.4955 | 259.9661 | 39.3 | 42.7081 | -3.4081 | 0.97874 | 24-03-2026 11:10 | 247.168 | 254.475 | 543.2 | 42.4125 | 43.3277 | -0.91519 | 259.9661 | 38.9 | 42.7081 | -3.8081 | 0.97129 | 24-03-2026 11:10 | 234.2 | 237.911 | 515.3 | 39.6518 | 41.2209 | -1.5691 | 247.3256 | 36.8 | 40.6315 | -3.8315 | 0.9844 | 24-03-2026 11:10 | 377.1423 | 448.5012 | -71.3589 | 2691.0072 | 352.7 | 442.0876 | -89.3876 | 24.4423
24-03-2026 11:00 | 1027 | 51.09 | 312.08 | 317.283 | 675.3 | 52.8805 | 60.6172 | -7.7367 | 363.7034 | 45.1 | 59.7504 | -14.6504 | 0.9836 | 24-03-2026 11:00 | 249.237 | 250.876 | 681.6 | 41.8127 | 60.6172 | -18.8046 | 363.7034 | 49.3 | 59.7504 | -10.4504 | 0.99347 | 24-03-2026 11:00 | 285.555 | 293.736 | 669.3 | 48.956 | 60.6172 | -11.6612 | 363.7034 | 45.7 | 59.7504 | -14.0504 | 0.97215 | 24-03-2026 11:00 | 328.489 | 331.27 | 677.5 | 55.2117 | 60.6172 | -5.4056 | 363.7034 | 45.3 | 59.7504 | -14.4504 | 0.99161 | 24-03-2026 11:00 | 214.598 | 217.822 | 501 | 36.3037 | 44.9017 | -8.598 | 269.4099 | 33.7 | 44.2596 | -10.5596 | 0.9852 | 24-03-2026 11:00 | 241.041 | 244.761 | 501.7 | 40.7935 | 44.9017 | -4.1082 | 269.4099 | 33.4 | 44.2596 | -10.8596 | 0.9848 | 24-03-2026 11:00 | 199.632 | 202.569 | 500.3 | 33.7615 | 44.9017 | -11.1402 | 269.4099 | 33.8 | 44.2596 | -10.4596 | 0.9855 | 24-03-2026 11:00 | 202.501 | 206.105 | 504.3 | 34.3508 | 44.9017 | -10.5508 | 269.4099 | 33.9 | 44.2596 | -10.3596 | 0.98251 | 24-03-2026 11:00 | 214.358 | 217.49 | 478.5 | 36.2483 | 42.7184 | -6.47 | 256.3102 | 32.2 | 42.1075 | -9.9075 | 0.9856 | 24-03-2026 11:00 | 380.3187 | 464.7939 | -84.4752 | 2788.7633 | 352.4 | 458.1473 | -105.7473 | 27.9187
24-03-2026 10:50 | 984 | 61.13 | 343.283 | 349.326 | 630.2 | 58.221 | 55.8332 | 2.3878 | 334.9993 | 54.9 | 55.0348 | -0.1348 | 0.9827 | 24-03-2026 10:50 | 338.658 | 344.655 | 632.3 | 57.4425 | 55.8332 | 1.6093 | 334.9993 | 52.2 | 55.0348 | -2.8348 | 0.9826 | 24-03-2026 10:50 | 335.684 | 345.133 | 623.6 | 57.5222 | 55.8332 | 1.6889 | 334.9993 | 54.4 | 55.0348 | -0.6348 | 0.97262 | 24-03-2026 10:50 | 324.006 | 329.676 | 632.2 | 54.946 | 55.8332 | -0.88722 | 334.9993 | 54.8 | 55.0348 | -0.2348 | 0.9828 | 24-03-2026 10:50 | 248.514 | 252.529 | 467.3 | 42.0882 | 41.3579 | 0.73023 | 248.1476 | 41.1 | 40.7665 | 0.33348 | 0.9841 | 24-03-2026 10:50 | 242.835 | 246.738 | 468.3 | 41.123 | 41.3579 | -0.23494 | 248.1476 | 41.2 | 40.7665 | 0.43348 | 0.98418 | 24-03-2026 10:50 | 243.496 | 248.627 | 466.5 | 41.4378 | 41.3579 | 0.079895 | 248.1476 | 40.8 | 40.7665 | 0.03348 | 0.97936 | 24-03-2026 10:50 | 243.221 | 250.737 | 470.4 | 41.7895 | 41.3579 | 0.43156 | 248.1476 | 40.9 | 40.7665 | 0.13348 | 0.97002 | 24-03-2026 10:50 | 226.132 | 229.28 | 446.3 | 38.2133 | 39.347 | -1.1336 | 236.0817 | 38.7 | 38.7843 | -0.084295 | 0.98627 | 24-03-2026 10:50 | 432.7835 | 428.1116 | 4.6719 | 2568.6695 | 419 | 421.9896 | -2.9896 | 13.7835
24-03-2026 10:40 | 959 | 53.38 | 321.23 | 326.719 | 575.3 | 54.4532 | 56.1044 | -1.6512 | 336.6261 | 51.9 | 55.3021 | -3.4021 | 0.9832 | 24-03-2026 10:40 | 324.915 | 330.534 | 580.1 | 55.089 | 56.1044 | -1.0154 | 336.6261 | 54 | 55.3021 | -1.3021 | 0.983 | 24-03-2026 10:40 | 318.207 | 327.024 | 569.2 | 54.504 | 56.1044 | -1.6004 | 336.6261 | 51.6 | 55.3021 | -3.7021 | 0.97304 | 24-03-2026 10:40 | 321.732 | 327.363 | 577.4 | 54.5605 | 56.1044 | -1.5439 | 336.6261 | 52.3 | 55.3021 | -3.0021 | 0.9828 | 24-03-2026 10:40 | 239.607 | 243.404 | 426.2 | 40.5673 | 41.5588 | -0.99145 | 249.3527 | 38.8 | 40.9645 | -2.1645 | 0.9844 | 24-03-2026 10:40 | 238.189 | 242.589 | 427.1 | 40.4315 | 41.5588 | -1.1273 | 249.3527 | 38.1 | 40.9645 | -2.8645 | 0.98186 | 24-03-2026 10:40 | 238.45 | 243.047 | 425.7 | 40.5078 | 41.5588 | -1.0509 | 249.3527 | 38.1 | 40.9645 | -2.8645 | 0.98109 | 24-03-2026 10:40 | 241.184 | 248.507 | 429.5 | 41.4178 | 41.5588 | -0.14095 | 249.3527 | 38.5 | 40.9645 | -2.4645 | 0.97053 | 24-03-2026 10:40 | 227.978 | 231.497 | 407.6 | 38.5828 | 39.538 | -0.9552 | 237.2282 | 36.7 | 38.9726 | -2.2726 | 0.9848 | 24-03-2026 10:40 | 420.114 | 430.1906 | -10.0766 | 2581.1435 | 400 | 424.0389 | -24.0389 | 20.114
24-03-2026 10:30 | 936 | 54.24 | 316.238 | 321.631 | 523.4 | 53.6052 | 54.5758 | -0.97062 | 327.4547 | 50.3 | 53.7954 | -3.4954 | 0.98323 | 24-03-2026 10:30 | 319.224 | 324.646 | 526.1 | 54.1077 | 54.5758 | -0.46812 | 327.4547 | 49.6 | 53.7954 | -4.1954 | 0.9833 | 24-03-2026 10:30 | 312.629 | 321.479 | 517.6 | 53.5798 | 54.5758 | -0.99595 | 327.4547 | 49.8 | 53.7954 | -3.9954 | 0.97247 | 24-03-2026 10:30 | 316.311 | 321.653 | 525.1 | 53.6088 | 54.5758 | -0.96695 | 327.4547 | 50.7 | 53.7954 | -3.0954 | 0.98339 | 24-03-2026 10:30 | 235.271 | 238.902 | 387.4 | 39.817 | 40.4265 | -0.60951 | 242.559 | 37.6 | 39.8484 | -2.2484 | 0.9848 | 24-03-2026 10:30 | 233.964 | 238.172 | 389 | 39.6953 | 40.4265 | -0.73117 | 242.559 | 37.6 | 39.8484 | -2.2484 | 0.98233 | 24-03-2026 10:30 | 234.3 | 238.591 | 387.6 | 39.7652 | 40.4265 | -0.66134 | 242.559 | 38.1 | 39.8484 | -1.7484 | 0.98202 | 24-03-2026 10:30 | 235.961 | 242.978 | 391 | 40.4963 | 40.4265 | 0.069826 | 242.559 | 38.4 | 39.8484 | -1.4484 | 0.97112 | 24-03-2026 10:30 | 223.397 | 226.799 | 370.9 | 37.7998 | 38.4608 | -0.66098 | 230.7649 | 36 | 37.9108 | -1.9108 | 0.985 | 24-03-2026 10:30 | 412.4752 | 418.47 | -5.9948 | 2510.8199 | 388.1 | 412.4859 | -24.3859 | 24.3752
24-03-2026 10:20 | 891 | 53.09 | 303.114 | 308.105 | 473.1 | 51.3508 | 52.1849 | -0.83406 | 313.1094 | 50 | 51.4387 | -1.4387 | 0.9838 | 24-03-2026 10:20 | 306.211 | 311.317 | 476.5 | 51.8862 | 52.1849 | -0.29873 | 313.1094 | 49.4 | 51.4387 | -2.0387 | 0.9836 | 24-03-2026 10:20 | 300.333 | 308.416 | 467.8 | 51.4027 | 52.1849 | -0.78223 | 313.1094 | 48 | 51.4387 | -3.4387 | 0.97379 | 24-03-2026 10:20 | 304.344 | 309.387 | 474.4 | 51.5645 | 52.1849 | -0.6204 | 313.1094 | 48.2 | 51.4387 | -3.2387 | 0.9837 | 24-03-2026 10:20 | 225.608 | 229.067 | 349.8 | 38.1778 | 38.6555 | -0.47765 | 231.9329 | 35.9 | 38.1027 | -2.2027 | 0.9849 | 24-03-2026 10:20 | 224.966 | 228.605 | 351.4 | 38.1008 | 38.6555 | -0.55465 | 231.9329 | 35.5 | 38.1027 | -2.6027 | 0.98408 | 24-03-2026 10:20 | 224.35 | 228.128 | 349.5 | 38.0213 | 38.6555 | -0.63415 | 231.9329 | 35.3 | 38.1027 | -2.8027 | 0.98344 | 24-03-2026 10:20 | 225.454 | 232.054 | 352.6 | 38.6757 | 38.6555 | 0.020188 | 231.9329 | 35.3 | 38.1027 | -2.8027 | 0.97156 | 24-03-2026 10:20 | 214.102 | 217.318 | 334.9 | 36.2197 | 36.7759 | -0.55623 | 220.6554 | 33.5 | 36.25 | -2.75 | 0.9852 | 24-03-2026 10:20 | 395.3995 | 400.1374 | -4.7379 | 2400.8244 | 371.1 | 394.4154 | -23.3154 | 24.2995
24-03-2026 10:10 | 808 | 52.81 | 289.511 | 294.039 | 423.1 | 49.0065 | 47.3751 | 1.6314 | 284.2507 | 35.7 | 46.6976 | -10.9976 | 0.9846 | 24-03-2026 10:10 | 216.267 | 294.046 | 427.1 | 49.0077 | 47.3751 | 1.6326 | 284.2507 | 37.3 | 46.6976 | -9.3976 | 0.73549 | 24-03-2026 10:10 | 282.033 | 290.531 | 419.8 | 48.4218 | 47.3751 | 1.0467 | 284.2507 | 37.1 | 46.6976 | -9.5976 | 0.97075 | 24-03-2026 10:10 | 270.775 | 275.066 | 426.2 | 45.8443 | 47.3751 | -1.5308 | 284.2507 | 37.8 | 46.6976 | -8.8976 | 0.9844 | 24-03-2026 10:10 | 221.409 | 224.644 | 313.9 | 37.4407 | 35.0927 | 2.348 | 210.556 | 28 | 34.5908 | -6.5908 | 0.9856 | 24-03-2026 10:10 | 202.226 | 205.097 | 315.9 | 34.1828 | 35.0927 | -0.90984 | 210.556 | 28.3 | 34.5908 | -6.2908 | 0.986 | 24-03-2026 10:10 | 200.839 | 207.971 | 314.2 | 34.6618 | 35.0927 | -0.43084 | 210.556 | 27.8 | 34.5908 | -6.7908 | 0.96571 | 24-03-2026 10:10 | 198.444 | 207.871 | 317.3 | 34.6452 | 35.0927 | -0.44751 | 210.556 | 28.3 | 34.5908 | -6.2908 | 0.95465 | 24-03-2026 10:10 | 184.66 | 187.339 | 301.4 | 31.2232 | 33.3863 | -2.1632 | 200.318 | 26.9 | 32.9089 | -6.0089 | 0.9857 | 24-03-2026 10:10 | 364.434 | 363.2575 | 1.1765 | 2179.5448 | 287.2 | 358.0629 | -70.8629 | 77.234
24-03-2026 10:00 | 590 | 52.81 | 216.681 | 219.847 | 387.4 | 36.6412 | 34.5932 | 2.048 | 207.5593 | 44 | 34.0985 | 9.9015 | 0.9856 | 24-03-2026 10:00 | 208.413 | 215.117 | 389.8 | 35.8528 | 34.5932 | 1.2596 | 207.5593 | 44.4 | 34.0985 | 10.3015 | 0.96884 | 24-03-2026 10:00 | 204.215 | 209.601 | 382.7 | 34.9335 | 34.5932 | 0.34029 | 207.5593 | 43.6 | 34.0985 | 9.5015 | 0.9743 | 24-03-2026 10:00 | 202.037 | 205.03 | 388.4 | 34.1717 | 34.5932 | -0.42155 | 207.5593 | 43.9 | 34.0985 | 9.8015 | 0.9854 | 24-03-2026 10:00 | 153.978 | 156.278 | 285.9 | 26.0463 | 25.6246 | 0.42173 | 153.7476 | 32.5 | 25.2582 | 7.2418 | 0.98528 | 24-03-2026 10:00 | 151.146 | 154.286 | 287.6 | 25.7143 | 25.6246 | 0.089732 | 153.7476 | 32.3 | 25.2582 | 7.0418 | 0.97965 | 24-03-2026 10:00 | 155.046 | 158.325 | 286.4 | 26.3875 | 25.6246 | 0.7629 | 153.7476 | 32.2 | 25.2582 | 6.9418 | 0.97929 | 24-03-2026 10:00 | 158.605 | 163.685 | 289 | 27.2808 | 25.6246 | 1.6562 | 153.7476 | 32.4 | 25.2582 | 7.1418 | 0.96896 | 24-03-2026 10:00 | 148.77 | 150.882 | 274.5 | 25.147 | 24.3786 | 0.76837 | 146.2718 | 31.3 | 24.03 | 7.27 | 0.986 | 24-03-2026 10:00 | 272.1752 | 265.2499 | 6.9253 | 1591.4993 | 336.6 | 261.4568 | 75.1432 | -64.4248
24-03-2026 09:50 | 899 | 53.38 | 302.899 | 305.308 | 343.4 | 50.8847 | 52.5942 | -1.7095 | 315.5651 | 46.7 | 51.8421 | -5.1421 |  | 24-03-2026 09:50 | 313.16 | 318.414 | 345.4 | 53.069 | 52.5942 | 0.47482 | 315.5651 | 48.3 | 51.8421 | -3.5421 |  | 24-03-2026 09:50 | 279.965 | 285.64 | 339.1 | 47.6067 | 52.5942 | -4.9875 | 315.5651 | 46.5 | 51.8421 | -5.3421 |  | 24-03-2026 09:50 | 306.133 | 311.206 | 344.5 | 51.8677 | 52.5942 | -0.72651 | 315.5651 | 47.5 | 51.8421 | -4.3421 |  | 24-03-2026 09:50 | 202.919 | 205.926 | 253.4 | 34.321 | 38.9586 | -4.6376 | 233.7519 | 35.1 | 38.4015 | -3.3015 |  | 24-03-2026 09:50 | 206.299 | 213.682 | 255.3 | 35.6137 | 38.9586 | -3.345 | 233.7519 | 35.4 | 38.4015 | -3.0015 |  | 24-03-2026 09:50 | 208.964 | 212.968 | 254.2 | 35.4947 | 38.9586 | -3.464 | 233.7519 | 35.6 | 38.4015 | -2.8015 |  | 24-03-2026 09:50 | 214.081 | 220.944 | 256.6 | 36.824 | 38.9586 | -2.1346 | 233.7519 | 36.1 | 38.4015 | -2.3015 |  | 24-03-2026 09:50 | 217.969 | 221.243 | 243.2 | 36.8738 | 37.0643 | -0.1905 | 222.386 | 33.7 | 36.5343 | -2.8343 |  | 24-03-2026 09:50 | 382.5552 | 403.2756 | -20.7205 | 2419.6538 | 364.9 | 397.5088 | -32.6088 | 17.6552
24-03-2026 09:40 | 859 | 53.09 | 305.815 | 310.693 | 296.7 | 51.7822 | 50.3107 | 1.4715 | 301.8641 | 42.4 | 49.5912 | -7.1912 |  | 24-03-2026 09:40 | 295.549 | 300.294 | 297.1 | 50.049 | 50.3107 | -0.26169 | 301.8641 | 88.8 | 49.5912 | 39.2088 |  | 24-03-2026 09:40 | 302.022 | 309.365 | 292.6 | 51.5608 | 50.3107 | 1.2501 | 301.8641 | 41.5 | 49.5912 | -8.0912 |  | 24-03-2026 09:40 | 308.51 | 312.952 | 297 | 52.1587 | 50.3107 | 1.848 | 301.8641 | 41.7 | 49.5912 | -7.8912 |  | 24-03-2026 09:40 | 227.393 | 230.739 | 218.3 | 38.4565 | 37.2672 | 1.1893 | 223.6031 | 30.9 | 36.7343 | -5.8343 |  | 24-03-2026 09:40 | 228.78 | 232.146 | 219.9 | 38.691 | 37.2672 | 1.4238 | 223.6031 | 30.7 | 36.7343 | -6.0343 |  | 24-03-2026 09:40 | 226.629 | 231.13 | 218.6 | 38.5217 | 37.2672 | 1.2545 | 223.6031 | 30 | 36.7343 | -6.7343 |  | 24-03-2026 09:40 | 223.707 | 231.908 | 220.5 | 38.6513 | 37.2672 | 1.3842 | 223.6031 | 30.3 | 36.7343 | -6.4343 |  | 24-03-2026 09:40 | 209.015 | 212.65 | 209.5 | 35.4417 | 35.4551 | -0.013438 | 212.7306 | 28.9 | 34.9481 | -6.0481 |  | 24-03-2026 09:40 | 395.3128 | 385.7666 | 9.5463 | 2314.5995 | 365.2 | 380.2501 | -15.0501 | 30.1128
24-03-2026 09:30 | 866 | 53.38 | 275.404 | 279.541 | 254.3 | 46.5902 | 50.6636 | -4.0734 | 303.9815 | 45.4 | 49.9391 | -4.5391 | [5 empty] | 0 | 50.6636 | -50.6636 | 303.9815 | 0 | 49.9391 | -49.9391 |  | 24-03-2026 09:30 | 274.025 | 278.254 | 251.1 | 46.3757 | 50.6636 | -4.2879 | 303.9815 | 44.5 | 49.9391 | -5.4391 |  | 24-03-2026 09:30 | 303.605 | 308.416 | 255.3 | 51.4027 | 50.6636 | 0.73909 | 303.9815 | 45.7 | 49.9391 | -4.2391 |  | 24-03-2026 09:30 | 197.244 | 200.045 | 187.4 | 33.3408 | 37.5286 | -4.1877 | 225.1715 | 33.8 | 36.9919 | -3.1919 |  | 24-03-2026 09:30 | 216.44 | 219.469 | 189.2 | 36.5782 | 37.5286 | -0.95041 | 225.1715 | 33.9 | 36.9919 | -3.0919 |  | 24-03-2026 09:30 | 194.81 | 197.536 | 188.6 | 32.9227 | 37.5286 | -4.6059 | 225.1715 | 33.7 | 36.9919 | -3.2919 |  | 24-03-2026 09:30 | 206.843 | 210.704 | 190.2 | 35.1173 | 37.5286 | -2.4112 | 225.1715 | 33.6 | 36.9919 | -3.3919 |  | 24-03-2026 09:30 | 207.191 | 210.154 | 180.6 | 35.0257 | 35.7038 | -0.67813 | 214.2228 | 31.9 | 35.1932 | -3.2932 |  | 24-03-2026 09:30 | 317.3532 | 388.4724 | -71.1192 | 2330.8345 | 302.5 | 382.9173 | -80.4173 | 14.8532
24-03-2026 09:20 | 759 | 52.52 | 275.374 | 279.284 | 208.9 | 46.5473 | 44.5522 | 1.9952 | 267.3129 | 23.1 | 43.9151 | -20.8151 |  | 24-03-2026 09:20 | 146.294 | 148.191 | 208.3 | 24.6985 | 44.5522 | -19.8537 | 267.3129 | 22.2 | 43.9151 | -21.7151 |  | 24-03-2026 09:20 | 252.536 | 260.646 | 206.6 | 43.441 | 44.5522 | -1.1112 | 267.3129 | 24 | 43.9151 | -19.9151 |  | 24-03-2026 09:20 | 287.774 | 291.979 | 209.6 | 48.6632 | 44.5522 | 4.111 | 267.3129 | 24.5 | 43.9151 | -19.4151 |  | 24-03-2026 09:20 | 195.721 | 198.339 | 153.6 | 33.0565 | 33.0016 | 0.054903 | 198.0096 | 18 | 32.5297 | -14.5297 |  | 24-03-2026 09:20 | 210.709 | 213.484 | 155.3 | 35.5807 | 33.0016 | 2.5791 | 198.0096 | 18.5 | 32.5297 | -14.0297 |  | 24-03-2026 09:20 | 205.664 | 208.675 | 154.9 | 34.7792 | 33.0016 | 1.7776 | 198.0096 | 18.4 | 32.5297 | -14.1297 |  | 24-03-2026 09:20 | 207.51 | 212.183 | 156.6 | 35.3638 | 33.0016 | 2.3622 | 198.0096 | 19 | 32.5297 | -13.5297 |  | 24-03-2026 09:20 | 203.357 | 206.056 | 148.7 | 34.3427 | 31.3969 | 2.9457 | 188.3816 | 18 | 30.948 | -12.948 |  | 24-03-2026 09:20 | 336.4728 | 341.6119 | -5.1391 | 2049.6716 | 185.7 | 336.7269 | -151.0269 | 150.7728
24-03-2026 09:10 | 371 | 52.81 | 133.003 | 134.7 | 185.8 | 22.45 | 21.7527 | 0.69732 | 130.5161 | 27.5 | 21.4416 | 6.0584 |  | 24-03-2026 09:10 | 204.964 | 207.664 | 186.1 | 34.6107 | 21.7527 | 12.858 | 130.5161 | 27.9 | 21.4416 | 6.4584 |  | 24-03-2026 09:10 | 131.364 | 133.748 | 182.6 | 22.2913 | 21.7527 | 0.53865 | 130.5161 | 26.7 | 21.4416 | 5.2584 |  | 24-03-2026 09:10 | 134.324 | 136.066 | 185.1 | 22.6777 | 21.7527 | 0.92499 | 130.5161 | 26.7 | 21.4416 | 5.2584 |  | 24-03-2026 09:10 | 98.422 | 99.455 | 135.6 | 16.5758 | 16.1131 | 0.46274 | 96.6786 | 19.8 | 15.8827 | 3.9173 |  | 24-03-2026 09:10 | 98.333 | 99.715 | 136.8 | 16.6192 | 16.1131 | 0.50607 | 96.6786 | 19.6 | 15.8827 | 3.7173 |  | 24-03-2026 09:10 | 98.175 | 99.398 | 136.5 | 16.5663 | 16.1131 | 0.45324 | 96.6786 | 19.5 | 15.8827 | 3.6173 |  | 24-03-2026 09:10 | 99.209 | 102.993 | 137.6 | 17.1655 | 16.1131 | 1.0524 | 96.6786 | 19.5 | 15.8827 | 3.6173 |  | 24-03-2026 09:10 | 93.709 | 94.895 | 130.7 | 15.8158 | 15.3296 | 0.48622 | 91.9777 | 18.8 | 15.1104 | 3.6896 |  | 24-03-2026 09:10 | 184.7723 | 166.7927 | 17.9796 | 1000.7564 | 206 | 164.4076 | 41.5924 | -21.2277
24-03-2026 09:00 | 530 | 52.52 | 226.898 | 229.91 | 158.3 | 38.3183 | 31.1102 | 7.2081 | 186.6612 | 23.2 | 30.6653 | -7.4653 |  | 24-03-2026 09:00 | 168.05 | 175.698 | 158.2 | 29.283 | 31.1102 | -1.8272 | 186.6612 | 24 | 30.6653 | -6.6653 |  | 24-03-2026 09:00 | 169.39 | 171.534 | 155.9 | 28.589 | 31.1102 | -2.5212 | 186.6612 | 23.4 | 30.6653 | -7.2653 |  | 24-03-2026 09:00 | 182.035 | 184.339 | 158.4 | 30.7232 | 31.1102 | -0.38703 | 186.6612 | 23.9 | 30.6653 | -6.7653 |  | 24-03-2026 09:00 | 113.952 | 115.371 | 115.8 | 19.2285 | 23.0446 | -3.8161 | 138.2676 | 17.5 | 22.7151 | -5.2151 |  | 24-03-2026 09:00 | 120.799 | 122.279 | 117.2 | 20.3798 | 23.0446 | -2.6648 | 138.2676 | 17.8 | 22.7151 | -4.9151 |  | 24-03-2026 09:00 | 109.451 | 110.814 | 117 | 18.469 | 23.0446 | -4.5756 | 138.2676 | 17.9 | 22.7151 | -4.8151 |  | 24-03-2026 09:00 | 110.56 | 112.444 | 118.1 | 18.7407 | 23.0446 | -4.3039 | 138.2676 | 18 | 22.7151 | -4.7151 |  | 24-03-2026 09:00 | 127.186 | 128.731 | 111.9 | 21.4552 | 21.9241 | -0.46891 | 131.5445 | 16.9 | 21.6106 | -4.7106 |  | 24-03-2026 09:00 | 225.1867 | 238.5433 | -13.3566 | 1431.2595 | 182.6 | 235.1321 | -52.5321 | 42.5867
24-03-2026 08:50 | 493 | 50.8 | 197.562 | 200.063 | 135.1 | 33.3438 | 29.1311 | 4.2127 | 174.7868 | 21.9 | 28.7146 | -6.8146 |  | 24-03-2026 08:50 | 226.755 | 229.695 | 134.2 | 38.2825 | 29.1311 | 9.1514 | 174.7868 | 21.5 | 28.7146 | -7.2146 |  | 24-03-2026 08:50 | 182.167 | 185.755 | 132.5 | 30.9592 | 29.1311 | 1.828 | 174.7868 | 21.6 | 28.7146 | -7.1146 |  | 24-03-2026 08:50 | 173.364 | 175.558 | 134.5 | 29.2597 | 29.1311 | 0.12853 | 174.7868 | 22.3 | 28.7146 | -6.4146 |  | 24-03-2026 08:50 | 129.146 | 130.5 | 98.3 | 21.75 | 21.5786 | 0.17138 | 129.4717 | 16.4 | 21.27 | -4.87 |  | 24-03-2026 08:50 | 139.81 | 141.522 | 99.4 | 23.587 | 21.5786 | 2.0084 | 129.4717 | 16.5 | 21.27 | -4.77 |  | 24-03-2026 08:50 | 124.905 | 126.422 | 99.1 | 21.0703 | 21.5786 | -0.50828 | 129.4717 | 16.2 | 21.27 | -5.07 |  | 24-03-2026 08:50 | 125.825 | 128.791 | 100.1 | 21.4652 | 21.5786 | -0.11345 | 129.4717 | 16.2 | 21.27 | -5.07 |  | 24-03-2026 08:50 | 124.552 | 126.078 | 95 | 21.013 | 20.5294 | 0.48362 | 123.1763 | 15.5 | 20.2358 | -4.7358 |  | 24-03-2026 08:50 | 240.7307 | 223.3684 | 17.3623 | 1340.2103 | 168.1 | 220.1742 | -52.0742 | 72.6307
24-03-2026 08:40 | 247 | 47.64 | 91.702 | 92.797 | 113.2 | 15.4662 | 14.7726 | 0.69361 | 88.6353 | 14.6 | 14.5613 | 0.038691 |  | 24-03-2026 08:40 | 89.177 | 88.205 | 112.7 | 14.7008 | 14.7726 | -0.071724 | 88.6353 | 14.7 | 14.5613 | 0.13869 |  | 24-03-2026 08:40 | 88.986 | 90.631 | 110.9 | 15.1052 | 14.7726 | 0.33261 | 88.6353 | 14.5 | 14.5613 | -0.061309 |  | 24-03-2026 08:40 | 88.042 | 89.027 | 112.2 | 14.8378 | 14.7726 | 0.065276 | 88.6353 | 14.5 | 14.5613 | -0.061309 |  | 24-03-2026 08:40 | 65.047 | 65.917 | 81.9 | 10.9862 | 10.9426 | 0.043532 | 65.6558 | 10.6 | 10.7862 | -0.18616 |  | 24-03-2026 08:40 | 65.529 | 66.392 | 82.9 | 11.0653 | 10.9426 | 0.1227 | 65.6558 | 10.8 | 10.7862 | 0.013845 |  | 24-03-2026 08:40 | 65.24 | 66.119 | 82.9 | 11.0198 | 10.9426 | 0.077199 | 65.6558 | 10.9 | 10.7862 | 0.11384 |  | 24-03-2026 08:40 | 65.215 | 67.213 | 83.9 | 11.2022 | 10.9426 | 0.25953 | 65.6558 | 10.8 | 10.7862 | 0.013845 |  | 24-03-2026 08:40 | 62.521 | 63.37 | 79.5 | 10.5617 | 10.4106 | 0.15111 | 62.4634 | 10.4 | 10.2617 | 0.13831 |  | 24-03-2026 08:40 | 114.9452 | 113.2713 | 1.6738 | 679.628 | 111.8 | 111.6515 | 0.14845 | 3.1452
24-03-2026 08:30 | 313 | 49.65 | 108.627 | 109.924 | 98.6 | 18.3207 | 18.5769 | -0.25619 | 111.4611 | 20.3 | 18.3112 | 1.9888 |  | 24-03-2026 08:30 | 113.001 | 114.328 | 98 | 19.0547 | 18.5769 | 0.47781 | 111.4611 | 20.4 | 18.3112 | 2.0888 |  | 24-03-2026 08:30 | 111.185 | 112.905 | 96.4 | 18.8175 | 18.5769 | 0.24065 | 111.4611 | 20 | 18.3112 | 1.6888 |  | 24-03-2026 08:30 | 112.139 | 113.513 | 97.7 | 18.9188 | 18.5769 | 0.34198 | 111.4611 | 20.4 | 18.3112 | 2.0888 |  | 24-03-2026 08:30 | 82.956 | 83.989 | 71.3 | 13.9982 | 13.7606 | 0.23754 | 82.5638 | 15 | 13.5639 | 1.4361 |  | 24-03-2026 08:30 | 83.055 | 84.072 | 72.1 | 14.012 | 13.7606 | 0.25137 | 82.5638 | 15.2 | 13.5639 | 1.6361 |  | 24-03-2026 08:30 | 83.065 | 84.099 | 72 | 14.0165 | 13.7606 | 0.25587 | 82.5638 | 14.8 | 13.5639 | 1.2361 |  | 24-03-2026 08:30 | 83.338 | 85.54 | 73.1 | 14.2567 | 13.7606 | 0.49604 | 82.5638 | 15.1 | 13.5639 | 1.5361 |  | 24-03-2026 08:30 | 79.537 | 80.544 | 69.1 | 13.424 | 13.0915 | 0.33246 | 78.5492 | 14.2 | 12.9043 | 1.2957 |  | 24-03-2026 08:30 | 144.819 | 142.4415 | 2.3775 | 854.6488 | 155.4 | 140.4046 | 14.9954 | -10.581
24-03-2026 08:20 | 409 | 45.92 | 141.258 | 142.93 | 78.3 | 23.8217 | 24.6214 | -0.7997 | 147.7282 | 20.4 | 24.2693 | -3.8693 |  | 24-03-2026 08:20 | 143.47 | 145.198 | 77.6 | 24.1997 | 24.6214 | -0.4217 | 147.7282 | 20.5 | 24.2693 | -3.7693 |  | 24-03-2026 08:20 | 141.092 | 143.24 | 76.4 | 23.8733 | 24.6214 | -0.74804 | 147.7282 | 20.2 | 24.2693 | -4.0693 |  | 24-03-2026 08:20 | 143.867 | 145.585 | 77.3 | 24.2642 | 24.6214 | -0.3572 | 147.7282 | 20.4 | 24.2693 | -3.8693 |  | 24-03-2026 08:20 | 105.378 | 106.604 | 56.3 | 17.7673 | 18.2381 | -0.47072 | 109.4283 | 15 | 17.9772 | -2.9772 |  | 24-03-2026 08:20 | 107.412 | 108.64 | 56.9 | 18.1067 | 18.2381 | -0.13139 | 109.4283 | 15.2 | 17.9772 | -2.7772 |  | 24-03-2026 08:20 | 106.854 | 108.097 | 57.2 | 18.0162 | 18.2381 | -0.22189 | 109.4283 | 15.1 | 17.9772 | -2.8772 |  | 24-03-2026 08:20 | 107.058 | 109.851 | 58 | 18.3085 | 18.2381 | 0.070447 | 109.4283 | 15.2 | 17.9772 | -2.7772 |  | 24-03-2026 08:20 | 102.585 | 103.768 | 54.9 | 17.2947 | 17.3512 | -0.056582 | 104.1075 | 14.4 | 17.1031 | -2.7031 |  | 24-03-2026 08:20 | 185.6522 | 188.7889 | -3.1368 | 1132.7337 | 156.4 | 186.0893 | -29.6893 | 29.2522
24-03-2026 08:10 | 319 | 41.61 | 109.675 | 110.845 | 57.9 | 18.4742 | 19.516 | -1.0419 | 117.0962 | 16.1 | 19.237 | -3.137 |  | 24-03-2026 08:10 | 108.186 | 111.097 | 57.1 | 18.5162 | 19.516 | -0.99987 | 117.0962 | 15.9 | 19.237 | -3.337 |  | 24-03-2026 08:10 | 107.831 | 109.304 | 56.2 | 18.2173 | 19.516 | -1.2987 | 117.0962 | 15.6 | 19.237 | -3.637 |  | 24-03-2026 08:10 | 109.586 | 110.827 | 56.9 | 18.4712 | 19.516 | -1.0449 | 117.0962 | 16.1 | 19.237 | -3.137 |  | 24-03-2026 08:10 | 80.014 | 80.961 | 41.3 | 13.4935 | 14.4563 | -0.96282 | 86.7379 | 11.7 | 14.2496 | -2.5496 |  | 24-03-2026 08:10 | 81.728 | 82.623 | 41.7 | 13.7705 | 14.4563 | -0.68582 | 86.7379 | 11.9 | 14.2496 | -2.3496 |  | 24-03-2026 08:10 | 80.685 | 81.624 | 42.1 | 13.604 | 14.4563 | -0.85232 | 86.7379 | 11.9 | 14.2496 | -2.3496 |  | 24-03-2026 08:10 | 82.033 | 84.165 | 42.8 | 14.0275 | 14.4563 | -0.42882 | 86.7379 | 12.1 | 14.2496 | -2.1496 |  | 24-03-2026 08:10 | 77.753 | 78.673 | 40.5 | 13.1122 | 13.7534 | -0.64123 | 82.5204 | 11.4 | 13.5567 | -2.1567 |  | 24-03-2026 08:10 | 141.6865 | 149.6428 | -7.9563 | 897.857 | 122.7 | 147.5029 | -24.8029 | 18.9865
24-03-2026 08:00 | 228 | 35.3 | 73.038 | 73.888 | 41.8 | 12.3147 | 14.2758 | -1.9612 | 85.655 | 11.9 | 14.0717 | -2.1717 |  | 24-03-2026 08:00 | 77.533 | 78.451 | 41.2 | 13.0752 | 14.2758 | -1.2007 | 85.655 | 12.3 | 14.0717 | -1.7717 |  | 24-03-2026 08:00 | 72.58 | 76.986 | 40.6 | 12.831 | 14.2758 | -1.4448 | 85.655 | 11.7 | 14.0717 | -2.3717 |  | 24-03-2026 08:00 | 76.163 | 77.065 | 40.8 | 12.8442 | 14.2758 | -1.4317 | 85.655 | 11.7 | 14.0717 | -2.3717 |  | 24-03-2026 08:00 | 56.172 | 57.018 | 29.6 | 9.503 | 10.5747 | -1.0717 | 63.4482 | 8.6 | 10.4235 | -1.8235 |  | 24-03-2026 08:00 | 57.13 | 57.859 | 29.8 | 9.6432 | 10.5747 | -0.93153 | 63.4482 | 8.7 | 10.4235 | -1.7235 |  | 24-03-2026 08:00 | 56.438 | 57.187 | 30.2 | 9.5312 | 10.5747 | -1.0435 | 63.4482 | 8.6 | 10.4235 | -1.8235 |  | 24-03-2026 08:00 | 57.993 | 59.605 | 30.7 | 9.9342 | 10.5747 | -0.64053 | 63.4482 | 8.9 | 10.4235 | -1.5235 |  | 24-03-2026 08:00 | 54.935 | 55.675 | 29.1 | 9.2792 | 10.0605 | -0.78135 | 60.3631 | 8.4 | 9.9166 | -1.5166 |  | 24-03-2026 08:00 | 98.9557 | 109.4626 | -10.507 | 656.7759 | 90.8 | 107.8973 | -17.0973 | 8.1557
24-03-2026 07:50 | 205 | 27.55 | 67.463 | 68.234 | 29.9 | 11.3723 | 13.1969 | -1.8246 | 79.1815 | 9.8 | 13.0082 | -3.2082 |  | 24-03-2026 07:50 | 66.624 | 67.726 | 28.9 | 11.2877 | 13.1969 | -1.9093 | 79.1815 | 9.6 | 13.0082 | -3.4082 |  | 24-03-2026 07:50 | 66.217 | 66.931 | 28.9 | 11.1552 | 13.1969 | -2.0418 | 79.1815 | 9.8 | 13.0082 | -3.2082 |  | 24-03-2026 07:50 | 67.16 | 67.962 | 29.1 | 11.327 | 13.1969 | -1.8699 | 79.1815 | 10 | 13.0082 | -3.0082 |  | 24-03-2026 07:50 | 48.859 | 49.553 | 21 | 8.2588 | 9.7755 | -1.5167 | 58.653 | 7.2 | 9.6357 | -2.4357 |  | 24-03-2026 07:50 | 49.991 | 50.665 | 21.1 | 8.4442 | 9.7755 | -1.3313 | 58.653 | 7.5 | 9.6357 | -2.1357 |  | 24-03-2026 07:50 | 49.887 | 50.58 | 21.6 | 8.43 | 9.7755 | -1.3455 | 58.653 | 7.5 | 9.6357 | -2.1357 |  | 24-03-2026 07:50 | 50.437 | 51.961 | 21.8 | 8.6602 | 9.7755 | -1.1153 | 58.653 | 7.4 | 9.6357 | -2.2357 |  | 24-03-2026 07:50 | 47.857 | 48.541 | 20.7 | 8.0902 | 9.3002 | -1.21 | 55.8011 | 7.1 | 9.1672 | -2.0672 |  | 24-03-2026 07:50 | 87.0255 | 101.1899 | -14.1644 | 607.1391 | 75.9 | 99.7428 | -23.8428 | 11.1255
24-03-2026 07:40 | 163 | 23.25 | 51.915 | 52.583 | 20.1 | 8.7638 | 10.6525 | -1.8887 | 63.915 | 7.8 | 10.5002 | -2.7002 |  | 24-03-2026 07:40 | 49.928 | 50.601 | 19.3 | 8.4335 | 10.6525 | -2.219 | 63.915 | 7.4 | 10.5002 | -3.1002 |  | 24-03-2026 07:40 | 50.737 | 51.437 | 19.1 | 8.5728 | 10.6525 | -2.0797 | 63.915 | 7.3 | 10.5002 | -3.2002 |  | 24-03-2026 07:40 | 51.419 | 52.117 | 19.1 | 8.6862 | 10.6525 | -1.9663 | 63.915 | 7.4 | 10.5002 | -3.1002 |  | 24-03-2026 07:40 | 37.166 | 37.747 | 13.8 | 6.2912 | 7.8907 | -1.5996 | 47.3445 | 5.4 | 7.7779 | -2.3779 |  | 24-03-2026 07:40 | 38.275 | 38.85 | 13.6 | 6.475 | 7.8907 | -1.4157 | 47.3445 | 5.4 | 7.7779 | -2.3779 |  | 24-03-2026 07:40 | 38.064 | 38.655 | 14.1 | 6.4425 | 7.8907 | -1.4482 | 47.3445 | 5.4 | 7.7779 | -2.3779 |  | 24-03-2026 07:40 | 38.642 | 39.837 | 14.4 | 6.6395 | 7.8907 | -1.2512 | 47.3445 | 5.6 | 7.7779 | -2.1779 |  | 24-03-2026 07:40 | 36.68 | 37.254 | 13.6 | 6.209 | 7.5071 | -1.2981 | 45.0424 | 5.2 | 7.3997 | -2.1997 |  | 24-03-2026 07:40 | 66.5135 | 81.6801 | -15.1666 | 490.0805 | 56.9 | 80.5121 | -23.6121 | 9.6135
24-03-2026 07:30 | 122 | 21.52 | 37.716 | 38.298 | 12.3 | 6.383 | 8.021 | -1.638 | 48.1261 | 5.2 | 7.9063 | -2.7063 |  | 24-03-2026 07:30 | 36.097 | 36.68 | 11.9 | 6.1133 | 8.021 | -1.9077 | 48.1261 | 5.3 | 7.9063 | -2.6063 |  | 24-03-2026 07:30 | 36.88 | 37.438 | 11.8 | 6.2397 | 8.021 | -1.7814 | 48.1261 | 5.2 | 7.9063 | -2.7063 |  | 24-03-2026 07:30 | 37.356 | 37.936 | 11.7 | 6.3227 | 8.021 | -1.6984 | 48.1261 | 5.2 | 7.9063 | -2.7063 |  | 24-03-2026 07:30 | 26.995 | 27.595 | 8.4 | 4.5992 | 5.9415 | -1.3423 | 35.649 | 3.7 | 5.8565 | -2.1565 |  | 24-03-2026 07:30 | 26.512 | 26.99 | 8.2 | 4.4983 | 5.9415 | -1.4432 | 35.649 | 3.7 | 5.8565 | -2.1565 |  | 24-03-2026 07:30 | 27.748 | 28.242 | 8.7 | 4.707 | 5.9415 | -1.2345 | 35.649 | 3.9 | 5.8565 | -1.9565 |  | 24-03-2026 07:30 | 28.266 | 29.171 | 8.8 | 4.8618 | 5.9415 | -1.0797 | 35.649 | 3.9 | 5.8565 | -1.9565 |  | 24-03-2026 07:30 | 26.356 | 26.867 | 8.4 | 4.4778 | 5.6526 | -1.1748 | 33.9156 | 3.7 | 5.5718 | -1.8718 |  | 24-03-2026 07:30 | 48.2028 | 61.5027 | -13.2999 | 369.0162 | 39.8 | 60.6232 | -20.8232 | 8.4028
24-03-2026 07:20 | 85 | 20.66 | 26.533 | 27.017 | 7.1 | 4.5028 | 5.605 | -1.1022 | 33.6302 | 3.6 | 5.5249 | -1.9249 |  | 24-03-2026 07:20 | 24.689 | 26.552 | 6.6 | 4.4253 | 5.605 | -1.1797 | 33.6302 | 3.5 | 5.5249 | -2.0249 |  | 24-03-2026 07:20 | 25.806 | 26.308 | 6.6 | 4.3847 | 5.605 | -1.2204 | 33.6302 | 3.5 | 5.5249 | -2.0249 |  | 24-03-2026 07:20 | 25.643 | 26.212 | 6.5 | 4.3687 | 5.605 | -1.2364 | 33.6302 | 3.5 | 5.5249 | -2.0249 |  | 24-03-2026 07:20 | 18.569 | 19.127 | 4.7 | 3.1878 | 4.1519 | -0.96405 | 24.9113 | 2.5 | 4.0925 | -1.5925 |  | 24-03-2026 07:20 | 18.249 | 18.582 | 4.5 | 3.097 | 4.1519 | -1.0549 | 24.9113 | 2.4 | 4.0925 | -1.6925 |  | 24-03-2026 07:20 | 19.121 | 19.551 | 4.8 | 3.2585 | 4.1519 | -0.89338 | 24.9113 | 2.6 | 4.0925 | -1.4925 |  | 24-03-2026 07:20 | 19.545 | 20.259 | 4.9 | 3.3765 | 4.1519 | -0.77538 | 24.9113 | 2.7 | 4.0925 | -1.3925 |  | 24-03-2026 07:20 | 17.971 | 18.387 | 4.7 | 3.0645 | 3.95 | -0.8855 | 23.7 | 2.4 | 3.8935 | -1.4935 |  | 24-03-2026 07:20 | 33.6658 | 42.9777 | -9.3118 | 257.866 | 26.7 | 42.3631 | -15.6631 | 6.9658
24-03-2026 07:10 | 40 | 19.23 | 17.101 | 17.511 | 3.5 | 2.9185 | 2.6507 | 0.26783 | 15.904 | 2.2 | 2.6128 | -0.41276 |  | 24-03-2026 07:10 | 16.663 | 17.158 | 3.1 | 2.8597 | 2.6507 | 0.209 | 15.904 | 2.1 | 2.6128 | -0.51276 |  | 24-03-2026 07:10 | 16.636 | 17.045 | 3.1 | 2.8408 | 2.6507 | 0.19016 | 15.904 | 2.1 | 2.6128 | -0.51276 |  | 24-03-2026 07:10 | 16.154 | 16.77 | 3 | 2.795 | 2.6507 | 0.14433 | 15.904 | 2 | 2.6128 | -0.61276 |  | 24-03-2026 07:10 | 11.784 | 12.366 | 2.2 | 2.061 | 1.9635 | 0.097542 | 11.7807 | 1.5 | 1.9354 | -0.43538 |  | 24-03-2026 07:10 | 11.423 | 11.781 | 2.1 | 1.9635 | 1.9635 | 4.1681e-05 | 11.7807 | 1.5 | 1.9354 | -0.43538 |  | 24-03-2026 07:10 | 12.08 | 12.451 | 2.2 | 2.0752 | 1.9635 | 0.11171 | 11.7807 | 1.5 | 1.9354 | -0.43538 |  | 24-03-2026 07:10 | 12.267 | 13.064 | 2.2 | 2.1773 | 1.9635 | 0.21388 | 11.7807 | 1.5 | 1.9354 | -0.43538 |  | 24-03-2026 07:10 | 11.205 | 11.569 | 2.3 | 1.9282 | 1.868 | 0.060179 | 11.2079 | 1.5 | 1.8413 | -0.34128 |  | 24-03-2026 07:10 | 21.6192 | 20.3245 | 1.2947 | 121.947 | 15.9 | 20.0339 | -4.1339 | 5.7192
24-03-2026 07:00 | 23 | 18.37 | 9.253 | 9.573 | 1.3 | 1.5955 | 1.5286 | 0.066869 | 9.1718 | 1.3 | 1.5068 | -0.20677 |  | 24-03-2026 07:00 | 8.947 | 9.541 | 1 | 1.5902 | 1.5286 | 0.061535 | 9.1718 | 1 | 1.5068 | -0.50677 |  | 24-03-2026 07:00 | 9.149 | 9.487 | 1 | 1.5812 | 1.5286 | 0.052535 | 9.1718 | 1 | 1.5068 | -0.50677 |  | 24-03-2026 07:00 | 8.927 | 9.742 | 1 | 1.6237 | 1.5286 | 0.095035 | 9.1718 | 1 | 1.5068 | -0.50677 |  | 24-03-2026 07:00 | 6.6 | 7.31 | 0.7 | 1.2183 | 1.1323 | 0.086014 | 6.7939 | 0.7 | 1.1161 | -0.41613 |  | 24-03-2026 07:00 | 6.282 | 6.54 | 0.6 | 1.09 | 1.1323 | -0.04232 | 6.7939 | 0.6 | 1.1161 | -0.51613 |  | 24-03-2026 07:00 | 6.649 | 6.922 | 0.7 | 1.1537 | 1.1323 | 0.021347 | 6.7939 | 0.7 | 1.1161 | -0.41613 |  | 24-03-2026 07:00 | 6.747 | 7.256 | 0.7 | 1.2093 | 1.1323 | 0.077014 | 6.7939 | 0.7 | 1.1161 | -0.41613 |  | 24-03-2026 07:00 | 6.124 | 6.386 | 0.8 | 1.0643 | 1.0773 | -0.012928 | 6.4636 | 0.8 | 1.0619 | -0.26186 |  | 24-03-2026 07:00 | 12.1262 | 11.7211 | 0.4051 | 70.3264 | 7.8 | 11.5535 | -3.7535 | 4.3262
[110 empty] | Total: - | 16948.7708 | 18694.5538 | -1745.783 |  | 16231.6 | 18427.2217 | -2195.6217 | 717.1708
Sum:- | 41295 |  | 13154.624 |  | 83884.7 |  |  |  |  | 2122.9 | 2403.2311 | -280.3311 | 0.98846 |  | 12325.85 |  | 81912.8 |  |  |  |  | 2135.3 | 2403.2311 | -267.9311 | 0.9795 |  | 13031.23 |  | 83258.9 |  |  |  |  | 2088.2 | 2403.2311 | -315.0311 | 0.97375 |  | 13349.426 |  | 84311 |  |  |  |  | 2113.3 | 2403.2311 | -289.9311 | 0.98411 |  | 9679.593 |  | 62846 |  |  |  |  | 1577.3 | 1780.1712 | -202.8712 | 0.98203 |  | 9856.092 |  | 62766.2 |  |  |  |  | 1572 | 1780.1712 | -208.1712 | 0.98258 |  | 9604.691 |  | 62336.4 |  |  |  |  | 1560.6 | 1780.1712 | -219.5712 | 0.98136 |  | 9599.479 |  | 62833.7 |  |  |  |  | 1570.8 | 1780.1712 | -209.3712 | 0.97042 |  | 9231.771 |  | 59619.7 |  |  |  |  | 1491.2 | 1693.6124 | -202.4124 | 0.9852

## 25 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
25-03-2026 19:00 | 0 | 39.61 | 0.018 | 0.088 | 2045.9 | 0.014667 | 0 | 0.014667 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.078 | 0.424 | 2066.5 | 0.070667 | 0 | 0.070667 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.001 | 0.056 | 2033.5 | 0.0093333 | 0 | 0.0093333 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.085 | 0.485 | 2045.8 | 0.080833 | 0 | 0.080833 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.074 | 0.085 | 1527.3 | 0.014167 | 0 | 0.014167 | 0 | 0 | 0 | 0 |  | 25-03-2026 19:00 | 0.05 | 0.066 | 1511 | 0.011 | 0 | 0.011 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.064 | 0.067 | 1510.4 | 0.011167 | 0 | 0.011167 | 0 | 0 | 0 | 0 |  | 25-03-2026 19:00 | 0.057 | 0.089 | 1516.1 | 0.014833 | 0 | 0.014833 | 0 | 0.1 | 0 | 0.1 |  | 25-03-2026 19:00 | 0.051 | 0.08 | 1435.3 | 0.013333 | 0 | 0.013333 | 0 | 0 | 0 | 0 |  | 25-03-2026 19:00 | 0.24 | 0 | 0.24 | 0 | 0.6 | 0 | 0.6 | 0.36 | 1 | 99.2%
25-03-2026 18:50 | 1 | 40.47 | 1.388 | 1.459 | 2045.8 | 0.24317 | 0.061438 | 0.18173 | 0.36863 | 0.4 | 0.060559 | 0.33944 |  | 25-03-2026 18:50 | 1.719 | 1.925 | 2066.4 | 0.32083 | 0.061438 | 0.2594 | 0.36863 | 0.4 | 0.060559 | 0.33944 |  | 25-03-2026 18:50 | 1.244 | 1.308 | 2033.4 | 0.218 | 0.061438 | 0.15656 | 0.36863 | 0.5 | 0.060559 | 0.43944 |  | 25-03-2026 18:50 | 1.301 | 1.714 | 2045.7 | 0.28567 | 0.061438 | 0.22423 | 0.36863 | 0.5 | 0.060559 | 0.43944 |  | 25-03-2026 18:50 | 0.789 | 0.908 | 1527.3 | 0.15133 | 0.04551 | 0.10582 | 0.27306 | 0.3 | 0.044859 | 0.25514 |  | 25-03-2026 18:50 | 0.779 | 0.819 | 1510.9 | 0.1365 | 0.04551 | 0.09099 | 0.27306 | 0.2 | 0.044859 | 0.15514 |  | 25-03-2026 18:50 | 0.747 | 0.785 | 1510.4 | 0.13083 | 0.04551 | 0.085324 | 0.27306 | 0.3 | 0.044859 | 0.25514 |  | 25-03-2026 18:50 | 0.857 | 1.02 | 1516 | 0.17 | 0.04551 | 0.12449 | 0.27306 | 0.3 | 0.044859 | 0.25514 |  | 25-03-2026 18:50 | 0.694 | 0.731 | 1435.3 | 0.12183 | 0.043297 | 0.078537 | 0.25978 | 0.3 | 0.042678 | 0.25732 |  | 25-03-2026 18:50 | 1.7782 | 0.47109 | 1.3071 | 2.8265 | 3.2 | 0.46435 | 2.7356 | 1.4218 | 2 | 99.64%
25-03-2026 18:40 | 8 | 41.9 | 4.286 | 4.423 | 2045.4 | 0.73717 | 0.4889 | 0.24826 | 2.9334 | 1.1 | 0.48191 | 0.61809 |  | 25-03-2026 18:40 | 4.67 | 5.101 | 2066 | 0.85017 | 0.4889 | 0.36126 | 2.9334 | 1.1 | 0.48191 | 0.61809 |  | 25-03-2026 18:40 | 4.209 | 4.42 | 2032.9 | 0.73667 | 0.4889 | 0.24776 | 2.9334 | 1 | 0.48191 | 0.51809 |  | 25-03-2026 18:40 | 4.272 | 4.866 | 2045.2 | 0.811 | 0.4889 | 0.3221 | 2.9334 | 1 | 0.48191 | 0.51809 |  | 25-03-2026 18:40 | 2.937 | 3.126 | 1527 | 0.521 | 0.36215 | 0.15885 | 2.1729 | 0.8 | 0.35697 | 0.44303 |  | 25-03-2026 18:40 | 2.867 | 3.014 | 1510.7 | 0.50233 | 0.36215 | 0.14018 | 2.1729 | 0.7 | 0.35697 | 0.34303 |  | 25-03-2026 18:40 | 2.855 | 3.002 | 1510.1 | 0.50033 | 0.36215 | 0.13818 | 2.1729 | 0.7 | 0.35697 | 0.34303 |  | 25-03-2026 18:40 | 2.879 | 3.118 | 1515.7 | 0.51967 | 0.36215 | 0.15752 | 2.1729 | 0.6 | 0.35697 | 0.24303 |  | 25-03-2026 18:40 | 2.686 | 2.824 | 1435 | 0.47067 | 0.34454 | 0.12613 | 2.0672 | 0.6 | 0.33961 | 0.26039 |  | 25-03-2026 18:40 | 5.649 | 3.7488 | 1.9002 | 22.4925 | 7.6 | 3.6951 | 3.9049 | 1.951 | 3 | 97.53%
25-03-2026 18:30 | 20 | 43.91 | 8.894 | 9.242 | 2044.3 | 1.5403 | 1.2131 | 0.32722 | 7.2787 | 1.9 | 1.1958 | 0.70423 |  | 25-03-2026 18:30 | 9.026 | 9.396 | 2064.9 | 1.566 | 1.2131 | 0.35288 | 7.2787 | 2.1 | 1.1958 | 0.90423 |  | 25-03-2026 18:30 | 8.782 | 9.133 | 2031.9 | 1.5222 | 1.2131 | 0.30905 | 7.2787 | 2 | 1.1958 | 0.80423 |  | 25-03-2026 18:30 | 8.809 | 9.28 | 2044.2 | 1.5467 | 1.2131 | 0.33355 | 7.2787 | 2 | 1.1958 | 0.80423 |  | 25-03-2026 18:30 | 6.438 | 6.757 | 1526.2 | 1.1262 | 0.89861 | 0.22756 | 5.3916 | 1.5 | 0.88576 | 0.61424 |  | 25-03-2026 18:30 | 6.049 | 6.318 | 1510 | 1.053 | 0.89861 | 0.15439 | 5.3916 | 1.5 | 0.88576 | 0.61424 |  | 25-03-2026 18:30 | 5.954 | 6.197 | 1509.4 | 1.0328 | 0.89861 | 0.13423 | 5.3916 | 1.3 | 0.88576 | 0.41424 |  | 25-03-2026 18:30 | 5.551 | 5.869 | 1515.1 | 0.97817 | 0.89861 | 0.079561 | 5.3916 | 1.2 | 0.88576 | 0.31424 |  | 25-03-2026 18:30 | 5.253 | 5.502 | 1434.4 | 0.917 | 0.85491 | 0.062088 | 5.1295 | 1.2 | 0.84269 | 0.35731 |  | 25-03-2026 18:30 | 11.2823 | 9.3018 | 1.9805 | 55.8109 | 14.7 | 9.1688 | 5.5312 | 3.4177 | 4 | 98.46%
25-03-2026 18:20 | 33 | 46.21 | 15.682 | 16.148 | 2042.4 | 2.6913 | 1.9844 | 0.70694 | 11.9063 | 3.4 | 1.956 | 1.444 |  | 25-03-2026 18:20 | 16.15 | 16.581 | 2062.8 | 2.7635 | 1.9844 | 0.77911 | 11.9063 | 3.7 | 1.956 | 1.744 |  | 25-03-2026 18:20 | 15.9 | 16.316 | 2029.9 | 2.7193 | 1.9844 | 0.73494 | 11.9063 | 3.5 | 1.956 | 1.544 |  | 25-03-2026 18:20 | 15.792 | 16.214 | 2042.2 | 2.7023 | 1.9844 | 0.71794 | 11.9063 | 3.5 | 1.956 | 1.544 |  | 25-03-2026 18:20 | 11.85 | 12.242 | 1524.7 | 2.0403 | 1.4699 | 0.57042 | 8.8195 | 2.6 | 1.4489 | 1.1511 |  | 25-03-2026 18:20 | 11.022 | 11.402 | 1508.5 | 1.9003 | 1.4699 | 0.43042 | 8.8195 | 2.4 | 1.4489 | 0.9511 |  | 25-03-2026 18:20 | 10.674 | 11.05 | 1508.1 | 1.8417 | 1.4699 | 0.37175 | 8.8195 | 2.5 | 1.4489 | 1.0511 |  | 25-03-2026 18:20 | 8.287 | 8.678 | 1513.9 | 1.4463 | 1.4699 | -0.023585 | 8.8195 | 1.7 | 1.4489 | 0.2511 |  | 25-03-2026 18:20 | 8.82 | 9.161 | 1433.2 | 1.5268 | 1.3984 | 0.12839 | 8.3907 | 1.9 | 1.3784 | 0.52155 |  | 25-03-2026 18:20 | 19.632 | 15.2157 | 4.4163 | 91.2941 | 25.2 | 14.9981 | 10.2019 | 5.568 | 5 | 98.62%
25-03-2026 18:10 | 47 | 48.5 | 26.337 | 26.225 | 2039 | 4.3708 | 2.8018 | 1.5691 | 16.8107 | 5.5 | 2.7617 | 2.7383 |  | 25-03-2026 18:10 | 27.133 | 27.695 | 2059.1 | 4.6158 | 2.8018 | 1.8141 | 16.8107 | 5.6 | 2.7617 | 2.8383 |  | 25-03-2026 18:10 | 26.495 | 27.041 | 2026.4 | 4.5068 | 2.8018 | 1.7051 | 16.8107 | 5.6 | 2.7617 | 2.8383 |  | 25-03-2026 18:10 | 26.333 | 26.884 | 2038.7 | 4.4807 | 2.8018 | 1.6789 | 16.8107 | 5.5 | 2.7617 | 2.7383 |  | 25-03-2026 18:10 | 19.731 | 20.263 | 1522.1 | 3.3772 | 2.0754 | 1.3018 | 12.4524 | 4.1 | 2.0457 | 2.0543 |  | 25-03-2026 18:10 | 18.739 | 19.2 | 1506.1 | 3.2 | 2.0754 | 1.1246 | 12.4524 | 3.9 | 2.0457 | 1.8543 |  | 25-03-2026 18:10 | 18.652 | 19.107 | 1505.6 | 3.1845 | 2.0754 | 1.1091 | 12.4524 | 3.9 | 2.0457 | 1.8543 |  | 25-03-2026 18:10 | 12.815 | 13.486 | 1512.2 | 2.2477 | 2.0754 | 0.17227 | 12.4524 | 3 | 2.0457 | 0.95428 |  | 25-03-2026 18:10 | 16.282 | 16.701 | 1431.3 | 2.7835 | 1.9745 | 0.80902 | 11.8469 | 3.7 | 1.9462 | 1.7538 |  | 25-03-2026 18:10 | 32.767 | 21.4832 | 11.2838 | 128.8992 | 40.8 | 21.176 | 19.624 | 8.033 | 6 | 98.36%
25-03-2026 18:00 | 62 | 49.65 | 39.642 | 40.303 | 2033.5 | 6.7172 | 3.6798 | 3.0374 | 22.0786 | 7.2 | 3.6271 | 3.5729 |  | 25-03-2026 18:00 | 41.218 | 41.91 | 2053.5 | 6.985 | 3.6798 | 3.3052 | 22.0786 | 7.4 | 3.6271 | 3.7729 |  | 25-03-2026 18:00 | 40.571 | 41.252 | 2020.8 | 6.8753 | 3.6798 | 3.1956 | 22.0786 | 7.5 | 3.6271 | 3.8729 |  | 25-03-2026 18:00 | 40.213 | 40.892 | 2033.2 | 6.8153 | 3.6798 | 3.1356 | 22.0786 | 7.4 | 3.6271 | 3.7729 |  | 25-03-2026 18:00 | 30.289 | 30.828 | 1518 | 5.138 | 2.7257 | 2.4123 | 16.3545 | 5.7 | 2.6868 | 3.0132 |  | 25-03-2026 18:00 | 28.847 | 29.406 | 1502.2 | 4.901 | 2.7257 | 2.1753 | 16.3545 | 5.4 | 2.6868 | 2.7132 |  | 25-03-2026 18:00 | 29.047 | 29.598 | 1501.7 | 4.933 | 2.7257 | 2.2073 | 16.3545 | 5.4 | 2.6868 | 2.7132 |  | 25-03-2026 18:00 | 24.914 | 25.576 | 1509.2 | 4.2627 | 2.7257 | 1.5369 | 16.3545 | 4.9 | 2.6868 | 2.2132 |  | 25-03-2026 18:00 | 27.06 | 27.615 | 1427.6 | 4.6025 | 2.5932 | 2.0093 | 15.5593 | 5 | 2.5561 | 2.4439 |  | 25-03-2026 18:00 | 51.23 | 28.2152 | 23.0148 | 169.2915 | 55.9 | 27.8118 | 28.0882 | 4.67 | 7 | 98.29%
25-03-2026 17:50 | 140 | 50.23 | 45.229 | 45.667 | 2026.3 | 7.6112 | 8.2907 | -0.67951 | 49.744 | 8.6 | 8.1721 | 0.42788 |  | 25-03-2026 17:50 | 46.082 | 46.836 | 2046.1 | 7.806 | 8.2907 | -0.48467 | 49.744 | 20.5 | 8.1721 | 12.3279 |  | 25-03-2026 17:50 | 45.834 | 46.57 | 2013.3 | 7.7617 | 8.2907 | -0.52901 | 49.744 | 8.6 | 8.1721 | 0.42788 |  | 25-03-2026 17:50 | 45.557 | 46.302 | 2025.8 | 7.717 | 8.2907 | -0.57367 | 49.744 | 8.5 | 8.1721 | 0.32788 |  | 25-03-2026 17:50 | 34.515 | 35.13 | 1512.3 | 5.855 | 6.1412 | -0.28624 | 36.8474 | 6.4 | 6.0534 | 0.34658 |  | 25-03-2026 17:50 | 32.767 | 33.357 | 1496.8 | 5.5595 | 6.1412 | -0.58174 | 36.8474 | 6.2 | 6.0534 | 0.14658 |  | 25-03-2026 17:50 | 33.047 | 33.639 | 1496.3 | 5.6065 | 6.1412 | -0.53474 | 36.8474 | 6.2 | 6.0534 | 0.14658 |  | 25-03-2026 17:50 | 32.656 | 33.551 | 1504.3 | 5.5918 | 6.1412 | -0.54941 | 36.8474 | 6.2 | 6.0534 | 0.14658 |  | 25-03-2026 17:50 | 30.794 | 31.355 | 1422.6 | 5.2258 | 5.8426 | -0.6168 | 35.0558 | 5.9 | 5.7591 | 0.14092 |  | 25-03-2026 17:50 | 58.7345 | 63.5703 | -4.8358 | 381.4217 | 77.1 | 62.6612 | 14.4388 | 18.3655 | 8 | 97.2%
25-03-2026 17:40 | 159 | 50.51 | 50.46 | 51.239 | 2017.7 | 8.5398 | 9.4057 | -0.86588 | 56.4343 | 11.4 | 9.2712 | 2.1288 | [5 empty] | 0 | 9.4057 | -9.4057 | 56.4343 | 0 | 9.2712 | -9.2712 |  | 25-03-2026 17:40 | 49.959 | 50.756 | 2004.7 | 8.4593 | 9.4057 | -0.94638 | 56.4343 | 11.6 | 9.2712 | 2.3288 |  | 25-03-2026 17:40 | 49.62 | 50.406 | 2017.3 | 8.401 | 9.4057 | -1.0047 | 56.4343 | 11.5 | 9.2712 | 2.2288 |  | 25-03-2026 17:40 | 37.008 | 37.663 | 1505.9 | 6.2772 | 6.9672 | -0.69003 | 41.8032 | 8.6 | 6.8676 | 1.7324 |  | 25-03-2026 17:40 | 35.95 | 36.59 | 1490.6 | 6.0983 | 6.9672 | -0.86886 | 41.8032 | 8.2 | 6.8676 | 1.3324 |  | 25-03-2026 17:40 | 36.043 | 36.685 | 1490.1 | 6.1142 | 6.9672 | -0.85303 | 41.8032 | 8.3 | 6.8676 | 1.4324 |  | 25-03-2026 17:40 | 35.805 | 36.723 | 1498.1 | 6.1205 | 6.9672 | -0.8467 | 41.8032 | 8.3 | 6.8676 | 1.4324 |  | 25-03-2026 17:40 | 33.969 | 34.581 | 1416.7 | 5.7635 | 6.6284 | -0.86493 | 39.7706 | 7.7 | 6.5336 | 1.1664 |  | 25-03-2026 17:40 | 55.7738 | 72.1201 | -16.3462 | 432.7205 | 75.6 | 71.0888 | 4.5112 | 19.8262 | 9 | 98.54%
25-03-2026 17:30 | 259 | 50.8 | 82.529 | 83.565 | 2006.3 | 13.9275 | 15.3042 | -1.3767 | 91.8251 | 15.2 | 15.0853 | 0.11466 |  | 25-03-2026 17:30 | 83.967 | 85.085 | 2025.6 | 14.1808 | 15.3042 | -1.1234 | 91.8251 | 15 | 15.0853 | -0.085336 |  | 25-03-2026 17:30 | 83.118 | 84.529 | 1993.1 | 14.0882 | 15.3042 | -1.216 | 91.8251 | 15.2 | 15.0853 | 0.11466 |  | 25-03-2026 17:30 | 82.333 | 83.392 | 2005.8 | 13.8987 | 15.3042 | -1.4055 | 91.8251 | 15.1 | 15.0853 | 0.014664 |  | 25-03-2026 17:30 | 62.278 | 63.13 | 1497.3 | 10.5217 | 11.3364 | -0.81477 | 68.0186 | 11.4 | 11.1743 | 0.22568 |  | 25-03-2026 17:30 | 59.817 | 60.648 | 1482.4 | 10.108 | 11.3364 | -1.2284 | 68.0186 | 11 | 11.1743 | -0.17432 |  | 25-03-2026 17:30 | 60.143 | 60.96 | 1481.8 | 10.16 | 11.3364 | -1.1764 | 68.0186 | 11.1 | 11.1743 | -0.074323 |  | 25-03-2026 17:30 | 59.835 | 61.572 | 1489.8 | 10.262 | 11.3364 | -1.0744 | 68.0186 | 10.9 | 11.1743 | -0.27432 |  | 25-03-2026 17:30 | 56.436 | 57.266 | 1409 | 9.5443 | 10.7852 | -1.2409 | 64.7113 | 10.4 | 10.631 | -0.23098 |  | 25-03-2026 17:30 | 106.6912 | 117.3477 | -10.6565 | 704.0862 | 115.3 | 115.6696 | -0.36962 | 8.6088
25-03-2026 17:20 | 301 | 50.51 | 98.497 | 99.703 | 1991.1 | 16.6172 | 17.8058 | -1.1886 | 106.8347 | 17.6 | 17.5512 | 0.048832 |  | 25-03-2026 17:20 | 100.501 | 101.763 | 2010.6 | 16.9605 | 17.8058 | -0.84529 | 106.8347 | 18.4 | 17.5512 | 0.84883 |  | 25-03-2026 17:20 | 98.999 | 100.548 | 1977.9 | 16.758 | 17.8058 | -1.0478 | 106.8347 | 17.8 | 17.5512 | 0.24883 |  | 25-03-2026 17:20 | 98.439 | 99.69 | 1990.7 | 16.615 | 17.8058 | -1.1908 | 106.8347 | 17.7 | 17.5512 | 0.14883 |  | 25-03-2026 17:20 | 74.168 | 75.145 | 1485.9 | 12.5242 | 13.1895 | -0.66531 | 79.1368 | 13.3 | 13.0009 | 0.29914 |  | 25-03-2026 17:20 | 71.583 | 72.533 | 1471.4 | 12.0888 | 13.1895 | -1.1006 | 79.1368 | 12.9 | 13.0009 | -0.10086 |  | 25-03-2026 17:20 | 71.801 | 72.747 | 1470.7 | 12.1245 | 13.1895 | -1.065 | 79.1368 | 12.9 | 13.0009 | -0.10086 |  | 25-03-2026 17:20 | 71.594 | 73.526 | 1478.9 | 12.2543 | 13.1895 | -0.93514 | 79.1368 | 13.1 | 13.0009 | 0.099135 |  | 25-03-2026 17:20 | 67.45 | 68.366 | 1398.6 | 11.3943 | 12.5482 | -1.1538 | 75.2889 | 12.3 | 12.3687 | -0.068713 |  | 25-03-2026 17:20 | 127.3368 | 136.5292 | -9.1924 | 819.1753 | 136 | 134.5768 | 1.4232 | 8.6632
25-03-2026 17:10 | 341 | 50.23 | 113.476 | 114.878 | 1973.5 | 19.1463 | 20.1937 | -1.0474 | 121.1623 | 20.4 | 19.9049 | 0.49506 |  | 25-03-2026 17:10 | 117.167 | 116.467 | 1992.2 | 19.4112 | 20.1937 | -0.78255 | 121.1623 | 20.1 | 19.9049 | 0.19506 |  | 25-03-2026 17:10 | 113.959 | 115.946 | 1960.1 | 19.3243 | 20.1937 | -0.86938 | 121.1623 | 20.1 | 19.9049 | 0.19506 |  | 25-03-2026 17:10 | 113.225 | 114.658 | 1973 | 19.1097 | 20.1937 | -1.084 | 121.1623 | 20.1 | 19.9049 | 0.19506 |  | 25-03-2026 17:10 | 85.292 | 86.389 | 1472.6 | 14.3982 | 14.9583 | -0.56014 | 89.7498 | 15.1 | 14.7444 | 0.3556 |  | 25-03-2026 17:10 | 82.528 | 83.598 | 1458.5 | 13.933 | 14.9583 | -1.0253 | 89.7498 | 14.6 | 14.7444 | -0.1444 |  | 25-03-2026 17:10 | 82.987 | 84.069 | 1457.8 | 14.0115 | 14.9583 | -0.94681 | 89.7498 | 14.7 | 14.7444 | -0.044404 |  | 25-03-2026 17:10 | 82.92 | 85.163 | 1465.8 | 14.1938 | 14.9583 | -0.76447 | 89.7498 | 14.5 | 14.7444 | -0.2444 |  | 25-03-2026 17:10 | 78.102 | 79.161 | 1386.3 | 13.1935 | 14.231 | -1.0375 | 85.3859 | 13.8 | 14.0275 | -0.22747 |  | 25-03-2026 17:10 | 146.7215 | 154.8391 | -8.1176 | 929.0344 | 153.4 | 152.6249 | 0.77513 | 6.6785
25-03-2026 17:00 | 392 | 50.8 | 133.06 | 132.937 | 1953.1 | 22.1562 | 23.1631 | -1.0069 | 138.9786 | 23.2 | 22.8319 | 0.36814 |  | 25-03-2026 17:00 | 132.812 | 134.534 | 1972.1 | 22.4223 | 23.1631 | -0.74076 | 138.9786 | 24.8 | 22.8319 | 1.9681 |  | 25-03-2026 17:00 | 130.966 | 133.485 | 1940 | 22.2475 | 23.1631 | -0.91559 | 138.9786 | 23.9 | 22.8319 | 1.0681 |  | 25-03-2026 17:00 | 131.046 | 132.759 | 1952.9 | 22.1265 | 23.1631 | -1.0366 | 138.9786 | 23.5 | 22.8319 | 0.66814 |  | 25-03-2026 17:00 | 98.161 | 99.404 | 1457.5 | 16.5673 | 17.1578 | -0.59051 | 102.9471 | 17.7 | 16.9125 | 0.78751 |  | 25-03-2026 17:00 | 95.911 | 97.115 | 1443.9 | 16.1858 | 17.1578 | -0.97201 | 102.9471 | 17.2 | 16.9125 | 0.28751 |  | 25-03-2026 17:00 | 95.926 | 97.121 | 1443.1 | 16.1868 | 17.1578 | -0.97101 | 102.9471 | 17.2 | 16.9125 | 0.28751 |  | 25-03-2026 17:00 | 96.504 | 99.334 | 1451.3 | 16.5557 | 17.1578 | -0.60218 | 102.9471 | 17.2 | 16.9125 | 0.28751 |  | 25-03-2026 17:00 | 91.15 | 92.313 | 1372.5 | 15.3855 | 16.3236 | -0.93807 | 97.9414 | 16.1 | 16.0901 | 0.0098615 |  | 25-03-2026 17:00 | 169.8337 | 177.6073 | -7.7737 | 1065.6439 | 180.8 | 175.0675 | 5.7325 | 10.9663
25-03-2026 16:50 | 435 | 51.09 | 147.521 | 149.419 | 1929.9 | 24.9032 | 25.6753 | -0.7721 | 154.0516 | 54.5 | 25.3081 | 29.1919 |  | 25-03-2026 16:50 | 149.887 | 151.861 | 1947.3 | 25.3102 | 25.6753 | -0.3651 | 154.0516 | 25.8 | 25.3081 | 0.49189 |  | 25-03-2026 16:50 | 147.938 | 150.889 | 1916.1 | 25.1482 | 25.6753 | -0.5271 | 154.0516 | 25.5 | 25.3081 | 0.19189 |  | 25-03-2026 16:50 | 147.063 | 149.015 | 1929.4 | 24.8358 | 25.6753 | -0.83943 | 154.0516 | 26.1 | 25.3081 | 0.79189 |  | 25-03-2026 16:50 | 110.631 | 112.054 | 1439.8 | 18.6757 | 19.0187 | -0.34305 | 114.1123 | 19.6 | 18.7467 | 0.85325 |  | 25-03-2026 16:50 | 107.733 | 109.097 | 1426.7 | 18.1828 | 19.0187 | -0.83588 | 114.1123 | 19.1 | 18.7467 | 0.35325 |  | 25-03-2026 16:50 | 108.207 | 109.577 | 1425.9 | 18.2628 | 19.0187 | -0.75588 | 114.1123 | 19.2 | 18.7467 | 0.45325 |  | 25-03-2026 16:50 | 108.081 | 111.119 | 1434.1 | 18.5198 | 19.0187 | -0.49888 | 114.1123 | 19.1 | 18.7467 | 0.35325 |  | 25-03-2026 16:50 | 101.835 | 103.145 | 1356.4 | 17.1908 | 18.0939 | -0.90312 | 108.5637 | 18 | 17.8352 | 0.16479 |  | 25-03-2026 16:50 | 191.0293 | 196.8699 | -5.8405 | 1181.2191 | 226.9 | 194.0546 | 32.8454 | 35.8707
25-03-2026 16:40 | 485 | 51.09 | 165.87 | 168.055 | 1903 | 28.0092 | 28.6264 | -0.61728 | 171.7587 | 0 | 28.2171 | -28.2171 |  | 25-03-2026 16:40 | 169.46 | 169.991 | 1921.5 | 28.3318 | 28.6264 | -0.29461 | 171.7587 | 28.2 | 28.2171 | -0.017084 |  | 25-03-2026 16:40 | 165.18 | 168.606 | 1890.6 | 28.101 | 28.6264 | -0.52544 | 171.7587 | 29.1 | 28.2171 | 0.88292 |  | 25-03-2026 16:40 | 165.129 | 167.372 | 1903.3 | 27.8953 | 28.6264 | -0.73111 | 171.7587 | 28.5 | 28.2171 | 0.28292 |  | 25-03-2026 16:40 | 124.249 | 125.86 | 1420.2 | 20.9767 | 21.2048 | -0.22811 | 127.2286 | 21.5 | 20.9015 | 0.59846 |  | 25-03-2026 16:40 | 121.218 | 122.777 | 1407.6 | 20.4628 | 21.2048 | -0.74194 | 127.2286 | 21.1 | 20.9015 | 0.19846 |  | 25-03-2026 16:40 | 121.523 | 123.074 | 1406.7 | 20.5123 | 21.2048 | -0.69244 | 127.2286 | 21.1 | 20.9015 | 0.19846 |  | 25-03-2026 16:40 | 121.401 | 124.614 | 1415 | 20.769 | 21.2048 | -0.43577 | 127.2286 | 21.1 | 20.9015 | 0.19846 |  | 25-03-2026 16:40 | 114.567 | 116.064 | 1338.4 | 19.344 | 20.1737 | -0.82971 | 121.0423 | 19.9 | 19.8852 | 0.01477 |  | 25-03-2026 16:40 | 214.4022 | 219.4986 | -5.0964 | 1316.9914 | 190.5 | 216.3597 | -25.8597 | -23.9022
25-03-2026 16:30 | 447 | 51.09 | 181.077 | 183.481 | 1875.4 | 30.5802 | 26.3835 | 4.1966 | 158.3013 | 27.3 | 26.0063 | 1.2937 |  | 25-03-2026 16:30 | 162.954 | 164.063 | 1893.3 | 27.3438 | 26.3835 | 0.96029 | 158.3013 | 27.2 | 26.0063 | 1.1937 |  | 25-03-2026 16:30 | 156.37 | 159.882 | 1861.5 | 26.647 | 26.3835 | 0.26345 | 158.3013 | 27 | 26.0063 | 0.99374 |  | 25-03-2026 16:30 | 150.178 | 152.202 | 1874.8 | 25.367 | 26.3835 | -1.0165 | 158.3013 | 26.6 | 26.0063 | 0.59374 |  | 25-03-2026 16:30 | 116.229 | 117.957 | 1398.7 | 19.6595 | 19.5434 | 0.11613 | 117.2602 | 20.1 | 19.2639 | 0.8361 |  | 25-03-2026 16:30 | 109.594 | 111.004 | 1386.5 | 18.5007 | 19.5434 | -1.0427 | 117.2602 | 19.4 | 19.2639 | 0.1361 |  | 25-03-2026 16:30 | 114.298 | 115.923 | 1385.6 | 19.3205 | 19.5434 | -0.22287 | 117.2602 | 19.6 | 19.2639 | 0.3361 |  | 25-03-2026 16:30 | 112.885 | 116.197 | 1393.9 | 19.3662 | 19.5434 | -0.1772 | 117.2602 | 19.5 | 19.2639 | 0.2361 |  | 25-03-2026 16:30 | 103.878 | 105.236 | 1318.5 | 17.5393 | 18.5931 | -1.0538 | 111.5586 | 18.3 | 18.3272 | -0.027212 |  | 25-03-2026 16:30 | 204.3242 | 202.3007 | 2.0234 | 1213.8045 | 205 | 199.4078 | 5.5922 | 0.67583
25-03-2026 16:20 | 461 | 50.23 | 171.032 | 169.865 | 1848.1 | 28.3108 | 27.3 | 1.0108 | 163.8 | 30.8 | 26.9096 | 3.8904 |  | 25-03-2026 16:20 | 173.781 | 170.378 | 1866.1 | 28.3963 | 27.3 | 1.0963 | 163.8 | 30.7 | 26.9096 | 3.7904 |  | 25-03-2026 16:20 | 160.375 | 165.741 | 1834.5 | 27.6235 | 27.3 | 0.32349 | 163.8 | 29.9 | 26.9096 | 2.9904 |  | 25-03-2026 16:20 | 154.767 | 156.853 | 1848.2 | 26.1422 | 27.3 | -1.1578 | 163.8 | 29.9 | 26.9096 | 2.9904 |  | 25-03-2026 16:20 | 123.184 | 124.794 | 1378.6 | 20.799 | 20.2222 | 0.57677 | 121.3334 | 22.4 | 19.9331 | 2.4669 |  | 25-03-2026 16:20 | 116.845 | 118.744 | 1367.1 | 19.7907 | 20.2222 | -0.43156 | 121.3334 | 21.9 | 19.9331 | 1.9669 |  | 25-03-2026 16:20 | 120.962 | 122.53 | 1366 | 20.4217 | 20.2222 | 0.19944 | 121.3334 | 21.9 | 19.9331 | 1.9669 |  | 25-03-2026 16:20 | 121.171 | 124.466 | 1374.4 | 20.7443 | 20.2222 | 0.52211 | 121.3334 | 21.9 | 19.9331 | 1.9669 |  | 25-03-2026 16:20 | 113.131 | 114.002 | 1300.2 | 19.0003 | 19.2389 | -0.23861 | 115.4337 | 20.6 | 18.9638 | 1.6362 |  | 25-03-2026 16:20 | 211.2288 | 209.3279 | 1.9009 | 1255.9673 | 230 | 206.3345 | 23.6655 | 18.7712
25-03-2026 16:10 | 624 | 50.8 | 213.484 | 216.515 | 1817.3 | 36.0858 | 36.8719 | -0.78603 | 221.2312 | 36.4 | 36.3446 | 0.055407 |  | 25-03-2026 16:10 | 215.853 | 218.962 | 1835.4 | 36.4937 | 36.8719 | -0.37819 | 221.2312 | 37.3 | 36.3446 | 0.95541 |  | 25-03-2026 16:10 | 212.812 | 217.71 | 1804.6 | 36.285 | 36.8719 | -0.58686 | 221.2312 | 36.9 | 36.3446 | 0.55541 |  | 25-03-2026 16:10 | 213.014 | 216.06 | 1818.3 | 36.01 | 36.8719 | -0.86186 | 221.2312 | 36.9 | 36.3446 | 0.55541 |  | 25-03-2026 16:10 | 159.705 | 161.858 | 1356.2 | 26.9763 | 27.3125 | -0.33616 | 163.8749 | 27.7 | 26.9219 | 0.77808 |  | 25-03-2026 16:10 | 156.297 | 158.384 | 1345.2 | 26.3973 | 27.3125 | -0.91516 | 163.8749 | 27.1 | 26.9219 | 0.17808 |  | 25-03-2026 16:10 | 156.69 | 158.802 | 1344.1 | 26.467 | 27.3125 | -0.84549 | 163.8749 | 27.2 | 26.9219 | 0.27808 |  | 25-03-2026 16:10 | 156.73 | 161.129 | 1352.5 | 26.8548 | 27.3125 | -0.45766 | 163.8749 | 27.3 | 26.9219 | 0.37808 |  | 25-03-2026 16:10 | 147.948 | 149.927 | 1279.6 | 24.9878 | 25.9845 | -0.99662 | 155.9067 | 25.7 | 25.6129 | 0.087127 |  | 25-03-2026 16:10 | 276.5578 | 282.7219 | -6.164 | 1696.3311 | 282.5 | 278.6789 | 3.8211 | 5.9422
25-03-2026 16:00 | 622 | 50.8 | 211.945 | 214.976 | 1780.9 | 35.8293 | 36.7537 | -0.92435 | 220.5221 | 40.5 | 36.2281 | 4.2719 |  | 25-03-2026 16:00 | 246.463 | 247.537 | 1798.1 | 41.2562 | 36.7537 | 4.5025 | 220.5221 | 63.6 | 36.2281 | 27.3719 |  | 25-03-2026 16:00 | 217.097 | 222.888 | 1767.7 | 37.148 | 36.7537 | 0.39432 | 220.5221 | 40.4 | 36.2281 | 4.1719 |  | 25-03-2026 16:00 | 215.142 | 218.263 | 1781.4 | 36.3772 | 36.7537 | -0.37652 | 220.5221 | 40.3 | 36.2281 | 4.0719 |  | 25-03-2026 16:00 | 166.156 | 168.413 | 1328.5 | 28.0688 | 27.2249 | 0.84388 | 163.3497 | 30.2 | 26.8356 | 3.3644 |  | 25-03-2026 16:00 | 161.492 | 164.091 | 1318.1 | 27.3485 | 27.2249 | 0.12355 | 163.3497 | 29.6 | 26.8356 | 2.7644 |  | 25-03-2026 16:00 | 165.868 | 168.647 | 1316.9 | 28.1078 | 27.2249 | 0.88288 | 163.3497 | 29.7 | 26.8356 | 2.8644 |  | 25-03-2026 16:00 | 165.694 | 170.664 | 1325.2 | 28.444 | 27.2249 | 1.2191 | 163.3497 | 29.6 | 26.8356 | 2.7644 |  | 25-03-2026 16:00 | 151.57 | 157.835 | 1253.9 | 26.3058 | 25.9012 | 0.40467 | 155.407 | 28 | 25.5308 | 2.4692 |  | 25-03-2026 16:00 | 288.8857 | 281.8157 | 7.07 | 1690.8942 | 331.9 | 277.7857 | 54.1143 | 43.0143
25-03-2026 15:50 | 581 | 49.94 | 190.696 | 193.286 | 1740.4 | 32.2143 | 34.4446 | -2.2303 | 206.6676 | 22.7 | 33.952 | -11.252 | [5 empty] | 0 | 34.4446 | -34.4446 | 206.6676 | 0 | 33.952 | -33.952 |  | 25-03-2026 15:50 | 189.268 | 192.231 | 1727.3 | 32.0385 | 34.4446 | -2.4061 | 206.6676 | 22.4 | 33.952 | -11.552 |  | 25-03-2026 15:50 | 201.768 | 204.571 | 1741.1 | 34.0952 | 34.4446 | -0.34944 | 206.6676 | 22.3 | 33.952 | -11.652 |  | 25-03-2026 15:50 | 143.558 | 145.449 | 1298.3 | 24.2415 | 25.5145 | -1.273 | 153.0871 | 16.7 | 25.1497 | -8.4497 |  | 25-03-2026 15:50 | 141.755 | 143.622 | 1288.5 | 23.937 | 25.5145 | -1.5775 | 153.0871 | 16.3 | 25.1497 | -8.8497 |  | 25-03-2026 15:50 | 140.829 | 142.669 | 1287.2 | 23.7782 | 25.5145 | -1.7364 | 153.0871 | 16.4 | 25.1497 | -8.7497 |  | 25-03-2026 15:50 | 143.326 | 147.335 | 1295.6 | 24.5558 | 25.5145 | -0.95869 | 153.0871 | 16.5 | 25.1497 | -8.6497 |  | 25-03-2026 15:50 | 134.565 | 136.365 | 1225.9 | 22.7275 | 24.2739 | -1.5464 | 145.6434 | 15.8 | 23.9268 | -8.1268 |  | 25-03-2026 15:50 | 217.588 | 264.1104 | -46.5224 | 1584.6625 | 149.1 | 260.3336 | -111.2336 | -68.488
25-03-2026 15:40 | 378 | 50.23 | 136.621 | 139.343 | 1717.7 | 23.2238 | 22.3848 | 0.83901 | 134.3089 | 20.1 | 22.0647 | -1.9647 |  | 25-03-2026 15:40 | 193.056 | 133.199 | 1734.5 | 22.1998 | 22.3848 | -0.18499 | 134.3089 | 21.9 | 22.0647 | -0.16472 |  | 25-03-2026 15:40 | 130.141 | 131.882 | 1704.9 | 21.9803 | 22.3848 | -0.40449 | 134.3089 | 20.2 | 22.0647 | -1.8647 |  | 25-03-2026 15:40 | 132.209 | 133.978 | 1718.8 | 22.3297 | 22.3848 | -0.055155 | 134.3089 | 20.2 | 22.0647 | -1.8647 |  | 25-03-2026 15:40 | 93.359 | 94.589 | 1281.6 | 15.7648 | 16.5813 | -0.81652 | 99.4881 | 15.2 | 16.3442 | -1.1442 |  | 25-03-2026 15:40 | 91.111 | 92.302 | 1272.2 | 15.3837 | 16.5813 | -1.1977 | 99.4881 | 15 | 16.3442 | -1.3442 |  | 25-03-2026 15:40 | 91.471 | 92.707 | 1270.8 | 15.4512 | 16.5813 | -1.1302 | 99.4881 | 15 | 16.3442 | -1.3442 |  | 25-03-2026 15:40 | 91.381 | 94.31 | 1279.1 | 15.7183 | 16.5813 | -0.86302 | 99.4881 | 15.1 | 16.3442 | -1.2442 |  | 25-03-2026 15:40 | 91.961 | 93.163 | 1210.1 | 15.5272 | 15.7751 | -0.24793 | 94.6506 | 14 | 15.5495 | -1.5495 |  | 25-03-2026 15:40 | 167.5788 | 171.6398 | -4.061 | 1029.8387 | 156.7 | 169.1853 | -12.4853 | -10.8788
25-03-2026 15:30 | 483 | 51.09 | 163.633 | 165.94 | 1697.6 | 27.6567 | 28.5084 | -0.85173 | 171.0504 | 43.2 | 28.1007 | 15.0993 |  | 25-03-2026 15:30 | 171.682 | 174.226 | 1712.6 | 29.0377 | 28.5084 | 0.52927 | 171.0504 | 41.6 | 28.1007 | 13.4993 |  | 25-03-2026 15:30 | 125.193 | 133.613 | 1684.7 | 22.2688 | 28.5084 | -6.2396 | 171.0504 | 42.2 | 28.1007 | 14.0993 |  | 25-03-2026 15:30 | 157.456 | 159.724 | 1698.6 | 26.6207 | 28.5084 | -1.8877 | 171.0504 | 42.6 | 28.1007 | 14.4993 |  | 25-03-2026 15:30 | 94.291 | 95.581 | 1266.4 | 15.9302 | 21.1173 | -5.1872 | 126.704 | 31.7 | 20.8154 | 10.8846 |  | 25-03-2026 15:30 | 113.089 | 114.637 | 1257.2 | 19.1062 | 21.1173 | -2.0112 | 126.704 | 31.3 | 20.8154 | 10.4846 |  | 25-03-2026 15:30 | 104.6 | 110.001 | 1255.8 | 18.3335 | 21.1173 | -2.7838 | 126.704 | 31.3 | 20.8154 | 10.4846 |  | 25-03-2026 15:30 | 125.69 | 127.397 | 1264 | 21.2328 | 21.1173 | 0.1155 | 126.704 | 31.5 | 20.8154 | 10.6846 |  | 25-03-2026 15:30 | 127.346 | 131.479 | 1196.1 | 21.9132 | 20.0905 | 1.8226 | 120.5431 | 29.8 | 19.8032 | 9.9968 |  | 25-03-2026 15:30 | 202.0997 | 218.5934 | -16.4938 | 1311.5605 | 325.2 | 215.4675 | 109.7325 | 123.1003
25-03-2026 15:20 | 804 | 50.8 | 268.123 | 272.427 | 1654.4 | 45.4045 | 47.508 | -2.1035 | 285.0478 | 44.8 | 46.8286 | -2.0286 |  | 25-03-2026 15:20 | 271.814 | 276.29 | 1671 | 46.0483 | 47.508 | -1.4596 | 285.0478 | 45.9 | 46.8286 | -0.92861 |  | 25-03-2026 15:20 | 266.583 | 273.593 | 1642.5 | 45.5988 | 47.508 | -1.9091 | 285.0478 | 44.5 | 46.8286 | -2.3286 |  | 25-03-2026 15:20 | 268.671 | 273.067 | 1656 | 45.5112 | 47.508 | -1.9968 | 285.0478 | 44.8 | 46.8286 | -2.0286 |  | 25-03-2026 15:20 | 200.792 | 203.772 | 1234.7 | 33.962 | 35.1911 | -1.2291 | 211.1466 | 33.5 | 34.6879 | -1.1879 |  | 25-03-2026 15:20 | 197.371 | 200.776 | 1225.9 | 33.4627 | 35.1911 | -1.7284 | 211.1466 | 32.9 | 34.6879 | -1.7879 |  | 25-03-2026 15:20 | 197.672 | 201.33 | 1224.5 | 33.555 | 35.1911 | -1.6361 | 211.1466 | 33.3 | 34.6879 | -1.3879 |  | 25-03-2026 15:20 | 198.29 | 204.173 | 1232.5 | 34.0288 | 35.1911 | -1.1623 | 211.1466 | 33.5 | 34.6879 | -1.1879 |  | 25-03-2026 15:20 | 187.517 | 190.315 | 1166.3 | 31.7192 | 33.48 | -1.7608 | 200.8798 | 31.7 | 33.0012 | -1.3012 |  | 25-03-2026 15:20 | 349.2905 | 364.2762 | -14.9857 | 2185.6574 | 344.9 | 359.0671 | -14.1671 | -4.3905
25-03-2026 15:10 | 816 | 52.52 | 272.661 | 277.111 | 1609.6 | 46.1852 | 47.898 | -1.7128 | 287.3878 | 45.7 | 47.213 | -1.513 |  | 25-03-2026 15:10 | 277.684 | 281.136 | 1625.1 | 46.856 | 47.898 | -1.042 | 287.3878 | 47.2 | 47.213 | -0.013028 |  | 25-03-2026 15:10 | 270.451 | 277.905 | 1598 | 46.3175 | 47.898 | -1.5805 | 287.3878 | 46.2 | 47.213 | -1.013 |  | 25-03-2026 15:10 | 273.037 | 277.533 | 1611.2 | 46.2555 | 47.898 | -1.6425 | 287.3878 | 46.5 | 47.213 | -0.71303 |  | 25-03-2026 15:10 | 203.38 | 206.435 | 1201.2 | 34.4058 | 35.48 | -1.0741 | 212.8799 | 35.2 | 34.9726 | 0.22739 |  | 25-03-2026 15:10 | 200.756 | 204.42 | 1193 | 34.07 | 35.48 | -1.41 | 212.8799 | 34.7 | 34.9726 | -0.27261 |  | 25-03-2026 15:10 | 200.094 | 204.259 | 1191.2 | 34.0432 | 35.48 | -1.4368 | 212.8799 | 34.2 | 34.9726 | -0.77261 |  | 25-03-2026 15:10 | 200.564 | 206.366 | 1199 | 34.3943 | 35.48 | -1.0856 | 212.8799 | 34.4 | 34.9726 | -0.57261 |  | 25-03-2026 15:10 | 190.441 | 193.263 | 1134.6 | 32.2105 | 33.7548 | -1.5443 | 202.5288 | 32.6 | 33.2721 | -0.67211 |  | 25-03-2026 15:10 | 354.738 | 367.2666 | -12.5286 | 2203.5995 | 356.7 | 362.0147 | -5.3147 | 1.962
25-03-2026 15:00 | 860 | 52.23 | 284.483 | 289.197 | 1563.9 | 48.1995 | 50.5374 | -2.3379 | 303.2244 | 48.1 | 49.8147 | -1.7147 | 0.9837 | 25-03-2026 15:00 | 287.199 | 292.934 | 1577.9 | 48.8223 | 50.5374 | -1.7151 | 303.2244 | 47.2 | 49.8147 | -2.6147 | 0.98042 | 25-03-2026 15:00 | 283.635 | 291.49 | 1551.8 | 48.5817 | 50.5374 | -1.9557 | 303.2244 | 47.7 | 49.8147 | -2.1147 | 0.97305 | 25-03-2026 15:00 | 284.359 | 289.159 | 1564.7 | 48.1932 | 50.5374 | -2.3442 | 303.2244 | 47.9 | 49.8147 | -1.9147 | 0.9834 | 25-03-2026 15:00 | 213.849 | 217.128 | 1166 | 36.188 | 37.4351 | -1.2471 | 224.6107 | 35.4 | 36.8998 | -1.4998 | 0.9849 | 25-03-2026 15:00 | 209.486 | 213.54 | 1158.3 | 35.59 | 37.4351 | -1.8451 | 224.6107 | 34.8 | 36.8998 | -2.0998 | 0.98102 | 25-03-2026 15:00 | 210.025 | 214.065 | 1157 | 35.6775 | 37.4351 | -1.7576 | 224.6107 | 34.9 | 36.8998 | -1.9998 | 0.98113 | 25-03-2026 15:00 | 210.636 | 216.799 | 1164.6 | 36.1332 | 37.4351 | -1.3019 | 224.6107 | 34.9 | 36.8998 | -1.9998 | 0.97157 | 25-03-2026 15:00 | 199.195 | 202.228 | 1102 | 33.7047 | 35.6149 | -1.9102 | 213.6892 | 33 | 35.1056 | -2.1056 | 0.985 | 25-03-2026 15:00 | 371.09 | 387.5049 | -16.4149 | 2325.0296 | 363.9 | 381.9636 | -18.0636 | -7.19
25-03-2026 14:50 | 864 | 54.24 | 286.569 | 291.454 | 1515.8 | 48.5757 | 50.3776 | -1.802 | 302.2659 | 48.3 | 49.6572 | -1.3572 | 0.98324 | 25-03-2026 14:50 | 289.631 | 294.497 | 1530.7 | 49.0828 | 50.3776 | -1.2948 | 302.2659 | 49.6 | 49.6572 | -0.057248 | 0.98348 | 25-03-2026 14:50 | 285.682 | 293.463 | 1504.1 | 48.9105 | 50.3776 | -1.4671 | 302.2659 | 47.4 | 49.6572 | -2.2572 | 0.97349 | 25-03-2026 14:50 | 285.612 | 290.463 | 1516.8 | 48.4105 | 50.3776 | -1.9671 | 302.2659 | 48.3 | 49.6572 | -1.3572 | 0.9833 | 25-03-2026 14:50 | 215.361 | 218.707 | 1130.6 | 36.4512 | 37.3168 | -0.86561 | 223.9007 | 36.2 | 36.7831 | -0.58315 | 0.9847 | 25-03-2026 14:50 | 210.808 | 214.387 | 1123.5 | 35.7312 | 37.3168 | -1.5856 | 223.9007 | 35.6 | 36.7831 | -1.1831 | 0.98331 | 25-03-2026 14:50 | 212.032 | 216.102 | 1122.1 | 36.017 | 37.3168 | -1.2998 | 223.9007 | 35.6 | 36.7831 | -1.1831 | 0.98117 | 25-03-2026 14:50 | 212.774 | 218.876 | 1129.7 | 36.4793 | 37.3168 | -0.83744 | 223.9007 | 35.9 | 36.7831 | -0.88315 | 0.97212 | 25-03-2026 14:50 | 200.559 | 203.655 | 1069 | 33.9425 | 35.5023 | -1.5598 | 213.0137 | 33.8 | 34.9946 | -1.1946 | 0.9848 | 25-03-2026 14:50 | 373.6007 | 386.28 | -12.6793 | 2317.6799 | 370.7 | 380.7562 | -10.0562 | -2.9007
25-03-2026 14:40 | 898 | 53.67 | 297.134 | 302.204 | 1467.5 | 50.3673 | 52.4765 | -2.1091 | 314.8588 | 49.9 | 51.7261 | -1.8261 | 0.98322 | 25-03-2026 14:40 | 301.233 | 306.38 | 1481.1 | 51.0633 | 52.4765 | -1.4131 | 314.8588 | 50.6 | 51.7261 | -1.1261 | 0.9832 | 25-03-2026 14:40 | 294.613 | 303.123 | 1456.7 | 50.5205 | 52.4765 | -1.956 | 314.8588 | 50 | 51.7261 | -1.7261 | 0.97193 | 25-03-2026 14:40 | 297.775 | 302.863 | 1468.5 | 50.4772 | 52.4765 | -1.9993 | 314.8588 | 49.9 | 51.7261 | -1.8261 | 0.9832 | 25-03-2026 14:40 | 222.04 | 225.49 | 1094.4 | 37.5817 | 38.8715 | -1.2898 | 233.2288 | 37.2 | 38.3156 | -1.1156 | 0.9847 | 25-03-2026 14:40 | 219.22 | 223.239 | 1087.9 | 37.2065 | 38.8715 | -1.665 | 233.2288 | 37.4 | 38.3156 | -0.9156 | 0.982 | 25-03-2026 14:40 | 219.119 | 223.755 | 1086.5 | 37.2925 | 38.8715 | -1.579 | 233.2288 | 37.3 | 38.3156 | -1.0156 | 0.97928 | 25-03-2026 14:40 | 220.247 | 226.783 | 1093.8 | 37.7972 | 38.8715 | -1.0743 | 233.2288 | 37.4 | 38.3156 | -0.9156 | 0.97118 | 25-03-2026 14:40 | 208.701 | 211.922 | 1035.2 | 35.3203 | 36.9814 | -1.661 | 221.8883 | 35.6 | 36.4525 | -0.85254 | 0.9848 | 25-03-2026 14:40 | 387.6265 | 402.3731 | -14.7466 | 2414.2385 | 385.3 | 396.6192 | -11.3192 | -2.3265
25-03-2026 14:30 | 930 | 53.96 | 307.864 | 313.093 | 1417.6 | 52.1822 | 54.2851 | -2.103 | 325.7108 | 52.8 | 53.5089 | -0.70886 | 0.9833 | 25-03-2026 14:30 | 313.03 | 318.693 | 1430.5 | 53.1155 | 54.2851 | -1.1696 | 325.7108 | 52.9 | 53.5089 | -0.60886 | 0.98223 | 25-03-2026 14:30 | 304.718 | 313.001 | 1406.7 | 52.1668 | 54.2851 | -2.1183 | 325.7108 | 51.1 | 53.5089 | -2.4089 | 0.97354 | 25-03-2026 14:30 | 307.578 | 312.929 | 1418.6 | 52.1548 | 54.2851 | -2.1303 | 325.7108 | 51.6 | 53.5089 | -1.9089 | 0.9829 | 25-03-2026 14:30 | 229.006 | 232.659 | 1057.2 | 38.7765 | 40.2112 | -1.4347 | 241.2673 | 38.5 | 39.6362 | -1.1362 | 0.9843 | 25-03-2026 14:30 | 226.765 | 230.987 | 1050.5 | 38.4978 | 40.2112 | -1.7134 | 241.2673 | 37.4 | 39.6362 | -2.2362 | 0.98172 | 25-03-2026 14:30 | 225.626 | 230.013 | 1049.2 | 38.3355 | 40.2112 | -1.8757 | 241.2673 | 37.4 | 39.6362 | -2.2362 | 0.98093 | 25-03-2026 14:30 | 226.272 | 232.925 | 1056.4 | 38.8208 | 40.2112 | -1.3904 | 241.2673 | 38 | 39.6362 | -1.6362 | 0.97144 | 25-03-2026 14:30 | 215.959 | 219.292 | 999.6 | 36.5487 | 38.256 | -1.7073 | 229.5359 | 36 | 37.7089 | -1.7089 | 0.9848 | 25-03-2026 14:30 | 400.5987 | 416.2414 | -15.6427 | 2497.4485 | 395.7 | 410.2892 | -14.5892 | -4.8987
25-03-2026 14:20 | 940 | 53.38 | 308.068 | 313.3 | 1364.8 | 52.2167 | 54.9928 | -2.7761 | 329.9568 | 50.1 | 54.2064 | -4.1064 | 0.9833 | 25-03-2026 14:20 | 312.509 | 318.327 | 1377.6 | 53.0545 | 54.9928 | -1.9383 | 329.9568 | 54.2 | 54.2064 | -0.0064018 | 0.98172 | 25-03-2026 14:20 | 305.344 | 314.113 | 1355.6 | 52.3522 | 54.9928 | -2.6406 | 329.9568 | 51.8 | 54.2064 | -2.4064 | 0.97208 | 25-03-2026 14:20 | 309.155 | 314.596 | 1367 | 52.4327 | 54.9928 | -2.5601 | 329.9568 | 52.2 | 54.2064 | -2.0064 | 0.9827 | 25-03-2026 14:20 | 230.821 | 234.551 | 1018.7 | 39.0918 | 40.7354 | -1.6436 | 244.4124 | 39.2 | 40.1529 | -0.95289 | 0.9841 | 25-03-2026 14:20 | 227.578 | 232.006 | 1013.1 | 38.6677 | 40.7354 | -2.0677 | 244.4124 | 38.5 | 40.1529 | -1.6529 | 0.98091 | 25-03-2026 14:20 | 227.981 | 232.325 | 1011.8 | 38.7208 | 40.7354 | -2.0146 | 244.4124 | 38.7 | 40.1529 | -1.4529 | 0.9813 | 25-03-2026 14:20 | 228.98 | 235.68 | 1018.4 | 39.28 | 40.7354 | -1.4554 | 244.4124 | 38.3 | 40.1529 | -1.8529 | 0.97157 | 25-03-2026 14:20 | 216.693 | 220.082 | 963.6 | 36.6803 | 38.7547 | -2.0744 | 232.5282 | 36.1 | 38.2005 | -2.1005 | 0.9846 | 25-03-2026 14:20 | 402.4967 | 421.6675 | -19.1708 | 2530.0051 | 399.1 | 415.6377 | -16.5377 | -3.3967
25-03-2026 14:10 | 953 | 52.81 | 311.533 | 316.953 | 1314.7 | 52.8255 | 55.8768 | -3.0513 | 335.261 | 53.9 | 55.0778 | -1.1778 | 0.9829 | 25-03-2026 14:10 | 316.754 | 322.33 | 1323.4 | 53.7217 | 55.8768 | -2.1552 | 335.261 | 53.4 | 55.0778 | -1.6778 | 0.9827 | 25-03-2026 14:10 | 308.812 | 317.689 | 1303.8 | 52.9482 | 55.8768 | -2.9287 | 335.261 | 52 | 55.0778 | -3.0778 | 0.97206 | 25-03-2026 14:10 | 311.856 | 317.411 | 1314.8 | 52.9018 | 55.8768 | -2.975 | 335.261 | 53.2 | 55.0778 | -1.8778 | 0.9825 | 25-03-2026 14:10 | 233.306 | 237.051 | 979.5 | 39.5085 | 41.3902 | -1.8817 | 248.3415 | 39.8 | 40.7984 | -0.99837 | 0.9842 | 25-03-2026 14:10 | 229.874 | 234.318 | 974.6 | 39.053 | 41.3902 | -2.3372 | 248.3415 | 39.2 | 40.7984 | -1.5984 | 0.98103 | 25-03-2026 14:10 | 230.723 | 235.404 | 973.1 | 39.234 | 41.3902 | -2.1562 | 248.3415 | 39.2 | 40.7984 | -1.5984 | 0.98012 | 25-03-2026 14:10 | 232.05 | 239.125 | 980.1 | 39.8542 | 41.3902 | -1.5361 | 248.3415 | 39.4 | 40.7984 | -1.3984 | 0.97041 | 25-03-2026 14:10 | 218.383 | 221.883 | 927.5 | 36.9805 | 39.3777 | -2.3972 | 236.2662 | 37.4 | 38.8146 | -1.4146 | 0.98423 | 25-03-2026 14:10 | 407.0273 | 428.446 | -21.4187 | 2570.676 | 407.5 | 422.3192 | -14.8192 | 0.47267
25-03-2026 14:00 | 992 | 53.38 | 322.422 | 327.671 | 1260.8 | 54.6118 | 58.035 | -3.4231 | 348.2097 | 54.4 | 57.2051 | -2.8051 | 0.98398 | 25-03-2026 14:00 | 327.378 | 333.277 | 1270 | 55.5462 | 58.035 | -2.4888 | 348.2097 | 53.7 | 57.2051 | -3.5051 | 0.9823 | 25-03-2026 14:00 | 319.747 | 329.323 | 1251.8 | 54.8872 | 58.035 | -3.1478 | 348.2097 | 54.6 | 57.2051 | -2.6051 | 0.97092 | 25-03-2026 14:00 | 323.04 | 328.861 | 1261.6 | 54.8102 | 58.035 | -3.2248 | 348.2097 | 54.6 | 57.2051 | -2.6051 | 0.9823 | 25-03-2026 14:00 | 241.639 | 245.618 | 939.7 | 40.9363 | 42.9889 | -2.0525 | 257.9331 | 40.7 | 42.3741 | -1.6741 | 0.9838 | 25-03-2026 14:00 | 238.682 | 243.558 | 935.4 | 40.593 | 42.9889 | -2.3959 | 257.9331 | 40.9 | 42.3741 | -1.4741 | 0.97998 | 25-03-2026 14:00 | 238.57 | 243.517 | 933.9 | 40.5862 | 42.9889 | -2.4027 | 257.9331 | 40.8 | 42.3741 | -1.5741 | 0.97969 | 25-03-2026 14:00 | 239.234 | 246.373 | 940.7 | 41.0622 | 42.9889 | -1.9267 | 257.9331 | 41 | 42.3741 | -1.3741 | 0.97102 | 25-03-2026 14:00 | 227.016 | 230.66 | 890.1 | 38.4433 | 40.8986 | -2.4552 | 245.3914 | 38.9 | 40.3137 | -1.4137 | 0.9842 | 25-03-2026 14:00 | 421.4763 | 444.9938 | -23.5175 | 2669.9628 | 419.6 | 438.6304 | -19.0304 | -1.8763
25-03-2026 13:50 | 1036 | 53.38 | 340.953 | 346.065 | 1206.4 | 57.6775 | 60.6091 | -2.9316 | 363.6545 | 58.5 | 59.7424 | -1.2424 | 0.98523 | 25-03-2026 13:50 | 347.088 | 353.342 | 1216.3 | 58.8903 | 60.6091 | -1.7188 | 363.6545 | 58.7 | 59.7424 | -1.0424 | 0.9823 | 25-03-2026 13:50 | 337.044 | 346.325 | 1197.2 | 57.7208 | 60.6091 | -2.8883 | 363.6545 | 58.3 | 59.7424 | -1.4424 | 0.9732 | 25-03-2026 13:50 | 340.644 | 346.747 | 1207 | 57.7912 | 60.6091 | -2.8179 | 363.6545 | 58.5 | 59.7424 | -1.2424 | 0.9824 | 25-03-2026 13:50 | 254.086 | 257.679 | 899 | 42.9465 | 44.8956 | -1.9491 | 269.3737 | 45.8 | 44.2536 | 1.5464 | 0.98606 | 25-03-2026 13:50 | 252.138 | 257.121 | 894.5 | 42.8535 | 44.8956 | -2.0421 | 269.3737 | 44.8 | 44.2536 | 0.54639 | 0.98062 | 25-03-2026 13:50 | 250.501 | 255.943 | 893.1 | 42.6572 | 44.8956 | -2.2385 | 269.3737 | 44.6 | 44.2536 | 0.34639 | 0.97874 | 25-03-2026 13:50 | 251.779 | 259.5 | 899.7 | 43.25 | 44.8956 | -1.6456 | 269.3737 | 44.8 | 44.2536 | 0.54639 | 0.97025 | 25-03-2026 13:50 | 239.656 | 243.528 | 851.2 | 40.588 | 42.7126 | -2.1246 | 256.2757 | 43.2 | 42.1018 | 1.0982 | 0.9841 | 25-03-2026 13:50 | 444.375 | 464.7314 | -20.3564 | 2788.3886 | 457.2 | 458.0858 | -0.88577 | 12.825
25-03-2026 13:40 | 1181 | 52.52 | 352.857 | 357.916 | 1147.9 | 59.6527 | 69.3229 | -9.6703 | 415.9375 | 34.1 | 68.3316 | -34.2316 | 0.98587 | 25-03-2026 13:40 | 352.863 | 357.885 | 1157.6 | 59.6475 | 69.3229 | -9.6754 | 415.9375 | 35.1 | 68.3316 | -33.2316 | 0.98597 | 25-03-2026 13:40 | 351.919 | 361.732 | 1138.9 | 60.2887 | 69.3229 | -9.0343 | 415.9375 | 34.6 | 68.3316 | -33.7316 | 0.97287 | 25-03-2026 13:40 | 352.399 | 357.511 | 1148.5 | 59.5852 | 69.3229 | -9.7378 | 415.9375 | 34.5 | 68.3316 | -33.8316 | 0.9857 | 25-03-2026 13:40 | 300.463 | 305.442 | 853.2 | 50.907 | 51.3503 | -0.44331 | 308.1019 | 26.9 | 50.616 | -23.716 | 0.9837 | 25-03-2026 13:40 | 298.202 | 303.589 | 849.7 | 50.5982 | 51.3503 | -0.75214 | 308.1019 | 26.4 | 50.616 | -24.216 | 0.98226 | 25-03-2026 13:40 | 297.389 | 303.371 | 848.5 | 50.5618 | 51.3503 | -0.78848 | 308.1019 | 26.7 | 50.616 | -23.916 | 0.98028 | 25-03-2026 13:40 | 302.791 | 312.16 | 854.9 | 52.0267 | 51.3503 | 0.67636 | 308.1019 | 26.7 | 50.616 | -23.916 | 0.96999 | 25-03-2026 13:40 | 287.029 | 291.667 | 808 | 48.6112 | 48.8535 | -0.24229 | 293.1208 | 24.5 | 48.1549 | -23.6549 | 0.9841 | 25-03-2026 13:40 | 491.8788 | 531.5464 | -39.6675 | 3189.2783 | 269.5 | 523.9453 | -254.4453 | -222.3788
25-03-2026 13:30 | 515 | 52.52 | 187.302 | 184.558 | 1113.8 | 30.7597 | 30.2297 | 0.52994 | 181.3783 | 37.4 | 29.7974 | 7.6026 | 1.0149 | 25-03-2026 13:30 | 187.46 | 190.199 | 1122.5 | 31.6998 | 30.2297 | 1.4701 | 181.3783 | 35.7 | 29.7974 | 5.9026 | 0.9856 | 25-03-2026 13:30 | 181.512 | 185.535 | 1104.3 | 30.9225 | 30.2297 | 0.69278 | 181.3783 | 34.3 | 29.7974 | 4.5026 | 0.97832 | 25-03-2026 13:30 | 183.134 | 185.791 | 1114 | 30.9652 | 30.2297 | 0.73544 | 181.3783 | 34.5 | 29.7974 | 4.7026 | 0.9857 | 25-03-2026 13:30 | 135.303 | 137.169 | 826.3 | 22.8615 | 22.3924 | 0.46911 | 134.3543 | 25.7 | 22.0722 | 3.6278 | 0.9864 | 25-03-2026 13:30 | 134.168 | 136.206 | 823.3 | 22.701 | 22.3924 | 0.30861 | 134.3543 | 25.4 | 22.0722 | 3.3278 | 0.98504 | 25-03-2026 13:30 | 133.248 | 135.071 | 821.8 | 22.5118 | 22.3924 | 0.11945 | 134.3543 | 25.3 | 22.0722 | 3.2278 | 0.9865 | 25-03-2026 13:30 | 133.43 | 137.07 | 828.2 | 22.845 | 22.3924 | 0.45261 | 134.3543 | 25.4 | 22.0722 | 3.3278 | 0.97344 | 25-03-2026 13:30 | 126.851 | 128.626 | 783.5 | 21.4377 | 21.3036 | 0.13408 | 127.8215 | 24 | 20.9989 | 3.0011 | 0.9862 | 25-03-2026 13:30 | 236.7042 | 231.792 | 4.9121 | 1390.7522 | 267.7 | 228.4774 | 39.2226 | 30.9958
25-03-2026 13:20 | 872 | 53.38 | 286.875 | 265.017 | 1076.4 | 44.1695 | 51.0146 | -6.8451 | 306.0876 | 43.5 | 50.2851 | -6.7851 | 1.0825 | 25-03-2026 13:20 | 284.614 | 289.212 | 1086.8 | 48.202 | 51.0146 | -2.8126 | 306.0876 | 44.9 | 50.2851 | -5.3851 | 0.9841 | 25-03-2026 13:20 | 297.212 | 304.928 | 1070 | 50.8213 | 51.0146 | -0.19326 | 306.0876 | 45.9 | 50.2851 | -4.3851 | 0.9747 | 25-03-2026 13:20 | 299.107 | 304.063 | 1079.5 | 50.6772 | 51.0146 | -0.33743 | 306.0876 | 46.3 | 50.2851 | -3.9851 | 0.9837 | 25-03-2026 13:20 | 219.753 | 223.054 | 800.6 | 37.1757 | 37.7886 | -0.61292 | 226.7315 | 34.6 | 37.2482 | -2.6482 | 0.9852 | 25-03-2026 13:20 | 217.661 | 220.931 | 797.9 | 36.8218 | 37.7886 | -0.96676 | 226.7315 | 34.3 | 37.2482 | -2.9482 | 0.9852 | 25-03-2026 13:20 | 215.645 | 219.811 | 796.5 | 36.6352 | 37.7886 | -1.1534 | 226.7315 | 34.3 | 37.2482 | -2.9482 | 0.98105 | 25-03-2026 13:20 | 212.973 | 219.872 | 802.8 | 36.6453 | 37.7886 | -1.1433 | 226.7315 | 34.4 | 37.2482 | -2.8482 | 0.96862 | 25-03-2026 13:20 | 203.273 | 206.327 | 759.5 | 34.3878 | 35.9512 | -1.5633 | 215.707 | 32.5 | 35.4371 | -2.9371 | 0.9852 | 25-03-2026 13:20 | 375.5358 | 391.1639 | -15.6281 | 2346.9835 | 350.7 | 385.5703 | -34.8703 | -24.8358
25-03-2026 13:10 | 704 | 52.23 | 250.942 | 254.763 | 1032.9 | 42.4605 | 41.3702 | 1.0903 | 248.2209 | 33.8 | 40.7786 | -6.9786 | 0.985 | 25-03-2026 13:10 | 251.954 | 255.791 | 1041.9 | 42.6318 | 41.3702 | 1.2617 | 248.2209 | 34.2 | 40.7786 | -6.5786 | 0.985 | 25-03-2026 13:10 | 243.46 | 249.237 | 1024.1 | 41.5395 | 41.3702 | 0.16935 | 248.2209 | 33.4 | 40.7786 | -7.3786 | 0.97682 | 25-03-2026 13:10 | 253.144 | 257.051 | 1033.2 | 42.8418 | 41.3702 | 1.4717 | 248.2209 | 33.4 | 40.7786 | -7.3786 | 0.9848 | 25-03-2026 13:10 | 181.191 | 183.782 | 766 | 30.6303 | 30.6446 | -0.014224 | 183.8673 | 25.1 | 30.2063 | -5.1063 | 0.9859 | 25-03-2026 13:10 | 182.486 | 185.021 | 763.6 | 30.8368 | 30.6446 | 0.19228 | 183.8673 | 24.8 | 30.2063 | -5.4063 | 0.9863 | 25-03-2026 13:10 | 177.19 | 179.987 | 762.2 | 29.9978 | 30.6446 | -0.64672 | 183.8673 | 24.9 | 30.2063 | -5.3063 | 0.98446 | 25-03-2026 13:10 | 177.362 | 181.666 | 768.4 | 30.2777 | 30.6446 | -0.36689 | 183.8673 | 25.4 | 30.2063 | -4.8063 | 0.97631 | 25-03-2026 13:10 | 171.147 | 173.542 | 727 | 28.9237 | 29.1545 | -0.23083 | 174.927 | 24 | 28.7376 | -4.7376 | 0.9862 | 25-03-2026 13:10 | 320.14 | 317.2133 | 2.9267 | 1903.28 | 259 | 312.6772 | -53.6772 | -61.14
25-03-2026 13:00 | 466 | 54.24 | 172.634 | 175.014 | 999.1 | 29.169 | 27.1713 | 1.9977 | 163.0277 | 28.4 | 26.7827 | 1.6173 | 0.9864 | 25-03-2026 13:00 | 167.782 | 170.147 | 1007.7 | 28.3578 | 27.1713 | 1.1866 | 163.0277 | 28.7 | 26.7827 | 1.9173 | 0.9861 | 25-03-2026 13:00 | 171.34 | 175.552 | 990.7 | 29.2587 | 27.1713 | 2.0874 | 163.0277 | 28.1 | 26.7827 | 1.3173 | 0.97601 | 25-03-2026 13:00 | 171.966 | 174.408 | 999.8 | 29.068 | 27.1713 | 1.8967 | 163.0277 | 28.4 | 26.7827 | 1.6173 | 0.986 | 25-03-2026 13:00 | 127.661 | 129.395 | 740.9 | 21.5658 | 20.1269 | 1.439 | 120.7612 | 21 | 19.8391 | 1.1609 | 0.9866 | 25-03-2026 13:00 | 126.886 | 128.609 | 738.8 | 21.4348 | 20.1269 | 1.308 | 120.7612 | 20.9 | 19.8391 | 1.0609 | 0.9866 | 25-03-2026 13:00 | 125.874 | 127.581 | 737.3 | 21.2635 | 20.1269 | 1.1366 | 120.7612 | 21.1 | 19.8391 | 1.2609 | 0.98662 | 25-03-2026 13:00 | 126.921 | 130.263 | 743 | 21.7105 | 20.1269 | 1.5836 | 120.7612 | 20.9 | 19.8391 | 1.0609 | 0.97434 | 25-03-2026 13:00 | 120.374 | 121.997 | 703 | 20.3328 | 19.1482 | 1.1846 | 114.8894 | 19.8 | 18.8744 | 0.92559 | 0.9867 | 25-03-2026 13:00 | 222.161 | 208.3408 | 13.8202 | 1250.045 | 217.3 | 205.3616 | 11.9384 | -4.861
25-03-2026 12:50 | 473 | 52.23 | 173.722 | 176.135 | 970.7 | 29.3558 | 27.7956 | 1.5603 | 166.7734 | 31.2 | 27.3981 | 3.8019 | 0.9863 | 25-03-2026 12:50 | 175.192 | 177.68 | 979 | 29.6133 | 27.7956 | 1.8178 | 166.7734 | 31.6 | 27.3981 | 4.2019 | 0.986 | 25-03-2026 12:50 | 173.061 | 177.057 | 962.6 | 29.5095 | 27.7956 | 1.7139 | 166.7734 | 31.1 | 27.3981 | 3.7019 | 0.97743 | 25-03-2026 12:50 | 174.02 | 176.491 | 971.4 | 29.4152 | 27.7956 | 1.6196 | 166.7734 | 31.2 | 27.3981 | 3.8019 | 0.986 | 25-03-2026 12:50 | 129.926 | 131.717 | 719.9 | 21.9528 | 20.5893 | 1.3635 | 123.5359 | 23.3 | 20.2949 | 3.0051 | 0.9864 | 25-03-2026 12:50 | 128.706 | 130.441 | 717.9 | 21.7402 | 20.5893 | 1.1509 | 123.5359 | 23 | 20.2949 | 2.7051 | 0.9867 | 25-03-2026 12:50 | 128.099 | 129.906 | 716.2 | 21.651 | 20.5893 | 1.0617 | 123.5359 | 22.8 | 20.2949 | 2.5051 | 0.98609 | 25-03-2026 12:50 | 128.861 | 132.525 | 722.1 | 22.0875 | 20.5893 | 1.4982 | 123.5359 | 23.2 | 20.2949 | 2.9051 | 0.97235 | 25-03-2026 12:50 | 121.781 | 123.448 | 683.2 | 20.5747 | 19.5882 | 0.98649 | 117.5291 | 21.9 | 19.3081 | 2.5919 | 0.9865 | 25-03-2026 12:50 | 225.9 | 213.1277 | 12.7723 | 1278.7663 | 239.3 | 210.08 | 29.22 | 13.4
25-03-2026 12:40 | 471 | 51.66 | 171.019 | 175.114 | 939.5 | 29.1857 | 27.7391 | 1.4466 | 166.4345 | 29.6 | 27.3424 | 2.2576 | 0.97662 | 25-03-2026 12:40 | 174.84 | 177.341 | 947.4 | 29.5568 | 27.7391 | 1.8178 | 166.4345 | 30.9 | 27.3424 | 3.5576 | 0.9859 | 25-03-2026 12:40 | 172.052 | 176.187 | 931.5 | 29.3645 | 27.7391 | 1.6254 | 166.4345 | 29.6 | 27.3424 | 2.2576 | 0.97653 | 25-03-2026 12:40 | 173.059 | 175.534 | 940.2 | 29.2557 | 27.7391 | 1.5166 | 166.4345 | 30 | 27.3424 | 2.6576 | 0.9859 | 25-03-2026 12:40 | 129.114 | 130.907 | 696.6 | 21.8178 | 20.5475 | 1.2704 | 123.2848 | 22.1 | 20.2536 | 1.8464 | 0.9863 | 25-03-2026 12:40 | 127.814 | 129.563 | 694.9 | 21.5938 | 20.5475 | 1.0464 | 123.2848 | 22.1 | 20.2536 | 1.8464 | 0.9865 | 25-03-2026 12:40 | 127.868 | 129.618 | 693.4 | 21.603 | 20.5475 | 1.0555 | 123.2848 | 21.9 | 20.2536 | 1.6464 | 0.9865 | 25-03-2026 12:40 | 127.51 | 131.086 | 698.9 | 21.8477 | 20.5475 | 1.3002 | 123.2848 | 22.2 | 20.2536 | 1.9464 | 0.97272 | 25-03-2026 12:40 | 120.683 | 122.347 | 661.3 | 20.3912 | 19.5484 | 0.8428 | 117.2902 | 21 | 19.2688 | 1.7312 | 0.9864 | 25-03-2026 12:40 | 224.6162 | 212.6945 | 11.9216 | 1276.1672 | 229.4 | 209.653 | 19.747 | 4.7838
25-03-2026 12:30 | 626 | 51.95 | 219.594 | 222.938 | 909.9 | 37.1563 | 36.8264 | 0.32996 | 220.9583 | 46.2 | 36.2998 | 9.9002 | 0.985 | 25-03-2026 12:30 | 227.276 | 230.76 | 916.5 | 38.46 | 36.8264 | 1.6336 | 220.9583 | 78.2 | 36.2998 | 41.9002 | 0.9849 | 25-03-2026 12:30 | 217.963 | 223.377 | 901.9 | 37.2295 | 36.8264 | 0.40312 | 220.9583 | 45.3 | 36.2998 | 9.0002 | 0.97576 | 25-03-2026 12:30 | 220.589 | 223.926 | 910.2 | 37.321 | 36.8264 | 0.49462 | 220.9583 | 46 | 36.2998 | 9.7002 | 0.9851 | 25-03-2026 12:30 | 164.103 | 166.467 | 674.5 | 27.7445 | 27.2788 | 0.4657 | 163.6728 | 34 | 26.8887 | 7.1113 | 0.9858 | 25-03-2026 12:30 | 163.633 | 166.021 | 672.8 | 27.6702 | 27.2788 | 0.39137 | 163.6728 | 34.2 | 26.8887 | 7.3113 | 0.98562 | 25-03-2026 12:30 | 161.828 | 164.743 | 671.5 | 27.4572 | 27.2788 | 0.17837 | 163.6728 | 34 | 26.8887 | 7.1113 | 0.98231 | 25-03-2026 12:30 | 164.558 | 169.225 | 676.7 | 28.2042 | 27.2788 | 0.92537 | 163.6728 | 33.9 | 26.8887 | 7.0113 | 0.97242 | 25-03-2026 12:30 | 155.612 | 157.838 | 640.3 | 26.3063 | 25.9524 | 0.35394 | 155.7144 | 32.2 | 25.5813 | 6.6187 | 0.9859 | 25-03-2026 12:30 | 287.5492 | 282.3731 | 5.1761 | 1694.2385 | 384 | 278.3352 | 105.6648 | 96.4508
25-03-2026 12:20 | 559 | 51.09 | 199.078 | 201.946 | 863.7 | 33.6577 | 32.9942 | 0.66348 | 197.9651 | 31 | 32.5224 | -1.5224 | 0.9858 |  |  |  |  | 0 | 32.9942 | -32.9942 | 197.9651 | 0 | 32.5224 | -32.5224 |  | 25-03-2026 12:20 | 199.531 | 204.387 | 856.6 | 34.0645 | 32.9942 | 1.0703 | 197.9651 | 30.7 | 32.5224 | -1.8224 | 0.97624 | 25-03-2026 12:20 | 200.765 | 203.719 | 864.2 | 33.9532 | 32.9942 | 0.95898 | 197.9651 | 31 | 32.5224 | -1.5224 | 0.9855 | 25-03-2026 12:20 | 150.817 | 152.943 | 640.5 | 25.4905 | 24.4401 | 1.0504 | 146.6408 | 23 | 24.0906 | -1.0906 | 0.9861 | 25-03-2026 12:20 | 148.329 | 150.564 | 638.6 | 25.094 | 24.4401 | 0.65386 | 146.6408 | 22.9 | 24.0906 | -1.1906 | 0.98516 | 25-03-2026 12:20 | 148.25 | 150.669 | 637.5 | 25.1115 | 24.4401 | 0.67136 | 146.6408 | 22.8 | 24.0906 | -1.2906 | 0.98394 | 25-03-2026 12:20 | 149.619 | 154.182 | 642.8 | 25.697 | 24.4401 | 1.2569 | 146.6408 | 23 | 24.0906 | -1.0906 | 0.97041 | 25-03-2026 12:20 | 141.311 | 143.288 | 608.1 | 23.8813 | 23.2518 | 0.62957 | 139.5106 | 21.8 | 22.9193 | -1.1193 | 0.9862 | 25-03-2026 12:20 | 226.9497 | 252.9891 | -26.0394 | 1517.9344 | 206.2 | 249.3713 | -43.1713 | -20.7497
25-03-2026 12:10 | 632 | 51.09 | 229.595 | 233.115 | 832.7 | 38.8525 | 37.3029 | 1.5496 | 223.8175 | 43.1 | 36.7695 | 6.3305 | 0.9849 | 25-03-2026 12:10 | 275.032 | 279.504 | 838.3 | 46.584 | 37.3029 | 9.2811 | 223.8175 | 42.9 | 36.7695 | 6.1305 | 0.984 | 25-03-2026 12:10 | 215.621 | 221.008 | 825.9 | 36.8347 | 37.3029 | -0.46824 | 223.8175 | 43.7 | 36.7695 | 6.9305 | 0.97563 | 25-03-2026 12:10 | 219.596 | 222.963 | 833.2 | 37.1605 | 37.3029 | -0.14241 | 223.8175 | 44.3 | 36.7695 | 7.5305 | 0.9849 | 25-03-2026 12:10 | 163.929 | 162.969 | 617.5 | 27.1615 | 27.6318 | -0.47029 | 165.7907 | 32.7 | 27.2367 | 5.4633 | 1.0059 | 25-03-2026 12:10 | 164.96 | 167.353 | 615.7 | 27.8922 | 27.6318 | 0.26038 | 165.7907 | 32.3 | 27.2367 | 5.0633 | 0.9857 | 25-03-2026 12:10 | 161.976 | 164.548 | 614.7 | 27.4247 | 27.6318 | -0.20712 | 165.7907 | 32 | 27.2367 | 4.7633 | 0.98437 | 25-03-2026 12:10 | 163.84 | 168.354 | 619.8 | 28.059 | 27.6318 | 0.42721 | 165.7907 | 32.3 | 27.2367 | 5.0633 | 0.97319 | 25-03-2026 12:10 | 155.819 | 158.096 | 586.3 | 26.3493 | 26.2882 | 0.061112 | 157.7293 | 30.6 | 25.9123 | 4.6877 | 0.9856 | 25-03-2026 12:10 | 296.3183 | 286.027 | 10.2913 | 1716.162 | 333.9 | 281.9368 | 51.9632 | 37.5817
25-03-2026 12:00 | 916 | 51.09 | 321.802 | 327.234 | 789.6 | 54.539 | 54.0656 | 0.47339 | 324.3937 | 41.1 | 53.2925 | -12.1925 | 0.9834 | 25-03-2026 12:00 | 324.133 | 329.671 | 795.4 | 54.9452 | 54.0656 | 0.87956 | 324.3937 | 41 | 53.2925 | -12.2925 | 0.9832 | 25-03-2026 12:00 | 313.829 | 323.204 | 782.2 | 53.8673 | 54.0656 | -0.19828 | 324.3937 | 39.6 | 53.2925 | -13.6925 | 0.97099 | 25-03-2026 12:00 | 314.435 | 319.018 | 788.9 | 53.1697 | 54.0656 | -0.89594 | 324.3937 | 39.8 | 53.2925 | -13.4925 | 0.98563 | 25-03-2026 12:00 | 237.671 | 240.65 | 584.8 | 40.1083 | 40.0486 | 0.059733 | 240.2916 | 30.2 | 39.4759 | -9.2759 | 0.98762 | 25-03-2026 12:00 | 232.442 | 237.348 | 583.4 | 39.558 | 40.0486 | -0.4906 | 240.2916 | 29.9 | 39.4759 | -9.5759 | 0.97933 | 25-03-2026 12:00 | 235.486 | 240.786 | 582.7 | 40.131 | 40.0486 | 0.0824 | 240.2916 | 30 | 39.4759 | -9.4759 | 0.97799 | 25-03-2026 12:00 | 237.34 | 244.911 | 587.5 | 40.8185 | 40.0486 | 0.7699 | 240.2916 | 30.1 | 39.4759 | -9.3759 | 0.96909 | 25-03-2026 12:00 | 222.898 | 226.338 | 555.7 | 37.723 | 38.1013 | -0.37828 | 228.6077 | 28.5 | 37.5564 | -9.0564 | 0.9848 | 25-03-2026 12:00 | 414.86 | 414.5581 | 0.30188 | 2487.3487 | 310.2 | 408.6299 | -98.4299 | -104.66
25-03-2026 11:50 | 693 | 51.37 | 239.401 | 243.181 | 748.5 | 40.5302 | 40.8592 | -0.32907 | 245.1554 | 40.9 | 40.2749 | 0.62505 | 0.98446 | 25-03-2026 11:50 | 253.252 | 257.265 | 754.4 | 42.8775 | 40.8592 | 2.0183 | 245.1554 | 43.3 | 40.2749 | 3.0251 | 0.9844 | 25-03-2026 11:50 | 248.074 | 254.544 | 742.6 | 42.424 | 40.8592 | 1.5648 | 245.1554 | 41 | 40.2749 | 0.72505 | 0.97458 | 25-03-2026 11:50 | 247.176 | 251.093 | 749.1 | 41.8488 | 40.8592 | 0.9896 | 245.1554 | 41.3 | 40.2749 | 1.0251 | 0.9844 | 25-03-2026 11:50 | 183.543 | 186.225 | 554.6 | 31.0375 | 30.2661 | 0.7714 | 181.5966 | 30.7 | 29.8333 | 0.8667 | 0.9856 | 25-03-2026 11:50 | 180.149 | 183.614 | 553.5 | 30.6023 | 30.2661 | 0.33623 | 181.5966 | 30.4 | 29.8333 | 0.5667 | 0.98113 | 25-03-2026 11:50 | 183.45 | 186.582 | 552.7 | 31.097 | 30.2661 | 0.8309 | 181.5966 | 30.8 | 29.8333 | 0.9667 | 0.98321 | 25-03-2026 11:50 | 184.938 | 190.33 | 557.4 | 31.7217 | 30.2661 | 1.4556 | 181.5966 | 30.7 | 29.8333 | 0.8667 | 0.97167 | 25-03-2026 11:50 | 174.398 | 176.91 | 527.2 | 29.485 | 28.7944 | 0.69055 | 172.7667 | 29 | 28.3827 | 0.61731 | 0.9858 | 25-03-2026 11:50 | 321.624 | 313.2958 | 8.3282 | 1879.7747 | 318.1 | 308.8157 | 9.2843 | -3.524
25-03-2026 11:40 | 610 | 51.09 | 212.808 | 215.961 | 707.6 | 35.9935 | 36.0044 | -0.010891 | 216.0263 | 41.7 | 35.4895 | 6.2105 | 0.9854 | 25-03-2026 11:40 | 221.348 | 220.61 | 711.1 | 36.7683 | 36.0044 | 0.76394 | 216.0263 | 40.2 | 35.4895 | 4.7105 | 1.0033 | 25-03-2026 11:40 | 212.406 | 217.827 | 701.6 | 36.3045 | 36.0044 | 0.30011 | 216.0263 | 39.9 | 35.4895 | 4.4105 | 0.97511 | 25-03-2026 11:40 | 215.5 | 218.76 | 707.8 | 36.46 | 36.0044 | 0.45561 | 216.0263 | 40.3 | 35.4895 | 4.8105 | 0.9851 | 25-03-2026 11:40 | 161.051 | 163.371 | 523.9 | 27.2285 | 26.6699 | 0.55858 | 160.0195 | 29.6 | 26.2885 | 3.3115 | 0.9858 | 25-03-2026 11:40 | 161.678 | 163.974 | 523.1 | 27.329 | 26.6699 | 0.65908 | 160.0195 | 29.4 | 26.2885 | 3.1115 | 0.986 | 25-03-2026 11:40 | 163.315 | 166.211 | 521.9 | 27.7018 | 26.6699 | 1.0319 | 160.0195 | 29.3 | 26.2885 | 3.0115 | 0.98258 | 25-03-2026 11:40 | 162.257 | 166.825 | 526.7 | 27.8042 | 26.6699 | 1.1342 | 160.0195 | 29.9 | 26.2885 | 3.6115 | 0.97262 | 25-03-2026 11:40 | 153.726 | 156.403 | 498.2 | 26.0672 | 25.3731 | 0.69404 | 152.2387 | 28.3 | 25.0103 | 3.2897 | 0.98288 | 25-03-2026 11:40 | 281.657 | 276.0704 | 5.5866 | 1656.4222 | 308.6 | 272.1226 | 36.4774 | 26.943
25-03-2026 11:30 | 609 | 51.66 | 211.953 | 215.159 | 665.9 | 35.8598 | 35.8664 | -0.0066165 | 215.1987 | 45.1 | 35.3536 | 9.7464 | 0.9851 | 25-03-2026 11:30 | 219.836 | 223.206 | 670.9 | 37.201 | 35.8664 | 1.3346 | 215.1987 | 45.6 | 35.3536 | 10.2464 | 0.9849 | 25-03-2026 11:30 | 210.357 | 216.897 | 661.7 | 36.1495 | 35.8664 | 0.28305 | 215.1987 | 45.6 | 35.3536 | 10.2464 | 0.96985 | 25-03-2026 11:30 | 211.37 | 214.589 | 667.5 | 35.7648 | 35.8664 | -0.10162 | 215.1987 | 46.1 | 35.3536 | 10.7464 | 0.985 | 25-03-2026 11:30 | 158.822 | 161.142 | 494.3 | 26.857 | 26.5677 | 0.28926 | 159.4064 | 34.1 | 26.1878 | 7.9122 | 0.9856 | 25-03-2026 11:30 | 155.516 | 158.37 | 493.7 | 26.395 | 26.5677 | -0.17274 | 159.4064 | 33.9 | 26.1878 | 7.7122 | 0.98198 | 25-03-2026 11:30 | 157.311 | 159.577 | 492.6 | 26.5962 | 26.5677 | 0.028426 | 159.4064 | 33.5 | 26.1878 | 7.3122 | 0.9858 | 25-03-2026 11:30 | 159.055 | 163.241 | 496.8 | 27.2068 | 26.5677 | 0.63909 | 159.4064 | 33.7 | 26.1878 | 7.5122 | 0.97436 | 25-03-2026 11:30 | 151.518 | 153.701 | 469.9 | 25.6168 | 25.2759 | 0.34092 | 151.6555 | 32.4 | 24.9145 | 7.4855 | 0.9858 | 25-03-2026 11:30 | 277.647 | 275.0127 | 2.6343 | 1650.0761 | 350 | 271.08 | 78.92 | 72.353
25-03-2026 11:20 | 801 | 51.37 | 286.811 | 258.891 | 620.8 | 43.1485 | 47.2269 | -4.0784 | 283.3615 | 38 | 46.5516 | -8.5516 | 1.1078 | 25-03-2026 11:20 | 278.062 | 282.583 | 625.3 | 47.0972 | 47.2269 | -0.12974 | 283.3615 | 37.5 | 46.5516 | -9.0516 | 0.984 | 25-03-2026 11:20 | 275.134 | 282.63 | 616.1 | 47.105 | 47.2269 | -0.12191 | 283.3615 | 36.1 | 46.5516 | -10.4516 | 0.97348 | 25-03-2026 11:20 | 276.528 | 281.024 | 621.4 | 46.8373 | 47.2269 | -0.38958 | 283.3615 | 36.6 | 46.5516 | -9.9516 | 0.984 | 25-03-2026 11:20 | 208.519 | 211.651 | 460.2 | 35.2752 | 34.9829 | 0.29227 | 209.8974 | 27.1 | 34.4826 | -7.3826 | 0.9852 | 25-03-2026 11:20 | 206.118 | 209.894 | 459.8 | 34.9823 | 34.9829 | -0.0005618 | 209.8974 | 27 | 34.4826 | -7.4826 | 0.98201 | 25-03-2026 11:20 | 207.069 | 210.557 | 459.1 | 35.0928 | 34.9829 | 0.10994 | 209.8974 | 26.8 | 34.4826 | -7.6826 | 0.98343 | 25-03-2026 11:20 | 209.008 | 214.873 | 463.1 | 35.8122 | 34.9829 | 0.82927 | 209.8974 | 27.1 | 34.4826 | -7.3826 | 0.9727 | 25-03-2026 11:20 | 190.906 | 193.735 | 437.5 | 32.2892 | 33.2819 | -0.99273 | 199.6914 | 25.2 | 32.806 | -7.606 | 0.9854 | 25-03-2026 11:20 | 357.6397 | 362.1211 | -4.4814 | 2172.7266 | 281.4 | 356.9428 | -75.5428 | -76.2397
25-03-2026 11:10 | 1012 | 51.37 | 228.722 | 236.726 | 582.8 | 39.4543 | 59.6675 | -20.2131 | 358.0047 | 52.7 | 58.8142 | -6.1142 | 0.96619 | 25-03-2026 11:10 | 350.898 | 267.078 | 587.8 | 44.513 | 59.6675 | -15.1545 | 358.0047 | 57.2 | 58.8142 | -1.6142 | 1.3138 | 25-03-2026 11:10 | 351.587 | 362.859 | 580 | 60.4765 | 59.6675 | 0.80905 | 358.0047 | 55.1 | 58.8142 | -3.7142 | 0.96894 | 25-03-2026 11:10 | 345.634 | 351.898 | 584.8 | 58.6497 | 59.6675 | -1.0178 | 358.0047 | 55.7 | 58.8142 | -3.1142 | 0.9822 | 25-03-2026 11:10 | 267.534 | 270.86 | 433.1 | 45.1433 | 44.1981 | 0.94522 | 265.1887 | 42.2 | 43.5661 | -1.3661 | 0.98772 | 25-03-2026 11:10 | 260.174 | 266.713 | 432.8 | 44.4522 | 44.1981 | 0.25405 | 265.1887 | 41.2 | 43.5661 | -2.3661 | 0.97548 | 25-03-2026 11:10 | 266.054 | 272.512 | 432.3 | 45.4187 | 44.1981 | 1.2206 | 265.1887 | 41.3 | 43.5661 | -2.2661 | 0.9763 | 25-03-2026 11:10 | 268.464 | 277.575 | 436 | 46.2625 | 44.1981 | 2.0644 | 265.1887 | 41.6 | 43.5661 | -1.9661 | 0.96718 | 25-03-2026 11:10 | 251.675 | 256.132 | 412.3 | 42.6887 | 42.049 | 0.63963 | 252.2942 | 39.4 | 41.4477 | -2.0477 | 0.9826 | 25-03-2026 11:10 | 427.0588 | 457.5113 | -30.4525 | 2745.0679 | 426.4 | 450.9689 | -24.5689 | -0.65883
25-03-2026 11:00 | 1048 | 51.66 | 349.125 | 355.307 | 530.1 | 59.2178 | 61.7209 | -2.5031 | 370.3255 | 56.9 | 60.8383 | -3.9383 | 0.9826 | 25-03-2026 11:00 | 352.831 | 358.86 | 530.6 | 59.81 | 61.7209 | -1.9109 | 370.3255 | 55.8 | 60.8383 | -5.0383 | 0.9832 | 25-03-2026 11:00 | 346.914 | 356.675 | 524.9 | 59.4458 | 61.7209 | -2.2751 | 370.3255 | 55.8 | 60.8383 | -5.0383 | 0.97263 | 25-03-2026 11:00 | 350.421 | 356.699 | 529.1 | 59.4498 | 61.7209 | -2.2711 | 370.3255 | 56.2 | 60.8383 | -4.6383 | 0.9824 | 25-03-2026 11:00 | 261.528 | 265.754 | 390.9 | 44.2923 | 45.7192 | -1.4269 | 274.3152 | 41.3 | 45.0654 | -3.7654 | 0.9841 | 25-03-2026 11:00 | 258.869 | 263.832 | 391.6 | 43.972 | 45.7192 | -1.7472 | 274.3152 | 41.6 | 45.0654 | -3.4654 | 0.98119 | 25-03-2026 11:00 | 259.569 | 264.352 | 391 | 44.0587 | 45.7192 | -1.6605 | 274.3152 | 41.7 | 45.0654 | -3.3654 | 0.98191 | 25-03-2026 11:00 | 261.514 | 269.415 | 394.4 | 44.9025 | 45.7192 | -0.8167 | 274.3152 | 42.1 | 45.0654 | -2.9654 | 0.97067 | 25-03-2026 11:00 | 247.087 | 251.003 | 372.9 | 41.8338 | 43.4962 | -1.6623 | 260.9769 | 40.3 | 42.8742 | -2.5742 | 0.9844 | 25-03-2026 11:00 | 456.9828 | 473.2566 | -16.2738 | 2839.5398 | 431.7 | 466.4891 | -34.7891 | -25.2828
25-03-2026 10:50 | 959 | 51.37 | 326.658 | 332.037 | 473.2 | 55.3395 | 56.5426 | -1.2031 | 339.2555 | 39.7 | 55.734 | -16.034 | 0.9838 | 25-03-2026 10:50 | 346.647 | 352.534 | 474.8 | 58.7557 | 56.5426 | 2.2131 | 339.2555 | 38.9 | 55.734 | -16.834 | 0.9833 | 25-03-2026 10:50 | 319.697 | 327.347 | 469.1 | 54.5578 | 56.5426 | -1.9847 | 339.2555 | 39.2 | 55.734 | -16.534 | 0.97663 | 25-03-2026 10:50 | 329.153 | 334.675 | 472.9 | 55.7792 | 56.5426 | -0.76341 | 339.2555 | 39.4 | 55.734 | -16.334 | 0.9835 | 25-03-2026 10:50 | 242.975 | 247.666 | 349.6 | 41.2777 | 41.8834 | -0.60572 | 251.3003 | 29.8 | 41.2845 | -11.4845 | 0.98106 | 25-03-2026 10:50 | 240.753 | 244.708 | 350 | 40.7847 | 41.8834 | -1.0987 | 251.3003 | 29.5 | 41.2845 | -11.7845 | 0.98384 | 25-03-2026 10:50 | 249.518 | 254.736 | 349.3 | 42.456 | 41.8834 | 0.57261 | 251.3003 | 29.5 | 41.2845 | -11.7845 | 0.97952 | 25-03-2026 10:50 | 253.542 | 261.805 | 352.3 | 43.6342 | 41.8834 | 1.7508 | 251.3003 | 29.5 | 41.2845 | -11.7845 | 0.96844 | 25-03-2026 10:50 | 234.392 | 237.889 | 332.6 | 39.6482 | 39.8469 | -0.19869 | 239.0812 | 27.5 | 39.277 | -11.777 | 0.9853 | 25-03-2026 10:50 | 432.2328 | 433.5507 | -1.3179 | 2601.3044 | 303 | 427.351 | -124.351 | -129.2328
25-03-2026 10:40 | 447 | 51.09 | 158.415 | 160.534 | 433.5 | 26.7557 | 26.3835 | 0.37212 | 158.3013 | 35.9 | 26.0063 | 9.8937 | 0.9868 | 25-03-2026 10:40 | 158.92 | 161.127 | 435.9 | 26.8545 | 26.3835 | 0.47095 | 158.3013 | 36 | 26.0063 | 9.9937 | 0.9863 | 25-03-2026 10:40 | 157.285 | 160.418 | 429.9 | 26.7363 | 26.3835 | 0.35279 | 158.3013 | 35.9 | 26.0063 | 9.8937 | 0.98047 | 25-03-2026 10:40 | 158.178 | 160.359 | 433.5 | 26.7265 | 26.3835 | 0.34295 | 158.3013 | 36.1 | 26.0063 | 10.0937 | 0.9864 | 25-03-2026 10:40 | 117.037 | 118.603 | 319.8 | 19.7672 | 19.5434 | 0.2238 | 117.2602 | 26.4 | 19.2639 | 7.1361 | 0.9868 | 25-03-2026 10:40 | 116.294 | 117.832 | 320.5 | 19.6387 | 19.5434 | 0.0953 | 117.2602 | 26.3 | 19.2639 | 7.0361 | 0.98695 | 25-03-2026 10:40 | 116.19 | 117.732 | 319.8 | 19.622 | 19.5434 | 0.078633 | 117.2602 | 26.2 | 19.2639 | 6.9361 | 0.9869 | 25-03-2026 10:40 | 116.802 | 119.993 | 322.8 | 19.9988 | 19.5434 | 0.45547 | 117.2602 | 26.3 | 19.2639 | 7.0361 | 0.97341 | 25-03-2026 10:40 | 110.476 | 111.949 | 305.1 | 18.6582 | 18.5931 | 0.065074 | 111.5586 | 25 | 18.3272 | 6.6728 | 0.98684 | 25-03-2026 10:40 | 204.7578 | 202.3007 | 2.4571 | 1213.8045 | 274.1 | 199.4078 | 74.6922 | 69.3422
25-03-2026 10:30 | 496 | 50.8 | 178.908 | 181.301 | 397.6 | 30.2168 | 29.3084 | 0.90843 | 175.8504 | 34.2 | 28.8893 | 5.3107 | 0.9868 | 25-03-2026 10:30 | 179.811 | 182.29 | 399.9 | 30.3817 | 29.3084 | 1.0733 | 175.8504 | 34.7 | 28.8893 | 5.8107 | 0.9864 | 25-03-2026 10:30 | 177.084 | 180.631 | 394 | 30.1052 | 29.3084 | 0.79676 | 175.8504 | 33.5 | 28.8893 | 4.6107 | 0.98036 | 25-03-2026 10:30 | 179.281 | 181.753 | 397.4 | 30.2922 | 29.3084 | 0.98376 | 175.8504 | 33.7 | 28.8893 | 4.8107 | 0.9864 | 25-03-2026 10:30 | 132.181 | 133.922 | 293.4 | 22.3203 | 21.7099 | 0.61041 | 130.2596 | 25.1 | 21.3995 | 3.7005 | 0.987 | 25-03-2026 10:30 | 131.7 | 133.421 | 294.2 | 22.2368 | 21.7099 | 0.52691 | 130.2596 | 24.9 | 21.3995 | 3.5005 | 0.9871 | 25-03-2026 10:30 | 131.25 | 132.965 | 293.6 | 22.1608 | 21.7099 | 0.45091 | 130.2596 | 24.8 | 21.3995 | 3.4005 | 0.9871 | 25-03-2026 10:30 | 132.118 | 135.433 | 296.5 | 22.5722 | 21.7099 | 0.86224 | 130.2596 | 24.9 | 21.3995 | 3.5005 | 0.97552 | 25-03-2026 10:30 | 124.856 | 126.501 | 280.1 | 21.0835 | 20.6543 | 0.42919 | 123.9258 | 23.5 | 20.359 | 3.141 | 0.987 | 25-03-2026 10:30 | 231.3695 | 224.7276 | 6.6419 | 1348.3658 | 259.3 | 221.514 | 37.786 | 27.9305
25-03-2026 10:20 | 306 | 50.51 | 112.956 | 114.386 | 363.4 | 19.0643 | 18.1016 | 0.96277 | 108.6094 | 18.2 | 17.8427 | 0.35728 | 0.9875 | 25-03-2026 10:20 | 112.677 | 114.048 | 365.2 | 19.008 | 18.1016 | 0.90643 | 108.6094 | 18.3 | 17.8427 | 0.45728 | 0.98798 | 25-03-2026 10:20 | 112.257 | 114.239 | 360.5 | 19.0398 | 18.1016 | 0.93827 | 108.6094 | 18.3 | 17.8427 | 0.45728 | 0.98265 | 25-03-2026 10:20 | 112.611 | 114.048 | 363.7 | 19.008 | 18.1016 | 0.90643 | 108.6094 | 18.4 | 17.8427 | 0.55728 | 0.9874 | 25-03-2026 10:20 | 83.752 | 84.847 | 268.3 | 14.1412 | 13.4086 | 0.7326 | 80.4514 | 13.6 | 13.2168 | 0.38317 | 0.98709 | 25-03-2026 10:20 | 83.021 | 84.097 | 269.3 | 14.0162 | 13.4086 | 0.6076 | 80.4514 | 13.5 | 13.2168 | 0.28317 | 0.98721 | 25-03-2026 10:20 | 83.147 | 84.225 | 268.8 | 14.0375 | 13.4086 | 0.62893 | 80.4514 | 13.5 | 13.2168 | 0.28317 | 0.9872 | 25-03-2026 10:20 | 83.622 | 85.894 | 271.6 | 14.3157 | 13.4086 | 0.9071 | 80.4514 | 13.6 | 13.2168 | 0.38317 | 0.97355 | 25-03-2026 10:20 | 78.8 | 79.846 | 256.6 | 13.3077 | 12.7566 | 0.55107 | 76.5396 | 12.8 | 12.5742 | 0.22583 | 0.9869 | 25-03-2026 10:20 | 145.9383 | 138.7971 | 7.1412 | 832.7828 | 140.2 | 136.8123 | 3.3877 | -5.7383
25-03-2026 10:10 | 295 | 50.23 | 111.16 | 113.17 | 345.2 | 18.8617 | 17.4696 | 1.392 | 104.8178 | 18.1 | 17.2198 | 0.88018 | 0.98224 | 25-03-2026 10:10 | 112.18 | 113.612 | 346.9 | 18.9353 | 17.4696 | 1.4657 | 104.8178 | 38 | 17.2198 | 20.7802 | 0.9874 | 25-03-2026 10:10 | 110.807 | 112.587 | 342.2 | 18.7645 | 17.4696 | 1.2949 | 104.8178 | 17.7 | 17.2198 | 0.48018 | 0.98419 | 25-03-2026 10:10 | 111.313 | 112.733 | 345.3 | 18.7888 | 17.4696 | 1.3192 | 104.8178 | 17.8 | 17.2198 | 0.58018 | 0.9874 | 25-03-2026 10:10 | 82.58 | 83.659 | 254.7 | 13.9432 | 12.9405 | 1.0027 | 77.6428 | 13.2 | 12.7554 | 0.44458 | 0.9871 | 25-03-2026 10:10 | 81.855 | 82.916 | 255.8 | 13.8193 | 12.9405 | 0.87886 | 77.6428 | 13.1 | 12.7554 | 0.34458 | 0.9872 | 25-03-2026 10:10 | 81.791 | 82.841 | 255.3 | 13.8068 | 12.9405 | 0.86636 | 77.6428 | 13.3 | 12.7554 | 0.54458 | 0.98733 | 25-03-2026 10:10 | 82.212 | 84.313 | 258 | 14.0522 | 12.9405 | 1.1117 | 77.6428 | 13.3 | 12.7554 | 0.54458 | 0.97508 | 25-03-2026 10:10 | 77.642 | 78.689 | 243.8 | 13.1148 | 12.3113 | 0.80358 | 73.8675 | 12.6 | 12.1352 | 0.4648 | 0.98669 | 25-03-2026 10:10 | 144.0867 | 133.9517 | 10.135 | 803.7101 | 157.1 | 132.0362 | 25.0638 | 13.0133
25-03-2026 10:00 | 305 | 50.51 | 115.001 | 116.433 | 327.1 | 19.4055 | 18.0424 | 1.3631 | 108.2545 | 20.5 | 17.7844 | 2.7156 | 0.9877 |  |  |  |  | 0 | 18.0424 | -18.0424 | 108.2545 | 0 | 17.7844 | -17.7844 |  | 25-03-2026 10:00 | 114.018 | 115.725 | 324.5 | 19.2875 | 18.0424 | 1.2451 | 108.2545 | 19.5 | 17.7844 | 1.7156 | 0.98525 | 25-03-2026 10:00 | 114.804 | 116.269 | 327.5 | 19.3782 | 18.0424 | 1.3358 | 108.2545 | 19.9 | 17.7844 | 2.1156 | 0.9874 | 25-03-2026 10:00 | 84.809 | 85.891 | 241.5 | 14.3152 | 13.3647 | 0.95042 | 80.1885 | 14.7 | 13.1736 | 1.5264 | 0.9874 | 25-03-2026 10:00 | 84.328 | 85.421 | 242.7 | 14.2368 | 13.3647 | 0.87208 | 80.1885 | 14.6 | 13.1736 | 1.4264 | 0.9872 | 25-03-2026 10:00 | 84.303 | 85.396 | 242 | 14.2327 | 13.3647 | 0.86792 | 80.1885 | 14.4 | 13.1736 | 1.2264 | 0.9872 | 25-03-2026 10:00 | 84.819 | 87.005 | 244.7 | 14.5008 | 13.3647 | 1.1361 | 80.1885 | 14.5 | 13.1736 | 1.3264 | 0.97488 | 25-03-2026 10:00 | 80.161 | 81.217 | 231.2 | 13.5362 | 12.7149 | 0.82126 | 76.2894 | 13.7 | 12.5331 | 1.1669 | 0.987 | 25-03-2026 10:00 | 128.8928 | 138.3436 | -9.4507 | 830.0613 | 131.8 | 136.3652 | -4.5652 | 2.9072
25-03-2026 09:50 | 318 | 50.23 | 118.359 | 119.869 | 306.6 | 19.9782 | 18.8317 | 1.1465 | 112.9901 | 24.7 | 18.5624 | 6.1376 |  | 25-03-2026 09:50 | 118.313 | 119.847 | 308.9 | 19.9745 | 18.8317 | 1.1428 | 112.9901 | 25.4 | 18.5624 | 6.8376 |  | 25-03-2026 09:50 | 116.737 | 118.846 | 305 | 19.8077 | 18.8317 | 0.97599 | 112.9901 | 24.8 | 18.5624 | 6.2376 |  | 25-03-2026 09:50 | 117.531 | 119.067 | 307.6 | 19.8445 | 18.8317 | 1.0128 | 112.9901 | 24.8 | 18.5624 | 6.2376 |  | 25-03-2026 09:50 | 87.025 | 88.144 | 226.8 | 14.6907 | 13.9494 | 0.74128 | 83.6963 | 18.3 | 13.7499 | 4.5501 |  | 25-03-2026 09:50 | 86.522 | 87.653 | 228.1 | 14.6088 | 13.9494 | 0.65944 | 83.6963 | 18.3 | 13.7499 | 4.5501 |  | 25-03-2026 09:50 | 86.374 | 87.52 | 227.6 | 14.5867 | 13.9494 | 0.63728 | 83.6963 | 18.2 | 13.7499 | 4.4501 |  | 25-03-2026 09:50 | 86.989 | 89.405 | 230.2 | 14.9008 | 13.9494 | 0.95144 | 83.6963 | 18.4 | 13.7499 | 4.6501 |  | 25-03-2026 09:50 | 82.084 | 83.19 | 217.5 | 13.865 | 13.2711 | 0.59388 | 79.6267 | 17.7 | 13.0813 | 4.6187 |  | 25-03-2026 09:50 | 152.2568 | 144.3954 | 7.8615 | 866.3723 | 190.6 | 142.3305 | 48.2695 | 38.3432
25-03-2026 09:40 | 633 | 50.8 | 222.777 | 225.826 | 281.9 | 37.6377 | 37.4037 | 0.234 | 224.422 | 32.9 | 36.8688 | -3.9688 |  | 25-03-2026 09:40 | 214.091 | 217.065 | 283.5 | 36.1775 | 37.4037 | -1.2262 | 224.422 | 33.2 | 36.8688 | -3.6688 |  | 25-03-2026 09:40 | 221.542 | 225.534 | 280.2 | 37.589 | 37.4037 | 0.18533 | 224.422 | 32.6 | 36.8688 | -4.2688 |  | 25-03-2026 09:40 | 229.032 | 232.237 | 282.8 | 38.7062 | 37.4037 | 1.3025 | 224.422 | 32.9 | 36.8688 | -3.9688 |  | 25-03-2026 09:40 | 164.935 | 167.124 | 208.5 | 27.854 | 27.7064 | 0.14758 | 166.2385 | 24.4 | 27.3102 | -2.9102 |  | 25-03-2026 09:40 | 167.592 | 169.799 | 209.8 | 28.2998 | 27.7064 | 0.59341 | 166.2385 | 24.3 | 27.3102 | -3.0102 |  | 25-03-2026 09:40 | 162.314 | 164.435 | 209.4 | 27.4058 | 27.7064 | -0.30059 | 166.2385 | 24.2 | 27.3102 | -3.1102 |  | 25-03-2026 09:40 | 164.693 | 168.339 | 211.8 | 28.0565 | 27.7064 | 0.35008 | 166.2385 | 24.4 | 27.3102 | -2.9102 |  | 25-03-2026 09:40 | 157.766 | 159.86 | 199.8 | 26.6433 | 26.3592 | 0.28411 | 158.1554 | 22.8 | 25.9823 | -3.1823 |  | 25-03-2026 09:40 | 288.3698 | 286.7996 | 1.5703 | 1720.7974 | 251.7 | 282.6983 | -30.9983 | -36.6698
25-03-2026 09:30 | 686 | 50.8 | 245.394 | 248.853 | 249 | 41.4755 | 40.5354 | 0.94009 | 243.2125 | 31.5 | 39.9558 | -8.4558 |  | 25-03-2026 09:30 | 255.793 | 259.504 | 250.3 | 43.2507 | 40.5354 | 2.7153 | 243.2125 | 31.1 | 39.9558 | -8.8558 |  | 25-03-2026 09:30 | 245.641 | 250.856 | 247.6 | 41.8093 | 40.5354 | 1.2739 | 243.2125 | 30.6 | 39.9558 | -9.3558 |  | 25-03-2026 09:30 | 247.845 | 251.434 | 249.9 | 41.9057 | 40.5354 | 1.3703 | 243.2125 | 30.9 | 39.9558 | -9.0558 |  | 25-03-2026 09:30 | 184.118 | 186.562 | 184.1 | 31.0937 | 30.0262 | 1.0674 | 180.1574 | 23.3 | 29.5969 | -6.2969 |  | 25-03-2026 09:30 | 184.557 | 187.026 | 185.5 | 31.171 | 30.0262 | 1.1448 | 180.1574 | 23.3 | 29.5969 | -6.2969 |  | 25-03-2026 09:30 | 183.441 | 185.876 | 185.2 | 30.9793 | 30.0262 | 0.9531 | 180.1574 | 23.3 | 29.5969 | -6.2969 |  | 25-03-2026 09:30 | 184.588 | 189.46 | 187.4 | 31.5767 | 30.0262 | 1.5504 | 180.1574 | 23.4 | 29.5969 | -6.1969 |  | 25-03-2026 09:30 | 175.382 | 177.728 | 177 | 29.6213 | 28.5662 | 1.0551 | 171.3974 | 22.2 | 28.1577 | -5.9577 |  | 25-03-2026 09:30 | 322.8832 | 310.8128 | 12.0704 | 1864.8768 | 239.6 | 306.3682 | -66.7682 | -83.2832
25-03-2026 09:20 | 715 | 50.8 | 266.305 | 270.114 | 217.5 | 45.019 | 42.249 | 2.77 | 253.494 | 30.4 | 41.6448 | -11.2448 |  | 25-03-2026 09:20 | 232.453 | 267.918 | 219.2 | 44.653 | 42.249 | 2.404 | 253.494 | 30.1 | 41.6448 | -11.5448 |  | 25-03-2026 09:20 | 232.324 | 240.42 | 217 | 40.07 | 42.249 | -2.179 | 253.494 | 30.2 | 41.6448 | -11.4448 |  | 25-03-2026 09:20 | 250.558 | 254.141 | 219 | 42.3568 | 42.249 | 0.10783 | 253.494 | 30.4 | 41.6448 | -11.2448 |  | 25-03-2026 09:20 | 186.992 | 189.436 | 160.8 | 31.5727 | 31.2956 | 0.27711 | 187.7734 | 22.6 | 30.848 | -8.248 |  | 25-03-2026 09:20 | 190.659 | 193.17 | 162.2 | 32.195 | 31.2956 | 0.89944 | 187.7734 | 22.5 | 30.848 | -8.348 |  | 25-03-2026 09:20 | 184.815 | 187.249 | 161.9 | 31.2082 | 31.2956 | -0.087394 | 187.7734 | 22.5 | 30.848 | -8.348 |  | 25-03-2026 09:20 | 189.632 | 194.195 | 164 | 32.3658 | 31.2956 | 1.0703 | 187.7734 | 22.7 | 30.848 | -8.148 |  | 25-03-2026 09:20 | 181.477 | 183.849 | 154.8 | 30.6415 | 29.7739 | 0.86765 | 178.6431 | 21.4 | 29.3481 | -7.9481 |  | 25-03-2026 09:20 | 330.082 | 323.9521 | 6.1299 | 1943.7127 | 232.8 | 319.3196 | -86.5196 | -97.282
25-03-2026 09:10 | 678 | 50.8 | 236.211 | 239.419 | 187.1 | 39.9032 | 40.0627 | -0.15953 | 240.3762 | 26.7 | 39.4898 | -12.7898 |  | 25-03-2026 09:10 | 245.475 | 248.91 | 189.1 | 41.485 | 40.0627 | 1.4223 | 240.3762 | 28.3 | 39.4898 | -11.1898 |  | 25-03-2026 09:10 | 240.721 | 245.464 | 186.8 | 40.9107 | 40.0627 | 0.84797 | 240.3762 | 27.7 | 39.4898 | -11.7898 |  | 25-03-2026 09:10 | 243.15 | 246.527 | 188.6 | 41.0878 | 40.0627 | 1.0251 | 240.3762 | 28 | 39.4898 | -11.4898 |  | 25-03-2026 09:10 | 179.537 | 181.846 | 138.2 | 30.3077 | 29.6761 | 0.6316 | 178.0564 | 20.4 | 29.2517 | -8.8517 |  | 25-03-2026 09:10 | 180.461 | 182.764 | 139.7 | 30.4607 | 29.6761 | 0.7846 | 178.0564 | 20.4 | 29.2517 | -8.8517 |  | 25-03-2026 09:10 | 179.474 | 181.833 | 139.4 | 30.3055 | 29.6761 | 0.62943 | 178.0564 | 20.4 | 29.2517 | -8.8517 |  | 25-03-2026 09:10 | 181.288 | 186.133 | 141.3 | 31.0222 | 29.6761 | 1.3461 | 178.0564 | 20.6 | 29.2517 | -8.6517 |  | 25-03-2026 09:10 | 171.949 | 174.161 | 133.4 | 29.0268 | 28.2331 | 0.79373 | 169.3986 | 19.4 | 27.8294 | -8.4294 |  | 25-03-2026 09:10 | 314.5095 | 307.1882 | 7.3213 | 1843.129 | 211.9 | 302.7954 | -90.8954 | -102.6095
25-03-2026 09:00 | 416 | 49.65 | 157.512 | 159.457 | 160.4 | 26.5762 | 24.69 | 1.8862 | 148.14 | 18.7 | 24.3369 | -5.6369 |  | 25-03-2026 09:00 | 137.382 | 150.161 | 160.8 | 25.0268 | 24.69 | 0.33683 | 148.14 | 18.9 | 24.3369 | -5.4369 |  | 25-03-2026 09:00 | 152.437 | 164.083 | 159.1 | 27.3472 | 24.69 | 2.6572 | 148.14 | 18.5 | 24.3369 | -5.8369 |  | 25-03-2026 09:00 | 147.007 | 148.853 | 160.6 | 24.8088 | 24.69 | 0.11883 | 148.14 | 18.2 | 24.3369 | -6.1369 |  | 25-03-2026 09:00 | 115.5 | 116.551 | 117.8 | 19.4252 | 18.2889 | 1.1363 | 109.7333 | 13.5 | 18.0274 | -4.5274 |  | 25-03-2026 09:00 | 110.504 | 112.335 | 119.3 | 18.7225 | 18.2889 | 0.43361 | 109.7333 | 13.4 | 18.0274 | -4.6274 |  | 25-03-2026 09:00 | 115.374 | 117.491 | 119 | 19.5818 | 18.2889 | 1.2929 | 109.7333 | 13.5 | 18.0274 | -4.5274 |  | 25-03-2026 09:00 | 114.09 | 118.555 | 120.7 | 19.7592 | 18.2889 | 1.4703 | 109.7333 | 13.5 | 18.0274 | -4.5274 |  | 25-03-2026 09:00 | 105.315 | 106.605 | 114 | 17.7675 | 17.3996 | 0.36789 | 104.3977 | 13 | 17.1508 | -4.1508 |  | 25-03-2026 09:00 | 199.0152 | 189.3152 | 9.7 | 1135.8911 | 141.2 | 186.608 | -45.408 | -57.8152
25-03-2026 08:50 | 316 | 49.94 | 117.155 | 118.602 | 141.7 | 19.767 | 18.7341 | 1.0329 | 112.4044 | 24.2 | 18.4662 | 5.7338 |  | 25-03-2026 08:50 | 120.475 | 121.988 | 141.9 | 20.3313 | 18.7341 | 1.5973 | 112.4044 | 24.4 | 18.4662 | 5.9338 |  | 25-03-2026 08:50 | 112.216 | 113.825 | 140.6 | 18.9708 | 18.7341 | 0.23676 | 112.4044 | 24.1 | 18.4662 | 5.6338 |  | 25-03-2026 08:50 | 112.012 | 113.43 | 142.4 | 18.905 | 18.7341 | 0.17093 | 112.4044 | 24.4 | 18.4662 | 5.9338 |  | 25-03-2026 08:50 | 82.496 | 83.549 | 104.3 | 13.9248 | 13.8771 | 0.047744 | 83.2625 | 17.9 | 13.6786 | 4.2214 |  | 25-03-2026 08:50 | 81.926 | 82.988 | 105.9 | 13.8313 | 13.8771 | -0.045756 | 83.2625 | 18 | 13.6786 | 4.3214 |  | 25-03-2026 08:50 | 82.623 | 83.686 | 105.5 | 13.9477 | 13.8771 | 0.070577 | 83.2625 | 17.9 | 13.6786 | 4.2214 |  | 25-03-2026 08:50 | 83.226 | 85.797 | 107.2 | 14.2995 | 13.8771 | 0.42241 | 83.2625 | 18.1 | 13.6786 | 4.4214 |  | 25-03-2026 08:50 | 79.463 | 80.493 | 101 | 13.4155 | 13.2023 | 0.21317 | 79.214 | 16.9 | 13.0135 | 3.8865 |  | 25-03-2026 08:50 | 147.393 | 143.647 | 3.746 | 861.8819 | 185.9 | 141.5928 | 44.3072 | 38.507
25-03-2026 08:40 | 453 | 47.93 | 151.784 | 154.119 | 117.5 | 25.6865 | 27.0631 | -1.3766 | 162.3787 | 15.5 | 26.6761 | -11.1761 |  | 25-03-2026 08:40 | 160.369 | 162.366 | 117.5 | 27.061 | 27.0631 | -0.0021229 | 162.3787 | 15.4 | 26.6761 | -11.2761 |  | 25-03-2026 08:40 | 161.24 | 164.465 | 116.5 | 27.4108 | 27.0631 | 0.34771 | 162.3787 | 15.8 | 26.6761 | -10.8761 |  | 25-03-2026 08:40 | 162.594 | 164.635 | 118 | 27.4392 | 27.0631 | 0.37604 | 162.3787 | 15.8 | 26.6761 | -10.8761 |  | 25-03-2026 08:40 | 119.806 | 121.237 | 86.4 | 20.2062 | 20.0468 | 0.15941 | 120.2805 | 11.9 | 19.7601 | -7.8601 |  | 25-03-2026 08:40 | 119.774 | 121.192 | 87.9 | 20.1987 | 20.0468 | 0.15191 | 120.2805 | 11.9 | 19.7601 | -7.8601 |  | 25-03-2026 08:40 | 119.106 | 120.528 | 87.6 | 20.088 | 20.0468 | 0.041242 | 120.2805 | 12.1 | 19.7601 | -7.6601 |  | 25-03-2026 08:40 | 119.297 | 122.482 | 89.1 | 20.4137 | 20.0468 | 0.36691 | 120.2805 | 12.1 | 19.7601 | -7.6601 |  | 25-03-2026 08:40 | 113.725 | 115.095 | 84.1 | 19.1825 | 19.072 | 0.11049 | 114.432 | 11.5 | 18.7993 | -7.2993 |  | 25-03-2026 08:40 | 207.6865 | 207.5115 | 0.17497 | 1245.0692 | 122 | 204.5441 | -82.5441 | -85.6865
25-03-2026 08:30 | 329 | 49.08 | 133.77 | 135.381 | 102 | 22.5635 | 19.5691 | 2.9944 | 117.4146 | 24.4 | 19.2893 | 5.1107 |  | 25-03-2026 08:30 | 112.146 | 113.531 | 102.1 | 18.9218 | 19.5691 | -0.64727 | 117.4146 | 24.2 | 19.2893 | 4.9107 |  | 25-03-2026 08:30 | 105.6 | 106.883 | 100.7 | 17.8138 | 19.5691 | -1.7553 | 117.4146 | 24.2 | 19.2893 | 4.9107 |  | 25-03-2026 08:30 | 115.533 | 116.948 | 102.2 | 19.4913 | 19.5691 | -0.077767 | 117.4146 | 24.6 | 19.2893 | 5.3107 |  | 25-03-2026 08:30 | 83.334 | 84.38 | 74.5 | 14.0633 | 14.4956 | -0.4323 | 86.9738 | 18 | 14.2883 | 3.7117 |  | 25-03-2026 08:30 | 88.339 | 89.48 | 76 | 14.9133 | 14.4956 | 0.4177 | 86.9738 | 18.2 | 14.2883 | 3.9117 |  | 25-03-2026 08:30 | 90.67 | 91.753 | 75.5 | 15.2922 | 14.4956 | 0.79654 | 86.9738 | 17.9 | 14.2883 | 3.6117 |  | 25-03-2026 08:30 | 88.896 | 92.143 | 77 | 15.3572 | 14.4956 | 0.86154 | 86.9738 | 18.2 | 14.2883 | 3.9117 |  | 25-03-2026 08:30 | 82.995 | 84.054 | 72.6 | 14.009 | 13.7908 | 0.2182 | 82.7448 | 17.2 | 13.5936 | 3.6064 |  | 25-03-2026 08:30 | 152.4255 | 150.0497 | 2.3758 | 900.2983 | 186.9 | 147.904 | 38.996 | 34.4745
25-03-2026 08:20 | 398 | 44.77 | 137.768 | 139.399 | 77.6 | 23.2332 | 24.0632 | -0.83007 | 144.3794 | 19.5 | 23.7191 | -4.2191 |  | 25-03-2026 08:20 | 139.99 | 141.676 | 77.9 | 23.6127 | 24.0632 | -0.45057 | 144.3794 | 19.8 | 23.7191 | -3.9191 |  | 25-03-2026 08:20 | 138.066 | 140.412 | 76.5 | 23.402 | 24.0632 | -0.66124 | 144.3794 | 19.2 | 23.7191 | -4.5191 |  | 25-03-2026 08:20 | 139.613 | 141.309 | 77.6 | 23.5515 | 24.0632 | -0.51174 | 144.3794 | 19.4 | 23.7191 | -4.3191 |  | 25-03-2026 08:20 | 102.541 | 103.744 | 56.5 | 17.2907 | 17.8246 | -0.53395 | 106.9477 | 14.2 | 17.5697 | -3.3697 |  | 25-03-2026 08:20 | 103.796 | 105.004 | 57.8 | 17.5007 | 17.8246 | -0.32395 | 106.9477 | 14.4 | 17.5697 | -3.1697 |  | 25-03-2026 08:20 | 103.35 | 104.513 | 57.6 | 17.4188 | 17.8246 | -0.40579 | 106.9477 | 14.4 | 17.5697 | -3.1697 |  | 25-03-2026 08:20 | 104.796 | 107.677 | 58.8 | 17.9462 | 17.8246 | 0.12155 | 106.9477 | 14.6 | 17.5697 | -2.9697 |  | 25-03-2026 08:20 | 99.317 | 100.413 | 55.4 | 16.7355 | 16.9579 | -0.22242 | 101.7475 | 14 | 16.7154 | -2.7154 |  | 25-03-2026 08:20 | 180.6912 | 184.5093 | -3.8182 | 1107.0561 | 149.5 | 181.8709 | -32.3709 | -31.1912
25-03-2026 08:10 | 306 | 42.19 | 104.55 | 105.745 | 58.1 | 17.6242 | 18.6804 | -1.0562 | 112.0822 | 15.5 | 18.4132 | -2.9132 |  | 25-03-2026 08:10 | 104.786 | 106.016 | 58.1 | 17.6693 | 18.6804 | -1.011 | 112.0822 | 16 | 18.4132 | -2.4132 |  | 25-03-2026 08:10 | 103.701 | 105.071 | 57.3 | 17.5118 | 18.6804 | -1.1685 | 112.0822 | 15.6 | 18.4132 | -2.8132 |  | 25-03-2026 08:10 | 105.369 | 106.595 | 58.2 | 17.7658 | 18.6804 | -0.91453 | 112.0822 | 15.8 | 18.4132 | -2.6132 |  | 25-03-2026 08:10 | 76.93 | 77.888 | 42.3 | 12.9813 | 13.8373 | -0.85597 | 83.0238 | 11.6 | 13.6394 | -2.0394 |  | 25-03-2026 08:10 | 78.346 | 79.274 | 43.4 | 13.2123 | 13.8373 | -0.62497 | 83.0238 | 11.8 | 13.6394 | -1.8394 |  | 25-03-2026 08:10 | 77.944 | 78.899 | 43.2 | 13.1498 | 13.8373 | -0.68747 | 83.0238 | 11.7 | 13.6394 | -1.9394 |  | 25-03-2026 08:10 | 79.13 | 81.032 | 44.2 | 13.5053 | 13.8373 | -0.33197 | 83.0238 | 11.9 | 13.6394 | -1.7394 |  | 25-03-2026 08:10 | 75.076 | 76.003 | 41.4 | 12.6672 | 13.1645 | -0.49732 | 78.9869 | 11.3 | 12.9762 | -1.6762 |  | 25-03-2026 08:10 | 136.0872 | 143.2352 | -7.148 | 859.411 | 121.2 | 141.1869 | -19.9869 | -14.8872
25-03-2026 08:00 | 255 | 38.46 | 84.046 | 86.038 | 42.6 | 14.3397 | 15.7832 | -1.4435 | 94.6992 | 12.9 | 15.5575 | -2.6575 |  | 25-03-2026 08:00 | 83.681 | 83.876 | 42.1 | 13.9793 | 15.7832 | -1.8039 | 94.6992 | 13.4 | 15.5575 | -2.1575 |  | 25-03-2026 08:00 | 84.014 | 85 | 41.7 | 14.1667 | 15.7832 | -1.6165 | 94.6992 | 12.5 | 15.5575 | -3.0575 |  | 25-03-2026 08:00 | 85.044 | 86.042 | 42.4 | 14.3403 | 15.7832 | -1.4429 | 94.6992 | 13.1 | 15.5575 | -2.4575 |  | 25-03-2026 08:00 | 62.236 | 63.043 | 30.7 | 10.5072 | 11.6913 | -1.1841 | 70.1476 | 9.4 | 11.5241 | -2.1241 |  | 25-03-2026 08:00 | 63.427 | 64.182 | 31.6 | 10.697 | 11.6913 | -0.99426 | 70.1476 | 9.7 | 11.5241 | -1.8241 |  | 25-03-2026 08:00 | 63.167 | 63.973 | 31.5 | 10.6622 | 11.6913 | -1.0291 | 70.1476 | 9.7 | 11.5241 | -1.8241 |  | 25-03-2026 08:00 | 64.204 | 66.188 | 32.3 | 11.0313 | 11.6913 | -0.65993 | 70.1476 | 9.9 | 11.5241 | -1.6241 |  | 25-03-2026 08:00 | 60.196 | 60.977 | 30.1 | 10.1628 | 11.1228 | -0.95996 | 66.7367 | 9.2 | 10.9637 | -1.7637 |  | 25-03-2026 08:00 | 109.8865 | 121.0207 | -11.1342 | 726.124 | 99.8 | 119.2901 | -19.4901 | -10.0865
25-03-2026 07:50 | 218 | 29.56 | 71.34 | 72.185 | 29.7 | 12.0308 | 13.9342 | -1.9033 | 83.6051 | 10.5 | 13.7349 | -3.2349 |  | 25-03-2026 07:50 | 69.881 | 70.744 | 28.7 | 11.7907 | 13.9342 | -2.1435 | 83.6051 | 10 | 13.7349 | -3.7349 |  | 25-03-2026 07:50 | 70.236 | 71.082 | 29.2 | 11.847 | 13.9342 | -2.0872 | 83.6051 | 10.4 | 13.7349 | -3.3349 |  | 25-03-2026 07:50 | 71.266 | 72.139 | 29.3 | 12.0232 | 13.9342 | -1.911 | 83.6051 | 10.5 | 13.7349 | -3.2349 |  | 25-03-2026 07:50 | 51.697 | 52.431 | 21.3 | 8.7385 | 10.3216 | -1.5831 | 61.9297 | 7.7 | 10.174 | -2.474 |  | 25-03-2026 07:50 | 53.041 | 53.761 | 21.9 | 8.9602 | 10.3216 | -1.3615 | 61.9297 | 7.9 | 10.174 | -2.274 |  | 25-03-2026 07:50 | 52.856 | 53.596 | 21.8 | 8.9327 | 10.3216 | -1.389 | 61.9297 | 7.8 | 10.174 | -2.374 |  | 25-03-2026 07:50 | 53.75 | 55.302 | 22.4 | 9.217 | 10.3216 | -1.1046 | 61.9297 | 8 | 10.174 | -2.174 |  | 25-03-2026 07:50 | 51.087 | 51.807 | 20.9 | 8.6345 | 9.8197 | -1.1852 | 58.9184 | 7.6 | 9.6793 | -2.0793 |  | 25-03-2026 07:50 | 92.1745 | 106.8429 | -14.6684 | 641.0577 | 80.4 | 105.3151 | -24.9151 | -11.7745
25-03-2026 07:40 | 176 | 28.41 | 55.515 | 56.246 | 19.2 | 9.3743 | 11.2956 | -1.9213 | 67.7738 | 8.1 | 11.1341 | -3.0341 |  | 25-03-2026 07:40 | 54.868 | 55.613 | 18.7 | 9.2688 | 11.2956 | -2.0268 | 67.7738 | 7.9 | 11.1341 | -3.2341 |  | 25-03-2026 07:40 | 54.404 | 55.126 | 18.8 | 9.1877 | 11.2956 | -2.108 | 67.7738 | 7.9 | 11.1341 | -3.2341 |  | 25-03-2026 07:40 | 55.322 | 56.068 | 18.8 | 9.3447 | 11.2956 | -1.951 | 67.7738 | 7.9 | 11.1341 | -3.2341 |  | 25-03-2026 07:40 | 40.092 | 40.719 | 13.6 | 6.7865 | 8.3671 | -1.5806 | 50.2028 | 5.7 | 8.2475 | -2.5475 |  | 25-03-2026 07:40 | 41.282 | 41.902 | 14 | 6.9837 | 8.3671 | -1.3835 | 50.2028 | 5.8 | 8.2475 | -2.4475 |  | 25-03-2026 07:40 | 41.066 | 41.7 | 14 | 6.95 | 8.3671 | -1.4171 | 50.2028 | 5.8 | 8.2475 | -2.4475 |  | 25-03-2026 07:40 | 42.035 | 43.24 | 14.4 | 7.2067 | 8.3671 | -1.1605 | 50.2028 | 6 | 8.2475 | -2.2475 |  | 25-03-2026 07:40 | 39.808 | 40.435 | 13.3 | 6.7392 | 7.9603 | -1.2211 | 47.7617 | 5.6 | 7.8465 | -2.2465 |  | 25-03-2026 07:40 | 71.8415 | 86.6113 | -14.7698 | 519.6681 | 60.7 | 85.3728 | -24.6728 | -11.1415
25-03-2026 07:30 | 130 | 25.54 | 39.234 | 39.836 | 11.1 | 6.6393 | 8.4282 | -1.7889 | 50.5691 | 5.1 | 8.3077 | -3.2077 |  | 25-03-2026 07:30 | 38.099 | 39.212 | 10.8 | 6.5353 | 8.4282 | -1.8929 | 50.5691 | 5 | 8.3077 | -3.3077 |  | 25-03-2026 07:30 | 38.585 | 39.166 | 10.9 | 6.5277 | 8.4282 | -1.9005 | 50.5691 | 5 | 8.3077 | -3.3077 |  | 25-03-2026 07:30 | 39.116 | 39.736 | 10.9 | 6.6227 | 8.4282 | -1.8055 | 50.5691 | 5 | 8.3077 | -3.3077 |  | 25-03-2026 07:30 | 28.386 | 28.903 | 7.9 | 4.8172 | 6.2431 | -1.4259 | 37.4586 | 3.7 | 6.1538 | -2.4538 |  | 25-03-2026 07:30 | 29.381 | 29.88 | 8.2 | 4.98 | 6.2431 | -1.2631 | 37.4586 | 3.9 | 6.1538 | -2.2538 |  | 25-03-2026 07:30 | 29.215 | 29.712 | 8.2 | 4.952 | 6.2431 | -1.2911 | 37.4586 | 3.8 | 6.1538 | -2.3538 |  | 25-03-2026 07:30 | 30.032 | 30.978 | 8.4 | 5.163 | 6.2431 | -1.0801 | 37.4586 | 3.9 | 6.1538 | -2.2538 |  | 25-03-2026 07:30 | 27.982 | 28.498 | 7.7 | 4.7497 | 5.9395 | -1.1899 | 35.6372 | 3.7 | 5.8546 | -2.1546 |  | 25-03-2026 07:30 | 50.9868 | 64.6247 | -13.6378 | 387.748 | 39.1 | 63.7005 | -24.6005 | -11.8868
25-03-2026 07:20 | 80 | 23.53 | 24.146 | 24.634 | 6 | 4.1057 | 5.2231 | -1.1175 | 31.3388 | 2.9 | 5.1484 | -2.2484 |  | 25-03-2026 07:20 | 22.922 | 23.724 | 5.8 | 3.954 | 5.2231 | -1.2691 | 31.3388 | 2.7 | 5.1484 | -2.4484 |  | 25-03-2026 07:20 | 23.512 | 24.007 | 5.9 | 4.0012 | 5.2231 | -1.222 | 31.3388 | 2.9 | 5.1484 | -2.2484 |  | 25-03-2026 07:20 | 23.591 | 24.088 | 5.9 | 4.0147 | 5.2231 | -1.2085 | 31.3388 | 2.9 | 5.1484 | -2.2484 |  | 25-03-2026 07:20 | 17.173 | 17.723 | 4.2 | 2.9538 | 3.869 | -0.91515 | 23.2139 | 2.1 | 3.8137 | -1.7137 |  | 25-03-2026 07:20 | 17.83 | 18.252 | 4.3 | 3.042 | 3.869 | -0.82699 | 23.2139 | 2.1 | 3.8137 | -1.7137 |  | 25-03-2026 07:20 | 17.81 | 18.237 | 4.4 | 3.0395 | 3.869 | -0.82949 | 23.2139 | 2.2 | 3.8137 | -1.6137 |  | 25-03-2026 07:20 | 18.287 | 19.083 | 4.5 | 3.1805 | 3.869 | -0.68849 | 23.2139 | 2.3 | 3.8137 | -1.5137 |  | 25-03-2026 07:20 | 16.706 | 17.112 | 4 | 2.852 | 3.6809 | -0.82886 | 22.0852 | 2 | 3.6282 | -1.6282 |  | 25-03-2026 07:20 | 31.1433 | 40.0493 | -8.906 | 240.296 | 22.1 | 39.4766 | -17.3766 | -9.0433
25-03-2026 07:10 | 32 | 22.39 | 13.374 | 13.76 | 3.1 | 2.2933 | 2.0975 | 0.19579 | 12.5853 | 1.9 | 2.0676 | -0.16755 |  | 25-03-2026 07:10 | 13.085 | 13.59 | 3.1 | 2.265 | 2.0975 | 0.16745 | 12.5853 | 1.9 | 2.0676 | -0.16755 |  | 25-03-2026 07:10 | 13.094 | 13.479 | 3 | 2.2465 | 2.0975 | 0.14895 | 12.5853 | 1.8 | 2.0676 | -0.26755 |  | 25-03-2026 07:10 | 12.914 | 13.616 | 3 | 2.2693 | 2.0975 | 0.17179 | 12.5853 | 1.8 | 2.0676 | -0.26755 |  | 25-03-2026 07:10 | 9.427 | 9.93 | 2.1 | 1.655 | 1.5537 | 0.10126 | 9.3224 | 1.3 | 1.5315 | -0.23152 |  | 25-03-2026 07:10 | 9.681 | 10.026 | 2.2 | 1.671 | 1.5537 | 0.11726 | 9.3224 | 1.4 | 1.5315 | -0.13152 |  | 25-03-2026 07:10 | 9.76 | 10.112 | 2.2 | 1.6853 | 1.5537 | 0.1316 | 9.3224 | 1.4 | 1.5315 | -0.13152 |  | 25-03-2026 07:10 | 10.067 | 10.596 | 2.2 | 1.766 | 1.5537 | 0.21226 | 9.3224 | 1.4 | 1.5315 | -0.13152 |  | 25-03-2026 07:10 | 9.033 | 9.371 | 2 | 1.5618 | 1.4782 | 0.083644 | 8.8691 | 1.2 | 1.4571 | -0.25705 |  | 25-03-2026 07:10 | 17.4133 | 16.0833 | 1.33 | 96.5 | 14.1 | 15.8533 | -1.7533 | -3.3133
25-03-2026 07:00 | 22 | 22.39 | 7.673 | 8.227 | 1.2 | 1.3712 | 1.4421 | -0.070896 | 8.6524 | 1.2 | 1.4214 | -0.22144 |  | 25-03-2026 07:00 | 7.283 | 8.462 | 1.2 | 1.4103 | 1.4421 | -0.03173 | 8.6524 | 1.2 | 1.4214 | -0.22144 |  | 25-03-2026 07:00 | 7.759 | 8.078 | 1.2 | 1.3463 | 1.4421 | -0.09573 | 8.6524 | 1.2 | 1.4214 | -0.22144 |  | 25-03-2026 07:00 | 7.817 | 8.646 | 1.2 | 1.441 | 1.4421 | -0.001063 | 8.6524 | 1.2 | 1.4214 | -0.22144 |  | 25-03-2026 07:00 | 5.568 | 6.081 | 0.8 | 1.0135 | 1.0682 | -0.054695 | 6.4092 | 0.8 | 1.0529 | -0.25292 |  | 25-03-2026 07:00 | 5.637 | 5.887 | 0.8 | 0.98117 | 1.0682 | -0.087028 | 6.4092 | 0.8 | 1.0529 | -0.25292 |  | 25-03-2026 07:00 | 5.624 | 5.88 | 0.8 | 0.98 | 1.0682 | -0.088195 | 6.4092 | 0.8 | 1.0529 | -0.25292 |  | 25-03-2026 07:00 | 5.79 | 6.277 | 0.8 | 1.0462 | 1.0682 | -0.022028 | 6.4092 | 0.8 | 1.0529 | -0.25292 |  | 25-03-2026 07:00 | 5.35 | 5.594 | 0.8 | 0.93233 | 1.0163 | -0.083922 | 6.0975 | 0.8 | 1.0017 | -0.20172 |  | 25-03-2026 07:00 | 10.522 | 11.0573 | -0.53529 | 66.3437 | 8.8 | 10.8992 | -2.0992 | -1.722
[110 empty] | Total: - | 16221.5525 | 16539.5796 | -318.0271 |  | 15691.8 | 16303.0636 | -611.2636 | -529.7525
Sum:- | 36529 |  | 12485.438 |  | 75834.3 |  |  |  |  | 2045.9 | 2126.2039 | -80.3039 | 0.992 |  | 12246.679 |  | 71513.8 |  |  |  |  | 2066.5 | 2126.2039 | -59.7039 | 0.99635 |  | 12395.989 |  | 75291.8 |  |  |  |  | 2033.5 | 2126.2039 | -92.7039 | 0.97535 |  | 12534.975 |  | 75862.1 |  |  |  |  | 2045.8 | 2126.2039 | -80.4039 | 0.98462 |  | 9361.227 |  | 56479.3 |  |  |  |  | 1527.3 | 1574.9658 | -47.6658 | 0.98623 |  | 9277.218 |  | 56111 |  |  |  |  | 1511 | 1574.9658 | -63.9658 | 0.98362 |  | 9285.534 |  | 56052.4 |  |  |  |  | 1510.4 | 1574.9658 | -64.5658 | 0.98293 |  | 9346.205 |  | 56417.2 |  |  |  |  | 1516.1 | 1574.9658 | -58.8658 | 0.97202 |  | 8846.794 |  | 53369.1 |  |  |  |  | 1435.3 | 1498.3849 | -63.0849 | 0.98538 | [8 empty] | -3.266%

## 26 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
26-03-2026 19:00 | 0 | 43.05 | 0 | 0 | 2331.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 2351.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 2317.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 2331.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 1732.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 1734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 1743.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 1645.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26-03-2026 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 99%
26-03-2026 18:50 | 7 | 43.91 | 0 | 0 | 2331.5 | 0 | 0.42459 | -0.42459 | 2.5475 | 0 | 0.41852 | -0.41852 |  | 26-03-2026 18:50 | 0 | 0 | 2351.5 | 0 | 0.42459 | -0.42459 | 2.5475 | 0 | 0.41852 | -0.41852 |  | 26-03-2026 18:50 | 0 | 0 | 2317.8 | 0 | 0.42459 | -0.42459 | 2.5475 | 0 | 0.41852 | -0.41852 |  | 26-03-2026 18:50 | 0 | 0 | 2331.7 | 0 | 0.42459 | -0.42459 | 2.5475 | 0 | 0.41852 | -0.41852 |  | 26-03-2026 18:50 | 0 | 0 | 1751 | 0 | 0.31451 | -0.31451 | 1.8871 | 0 | 0.31001 | -0.31001 |  | 26-03-2026 18:50 | 0 | 0 | 1732.8 | 0 | 0.31451 | -0.31451 | 1.8871 | 0 | 0.31001 | -0.31001 |  | 26-03-2026 18:50 | 0 | 0 | 1734 | 0 | 0.31451 | -0.31451 | 1.8871 | 0 | 0.31001 | -0.31001 |  | 26-03-2026 18:50 | 0 | 0 | 1743.2 | 0 | 0.31451 | -0.31451 | 1.8871 | 0 | 0.31001 | -0.31001 |  | 26-03-2026 18:50 | 0 | 0 | 1645.9 | 0 | 0.29922 | -0.29922 | 1.7953 | 0 | 0.29494 | -0.29494 |  | 26-03-2026 18:50 | 0 | 3.2556 | -3.2556 | 19.5338 | 0 | 3.2091 | -3.2091 | 0 | 2 | 99.15%
26-03-2026 18:40 | 10 | 44.77 | 0 | 0 | 2331.5 | 0 | 0.6046 | -0.6046 | 3.6276 | 0 | 0.59596 | -0.59596 |  | 26-03-2026 18:40 | 0 | 0 | 2351.5 | 0 | 0.6046 | -0.6046 | 3.6276 | 0 | 0.59596 | -0.59596 |  | 26-03-2026 18:40 | 0 | 0 | 2317.8 | 0 | 0.6046 | -0.6046 | 3.6276 | 0 | 0.59596 | -0.59596 |  | 26-03-2026 18:40 | 0 | 0 | 2331.7 | 0 | 0.6046 | -0.6046 | 3.6276 | 0 | 0.59596 | -0.59596 |  | 26-03-2026 18:40 | 0 | 0 | 1751 | 0 | 0.44785 | -0.44785 | 2.6871 | 0 | 0.44145 | -0.44145 |  | 26-03-2026 18:40 | 0 | 0 | 1732.8 | 0 | 0.44785 | -0.44785 | 2.6871 | 0 | 0.44145 | -0.44145 |  | 26-03-2026 18:40 | 0 | 0 | 1734 | 0 | 0.44785 | -0.44785 | 2.6871 | 0 | 0.44145 | -0.44145 |  | 26-03-2026 18:40 | 0 | 0 | 1743.2 | 0 | 0.44785 | -0.44785 | 2.6871 | 0 | 0.44145 | -0.44145 |  | 26-03-2026 18:40 | 0 | 0 | 1645.9 | 0 | 0.42608 | -0.42608 | 2.5565 | 0 | 0.41999 | -0.41999 |  | 26-03-2026 18:40 | 0 | 4.6359 | -4.6359 | 27.8155 | 0 | 4.5696 | -4.5696 | 0 | 3 | 96.96%
26-03-2026 18:30 | 12 | 45.35 | 0 | 0 | 2331.5 | 0 | 0.72394 | -0.72394 | 4.3437 | 0 | 0.71359 | -0.71359 |  | 26-03-2026 18:30 | 0 | 0 | 2351.5 | 0 | 0.72394 | -0.72394 | 4.3437 | 0 | 0.71359 | -0.71359 |  | 26-03-2026 18:30 | 0 | 0 | 2317.8 | 0 | 0.72394 | -0.72394 | 4.3437 | 0 | 0.71359 | -0.71359 |  | 26-03-2026 18:30 | 0 | 0 | 2331.7 | 0 | 0.72394 | -0.72394 | 4.3437 | 0 | 0.71359 | -0.71359 |  | 26-03-2026 18:30 | 0 | 0 | 1751 | 0 | 0.53625 | -0.53625 | 3.2175 | 0 | 0.52859 | -0.52859 |  | 26-03-2026 18:30 | 0 | 0 | 1732.8 | 0 | 0.53625 | -0.53625 | 3.2175 | 0 | 0.52859 | -0.52859 |  | 26-03-2026 18:30 | 0 | 0 | 1734 | 0 | 0.53625 | -0.53625 | 3.2175 | 0 | 0.52859 | -0.52859 |  | 26-03-2026 18:30 | 0 | 0 | 1743.2 | 0 | 0.53625 | -0.53625 | 3.2175 | 0 | 0.52859 | -0.52859 |  | 26-03-2026 18:30 | 0 | 0 | 1645.9 | 0 | 0.51018 | -0.51018 | 3.0611 | 0 | 0.50288 | -0.50288 |  | 26-03-2026 18:30 | 0 | 5.551 | -5.551 | 33.3058 | 0 | 5.4716 | -5.4716 | 0 | 4 | 98.37%
26-03-2026 18:20 | 27 | 46.78 | 0 | 0 | 2331.5 | 0 | 1.6201 | -1.6201 | 9.7206 | 0 | 1.5969 | -1.5969 |  | 26-03-2026 18:20 | 0 | 0 | 2351.5 | 0 | 1.6201 | -1.6201 | 9.7206 | 0 | 1.5969 | -1.5969 |  | 26-03-2026 18:20 | 0 | 0 | 2317.8 | 0 | 1.6201 | -1.6201 | 9.7206 | 0 | 1.5969 | -1.5969 |  | 26-03-2026 18:20 | 0 | 0 | 2331.7 | 0 | 1.6201 | -1.6201 | 9.7206 | 0 | 1.5969 | -1.5969 |  | 26-03-2026 18:20 | 0 | 0 | 1751 | 0 | 1.2001 | -1.2001 | 7.2004 | 0 | 1.1829 | -1.1829 |  | 26-03-2026 18:20 | 0 | 0 | 1732.8 | 0 | 1.2001 | -1.2001 | 7.2004 | 0 | 1.1829 | -1.1829 |  | 26-03-2026 18:20 | 0 | 0 | 1734 | 0 | 1.2001 | -1.2001 | 7.2004 | 0 | 1.1829 | -1.1829 |  | 26-03-2026 18:20 | 0 | 0 | 1743.2 | 0 | 1.2001 | -1.2001 | 7.2004 | 0 | 1.1829 | -1.1829 |  | 26-03-2026 18:20 | 0 | 0 | 1645.9 | 0 | 1.1417 | -1.1417 | 6.8503 | 0 | 1.1254 | -1.1254 |  | 26-03-2026 18:20 | 0 | 12.4224 | -12.4224 | 74.5342 | 0 | 12.2447 | -12.2447 | 0 | 5 | 97.63%
26-03-2026 18:10 | 51 | 48.22 | 0 | 0 | 2331.5 | 0 | 3.0435 | -3.0435 | 18.2609 | 0 | 3 | -3 |  | 26-03-2026 18:10 | 0 | 0 | 2351.5 | 0 | 3.0435 | -3.0435 | 18.2609 | 0 | 3 | -3 |  | 26-03-2026 18:10 | 0 | 0 | 2317.8 | 0 | 3.0435 | -3.0435 | 18.2609 | 0 | 3 | -3 |  | 26-03-2026 18:10 | 0 | 0 | 2331.7 | 0 | 3.0435 | -3.0435 | 18.2609 | 0 | 3 | -3 |  | 26-03-2026 18:10 | 0 | 0 | 1751 | 0 | 2.2544 | -2.2544 | 13.5266 | 0 | 2.2222 | -2.2222 |  | 26-03-2026 18:10 | 0 | 0 | 1732.8 | 0 | 2.2544 | -2.2544 | 13.5266 | 0 | 2.2222 | -2.2222 |  | 26-03-2026 18:10 | 0 | 0 | 1734 | 0 | 2.2544 | -2.2544 | 13.5266 | 0 | 2.2222 | -2.2222 |  | 26-03-2026 18:10 | 0 | 0 | 1743.2 | 0 | 2.2544 | -2.2544 | 13.5266 | 0 | 2.2222 | -2.2222 |  | 26-03-2026 18:10 | 0 | 0 | 1645.9 | 0 | 2.1448 | -2.1448 | 12.8689 | 0 | 2.1141 | -2.1141 |  | 26-03-2026 18:10 | 0 | 23.3364 | -23.3364 | 140.0187 | 0 | 23.0027 | -23.0027 | 0 | 6 | 97.85%
26-03-2026 18:00 | 60 | 48.5 | 0 | 0 | 2331.5 | 0 | 3.5767 | -3.5767 | 21.4605 | 4 | 3.5256 | 0.4744 |  | 26-03-2026 18:00 | 0 | 0 | 2351.5 | 0 | 3.5767 | -3.5767 | 21.4605 | 4.2 | 3.5256 | 0.6744 |  | 26-03-2026 18:00 | 0 | 0 | 2317.8 | 0 | 3.5767 | -3.5767 | 21.4605 | 4 | 3.5256 | 0.4744 |  | 26-03-2026 18:00 | 0 | 0 | 2331.7 | 0 | 3.5767 | -3.5767 | 21.4605 | 4.1 | 3.5256 | 0.5744 |  | 26-03-2026 18:00 | 0 | 0 | 1751 | 0 | 2.6494 | -2.6494 | 15.8966 | 3 | 2.6116 | 0.38845 |  | 26-03-2026 18:00 | 0 | 0 | 1732.8 | 0 | 2.6494 | -2.6494 | 15.8966 | 2.9 | 2.6116 | 0.28845 |  | 26-03-2026 18:00 | 0 | 0 | 1734 | 0 | 2.6494 | -2.6494 | 15.8966 | 2.9 | 2.6116 | 0.28845 |  | 26-03-2026 18:00 | 0 | 0 | 1743.2 | 0 | 2.6494 | -2.6494 | 15.8966 | 3 | 2.6116 | 0.38845 |  | 26-03-2026 18:00 | 0 | 0 | 1645.9 | 0 | 2.5206 | -2.5206 | 15.1237 | 2.8 | 2.4846 | 0.31543 |  | 26-03-2026 18:00 | 0 | 27.4254 | -27.4254 | 164.5521 | 30.9 | 27.0332 | 3.8668 | 30.9 | 7 | 97.97%
26-03-2026 17:50 | 81 | 48.5 | 29.871 | 30.481 | 2327.5 | 5.0802 | 4.8286 | 0.25156 | 28.9716 | 5.4 | 4.7596 | 0.64044 |  | 26-03-2026 17:50 | 30.979 | 31.442 | 2347.3 | 5.2403 | 4.8286 | 0.41173 | 28.9716 | 5.3 | 4.7596 | 0.54044 |  | 26-03-2026 17:50 | 29.501 | 30.128 | 2313.8 | 5.0213 | 4.8286 | 0.19273 | 28.9716 | 5.4 | 4.7596 | 0.64044 |  | 26-03-2026 17:50 | 29.93 | 30.563 | 2327.6 | 5.0938 | 4.8286 | 0.26523 | 28.9716 | 5.4 | 4.7596 | 0.64044 |  | 26-03-2026 17:50 | 21.902 | 22.436 | 1748 | 3.7393 | 3.5767 | 0.16259 | 21.4605 | 4 | 3.5256 | 0.4744 |  | 26-03-2026 17:50 | 21.739 | 22.276 | 1729.9 | 3.7127 | 3.5767 | 0.13592 | 21.4605 | 4 | 3.5256 | 0.4744 |  | 26-03-2026 17:50 | 21.773 | 22.313 | 1731.1 | 3.7188 | 3.5767 | 0.14209 | 21.4605 | 4 | 3.5256 | 0.4744 |  | 26-03-2026 17:50 | 21.873 | 22.52 | 1740.2 | 3.7533 | 3.5767 | 0.17659 | 21.4605 | 3.9 | 3.5256 | 0.3744 |  | 26-03-2026 17:50 | 20.633 | 21.153 | 1643.1 | 3.5255 | 3.4028 | 0.12267 | 20.417 | 3.7 | 3.3542 | 0.34583 |  | 26-03-2026 17:50 | 38.8853 | 37.0242 | 1.8611 | 222.1454 | 41.1 | 36.4948 | 4.6052 | 2.2147 | 8 | 96.91%
26-03-2026 17:40 | 83 | 48.5 | 30.825 | 31.438 | 2322.1 | 5.2397 | 4.9478 | 0.29184 | 29.687 | 4.8 | 4.8771 | -0.077076 |  | 26-03-2026 17:40 | 30.694 | 31.311 | 2342 | 5.2185 | 4.9478 | 0.27067 | 29.687 | 4.7 | 4.8771 | -0.17708 |  | 26-03-2026 17:40 | 30.609 | 31.221 | 2308.4 | 5.2035 | 4.9478 | 0.25567 | 29.687 | 4.6 | 4.8771 | -0.27708 |  | 26-03-2026 17:40 | 30.782 | 31.397 | 2322.2 | 5.2328 | 4.9478 | 0.285 | 29.687 | 4.7 | 4.8771 | -0.17708 |  | 26-03-2026 17:40 | 22.845 | 23.4 | 1744 | 3.9 | 3.6651 | 0.23494 | 21.9904 | 3.5 | 3.6126 | -0.11265 |  | 26-03-2026 17:40 | 22.523 | 23.046 | 1725.9 | 3.841 | 3.6651 | 0.17594 | 21.9904 | 3.5 | 3.6126 | -0.11265 |  | 26-03-2026 17:40 | 22.534 | 23.086 | 1727.1 | 3.8477 | 3.6651 | 0.18261 | 21.9904 | 3.4 | 3.6126 | -0.21265 |  | 26-03-2026 17:40 | 22.722 | 23.501 | 1736.3 | 3.9168 | 3.6651 | 0.25177 | 21.9904 | 3.5 | 3.6126 | -0.11265 |  | 26-03-2026 17:40 | 21.314 | 21.838 | 1639.4 | 3.6397 | 3.4868 | 0.15282 | 20.9211 | 3.2 | 3.437 | -0.23699 |  | 26-03-2026 17:40 | 40.0397 | 37.9384 | 2.1013 | 227.6304 | 35.9 | 37.3959 | -1.4959 | -4.1397 | 9 | 98.18%
26-03-2026 17:30 | 77 | 48.79 | 29.003 | 29.613 | 2317.3 | 4.9355 | 4.5851 | 0.35042 | 27.5105 | 4.6 | 4.5195 | 0.080488 |  | 26-03-2026 17:30 | 28.945 | 29.569 | 2337.3 | 4.9282 | 4.5851 | 0.34309 | 27.5105 | 4.8 | 4.5195 | 0.28049 |  | 26-03-2026 17:30 | 28.44 | 29.05 | 2303.8 | 4.8417 | 4.5851 | 0.25659 | 27.5105 | 4.7 | 4.5195 | 0.18049 |  | 26-03-2026 17:30 | 28.863 | 29.491 | 2317.5 | 4.9152 | 4.5851 | 0.33009 | 27.5105 | 4.7 | 4.5195 | 0.18049 |  | 26-03-2026 17:30 | 21.185 | 21.71 | 1740.5 | 3.6183 | 3.3964 | 0.22198 | 20.3781 | 3.4 | 3.3478 | 0.052213 |  | 26-03-2026 17:30 | 21.002 | 21.523 | 1722.4 | 3.5872 | 3.3964 | 0.19081 | 20.3781 | 3.4 | 3.3478 | 0.052213 |  | 26-03-2026 17:30 | 20.871 | 21.397 | 1723.7 | 3.5662 | 3.3964 | 0.16981 | 20.3781 | 3.4 | 3.3478 | 0.052213 |  | 26-03-2026 17:30 | 20.982 | 21.759 | 1732.8 | 3.6265 | 3.3964 | 0.23015 | 20.3781 | 3.4 | 3.3478 | 0.052213 |  | 26-03-2026 17:30 | 19.776 | 20.289 | 1636.2 | 3.3815 | 3.2312 | 0.15029 | 19.3873 | 3.3 | 3.185 | 0.115 |  | 26-03-2026 17:30 | 37.4002 | 35.1569 | 2.2432 | 210.9417 | 35.7 | 34.6542 | 1.0458 | -1.7002
26-03-2026 17:20 | 73 | 48.79 | 27.211 | 27.815 | 2312.7 | 4.6358 | 4.3469 | 0.28894 | 26.0814 | 5.5 | 4.2847 | 1.2153 |  | 26-03-2026 17:20 | 27.518 | 28.148 | 2332.5 | 4.6913 | 4.3469 | 0.34444 | 26.0814 | 5.3 | 4.2847 | 1.0153 |  | 26-03-2026 17:20 | 26.919 | 27.525 | 2299.1 | 4.5875 | 4.3469 | 0.24061 | 26.0814 | 5.2 | 4.2847 | 0.91527 |  | 26-03-2026 17:20 | 27.279 | 27.905 | 2312.8 | 4.6508 | 4.3469 | 0.30394 | 26.0814 | 5.3 | 4.2847 | 1.0153 |  | 26-03-2026 17:20 | 20.066 | 20.578 | 1737.1 | 3.4297 | 3.2199 | 0.20975 | 19.3195 | 4 | 3.1739 | 0.82612 |  | 26-03-2026 17:20 | 19.894 | 20.41 | 1719 | 3.4017 | 3.2199 | 0.18175 | 19.3195 | 3.9 | 3.1739 | 0.72612 |  | 26-03-2026 17:20 | 19.854 | 20.371 | 1720.3 | 3.3952 | 3.2199 | 0.17525 | 19.3195 | 3.9 | 3.1739 | 0.72612 |  | 26-03-2026 17:20 | 19.994 | 20.784 | 1729.4 | 3.464 | 3.2199 | 0.24408 | 19.3195 | 4 | 3.1739 | 0.82612 |  | 26-03-2026 17:20 | 18.844 | 19.349 | 1632.9 | 3.2248 | 3.0634 | 0.16148 | 18.3801 | 3.6 | 3.0195 | 0.58045 |  | 26-03-2026 17:20 | 35.4808 | 33.3306 | 2.1502 | 199.9837 | 40.7 | 32.854 | 7.846 | 5.2192
26-03-2026 17:10 | 109 | 48.79 | 39.936 | 40.704 | 2307.2 | 6.784 | 6.4906 | 0.29343 | 38.9434 | 8.8 | 6.3978 | 2.4022 |  | 26-03-2026 17:10 | 39.778 | 40.536 | 2327.2 | 6.756 | 6.4906 | 0.26543 | 38.9434 | 8.9 | 6.3978 | 2.5022 |  | 26-03-2026 17:10 | 39.205 | 39.944 | 2293.9 | 6.6573 | 6.4906 | 0.16677 | 38.9434 | 8.8 | 6.3978 | 2.4022 |  | 26-03-2026 17:10 | 39.66 | 40.403 | 2307.5 | 6.7338 | 6.4906 | 0.24327 | 38.9434 | 8.8 | 6.3978 | 2.4022 |  | 26-03-2026 17:10 | 29.375 | 29.99 | 1733.1 | 4.9983 | 4.8078 | 0.19051 | 28.847 | 6.5 | 4.7391 | 1.7609 |  | 26-03-2026 17:10 | 29.136 | 29.743 | 1715.1 | 4.9572 | 4.8078 | 0.14934 | 28.847 | 6.4 | 4.7391 | 1.6609 |  | 26-03-2026 17:10 | 29.021 | 29.631 | 1716.4 | 4.9385 | 4.8078 | 0.13067 | 28.847 | 6.4 | 4.7391 | 1.6609 |  | 26-03-2026 17:10 | 29.392 | 30.272 | 1725.4 | 5.0453 | 4.8078 | 0.23751 | 28.847 | 6.4 | 4.7391 | 1.6609 |  | 26-03-2026 17:10 | 27.492 | 28.115 | 1629.3 | 4.6858 | 4.5741 | 0.11178 | 27.4443 | 6.2 | 4.5086 | 1.6914 |  | 26-03-2026 17:10 | 51.5563 | 49.7676 | 1.7887 | 298.6057 | 67.2 | 49.0559 | 18.1441 | 15.6437
26-03-2026 17:00 | 198 | 48.79 | 71.198 | 72.202 | 2298.4 | 12.0337 | 11.7902 | 0.24346 | 70.7412 | 16 | 11.6216 | 4.3784 |  | 26-03-2026 17:00 | 72.792 | 72.26 | 2318.3 | 12.0433 | 11.7902 | 0.25313 | 70.7412 | 16.7 | 11.6216 | 5.0784 |  | 26-03-2026 17:00 | 69.947 | 70.962 | 2285.1 | 11.827 | 11.7902 | 0.036797 | 70.7412 | 15.8 | 11.6216 | 4.1784 |  | 26-03-2026 17:00 | 70.632 | 71.657 | 2298.7 | 11.9428 | 11.7902 | 0.15263 | 70.7412 | 16.4 | 11.6216 | 4.7784 |  | 26-03-2026 17:00 | 52.082 | 52.94 | 1726.6 | 8.8233 | 8.7335 | 0.08985 | 52.4009 | 11.9 | 8.6086 | 3.2914 |  | 26-03-2026 17:00 | 51.832 | 52.686 | 1708.7 | 8.781 | 8.7335 | 0.047516 | 52.4009 | 11.9 | 8.6086 | 3.2914 |  | 26-03-2026 17:00 | 51.365 | 52.216 | 1710 | 8.7027 | 8.7335 | -0.030817 | 52.4009 | 11.6 | 8.6086 | 2.9914 |  | 26-03-2026 17:00 | 51.56 | 53.225 | 1719 | 8.8708 | 8.7335 | 0.13735 | 52.4009 | 11.6 | 8.6086 | 2.9914 |  | 26-03-2026 17:00 | 49.422 | 50.321 | 1623.1 | 8.3868 | 8.3088 | 0.078005 | 49.853 | 11.1 | 8.19 | 2.91 |  | 26-03-2026 17:00 | 91.4115 | 90.4036 | 1.0079 | 542.4214 | 123 | 89.1108 | 33.8892 | 31.5885
26-03-2026 16:50 | 383 | 49.36 | 119.181 | 120.763 | 2282.4 | 20.1272 | 22.7567 | -2.6295 | 136.54 | 42.4 | 22.4312 | 19.9688 |  | 26-03-2026 16:50 | 174.993 | 177.388 | 2301.6 | 29.5647 | 22.7567 | 6.808 | 136.54 | 24.6 | 22.4312 | 2.1688 |  | 26-03-2026 16:50 | 110.014 | 112.202 | 2269.3 | 18.7003 | 22.7567 | -4.0563 | 136.54 | 23.8 | 22.4312 | 1.3688 |  | 26-03-2026 16:50 | 158.185 | 160.301 | 2282.3 | 26.7168 | 22.7567 | 3.9602 | 136.54 | 23.6 | 22.4312 | 1.1688 |  | 26-03-2026 16:50 | 88.528 | 89.703 | 1714.7 | 14.9505 | 16.8568 | -1.9063 | 101.1408 | 17.3 | 16.6157 | 0.68426 |  | 26-03-2026 16:50 | 95.648 | 96.869 | 1696.8 | 16.1448 | 16.8568 | -0.71196 | 101.1408 | 17.1 | 16.6157 | 0.48426 |  | 26-03-2026 16:50 | 85.598 | 86.761 | 1698.4 | 14.4602 | 16.8568 | -2.3966 | 101.1408 | 16.9 | 16.6157 | 0.28426 |  | 26-03-2026 16:50 | 86.714 | 89.012 | 1707.4 | 14.8353 | 16.8568 | -2.0215 | 101.1408 | 16.7 | 16.6157 | 0.084259 |  | 26-03-2026 16:50 | 83.054 | 84.199 | 1612 | 14.0332 | 16.0372 | -2.004 | 96.2229 | 16 | 15.8078 | 0.19218 |  | 26-03-2026 16:50 | 169.533 | 174.491 | -4.958 | 1046.946 | 198.4 | 171.9958 | 26.4042 | 28.867
26-03-2026 16:40 | 275 | 49.08 | 98.816 | 100.024 | 2258.4 | 16.6707 | 16.3572 | 0.31352 | 98.1429 | 0 | 16.1232 | -16.1232 |  | 26-03-2026 16:40 | 97.5 | 98.884 | 2277 | 16.4807 | 16.3572 | 0.12352 | 98.1429 | 17.7 | 16.1232 | 1.5768 |  | 26-03-2026 16:40 | 98.41 | 100.404 | 2245.5 | 16.734 | 16.3572 | 0.37685 | 98.1429 | 18 | 16.1232 | 1.8768 |  | 26-03-2026 16:40 | 98.68 | 100 | 2258.7 | 16.6667 | 16.3572 | 0.30952 | 98.1429 | 18.1 | 16.1232 | 1.9768 |  | 26-03-2026 16:40 | 73.308 | 74.341 | 1697.4 | 12.3902 | 12.1164 | 0.27376 | 72.6984 | 13.4 | 11.9431 | 1.4569 |  | 26-03-2026 16:40 | 72.649 | 73.681 | 1679.7 | 12.2802 | 12.1164 | 0.16376 | 72.6984 | 13.4 | 11.9431 | 1.4569 |  | 26-03-2026 16:40 | 72.716 | 73.734 | 1681.5 | 12.289 | 12.1164 | 0.17259 | 72.6984 | 13.5 | 11.9431 | 1.5569 |  | 26-03-2026 16:40 | 72.857 | 75.01 | 1690.7 | 12.5017 | 12.1164 | 0.38526 | 72.6984 | 13.6 | 11.9431 | 1.6569 |  | 26-03-2026 16:40 | 68.741 | 69.724 | 1596 | 11.6207 | 11.5273 | 0.093405 | 69.1636 | 12.8 | 11.3624 | 1.4376 |  | 26-03-2026 16:40 | 127.6337 | 125.4215 | 2.2122 | 752.529 | 120.5 | 123.628 | -3.128 | -7.1337
26-03-2026 16:30 | 442 | 49.36 | 157.282 | 159.37 | 2240 | 26.5617 | 26.2623 | 0.2994 | 157.5736 | 26 | 25.8867 | 0.11328 |  | 26-03-2026 16:30 | 137.873 | 155.723 | 2259.3 | 25.9538 | 26.2623 | -0.30843 | 157.5736 | 26.8 | 25.8867 | 0.91328 |  | 26-03-2026 16:30 | 152.099 | 155.086 | 2227.5 | 25.8477 | 26.2623 | -0.4146 | 157.5736 | 26.1 | 25.8867 | 0.21328 |  | 26-03-2026 16:30 | 144.871 | 146.839 | 2240.6 | 24.4732 | 26.2623 | -1.7891 | 157.5736 | 26.2 | 25.8867 | 0.31328 |  | 26-03-2026 16:30 | 122.245 | 123.792 | 1684 | 20.632 | 19.4535 | 1.1785 | 116.7212 | 19.4 | 19.1753 | 0.22465 |  | 26-03-2026 16:30 | 112.081 | 117.3 | 1666.3 | 19.55 | 19.4535 | 0.096469 | 116.7212 | 19.1 | 19.1753 | -0.075346 |  | 26-03-2026 16:30 | 98.69 | 102.895 | 1668 | 17.1492 | 19.4535 | -2.3044 | 116.7212 | 18.9 | 19.1753 | -0.27535 |  | 26-03-2026 16:30 | 97.035 | 101.089 | 1677.1 | 16.8482 | 19.4535 | -2.6054 | 116.7212 | 19.4 | 19.1753 | 0.22465 |  | 26-03-2026 16:30 | 87.642 | 88.85 | 1583.2 | 14.8083 | 18.5076 | -3.6993 | 111.0458 | 18.3 | 18.243 | 0.057034 |  | 26-03-2026 16:30 | 191.824 | 201.3708 | -9.5468 | 1208.2249 | 200.2 | 198.4912 | 1.7088 | 8.376
26-03-2026 16:20 | 447 | 49.36 | 152.152 | 154.362 | 2214 | 25.727 | 26.5594 | -0.83235 | 159.3561 | 28.7 | 26.1796 | 2.5204 |  | 26-03-2026 16:20 | 166.522 | 168.84 | 2232.5 | 28.14 | 26.5594 | 1.5806 | 159.3561 | 28.3 | 26.1796 | 2.1204 |  | 26-03-2026 16:20 | 154.244 | 157.763 | 2201.4 | 26.2938 | 26.5594 | -0.26552 | 159.3561 | 29.3 | 26.1796 | 3.1204 |  | 26-03-2026 16:20 | 162.984 | 165.214 | 2214.4 | 27.5357 | 26.5594 | 0.97632 | 159.3561 | 28.9 | 26.1796 | 2.7204 |  | 26-03-2026 16:20 | 122.138 | 123.747 | 1664.6 | 20.6245 | 19.6736 | 0.95091 | 118.0416 | 22.3 | 19.3923 | 2.9077 |  | 26-03-2026 16:20 | 118.514 | 120.339 | 1647.2 | 20.0565 | 19.6736 | 0.38291 | 118.0416 | 21.5 | 19.3923 | 2.1077 |  | 26-03-2026 16:20 | 122.271 | 123.881 | 1649.1 | 20.6468 | 19.6736 | 0.97324 | 118.0416 | 21.9 | 19.3923 | 2.5077 |  | 26-03-2026 16:20 | 112.944 | 116.471 | 1657.7 | 19.4118 | 19.6736 | -0.26176 | 118.0416 | 21.5 | 19.3923 | 2.1077 |  | 26-03-2026 16:20 | 105.017 | 105.85 | 1564.9 | 17.6417 | 18.717 | -1.0753 | 112.3019 | 20 | 18.4493 | 1.5507 |  | 26-03-2026 16:20 | 206.0778 | 203.6488 | 2.4291 | 1221.8926 | 222.4 | 200.7366 | 21.6634 | 16.3222
26-03-2026 16:10 | 325 | 49.65 | 114.17 | 116.068 | 2185.3 | 19.3447 | 19.2891 | 0.055603 | 115.7344 | 27.3 | 19.0132 | 8.2868 |  | 26-03-2026 16:10 | 93.584 | 119.721 | 2204.2 | 19.9535 | 19.2891 | 0.66444 | 115.7344 | 28.7 | 19.0132 | 9.6868 |  | 26-03-2026 16:10 | 114.978 | 118.683 | 2172.1 | 19.7805 | 19.2891 | 0.49144 | 115.7344 | 27.4 | 19.0132 | 8.3868 |  | 26-03-2026 16:10 | 106.796 | 108.236 | 2185.5 | 18.0393 | 19.2891 | -1.2497 | 115.7344 | 27 | 19.0132 | 7.9868 |  | 26-03-2026 16:10 | 86.771 | 87.975 | 1642.3 | 14.6625 | 14.2882 | 0.3743 | 85.7292 | 20 | 14.0839 | 5.9161 |  | 26-03-2026 16:10 | 79.327 | 80.597 | 1625.7 | 13.4328 | 14.2882 | -0.85536 | 85.7292 | 19.7 | 14.0839 | 5.6161 |  | 26-03-2026 16:10 | 83.8 | 85.563 | 1627.2 | 14.2605 | 14.2882 | -0.027695 | 85.7292 | 19.4 | 14.0839 | 5.3161 |  | 26-03-2026 16:10 | 80.402 | 83.259 | 1636.2 | 13.8765 | 14.2882 | -0.4117 | 85.7292 | 19.4 | 14.0839 | 5.3161 |  | 26-03-2026 16:10 | 74.061 | 75.12 | 1544.9 | 12.52 | 13.5934 | -1.0734 | 81.5607 | 18.8 | 13.3991 | 5.4009 |  | 26-03-2026 16:10 | 145.8703 | 147.9025 | -2.0321 | 887.4149 | 207.7 | 145.7875 | 61.9125 | 61.8297
26-03-2026 16:00 | 594 | 49.65 | 212.441 | 215.436 | 2158 | 35.906 | 35.2545 | 0.65153 | 211.5268 | 34.5 | 34.7503 | -0.25033 |  | 26-03-2026 16:00 | 227.264 | 217.29 | 2175.5 | 36.215 | 35.2545 | 0.96053 | 211.5268 | 33.7 | 34.7503 | -1.0503 |  | 26-03-2026 16:00 | 207.84 | 211.444 | 2144.7 | 35.2407 | 35.2545 | -0.013806 | 211.5268 | 34.3 | 34.7503 | -0.45033 |  | 26-03-2026 16:00 | 208.181 | 211.18 | 2158.5 | 35.1967 | 35.2545 | -0.057806 | 211.5268 | 34.6 | 34.7503 | -0.15033 |  | 26-03-2026 16:00 | 165.138 | 167.381 | 1622.3 | 27.8968 | 26.1144 | 1.7824 | 156.6865 | 26.7 | 25.741 | 0.95901 |  | 26-03-2026 16:00 | 158.535 | 161.575 | 1606 | 26.9292 | 26.1144 | 0.81474 | 156.6865 | 26.1 | 25.741 | 0.35901 |  | 26-03-2026 16:00 | 162.204 | 165.054 | 1607.8 | 27.509 | 26.1144 | 1.3946 | 156.6865 | 26.9 | 25.741 | 1.159 |  | 26-03-2026 16:00 | 155.491 | 160.011 | 1616.8 | 26.6685 | 26.1144 | 0.55408 | 156.6865 | 27 | 25.741 | 1.259 |  | 26-03-2026 16:00 | 147.064 | 149.046 | 1526.1 | 24.841 | 24.8446 | -0.0036404 | 149.0678 | 24.7 | 24.4894 | 0.21064 |  | 26-03-2026 16:00 | 276.4028 | 270.3202 | 6.0826 | 1621.9214 | 268.5 | 266.4547 | 2.0453 | -7.9028
26-03-2026 15:50 | 417 | 49.65 | 111.095 | 143.432 | 2123.5 | 23.9053 | 24.7494 | -0.84402 | 148.4961 | 35.6 | 24.3954 | 11.2046 |  | 26-03-2026 15:50 | 148.482 | 150.544 | 2141.8 | 25.0907 | 24.7494 | 0.34131 | 148.4961 | 36.6 | 24.3954 | 12.2046 |  | 26-03-2026 15:50 | 159.465 | 162.532 | 2110.4 | 27.0887 | 24.7494 | 2.3393 | 148.4961 | 36.1 | 24.3954 | 11.7046 |  | 26-03-2026 15:50 | 159.804 | 162.679 | 2123.9 | 27.1132 | 24.7494 | 2.3638 | 148.4961 | 36.5 | 24.3954 | 12.1046 |  | 26-03-2026 15:50 | 126.057 | 127.756 | 1595.6 | 21.2927 | 18.3329 | 2.9598 | 109.9971 | 27.4 | 18.0707 | 9.3293 |  | 26-03-2026 15:50 | 127.683 | 129.745 | 1579.9 | 21.6242 | 18.3329 | 3.2913 | 109.9971 | 26.7 | 18.0707 | 8.6293 |  | 26-03-2026 15:50 | 134.326 | 136.15 | 1580.9 | 22.6917 | 18.3329 | 4.3588 | 109.9971 | 26.8 | 18.0707 | 8.7293 |  | 26-03-2026 15:50 | 139.6 | 143.059 | 1589.8 | 23.8432 | 18.3329 | 5.5103 | 109.9971 | 27.5 | 18.0707 | 9.4293 |  | 26-03-2026 15:50 | 130.609 | 132.41 | 1501.4 | 22.0683 | 17.4414 | 4.6269 | 104.6486 | 25.9 | 17.192 | 8.708 |  | 26-03-2026 15:50 | 214.7178 | 189.7703 | 24.9476 | 1138.6216 | 279.1 | 187.0565 | 92.0435 | 64.3822
26-03-2026 15:40 | 731 | 50.23 | 247.986 | 251.737 | 2087.9 | 41.9562 | 43.2892 | -1.333 | 259.735 | 42.2 | 42.6701 | -0.47013 |  | 26-03-2026 15:40 | 253.522 | 255.095 | 2105.2 | 42.5158 | 43.2892 | -0.77333 | 259.735 | 42.8 | 42.6701 | 0.12987 |  | 26-03-2026 15:40 | 247.677 | 253.759 | 2074.3 | 42.2932 | 43.2892 | -0.996 | 259.735 | 42.1 | 42.6701 | -0.57013 |  | 26-03-2026 15:40 | 249.084 | 252.954 | 2087.4 | 42.159 | 43.2892 | -1.1302 | 259.735 | 42.4 | 42.6701 | -0.27013 |  | 26-03-2026 15:40 | 186.947 | 189.601 | 1568.2 | 31.6002 | 32.066 | -0.46588 | 192.3963 | 32.3 | 31.6075 | 0.6925 |  | 26-03-2026 15:40 | 183.524 | 186.616 | 1553.2 | 31.1027 | 32.066 | -0.96338 | 192.3963 | 31.8 | 31.6075 | 0.1925 |  | 26-03-2026 15:40 | 183.653 | 186.797 | 1554.1 | 31.1328 | 32.066 | -0.93322 | 192.3963 | 31.8 | 31.6075 | 0.1925 |  | 26-03-2026 15:40 | 183.62 | 188.803 | 1562.3 | 31.4672 | 32.066 | -0.59888 | 192.3963 | 31.4 | 31.6075 | -0.2075 |  | 26-03-2026 15:40 | 173.759 | 176.225 | 1475.5 | 29.3708 | 30.5069 | -1.136 | 183.0412 | 29.7 | 30.0706 | -0.37063 |  | 26-03-2026 15:40 | 323.5978 | 331.9277 | -8.3299 | 1991.5664 | 326.5 | 327.1812 | -0.68117 | 2.9022
26-03-2026 15:30 | 766 | 49.94 | 260.181 | 264.197 | 2045.7 | 44.0328 | 45.4123 | -1.3795 | 272.474 | 46.4 | 44.7629 | 1.6371 |  | 26-03-2026 15:30 | 263.669 | 267.584 | 2062.4 | 44.5973 | 45.4123 | -0.815 | 272.474 | 47 | 44.7629 | 2.2371 |  | 26-03-2026 15:30 | 259.525 | 266.464 | 2032.2 | 44.4107 | 45.4123 | -1.0017 | 272.474 | 44 | 44.7629 | -0.76294 |  | 26-03-2026 15:30 | 260.72 | 264.825 | 2045 | 44.1375 | 45.4123 | -1.2748 | 272.474 | 44.2 | 44.7629 | -0.56294 |  | 26-03-2026 15:30 | 195.779 | 198.609 | 1535.9 | 33.1015 | 33.6388 | -0.53727 | 201.8326 | 32.6 | 33.1577 | -0.55773 |  | 26-03-2026 15:30 | 192.245 | 195.254 | 1521.4 | 32.5423 | 33.6388 | -1.0964 | 201.8326 | 32 | 33.1577 | -1.1577 |  | 26-03-2026 15:30 | 192.444 | 195.712 | 1522.3 | 32.6187 | 33.6388 | -1.0201 | 201.8326 | 32.1 | 33.1577 | -1.0577 |  | 26-03-2026 15:30 | 192.853 | 198.421 | 1530.9 | 33.0702 | 33.6388 | -0.5686 | 201.8326 | 32.1 | 33.1577 | -1.0577 |  | 26-03-2026 15:30 | 182.184 | 184.808 | 1445.8 | 30.8013 | 32.0031 | -1.2018 | 192.0187 | 30.3 | 31.5455 | -1.2455 |  | 26-03-2026 15:30 | 339.3123 | 348.2075 | -8.8952 | 2089.2452 | 340.7 | 343.2282 | -2.5282 | 1.3877
26-03-2026 15:20 | 786 | 50.23 | 266.404 | 270.545 | 1999.3 | 45.0908 | 46.5462 | -1.4554 | 279.2773 | 43.3 | 45.8806 | -2.5806 |  | 26-03-2026 15:20 | 271.034 | 274.351 | 2015.4 | 45.7252 | 46.5462 | -0.82105 | 279.2773 | 45.1 | 45.8806 | -0.78061 |  | 26-03-2026 15:20 | 265.83 | 272.763 | 1988.2 | 45.4605 | 46.5462 | -1.0857 | 279.2773 | 44.9 | 45.8806 | -0.98061 |  | 26-03-2026 15:20 | 267.662 | 271.931 | 2000.8 | 45.3218 | 46.5462 | -1.2244 | 279.2773 | 45.2 | 45.8806 | -0.68061 |  | 26-03-2026 15:20 | 200.903 | 203.797 | 1503.3 | 33.9662 | 34.4787 | -0.51251 | 206.8721 | 34.4 | 33.9856 | 0.41437 |  | 26-03-2026 15:20 | 197.356 | 200.712 | 1489.4 | 33.452 | 34.4787 | -1.0267 | 206.8721 | 33.8 | 33.9856 | -0.18563 |  | 26-03-2026 15:20 | 197.739 | 201.159 | 1490.2 | 33.5265 | 34.4787 | -0.95218 | 206.8721 | 33.8 | 33.9856 | -0.18563 |  | 26-03-2026 15:20 | 198.06 | 203.76 | 1498.8 | 33.96 | 34.4787 | -0.51868 | 206.8721 | 33.9 | 33.9856 | -0.085634 |  | 26-03-2026 15:20 | 186.937 | 189.63 | 1415.5 | 31.605 | 32.8022 | -1.1972 | 196.8132 | 32 | 32.3331 | -0.33312 |  | 26-03-2026 15:20 | 348.108 | 356.9018 | -8.7938 | 2141.4107 | 346.4 | 351.7981 | -5.3981 | -1.708
26-03-2026 15:10 | 842 | 50.23 | 284.65 | 289.27 | 1956 | 48.2117 | 49.8625 | -1.6508 | 299.1749 | 48.8 | 49.1495 | -0.34945 |  | 26-03-2026 15:10 | 288.324 | 293.035 | 1970.3 | 48.8392 | 49.8625 | -1.0233 | 299.1749 | 46.2 | 49.1495 | -2.9495 |  | 26-03-2026 15:10 | 282.004 | 289.746 | 1943.3 | 48.291 | 49.8625 | -1.5715 | 299.1749 | 47.3 | 49.1495 | -1.8495 |  | 26-03-2026 15:10 | 284.822 | 289.02 | 1955.6 | 48.17 | 49.8625 | -1.6925 | 299.1749 | 48.2 | 49.1495 | -0.94945 |  | 26-03-2026 15:10 | 213.258 | 216.418 | 1468.9 | 36.0697 | 36.9352 | -0.86551 | 221.6111 | 35.8 | 36.407 | -0.607 |  | 26-03-2026 15:10 | 209.509 | 213.322 | 1455.6 | 35.5537 | 36.9352 | -1.3815 | 221.6111 | 35.1 | 36.407 | -1.307 |  | 26-03-2026 15:10 | 209.833 | 213.7 | 1456.4 | 35.6167 | 36.9352 | -1.3185 | 221.6111 | 35.2 | 36.407 | -1.207 |  | 26-03-2026 15:10 | 209.962 | 215.973 | 1464.9 | 35.9955 | 36.9352 | -0.93968 | 221.6111 | 35.2 | 36.407 | -1.207 |  | 26-03-2026 15:10 | 198.294 | 201.212 | 1383.5 | 33.5353 | 35.1392 | -1.6039 | 210.8355 | 33.2 | 34.6368 | -1.4368 |  | 26-03-2026 15:10 | 370.2827 | 382.3299 | -12.0472 | 2293.9794 | 365 | 376.8626 | -11.8626 | -5.2827
26-03-2026 15:00 | 843 | 49.94 | 283.751 | 288.336 | 1907.2 | 48.056 | 49.9773 | -1.9213 | 299.8637 | 48.7 | 49.2626 | -0.56261 | 0.9841 | 26-03-2026 15:00 | 287.133 | 291.861 | 1924.1 | 48.6435 | 49.9773 | -1.3338 | 299.8637 | 49.8 | 49.2626 | 0.53739 | 0.9838 | 26-03-2026 15:00 | 282.519 | 289.989 | 1896 | 48.3315 | 49.9773 | -1.6458 | 299.8637 | 48.5 | 49.2626 | -0.76261 | 0.97424 | 26-03-2026 15:00 | 283.894 | 288.539 | 1907.4 | 48.0898 | 49.9773 | -1.8875 | 299.8637 | 48.1 | 49.2626 | -1.1626 | 0.9839 | 26-03-2026 15:00 | 213.098 | 216.277 | 1433.1 | 36.0462 | 37.0202 | -0.97404 | 222.1213 | 36.1 | 36.4908 | -0.39082 | 0.9853 | 26-03-2026 15:00 | 209.236 | 212.994 | 1420.5 | 35.499 | 37.0202 | -1.5212 | 222.1213 | 35.4 | 36.4908 | -1.0908 | 0.98236 | 26-03-2026 15:00 | 209.874 | 213.586 | 1421.2 | 35.5977 | 37.0202 | -1.4225 | 222.1213 | 35.6 | 36.4908 | -0.89082 | 0.98262 | 26-03-2026 15:00 | 210.501 | 216.778 | 1429.7 | 36.1297 | 37.0202 | -0.89054 | 222.1213 | 35.9 | 36.4908 | -0.59082 | 0.97104 | 26-03-2026 15:00 | 198.525 | 201.507 | 1350.3 | 33.5845 | 35.2201 | -1.6356 | 211.3209 | 33.7 | 34.7165 | -1.0165 | 0.9852 | 26-03-2026 15:00 | 369.9778 | 383.2101 | -13.2323 | 2299.2608 | 371.8 | 377.7302 | -5.9302 | 1.8222
26-03-2026 14:50 | 882 | 50.23 | 295.526 | 300.362 | 1858.5 | 50.0603 | 52.2313 | -2.1709 | 313.3875 | 48.3 | 51.4843 | -3.1843 | 0.9839 | 26-03-2026 14:50 | 299.566 | 304.327 | 1874.3 | 50.7212 | 52.2313 | -1.5101 | 313.3875 | 53.4 | 51.4843 | 1.9157 | 0.98436 | 26-03-2026 14:50 | 294.351 | 302.639 | 1847.5 | 50.4398 | 52.2313 | -1.7914 | 313.3875 | 50.8 | 51.4843 | -0.68434 | 0.97261 | 26-03-2026 14:50 | 295.86 | 300.793 | 1859.3 | 50.1322 | 52.2313 | -2.0991 | 313.3875 | 51.1 | 51.4843 | -0.38434 | 0.9836 | 26-03-2026 14:50 | 222.648 | 226.033 | 1397 | 37.6722 | 38.6898 | -1.0176 | 232.1389 | 38.3 | 38.1366 | 0.16345 | 0.98502 | 26-03-2026 14:50 | 218.123 | 222.082 | 1385.1 | 37.0137 | 38.6898 | -1.6761 | 232.1389 | 37.6 | 38.1366 | -0.53655 | 0.98217 | 26-03-2026 14:50 | 219.475 | 223.555 | 1385.6 | 37.2592 | 38.6898 | -1.4306 | 232.1389 | 37.7 | 38.1366 | -0.43655 | 0.98175 | 26-03-2026 14:50 | 220.359 | 226.894 | 1393.8 | 37.8157 | 38.6898 | -0.87415 | 232.1389 | 37.8 | 38.1366 | -0.33655 | 0.9712 | 26-03-2026 14:50 | 207.198 | 210.289 | 1316.6 | 35.0482 | 36.8086 | -1.7604 | 220.8514 | 35.7 | 36.2822 | -0.58221 | 0.9853 | 26-03-2026 14:50 | 386.1623 | 400.4928 | -14.3305 | 2402.957 | 390.7 | 394.7658 | -4.0658 | 4.5377
26-03-2026 14:40 | 969 | 49.94 | 322.073 | 327.576 | 1810.2 | 54.596 | 57.4472 | -2.8512 | 344.6832 | 54.6 | 56.6257 | -2.0257 | 0.9832 | 26-03-2026 14:40 | 327.37 | 333.032 | 1820.9 | 55.5053 | 57.4472 | -1.9419 | 344.6832 | 53.1 | 56.6257 | -3.5257 | 0.983 | 26-03-2026 14:40 | 320.429 | 329.71 | 1796.7 | 54.9517 | 57.4472 | -2.4955 | 344.6832 | 53.5 | 56.6257 | -3.1257 | 0.97185 | 26-03-2026 14:40 | 322.674 | 328.254 | 1808.2 | 54.709 | 57.4472 | -2.7382 | 344.6832 | 53.8 | 56.6257 | -2.8257 | 0.983 | 26-03-2026 14:40 | 241.752 | 245.533 | 1358.7 | 40.9222 | 42.5535 | -1.6313 | 255.3209 | 40.4 | 41.945 | -1.545 | 0.9846 | 26-03-2026 14:40 | 237.526 | 242.029 | 1347.5 | 40.3382 | 42.5535 | -2.2153 | 255.3209 | 39.8 | 41.945 | -2.145 | 0.98139 | 26-03-2026 14:40 | 237.812 | 242.485 | 1347.9 | 40.4142 | 42.5535 | -2.1393 | 255.3209 | 39.8 | 41.945 | -2.145 | 0.98073 | 26-03-2026 14:40 | 238.907 | 246.153 | 1356 | 41.0255 | 42.5535 | -1.528 | 255.3209 | 40 | 41.945 | -1.945 | 0.97056 | 26-03-2026 14:40 | 225.243 | 228.766 | 1280.9 | 38.1277 | 40.4844 | -2.3567 | 242.9062 | 37.7 | 39.9054 | -2.2054 | 0.9846 | 26-03-2026 14:40 | 420.5897 | 440.4871 | -19.8974 | 2642.9225 | 412.7 | 434.1881 | -21.4881 | -7.8897
26-03-2026 14:30 | 952 | 49.94 | 345.904 | 351.779 | 1755.6 | 58.6298 | 56.4394 | 2.1905 | 338.6361 | 50 | 55.6323 | -5.6323 | 0.9833 | 26-03-2026 14:30 | 321.643 | 328.756 | 1767.8 | 54.7927 | 56.4394 | -1.6467 | 338.6361 | 48.7 | 55.6323 | -6.9323 | 0.97836 | 26-03-2026 14:30 | 324.365 | 333.786 | 1743.2 | 55.631 | 56.4394 | -0.80835 | 338.6361 | 49.4 | 55.6323 | -6.2323 | 0.97178 | 26-03-2026 14:30 | 335.474 | 341.241 | 1754.4 | 56.8735 | 56.4394 | 0.43415 | 338.6361 | 49.4 | 55.6323 | -6.2323 | 0.9831 | 26-03-2026 14:30 | 253.69 | 257.736 | 1318.3 | 42.956 | 41.8069 | 1.1491 | 250.8416 | 38.2 | 41.2091 | -3.0091 | 0.9843 | 26-03-2026 14:30 | 247.663 | 253.958 | 1307.7 | 42.3263 | 41.8069 | 0.5194 | 250.8416 | 37.4 | 41.2091 | -3.8091 | 0.97521 | 26-03-2026 14:30 | 250.693 | 255.611 | 1308.1 | 42.6018 | 41.8069 | 0.7949 | 250.8416 | 37.8 | 41.2091 | -3.4091 | 0.98076 | 26-03-2026 14:30 | 252.256 | 259.633 | 1316 | 43.2722 | 41.8069 | 1.4652 | 250.8416 | 37.9 | 41.2091 | -3.3091 | 0.97159 | 26-03-2026 14:30 | 238.166 | 241.867 | 1243.2 | 40.3112 | 39.7741 | 0.53705 | 238.6447 | 35.6 | 39.2053 | -3.6053 | 0.9847 | 26-03-2026 14:30 | 437.3945 | 432.7592 | 4.6353 | 2596.5555 | 384.4 | 426.5708 | -42.1708 | -52.9945
26-03-2026 14:20 | 1122 | 49.65 | 334.236 | 340.016 | 1705.6 | 56.6693 | 66.5918 | -9.9224 | 399.5507 | 41.6 | 65.6395 | -24.0395 | 0.983 | 26-03-2026 14:20 | 324.106 | 253.149 | 1719.1 | 42.1915 | 66.5918 | -24.4003 | 399.5507 | 43.6 | 65.6395 | -22.0395 | 1.2803 | 26-03-2026 14:20 | 316.781 | 339.976 | 1693.8 | 56.6627 | 66.5918 | -9.9291 | 399.5507 | 41.5 | 65.6395 | -24.1395 | 0.93177 | 26-03-2026 14:20 | 292.671 | 297.581 | 1705 | 49.5968 | 66.5918 | -16.9949 | 399.5507 | 42.5 | 65.6395 | -23.1395 | 0.9835 | 26-03-2026 14:20 | 220.412 | 264.87 | 1280.1 | 44.145 | 49.3272 | -5.1822 | 295.9635 | 33.2 | 48.6219 | -15.4219 | 0.83215 | 26-03-2026 14:20 | 243.251 | 258.643 | 1270.3 | 43.1072 | 49.3272 | -6.2201 | 295.9635 | 32.7 | 48.6219 | -15.9219 | 0.94049 | 26-03-2026 14:20 | 258.318 | 278.056 | 1270.3 | 46.3427 | 49.3272 | -2.9846 | 295.9635 | 33.2 | 48.6219 | -15.4219 | 0.92901 | 26-03-2026 14:20 | 250.606 | 267.393 | 1278.1 | 44.5655 | 49.3272 | -4.7617 | 295.9635 | 33.8 | 48.6219 | -14.8219 | 0.93722 | 26-03-2026 14:20 | 228.685 | 236.481 | 1207.6 | 39.4135 | 46.9288 | -7.5153 | 281.5726 | 31.7 | 46.2577 | -14.5577 | 0.96703 | 26-03-2026 14:20 | 422.6942 | 510.6049 | -87.9107 | 3063.6293 | 333.8 | 503.3032 | -169.5032 | -88.8942
26-03-2026 14:10 | 956 | 49.94 | 308.702 | 313.817 | 1664 | 52.3028 | 56.6765 | -4.3737 | 340.059 | 40.5 | 55.866 | -15.366 | 0.9837 | 26-03-2026 14:10 | 346.345 | 354.097 | 1675.5 | 59.0162 | 56.6765 | 2.3397 | 340.059 | 39.3 | 55.866 | -16.566 | 0.97811 | 26-03-2026 14:10 | 304.205 | 316.634 | 1652.3 | 52.7723 | 56.6765 | -3.9042 | 340.059 | 40.4 | 55.866 | -15.466 | 0.96075 | 26-03-2026 14:10 | 315.09 | 320.441 | 1662.5 | 53.4068 | 56.6765 | -3.2697 | 340.059 | 39.8 | 55.866 | -16.066 | 0.9833 | 26-03-2026 14:10 | 242.709 | 248.648 | 1246.9 | 41.4413 | 41.9826 | -0.54125 | 251.8955 | 30.2 | 41.3822 | -11.1822 | 0.97611 | 26-03-2026 14:10 | 227.027 | 232.502 | 1237.6 | 38.7503 | 41.9826 | -3.2323 | 251.8955 | 29.7 | 41.3822 | -11.6822 | 0.97645 | 26-03-2026 14:10 | 235.183 | 238.692 | 1237.1 | 39.782 | 41.9826 | -2.2006 | 251.8955 | 29.6 | 41.3822 | -11.7822 | 0.9853 | 26-03-2026 14:10 | 231.092 | 238.212 | 1244.3 | 39.702 | 41.9826 | -2.2806 | 251.8955 | 29.7 | 41.3822 | -11.6822 | 0.97011 | 26-03-2026 14:10 | 219.045 | 223.283 | 1175.9 | 37.2138 | 39.9412 | -2.7274 | 239.6474 | 28 | 39.3701 | -11.3701 | 0.98102 | 26-03-2026 14:10 | 414.3877 | 434.5776 | -20.1899 | 2607.4654 | 307.2 | 428.3631 | -121.1631 | -107.1877
26-03-2026 14:00 | 654 | 49.65 | 232.63 | 236.149 | 1623.5 | 39.3582 | 38.8155 | 0.54264 | 232.8932 | 46 | 38.2605 | 7.7395 | 0.9851 | 26-03-2026 14:00 | 218.787 | 222.119 | 1636.2 | 37.0198 | 38.8155 | -1.7957 | 232.8932 | 46.9 | 38.2605 | 8.6395 | 0.985 | 26-03-2026 14:00 | 227.425 | 242.699 | 1611.9 | 40.4498 | 38.8155 | 1.6343 | 232.8932 | 45.6 | 38.2605 | 7.3395 | 0.93707 | 26-03-2026 14:00 | 218.811 | 222.326 | 1622.7 | 37.0543 | 38.8155 | -1.7612 | 232.8932 | 46.1 | 38.2605 | 7.8395 | 0.98419 | 26-03-2026 14:00 | 202.507 | 214.241 | 1216.7 | 35.7068 | 28.7522 | 6.9546 | 172.5135 | 35 | 28.3411 | 6.6589 | 0.94523 | 26-03-2026 14:00 | 176.586 | 186.259 | 1207.9 | 31.0432 | 28.7522 | 2.2909 | 172.5135 | 34.7 | 28.3411 | 6.3589 | 0.94807 | 26-03-2026 14:00 | 209.392 | 213.357 | 1207.5 | 35.5595 | 28.7522 | 6.8073 | 172.5135 | 34.7 | 28.3411 | 6.3589 | 0.98142 | 26-03-2026 14:00 | 201.739 | 210.705 | 1214.6 | 35.1175 | 28.7522 | 6.3653 | 172.5135 | 35 | 28.3411 | 6.6589 | 0.95745 | 26-03-2026 14:00 | 184.959 | 192.718 | 1147.9 | 32.1197 | 27.3542 | 4.7655 | 164.1252 | 33.1 | 26.963 | 6.137 | 0.95974 | 26-03-2026 14:00 | 323.4288 | 297.6253 | 25.8035 | 1785.7518 | 357.1 | 293.3693 | 63.7307 | 33.6712
26-03-2026 13:50 | 658 | 49.94 | 251.669 | 204.51 | 1577.5 | 34.085 | 39.0096 | -4.9246 | 234.0573 | 45.2 | 38.4517 | 6.7483 | 1.2306 | 26-03-2026 13:50 | 208.016 | 211.141 | 1589.3 | 35.1902 | 39.0096 | -3.8194 | 234.0573 | 45.4 | 38.4517 | 6.9483 | 0.9852 | 26-03-2026 13:50 | 211.832 | 217.675 | 1566.3 | 36.2792 | 39.0096 | -2.7304 | 234.0573 | 45.1 | 38.4517 | 6.6483 | 0.97316 | 26-03-2026 13:50 | 218.55 | 221.743 | 1576.6 | 36.9572 | 39.0096 | -2.0524 | 234.0573 | 45.5 | 38.4517 | 7.0483 | 0.9856 | 26-03-2026 13:50 | 162.397 | 164.686 | 1181.7 | 27.4477 | 28.896 | -1.4483 | 173.3758 | 33.9 | 28.4828 | 5.4172 | 0.9861 | 26-03-2026 13:50 | 162.978 | 165.779 | 1173.2 | 27.6298 | 28.896 | -1.2661 | 173.3758 | 33.4 | 28.4828 | 4.9172 | 0.9831 | 26-03-2026 13:50 | 149.628 | 152.28 | 1172.8 | 25.38 | 28.896 | -3.516 | 173.3758 | 33.9 | 28.4828 | 5.4172 | 0.98258 | 26-03-2026 13:50 | 148.496 | 152.942 | 1179.6 | 25.4903 | 28.896 | -3.4056 | 173.3758 | 34.4 | 28.4828 | 5.9172 | 0.97093 | 26-03-2026 13:50 | 143.602 | 145.641 | 1114.8 | 24.2735 | 27.4909 | -3.2174 | 164.9456 | 32.3 | 27.0978 | 5.2022 | 0.986 | 26-03-2026 13:50 | 272.7328 | 299.113 | -26.3802 | 1794.678 | 349.1 | 294.8357 | 54.2643 | 76.3672
26-03-2026 13:40 | 896 | 49.94 | 352.451 | 358.109 | 1532.3 | 59.6848 | 53.1194 | 6.5654 | 318.7163 | 50.3 | 52.3598 | -2.0598 | 0.9842 | 26-03-2026 13:40 | 338.265 | 344.255 | 1543.9 | 57.3758 | 53.1194 | 4.2564 | 318.7163 | 50.6 | 52.3598 | -1.7598 | 0.9826 | 26-03-2026 13:40 | 281.08 | 290.508 | 1521.2 | 48.418 | 53.1194 | -4.7014 | 318.7163 | 49.6 | 52.3598 | -2.7598 | 0.96755 | 26-03-2026 13:40 | 276.616 | 281.171 | 1531.1 | 46.8618 | 53.1194 | -6.2576 | 318.7163 | 49.9 | 52.3598 | -2.4598 | 0.9838 | 26-03-2026 13:40 | 223.289 | 229.818 | 1147.8 | 38.303 | 39.3477 | -1.0447 | 236.0862 | 37.5 | 38.785 | -1.285 | 0.97159 | 26-03-2026 13:40 | 205.089 | 210.636 | 1139.8 | 35.106 | 39.3477 | -4.2417 | 236.0862 | 37.5 | 38.785 | -1.285 | 0.97367 | 26-03-2026 13:40 | 187.262 | 189.959 | 1138.9 | 31.6598 | 39.3477 | -7.6879 | 236.0862 | 37.3 | 38.785 | -1.485 | 0.9858 | 26-03-2026 13:40 | 193.434 | 204.637 | 1145.2 | 34.1062 | 39.3477 | -5.2415 | 236.0862 | 37.8 | 38.785 | -0.98503 | 0.94525 | 26-03-2026 13:40 | 199.997 | 202.94 | 1082.5 | 33.8233 | 37.4345 | -3.6111 | 224.6068 | 35.4 | 36.8991 | -1.4991 | 0.9855 | 26-03-2026 13:40 | 385.3388 | 407.3028 | -21.964 | 2443.8169 | 385.9 | 401.4784 | -15.5784 | 0.56117
26-03-2026 13:30 | 921 | 50.23 | 313.266 | 314.759 | 1482 | 52.4598 | 54.5408 | -2.081 | 327.2448 | 55.6 | 53.7609 | 1.8391 | 0.99526 | 26-03-2026 13:30 | 318.366 | 327.321 | 1493.3 | 54.5535 | 54.5408 | 0.012703 | 327.2448 | 56.3 | 53.7609 | 2.5391 | 0.97264 | 26-03-2026 13:30 | 322.809 | 333.589 | 1471.6 | 55.5982 | 54.5408 | 1.0574 | 327.2448 | 55.7 | 53.7609 | 1.9391 | 0.96768 | 26-03-2026 13:30 | 315.773 | 321.267 | 1481.2 | 53.5445 | 54.5408 | -0.9963 | 327.2448 | 55.8 | 53.7609 | 2.0391 | 0.9829 | 26-03-2026 13:30 | 229.394 | 239.939 | 1110.3 | 39.9898 | 40.4006 | -0.41076 | 242.4035 | 42.9 | 39.8229 | 3.0771 | 0.95605 | 26-03-2026 13:30 | 228.555 | 232.059 | 1102.3 | 38.6765 | 40.4006 | -1.7241 | 242.4035 | 41.7 | 39.8229 | 1.8771 | 0.9849 | 26-03-2026 13:30 | 233.263 | 236.806 | 1101.6 | 39.4677 | 40.4006 | -0.93292 | 242.4035 | 41.9 | 39.8229 | 2.0771 | 0.98504 | 26-03-2026 13:30 | 236.089 | 243.15 | 1107.4 | 40.525 | 40.4006 | 0.12441 | 242.4035 | 42.7 | 39.8229 | 2.8771 | 0.97096 | 26-03-2026 13:30 | 213.35 | 222.313 | 1047.1 | 37.0522 | 38.4362 | -1.384 | 230.6169 | 40.2 | 37.8865 | 2.3135 | 0.95968 | 26-03-2026 13:30 | 411.8672 | 418.2017 | -6.3345 | 2509.2102 | 432.8 | 412.2214 | 20.5786 | 20.9328
26-03-2026 13:20 | 867 | 50.23 | 253.207 | 273.818 | 1426.4 | 45.6363 | 51.343 | -5.7066 | 308.0578 | 53 | 50.6088 | 2.3912 | 0.92473 | 26-03-2026 13:20 | 288.266 | 293.132 | 1437 | 48.8553 | 51.343 | -2.4876 | 308.0578 | 56.9 | 50.6088 | 6.2912 | 0.9834 | 26-03-2026 13:20 | 297.292 | 306.624 | 1415.9 | 51.104 | 51.343 | -0.23896 | 308.0578 | 53.6 | 50.6088 | 2.9912 | 0.96957 | 26-03-2026 13:20 | 296.929 | 301.972 | 1425.4 | 50.3287 | 51.343 | -1.0143 | 308.0578 | 53.7 | 50.6088 | 3.0912 | 0.9833 | 26-03-2026 13:20 | 240.747 | 244.463 | 1067.4 | 40.7438 | 38.0318 | 2.712 | 228.191 | 42.2 | 37.488 | 4.712 | 0.9848 | 26-03-2026 13:20 | 232.775 | 237.189 | 1060.6 | 39.5315 | 38.0318 | 1.4997 | 228.191 | 41.6 | 37.488 | 4.112 | 0.98139 | 26-03-2026 13:20 | 246.563 | 251.57 | 1059.7 | 41.9283 | 38.0318 | 3.8965 | 228.191 | 41.6 | 37.488 | 4.112 | 0.9801 | 26-03-2026 13:20 | 237.945 | 245.311 | 1064.7 | 40.8852 | 38.0318 | 2.8533 | 228.191 | 41.7 | 37.488 | 4.212 | 0.96997 | 26-03-2026 13:20 | 207.584 | 216.29 | 1006.9 | 36.0483 | 36.1826 | -0.13424 | 217.0954 | 39 | 35.6652 | 3.3348 | 0.95975 | 26-03-2026 13:20 | 395.0615 | 393.6817 | 1.3798 | 2362.0904 | 423.3 | 388.0521 | 35.2479 | 28.2385
26-03-2026 13:10 | 1096 | 49.94 | 347.649 | 353.122 | 1373.4 | 58.8537 | 64.9764 | -6.1227 | 389.8584 | 52.7 | 64.0472 | -11.3472 | 0.9845 | 26-03-2026 13:10 | 342.679 | 347.968 | 1380.1 | 57.9947 | 64.9764 | -6.9817 | 389.8584 | 49.8 | 64.0472 | -14.2472 | 0.9848 | 26-03-2026 13:10 | 346.684 | 356.826 | 1362.3 | 59.471 | 64.9764 | -5.5054 | 389.8584 | 52.7 | 64.0472 | -11.3472 | 0.97158 | 26-03-2026 13:10 | 343.404 | 348.49 | 1371.7 | 58.0817 | 64.9764 | -6.8947 | 389.8584 | 52.4 | 64.0472 | -11.6472 | 0.98541 | 26-03-2026 13:10 | 271.419 | 275.86 | 1025.2 | 45.9767 | 48.1307 | -2.154 | 288.784 | 40.5 | 47.4424 | -6.9424 | 0.9839 | 26-03-2026 13:10 | 268.249 | 273.519 | 1019 | 45.5865 | 48.1307 | -2.5442 | 288.784 | 39.9 | 47.4424 | -7.5424 | 0.98073 | 26-03-2026 13:10 | 266.826 | 272.329 | 1018.1 | 45.3882 | 48.1307 | -2.7425 | 288.784 | 40.2 | 47.4424 | -7.2424 | 0.97979 | 26-03-2026 13:10 | 266.991 | 274.798 | 1023 | 45.7997 | 48.1307 | -2.331 | 288.784 | 39.9 | 47.4424 | -7.5424 | 0.97159 | 26-03-2026 13:10 | 253.761 | 257.887 | 967.9 | 42.9812 | 45.7904 | -2.8092 | 274.7422 | 37.9 | 45.1356 | -7.2356 | 0.984 | 26-03-2026 13:10 | 460.1332 | 498.2186 | -38.0855 | 2989.3117 | 406 | 491.0941 | -85.0941 | -54.1332
26-03-2026 13:00 | 632 | 49.65 | 205.778 | 208.912 | 1320.7 | 34.8187 | 37.5098 | -2.6911 | 225.0589 | 56.5 | 36.9734 | 19.5266 | 0.985 | 26-03-2026 13:00 | 214.664 | 218.022 | 1330.3 | 36.337 | 37.5098 | -1.1728 | 225.0589 | 56.5 | 36.9734 | 19.5266 | 0.9846 | 26-03-2026 13:00 | 204.715 | 209.627 | 1309.6 | 34.9378 | 37.5098 | -2.572 | 225.0589 | 55.6 | 36.9734 | 18.6266 | 0.97657 | 26-03-2026 13:00 | 271.52 | 275.963 | 1319.3 | 45.9938 | 37.5098 | 8.484 | 225.0589 | 55.3 | 36.9734 | 18.3266 | 0.9839 | 26-03-2026 13:00 | 176.735 | 179.354 | 984.7 | 29.8923 | 27.785 | 2.1073 | 166.7103 | 41.7 | 27.3877 | 14.3123 | 0.9854 | 26-03-2026 13:00 | 187.328 | 194.285 | 979.1 | 32.3808 | 27.785 | 4.5958 | 166.7103 | 41.6 | 27.3877 | 14.2123 | 0.96419 | 26-03-2026 13:00 | 175.267 | 177.846 | 977.9 | 29.641 | 27.785 | 1.856 | 166.7103 | 41.7 | 27.3877 | 14.3123 | 0.9855 | 26-03-2026 13:00 | 183.682 | 186.385 | 983.1 | 31.0642 | 27.785 | 3.2791 | 166.7103 | 41.8 | 27.3877 | 14.4123 | 0.9855 | 26-03-2026 13:00 | 175.87 | 178.476 | 930 | 29.746 | 26.434 | 3.312 | 158.6042 | 39.5 | 26.056 | 13.444 | 0.9854 | 26-03-2026 13:00 | 304.8117 | 287.6134 | 17.1982 | 1725.6807 | 430.2 | 283.5006 | 146.6994 | 125.3883
26-03-2026 12:50 | 1066 | 49.65 | 349.118 | 355.792 | 1264.2 | 59.2987 | 63.2681 | -3.9695 | 379.6088 | 58.3 | 62.3634 | -4.0634 | 0.98124 | 26-03-2026 12:50 | 351.62 | 358.707 | 1273.8 | 59.7845 | 63.2681 | -3.4836 | 379.6088 | 58.6 | 62.3634 | -3.7634 | 0.98024 | 26-03-2026 12:50 | 347.697 | 357.666 | 1254 | 59.611 | 63.2681 | -3.6571 | 379.6088 | 58.2 | 62.3634 | -4.1634 | 0.97213 | 26-03-2026 12:50 | 341.829 | 347.387 | 1264 | 57.8978 | 63.2681 | -5.3703 | 379.6088 | 57.7 | 62.3634 | -4.6634 | 0.984 | 26-03-2026 12:50 | 263.725 | 268.013 | 943 | 44.6688 | 46.8653 | -2.1964 | 281.1917 | 44.1 | 46.1951 | -2.0951 | 0.984 | 26-03-2026 12:50 | 260.004 | 265.018 | 937.5 | 44.1697 | 46.8653 | -2.6956 | 281.1917 | 43 | 46.1951 | -3.1951 | 0.98108 | 26-03-2026 12:50 | 260.536 | 265.973 | 936.2 | 44.3288 | 46.8653 | -2.5364 | 281.1917 | 43 | 46.1951 | -3.1951 | 0.97956 | 26-03-2026 12:50 | 261.27 | 268.696 | 941.3 | 44.7827 | 46.8653 | -2.0826 | 281.1917 | 43.1 | 46.1951 | -3.0951 | 0.97236 | 26-03-2026 12:50 | 246.711 | 250.748 | 890.5 | 41.7913 | 44.5865 | -2.7952 | 267.5191 | 41.2 | 43.9489 | -2.7489 | 0.9839 | 26-03-2026 12:50 | 456.3333 | 485.1201 | -28.7868 | 2910.7209 | 447.2 | 478.1829 | -30.9829 | -9.1333
26-03-2026 12:40 | 1061 | 49.94 | 347.17 | 353.2 | 1205.9 | 58.8667 | 62.9014 | -4.0348 | 377.4085 | 56.9 | 62.0019 | -5.1019 | 0.98293 | 26-03-2026 12:40 | 342 | 349.343 | 1215.2 | 58.2238 | 62.9014 | -4.6776 | 377.4085 | 60.4 | 62.0019 | -1.6019 | 0.97898 | 26-03-2026 12:40 | 345.958 | 356.455 | 1195.8 | 59.4092 | 62.9014 | -3.4923 | 377.4085 | 57.6 | 62.0019 | -4.4019 | 0.97055 | 26-03-2026 12:40 | 343.624 | 349.353 | 1206.3 | 58.2255 | 62.9014 | -4.6759 | 377.4085 | 57.4 | 62.0019 | -4.6019 | 0.9836 | 26-03-2026 12:40 | 262.484 | 266.752 | 898.9 | 44.4587 | 46.5936 | -2.135 | 279.5619 | 43.6 | 45.9274 | -2.3274 | 0.984 | 26-03-2026 12:40 | 258.784 | 263.964 | 894.5 | 43.994 | 46.5936 | -2.5996 | 279.5619 | 43.7 | 45.9274 | -2.2274 | 0.98038 | 26-03-2026 12:40 | 259.298 | 264.534 | 893.2 | 44.089 | 46.5936 | -2.5046 | 279.5619 | 43.8 | 45.9274 | -2.1274 | 0.98021 | 26-03-2026 12:40 | 259.222 | 267.002 | 898.2 | 44.5003 | 46.5936 | -2.0933 | 279.5619 | 43.7 | 45.9274 | -2.2274 | 0.97086 | 26-03-2026 12:40 | 244.795 | 248.75 | 849.3 | 41.4583 | 44.3281 | -2.8698 | 265.9685 | 40.8 | 43.6942 | -2.8942 | 0.9841 | 26-03-2026 12:40 | 453.2255 | 482.3084 | -29.0829 | 2893.8501 | 447.9 | 475.4113 | -27.5113 | -5.3255
26-03-2026 12:30 | 1061 | 49.94 | 350.239 | 356.369 | 1149 | 59.3948 | 62.9014 | -3.5066 | 377.4085 | 58.4 | 62.0019 | -3.6019 | 0.9828 | 26-03-2026 12:30 | 352.819 | 354.912 | 1154.8 | 59.152 | 62.9014 | -3.7494 | 377.4085 | 56.3 | 62.0019 | -5.7019 | 0.9941 | 26-03-2026 12:30 | 348.317 | 358.571 | 1138.2 | 59.7618 | 62.9014 | -3.1396 | 377.4085 | 57.6 | 62.0019 | -4.4019 | 0.9714 | 26-03-2026 12:30 | 349.637 | 355.575 | 1148.9 | 59.2625 | 62.9014 | -3.6389 | 377.4085 | 57.4 | 62.0019 | -4.6019 | 0.9833 | 26-03-2026 12:30 | 263.81 | 268.55 | 855.3 | 44.7583 | 46.5936 | -1.8353 | 279.5619 | 43.6 | 45.9274 | -2.3274 | 0.98235 | 26-03-2026 12:30 | 260.114 | 265.481 | 850.8 | 44.2468 | 46.5936 | -2.3468 | 279.5619 | 42.4 | 45.9274 | -3.5274 | 0.97978 | 26-03-2026 12:30 | 260.399 | 265.926 | 849.4 | 44.321 | 46.5936 | -2.2726 | 279.5619 | 44.1 | 45.9274 | -1.8274 | 0.97922 | 26-03-2026 12:30 | 260.514 | 268.512 | 854.5 | 44.752 | 46.5936 | -1.8416 | 279.5619 | 43 | 45.9274 | -2.9274 | 0.97021 | 26-03-2026 12:30 | 246.475 | 250.457 | 808.5 | 41.7428 | 44.3281 | -2.5853 | 265.9685 | 40.8 | 43.6942 | -2.8942 | 0.9841 | 26-03-2026 12:30 | 457.3922 | 482.3084 | -24.9162 | 2893.8501 | 443.6 | 475.4113 | -31.8113 | -13.7922
26-03-2026 12:20 | 1057 | 49.65 | 348.091 | 353.967 | 1090.6 | 58.9945 | 62.734 | -3.7395 | 376.4038 | 56.4 | 61.8369 | -5.4369 | 0.9834 | 26-03-2026 12:20 | 352.71 | 358.737 | 1098.5 | 59.7895 | 62.734 | -2.9445 | 376.4038 | 60.1 | 61.8369 | -1.7369 | 0.9832 | 26-03-2026 12:20 | 347.857 | 357.745 | 1080.6 | 59.6242 | 62.734 | -3.1098 | 376.4038 | 56.4 | 61.8369 | -5.4369 | 0.97236 | 26-03-2026 12:20 | 348.266 | 354.145 | 1091.5 | 59.0242 | 62.734 | -3.7098 | 376.4038 | 57.2 | 61.8369 | -4.6369 | 0.9834 | 26-03-2026 12:20 | 263.226 | 267.425 | 811.7 | 44.5708 | 46.4696 | -1.8988 | 278.8176 | 43.3 | 45.8051 | -2.5051 | 0.9843 | 26-03-2026 12:20 | 259.485 | 264.233 | 808.4 | 44.0388 | 46.4696 | -2.4308 | 278.8176 | 42.6 | 45.8051 | -3.2051 | 0.98203 | 26-03-2026 12:20 | 259.889 | 265.268 | 805.3 | 44.2113 | 46.4696 | -2.2583 | 278.8176 | 41 | 45.8051 | -4.8051 | 0.97972 | 26-03-2026 12:20 | 260.124 | 268.122 | 811.5 | 44.687 | 46.4696 | -1.7826 | 278.8176 | 42.3 | 45.8051 | -3.5051 | 0.97017 | 26-03-2026 12:20 | 245.929 | 249.902 | 767.7 | 41.6503 | 44.2101 | -2.5597 | 265.2605 | 39.9 | 43.5779 | -3.6779 | 0.9841 | 26-03-2026 12:20 | 456.5907 | 481.0244 | -24.4337 | 2886.1463 | 439.2 | 474.1457 | -34.9457 | -17.3907
26-03-2026 12:10 | 1055 | 49.65 | 347.519 | 353.458 | 1034.2 | 58.9097 | 62.6153 | -3.7056 | 375.6916 | 55.9 | 61.7199 | -5.8199 | 0.9832 | 26-03-2026 12:10 | 336.89 | 343.098 | 1038.4 | 57.183 | 62.6153 | -5.4323 | 375.6916 | 55 | 61.7199 | -6.7199 | 0.98191 | 26-03-2026 12:10 | 345.565 | 356.001 | 1024.2 | 59.3335 | 62.6153 | -3.2818 | 375.6916 | 57.1 | 61.7199 | -4.6199 | 0.97069 | 26-03-2026 12:10 | 346.282 | 352.271 | 1034.3 | 58.7118 | 62.6153 | -3.9034 | 375.6916 | 56.8 | 61.7199 | -4.9199 | 0.983 | 26-03-2026 12:10 | 261.536 | 265.789 | 768.4 | 44.2982 | 46.3817 | -2.0835 | 278.2901 | 42.6 | 45.7184 | -3.1184 | 0.984 | 26-03-2026 12:10 | 257.375 | 262.35 | 765.8 | 43.725 | 46.3817 | -2.6567 | 278.2901 | 42 | 45.7184 | -3.7184 | 0.98104 | 26-03-2026 12:10 | 258.298 | 263.401 | 764.3 | 43.9002 | 46.3817 | -2.4815 | 278.2901 | 42.2 | 45.7184 | -3.5184 | 0.98063 | 26-03-2026 12:10 | 259.362 | 266.863 | 769.2 | 44.4772 | 46.3817 | -1.9045 | 278.2901 | 42.4 | 45.7184 | -3.3184 | 0.97189 | 26-03-2026 12:10 | 244.781 | 248.761 | 727.8 | 41.4602 | 44.1264 | -2.6663 | 264.7585 | 40 | 43.4954 | -3.4954 | 0.984 | 26-03-2026 12:10 | 451.9987 | 480.1142 | -28.1155 | 2880.6853 | 434 | 473.2486 | -39.2486 | -17.9987
26-03-2026 12:00 | 997 | 49.65 | 328.254 | 333.965 | 978.3 | 55.6608 | 59.1729 | -3.5121 | 355.0375 | 56.2 | 58.3267 | -2.1267 | 0.9829 | 26-03-2026 12:00 | 335.369 | 341.308 | 983.4 | 56.8847 | 59.1729 | -2.2882 | 355.0375 | 54.6 | 58.3267 | -3.7267 | 0.9826 | 26-03-2026 12:00 | 327.017 | 336.195 | 967.1 | 56.0325 | 59.1729 | -3.1404 | 355.0375 | 54.2 | 58.3267 | -4.1267 | 0.9727 | 26-03-2026 12:00 | 329.949 | 335.792 | 977.5 | 55.9653 | 59.1729 | -3.2076 | 355.0375 | 54.9 | 58.3267 | -3.4267 | 0.9826 | 26-03-2026 12:00 | 246.564 | 250.548 | 725.8 | 41.758 | 43.8318 | -2.0738 | 262.9907 | 41.6 | 43.205 | -1.605 | 0.9841 | 26-03-2026 12:00 | 243.476 | 248.055 | 723.8 | 41.3425 | 43.8318 | -2.4893 | 262.9907 | 41.1 | 43.205 | -2.105 | 0.98154 | 26-03-2026 12:00 | 243.409 | 247.832 | 722.1 | 41.3053 | 43.8318 | -2.5265 | 262.9907 | 41 | 43.205 | -2.205 | 0.98215 | 26-03-2026 12:00 | 245.206 | 252.523 | 726.8 | 42.0872 | 43.8318 | -1.7446 | 262.9907 | 41.3 | 43.205 | -1.905 | 0.97102 | 26-03-2026 12:00 | 231.488 | 235.181 | 687.8 | 39.1968 | 41.7005 | -2.5037 | 250.2031 | 38.9 | 41.1042 | -2.2042 | 0.9843 | 26-03-2026 12:00 | 430.2332 | 453.7193 | -23.4861 | 2722.3158 | 423.8 | 447.2311 | -23.4311 | -6.4332
26-03-2026 11:50 | 1035 | 49.65 | 341.403 | 347.413 | 922.1 | 57.9022 | 61.4282 | -3.5261 | 368.5695 | 56.8 | 60.5498 | -3.7498 | 0.9827 | 26-03-2026 11:50 | 346.639 | 352.892 | 928.8 | 58.8153 | 61.4282 | -2.6129 | 368.5695 | 58.3 | 60.5498 | -2.2498 | 0.98228 | 26-03-2026 11:50 | 337.832 | 347.499 | 912.9 | 57.9165 | 61.4282 | -3.5117 | 368.5695 | 56.6 | 60.5498 | -3.9498 | 0.97218 | 26-03-2026 11:50 | 342.931 | 349.378 | 922.6 | 58.2297 | 61.4282 | -3.1986 | 368.5695 | 57.1 | 60.5498 | -3.4498 | 0.98155 | 26-03-2026 11:50 | 256.663 | 260.81 | 684.2 | 43.4683 | 45.5024 | -2.0341 | 273.0144 | 42 | 44.8517 | -2.8517 | 0.9841 | 26-03-2026 11:50 | 253.779 | 258.399 | 682.7 | 43.0665 | 45.5024 | -2.4359 | 273.0144 | 41.5 | 44.8517 | -3.3517 | 0.98212 | 26-03-2026 11:50 | 253.842 | 259.015 | 681.1 | 43.1692 | 45.5024 | -2.3332 | 273.0144 | 41.6 | 44.8517 | -3.2517 | 0.98003 | 26-03-2026 11:50 | 254.975 | 262.389 | 685.5 | 43.7315 | 45.5024 | -1.7709 | 273.0144 | 41.8 | 44.8517 | -3.0517 | 0.97174 | 26-03-2026 11:50 | 241.021 | 244.915 | 648.9 | 40.8192 | 43.2899 | -2.4707 | 259.7394 | 39.7 | 42.6709 | -2.9709 | 0.9841 | 26-03-2026 11:50 | 447.1183 | 471.0125 | -23.8942 | 2826.0751 | 435.4 | 464.277 | -28.877 | -11.7183
26-03-2026 11:40 | 1013 | 49.94 | 336.749 | 342.608 | 865.3 | 57.1013 | 60.0557 | -2.9544 | 360.3344 | 56.2 | 59.1969 | -2.9969 | 0.9829 | 26-03-2026 11:40 | 341.062 | 347.031 | 870.5 | 57.8385 | 60.0557 | -2.2172 | 360.3344 | 56.1 | 59.1969 | -3.0969 | 0.9828 | 26-03-2026 11:40 | 333.505 | 342.804 | 856.3 | 57.134 | 60.0557 | -2.9217 | 360.3344 | 54.4 | 59.1969 | -4.7969 | 0.97287 | 26-03-2026 11:40 | 336.859 | 342.742 | 865.5 | 57.1237 | 60.0557 | -2.9321 | 360.3344 | 54.9 | 59.1969 | -4.2969 | 0.98284 | 26-03-2026 11:40 | 251.738 | 255.697 | 642.2 | 42.6162 | 44.4857 | -1.8696 | 266.9144 | 42.7 | 43.8496 | -1.1496 | 0.98452 | 26-03-2026 11:40 | 248.554 | 253.417 | 641.2 | 42.2362 | 44.4857 | -2.2496 | 266.9144 | 41.2 | 43.8496 | -2.6496 | 0.98081 | 26-03-2026 11:40 | 248.975 | 254.099 | 639.5 | 42.3498 | 44.4857 | -2.1359 | 266.9144 | 41.2 | 43.8496 | -2.6496 | 0.97983 | 26-03-2026 11:40 | 250.318 | 257.526 | 643.7 | 42.921 | 44.4857 | -1.5647 | 266.9144 | 41.5 | 43.8496 | -2.3496 | 0.97201 | 26-03-2026 11:40 | 236.752 | 240.504 | 609.2 | 40.084 | 42.3227 | -2.2387 | 253.936 | 39.3 | 41.7175 | -2.4175 | 0.9844 | 26-03-2026 11:40 | 439.4047 | 460.4886 | -21.0839 | 2762.9314 | 427.5 | 453.9036 | -26.4036 | -11.9047
26-03-2026 11:30 | 905 | 49.65 | 315.95 | 321.349 | 809.1 | 53.5582 | 53.7126 | -0.15446 | 322.2757 | 55.9 | 52.9445 | 2.9555 | 0.9832 | 26-03-2026 11:30 | 325.924 | 332.311 | 814.4 | 55.3852 | 53.7126 | 1.6725 | 322.2757 | 55.1 | 52.9445 | 2.1555 | 0.98078 | 26-03-2026 11:30 | 305.644 | 314.704 | 801.9 | 52.4507 | 53.7126 | -1.262 | 322.2757 | 55.2 | 52.9445 | 2.2555 | 0.97121 | 26-03-2026 11:30 | 306.216 | 311.48 | 810.6 | 51.9133 | 53.7126 | -1.7993 | 322.2757 | 55.9 | 52.9445 | 2.9555 | 0.9831 | 26-03-2026 11:30 | 242.097 | 245.984 | 599.5 | 40.9973 | 39.7871 | 1.2102 | 238.7228 | 39.9 | 39.2182 | 0.68183 | 0.9842 | 26-03-2026 11:30 | 229.137 | 232.745 | 600 | 38.7908 | 39.7871 | -0.99629 | 238.7228 | 40.7 | 39.2182 | 1.4818 | 0.9845 | 26-03-2026 11:30 | 226.036 | 230.891 | 598.3 | 38.4818 | 39.7871 | -1.3053 | 238.7228 | 40.6 | 39.2182 | 1.3818 | 0.97897 | 26-03-2026 11:30 | 232.241 | 239.073 | 602.2 | 39.8455 | 39.7871 | 0.058372 | 238.7228 | 41 | 39.2182 | 1.7818 | 0.97142 | 26-03-2026 11:30 | 220.287 | 223.71 | 569.9 | 37.285 | 37.8525 | -0.56752 | 227.1151 | 39.3 | 37.3112 | 1.9888 | 0.9847 | 26-03-2026 11:30 | 408.7078 | 411.8515 | -3.1437 | 2471.1092 | 423.6 | 405.9621 | 17.6379 | 14.8922
26-03-2026 11:20 | 1000 | 49.65 | 337.249 | 342.977 | 753.2 | 57.1628 | 59.351 | -2.1881 | 356.1058 | 48 | 58.5022 | -10.5022 | 0.9833 | 26-03-2026 11:20 | 340.865 | 346.76 | 759.3 | 57.7933 | 59.351 | -1.5576 | 356.1058 | 51 | 58.5022 | -7.5022 | 0.983 | 26-03-2026 11:20 | 334.56 | 343.86 | 746.7 | 57.31 | 59.351 | -2.041 | 356.1058 | 49.5 | 58.5022 | -9.0022 | 0.97295 | 26-03-2026 11:20 | 337.902 | 343.781 | 754.7 | 57.2968 | 59.351 | -2.0541 | 356.1058 | 50.2 | 58.5022 | -8.3022 | 0.9829 | 26-03-2026 11:20 | 251.673 | 255.609 | 559.6 | 42.6015 | 43.9637 | -1.3622 | 263.7821 | 37.6 | 43.335 | -5.735 | 0.9846 | 26-03-2026 11:20 | 249.837 | 254.459 | 559.3 | 42.4098 | 43.9637 | -1.5538 | 263.7821 | 37.9 | 43.335 | -5.435 | 0.98184 | 26-03-2026 11:20 | 249.155 | 254.157 | 557.7 | 42.3595 | 43.9637 | -1.6042 | 263.7821 | 38.1 | 43.335 | -5.235 | 0.98032 | 26-03-2026 11:20 | 251.287 | 258.991 | 561.2 | 43.1652 | 43.9637 | -0.79851 | 263.7821 | 38.5 | 43.335 | -4.835 | 0.97025 | 26-03-2026 11:20 | 237.807 | 241.422 | 530.6 | 40.237 | 41.826 | -1.589 | 250.956 | 35.8 | 41.2279 | -5.4279 | 0.98503 | 26-03-2026 11:20 | 440.336 | 455.0846 | -14.7486 | 2730.5074 | 386.6 | 448.5769 | -61.9769 | -53.736
26-03-2026 11:10 | 842 | 49.36 | 293.063 | 297.737 | 705.2 | 49.6228 | 50.029 | -0.40619 | 300.1741 | 37.7 | 49.3136 | -11.6136 | 0.9843 | 26-03-2026 11:10 | 297.136 | 301.937 | 708.3 | 50.3228 | 50.029 | 0.29381 | 300.1741 | 37.5 | 49.3136 | -11.8136 | 0.9841 | 26-03-2026 11:10 | 286.456 | 294.665 | 697.2 | 49.1108 | 50.029 | -0.91819 | 300.1741 | 36.8 | 49.3136 | -12.5136 | 0.97214 | 26-03-2026 11:10 | 285.817 | 290.435 | 704.5 | 48.4058 | 50.029 | -1.6232 | 300.1741 | 36.5 | 49.3136 | -12.8136 | 0.9841 | 26-03-2026 11:10 | 214.572 | 217.685 | 522 | 36.2808 | 37.0585 | -0.7777 | 222.3512 | 27.2 | 36.5286 | -9.3286 | 0.9857 | 26-03-2026 11:10 | 213.419 | 216.865 | 521.4 | 36.1442 | 37.0585 | -0.91437 | 222.3512 | 26.1 | 36.5286 | -10.4286 | 0.98411 | 26-03-2026 11:10 | 207.906 | 210.901 | 519.6 | 35.1502 | 37.0585 | -1.9084 | 222.3512 | 26 | 36.5286 | -10.5286 | 0.9858 | 26-03-2026 11:10 | 203.22 | 208.505 | 522.7 | 34.7508 | 37.0585 | -2.3077 | 222.3512 | 25.7 | 36.5286 | -10.8286 | 0.97465 | 26-03-2026 11:10 | 195.407 | 198.222 | 494.8 | 33.037 | 35.2566 | -2.2196 | 211.5396 | 24.4 | 34.7524 | -10.3524 | 0.9858 | 26-03-2026 11:10 | 372.8253 | 383.6069 | -10.7815 | 2301.6411 | 277.9 | 378.1213 | -100.2213 | -94.9253
26-03-2026 11:00 | 482 | 49.36 | 177.779 | 180.395 | 667.5 | 30.0658 | 28.6389 | 1.4269 | 171.8337 | 48.9 | 28.2294 | 20.6706 | 0.9855 | 26-03-2026 11:00 | 191 | 196.429 | 670.8 | 32.7382 | 28.6389 | 4.0992 | 171.8337 | 49 | 28.2294 | 20.7706 | 0.97236 | 26-03-2026 11:00 | 162.809 | 166.576 | 660.4 | 27.7627 | 28.6389 | -0.87628 | 171.8337 | 47.9 | 28.2294 | 19.6706 | 0.97739 | 26-03-2026 11:00 | 159.937 | 162.194 | 668 | 27.0323 | 28.6389 | -1.6066 | 171.8337 | 48.2 | 28.2294 | 19.9706 | 0.98608 | 26-03-2026 11:00 | 122.636 | 125.866 | 494.8 | 20.9777 | 21.214 | -0.23637 | 127.2842 | 35.8 | 20.9107 | 14.8893 | 0.97434 | 26-03-2026 11:00 | 117.944 | 120.652 | 495.3 | 20.1087 | 21.214 | -1.1054 | 127.2842 | 35.5 | 20.9107 | 14.5893 | 0.97756 | 26-03-2026 11:00 | 126.684 | 128.747 | 493.6 | 21.4578 | 21.214 | 0.2438 | 127.2842 | 35.8 | 20.9107 | 14.8893 | 0.98398 | 26-03-2026 11:00 | 125.106 | 129.537 | 497 | 21.5895 | 21.214 | 0.37547 | 127.2842 | 35.9 | 20.9107 | 14.9893 | 0.96579 | 26-03-2026 11:00 | 115.296 | 117.059 | 470.4 | 19.5098 | 20.1825 | -0.67269 | 121.0951 | 34 | 19.8939 | 14.1061 | 0.98494 | 26-03-2026 11:00 | 221.2425 | 219.5944 | 1.6481 | 1317.5665 | 371 | 216.4542 | 154.5458 | 149.7575
26-03-2026 10:50 | 948 | 49.65 | 319.644 | 325.04 | 618.6 | 54.1733 | 56.2647 | -2.0914 | 337.5883 | 49.9 | 55.4601 | -5.5601 | 0.9834 | 26-03-2026 10:50 | 323.239 | 328.729 | 621.8 | 54.7882 | 56.2647 | -1.4765 | 337.5883 | 50.1 | 55.4601 | -5.3601 | 0.9833 | 26-03-2026 10:50 | 317.125 | 326.091 | 612.5 | 54.3485 | 56.2647 | -1.9162 | 337.5883 | 49.6 | 55.4601 | -5.8601 | 0.9725 | 26-03-2026 10:50 | 321.108 | 326.628 | 619.8 | 54.438 | 56.2647 | -1.8267 | 337.5883 | 50.6 | 55.4601 | -4.8601 | 0.9831 | 26-03-2026 10:50 | 239.94 | 243.668 | 459 | 40.6113 | 41.6776 | -1.0662 | 250.0654 | 37.7 | 41.0816 | -3.3816 | 0.9847 | 26-03-2026 10:50 | 237.771 | 241.858 | 459.8 | 40.3097 | 41.6776 | -1.3679 | 250.0654 | 37.4 | 41.0816 | -3.6816 | 0.9831 | 26-03-2026 10:50 | 237.72 | 242.264 | 457.8 | 40.3773 | 41.6776 | -1.3002 | 250.0654 | 36.9 | 41.0816 | -4.1816 | 0.98124 | 26-03-2026 10:50 | 239.046 | 246.106 | 461.1 | 41.0177 | 41.6776 | -0.6599 | 250.0654 | 37 | 41.0816 | -4.0816 | 0.97131 | 26-03-2026 10:50 | 226.381 | 229.875 | 436.4 | 38.3125 | 39.651 | -1.3385 | 237.9063 | 35 | 39.084 | -4.084 | 0.9848 | 26-03-2026 10:50 | 418.3765 | 431.4202 | -13.0437 | 2588.521 | 384.2 | 425.2509 | -41.0509 | -34.1765
26-03-2026 10:40 | 615 | 49.65 | 212.28 | 217.095 | 568.7 | 36.1825 | 36.5008 | -0.31834 | 219.0051 | 46.9 | 35.9789 | 10.9211 | 0.97782 | 26-03-2026 10:40 | 189 | 199.509 | 571.7 | 33.2515 | 36.5008 | -3.2493 | 219.0051 | 46.8 | 35.9789 | 10.8211 | 0.94733 | 26-03-2026 10:40 | 224.391 | 230.482 | 562.9 | 38.4137 | 36.5008 | 1.9128 | 219.0051 | 46.3 | 35.9789 | 10.3211 | 0.97357 | 26-03-2026 10:40 | 181.095 | 183.76 | 569.2 | 30.6267 | 36.5008 | -5.8742 | 219.0051 | 46.5 | 35.9789 | 10.5211 | 0.9855 | 26-03-2026 10:40 | 144.018 | 147.641 | 421.3 | 24.6068 | 27.0377 | -2.4308 | 162.226 | 34.5 | 26.651 | 7.849 | 0.97546 | 26-03-2026 10:40 | 132.549 | 134.801 | 422.4 | 22.4668 | 27.0377 | -4.5708 | 162.226 | 34.3 | 26.651 | 7.649 | 0.98329 | 26-03-2026 10:40 | 150.419 | 155.95 | 420.9 | 25.9917 | 27.0377 | -1.046 | 162.226 | 34.2 | 26.651 | 7.549 | 0.96453 | 26-03-2026 10:40 | 145.444 | 150.279 | 424.1 | 25.0465 | 27.0377 | -1.9912 | 162.226 | 34.4 | 26.651 | 7.749 | 0.96783 | 26-03-2026 10:40 | 129.112 | 130.723 | 401.4 | 21.7872 | 25.723 | -3.9358 | 154.3379 | 33.2 | 25.3551 | 7.8449 | 0.98768 | 26-03-2026 10:40 | 258.3733 | 279.877 | -21.5037 | 1679.262 | 357.1 | 275.8748 | 81.2252 | 98.7267
26-03-2026 10:30 | 843 | 49.65 | 288.019 | 292.583 | 521.8 | 48.7638 | 50.0329 | -1.269 | 300.1972 | 48.2 | 49.3174 | -1.1174 | 0.9844 | 26-03-2026 10:30 | 288.433 | 293.093 | 524.9 | 48.8488 | 50.0329 | -1.184 | 300.1972 | 45.9 | 49.3174 | -3.4174 | 0.9841 | 26-03-2026 10:30 | 287.089 | 294.966 | 516.6 | 49.161 | 50.0329 | -0.87186 | 300.1972 | 45 | 49.3174 | -4.3174 | 0.9733 | 26-03-2026 10:30 | 289.361 | 294.066 | 522.7 | 49.011 | 50.0329 | -1.0219 | 300.1972 | 45.5 | 49.3174 | -3.8174 | 0.984 | 26-03-2026 10:30 | 216.227 | 219.408 | 386.8 | 36.568 | 37.0614 | -0.49338 | 222.3683 | 33.9 | 36.5314 | -2.6314 | 0.9855 | 26-03-2026 10:30 | 214.87 | 218.228 | 388.1 | 36.3713 | 37.0614 | -0.69005 | 222.3683 | 33.9 | 36.5314 | -2.6314 | 0.98461 | 26-03-2026 10:30 | 214.567 | 218.403 | 386.7 | 36.4005 | 37.0614 | -0.66088 | 222.3683 | 34.2 | 36.5314 | -2.3314 | 0.98244 | 26-03-2026 10:30 | 216.049 | 222.321 | 389.7 | 37.0535 | 37.0614 | -0.00788 | 222.3683 | 34.6 | 36.5314 | -1.9314 | 0.97179 | 26-03-2026 10:30 | 202.877 | 205.883 | 368.2 | 34.3138 | 35.2593 | -0.94548 | 211.5559 | 32 | 34.7551 | -2.7551 | 0.9854 | 26-03-2026 10:30 | 376.4918 | 383.6363 | -7.1445 | 2301.8177 | 353.2 | 378.1503 | -24.9503 | -23.2918
26-03-2026 10:20 | 722 | 49.65 | 259.289 | 263.318 | 473.6 | 43.8863 | 42.8514 | 1.0349 | 257.1084 | 44.9 | 42.2386 | 2.6614 | 0.9847 | 26-03-2026 10:20 | 276.689 | 276.874 | 479 | 46.1457 | 42.8514 | 3.2943 | 257.1084 | 48.1 | 42.2386 | 5.8614 | 0.99933 | 26-03-2026 10:20 | 243.358 | 249.271 | 471.6 | 41.5452 | 42.8514 | -1.3062 | 257.1084 | 46.6 | 42.2386 | 4.3614 | 0.97628 | 26-03-2026 10:20 | 249.354 | 253.254 | 477.2 | 42.209 | 42.8514 | -0.6424 | 257.1084 | 47.8 | 42.2386 | 5.5614 | 0.9846 | 26-03-2026 10:20 | 185.774 | 188.412 | 352.9 | 31.402 | 31.7418 | -0.33978 | 190.4507 | 35.5 | 31.2879 | 4.2121 | 0.986 | 26-03-2026 10:20 | 183.898 | 187.166 | 354.2 | 31.1943 | 31.7418 | -0.54744 | 190.4507 | 35.3 | 31.2879 | 4.0121 | 0.98254 | 26-03-2026 10:20 | 183.552 | 186.177 | 352.5 | 31.0295 | 31.7418 | -0.71228 | 190.4507 | 34.9 | 31.2879 | 3.6121 | 0.9859 | 26-03-2026 10:20 | 186.552 | 191.525 | 355.1 | 31.9208 | 31.7418 | 0.17906 | 190.4507 | 35.1 | 31.2879 | 3.8121 | 0.97403 | 26-03-2026 10:20 | 177.318 | 179.89 | 336.2 | 29.9817 | 30.1984 | -0.2167 | 181.1902 | 33.2 | 29.7665 | 3.4335 | 0.9857 | 26-03-2026 10:20 | 329.3145 | 328.5711 | 0.74345 | 1971.4263 | 361.4 | 323.8725 | 37.5275 | 32.0855
26-03-2026 10:10 | 818 | 49.65 | 282.823 | 287.247 | 428.7 | 47.8745 | 48.5491 | -0.67459 | 291.2945 | 43.5 | 47.8548 | -4.3548 | 0.9846 | 26-03-2026 10:10 | 288.077 | 292.672 | 430.9 | 48.7787 | 48.5491 | 0.22958 | 291.2945 | 45.2 | 47.8548 | -2.6548 | 0.9843 | 26-03-2026 10:10 | 280.594 | 288.284 | 425 | 48.0473 | 48.5491 | -0.50176 | 291.2945 | 43.2 | 47.8548 | -4.6548 | 0.97332 | 26-03-2026 10:10 | 282.506 | 287.012 | 429.4 | 47.8353 | 48.5491 | -0.71376 | 291.2945 | 43.1 | 47.8548 | -4.7548 | 0.9843 | 26-03-2026 10:10 | 209.966 | 212.99 | 317.4 | 35.4983 | 35.9623 | -0.46395 | 215.7737 | 32.1 | 35.448 | -3.348 | 0.9858 | 26-03-2026 10:10 | 209.448 | 212.844 | 318.9 | 35.474 | 35.9623 | -0.48829 | 215.7737 | 32.4 | 35.448 | -3.048 | 0.98404 | 26-03-2026 10:10 | 209.512 | 213.25 | 317.6 | 35.5417 | 35.9623 | -0.42062 | 215.7737 | 31.9 | 35.448 | -3.548 | 0.98247 | 26-03-2026 10:10 | 211.301 | 217.931 | 320 | 36.3218 | 35.9623 | 0.35955 | 215.7737 | 32.2 | 35.448 | -3.248 | 0.96958 | 26-03-2026 10:10 | 199.549 | 202.423 | 303 | 33.7372 | 34.2137 | -0.4765 | 205.282 | 30.8 | 33.7244 | -2.9244 | 0.9858 | 26-03-2026 10:10 | 369.1088 | 372.2592 | -3.1503 | 2233.555 | 334.4 | 366.9359 | -32.5359 | -34.7088
26-03-2026 10:00 | 768 | 49.65 | 266.736 | 270.825 | 385.2 | 45.1375 | 45.5815 | -0.44404 | 273.4892 | 41.8 | 44.9297 | -3.1297 | 0.9849 | 26-03-2026 10:00 | 267.273 | 271.453 | 385.7 | 45.2422 | 45.5815 | -0.33937 | 273.4892 | 42 | 44.9297 | -2.9297 | 0.9846 | 26-03-2026 10:00 | 264.361 | 271.041 | 381.8 | 45.1735 | 45.5815 | -0.40804 | 273.4892 | 42.5 | 44.9297 | -2.4297 | 0.97535 | 26-03-2026 10:00 | 266.061 | 270.277 | 386.3 | 45.0462 | 45.5815 | -0.53537 | 273.4892 | 43 | 44.9297 | -1.9297 | 0.9844 | 26-03-2026 10:00 | 200.03 | 202.496 | 285.3 | 33.7493 | 33.7641 | -0.014771 | 202.5846 | 32 | 33.2813 | -1.2813 | 0.98782 | 26-03-2026 10:00 | 196.802 | 199.922 | 286.5 | 33.3203 | 33.7641 | -0.44377 | 202.5846 | 31.5 | 33.2813 | -1.7813 | 0.98439 | 26-03-2026 10:00 | 199.68 | 203.234 | 285.7 | 33.8723 | 33.7641 | 0.10823 | 202.5846 | 31.9 | 33.2813 | -1.3813 | 0.98251 | 26-03-2026 10:00 | 201.317 | 207.445 | 287.8 | 34.5742 | 33.7641 | 0.81006 | 202.5846 | 32.1 | 33.2813 | -1.1813 | 0.97046 | 26-03-2026 10:00 | 187.51 | 190.192 | 272.2 | 31.6987 | 32.1224 | -0.4237 | 192.7342 | 30.1 | 31.663 | -1.563 | 0.9859 | 26-03-2026 10:00 | 347.8142 | 349.5049 | -1.6908 | 2097.0297 | 326.9 | 344.507 | -17.607 | -20.9142
Avg. of B56 & B58 | 730 | 50.8 | 253.753 | 259.499 | 343.4 | 43.2498 | 43.1354 | 0.11448 | 258.8121 | 41.3 | 42.5185 | -1.2185 |  | 26-03-2026 09:50 | 257.327 | 261.272 | 343.7 | 43.5453 | 43.1354 | 0.40998 | 258.8121 | 41 | 42.5185 | -1.5185 |  | 26-03-2026 09:50 | 252.893 | 258.886 | 339.3 | 43.1477 | 43.1354 | 0.012317 | 258.8121 | 40.9 | 42.5185 | -1.6185 |  | 26-03-2026 09:50 | 255.7 | 259.647 | 343.3 | 43.2745 | 43.1354 | 0.13915 | 258.8121 | 41.4 | 42.5185 | -1.1185 |  | 26-03-2026 09:50 | 189.744 | 192.399 | 253.3 | 32.0665 | 31.9521 | 0.11439 | 191.7127 | 30.6 | 31.4952 | -0.8952 |  | 26-03-2026 09:50 | 189.522 | 192.14 | 255 | 32.0233 | 31.9521 | 0.071222 | 191.7127 | 30.6 | 31.4952 | -0.8952 |  | 26-03-2026 09:50 | 189.099 | 191.845 | 253.8 | 31.9742 | 31.9521 | 0.022055 | 191.7127 | 30.6 | 31.4952 | -0.8952 |  | 26-03-2026 09:50 | 190.717 | 196.247 | 255.7 | 32.7078 | 31.9521 | 0.75572 | 191.7127 | 30.9 | 31.4952 | -0.5952 |  | 26-03-2026 09:50 | 180.37 | 182.912 | 242.1 | 30.4853 | 30.3985 | 0.086857 | 182.3909 | 29.1 | 29.9638 | -0.86378 |  | Avg. of B56 & B58 | 332.4745 | 330.7483 | 1.7262 | 1984.4899 | 316.4 | 326.0186 | -9.6186 | -16.0745
26-03-2026 09:40 | 692 | 51.95 | 241.469 | 244.997 | 302.1 | 40.8328 | 40.709 | 0.1238 | 244.2542 | 40.7 | 40.1269 | 0.57311 |  | 26-03-2026 09:40 | 242.73 | 247.058 | 302.7 | 41.1763 | 40.709 | 0.4673 | 244.2542 | 39.4 | 40.1269 | -0.72689 |  | 26-03-2026 09:40 | 239.03 | 244.325 | 298.4 | 40.7208 | 40.709 | 0.011804 | 244.2542 | 38.6 | 40.1269 | -1.5269 |  | 26-03-2026 09:40 | 242.242 | 245.856 | 301.9 | 40.976 | 40.709 | 0.26697 | 244.2542 | 39.2 | 40.1269 | -0.92689 |  | 26-03-2026 09:40 | 179.391 | 181.864 | 222.7 | 30.3107 | 30.1548 | 0.15583 | 180.929 | 29 | 29.7236 | -0.72362 |  | 26-03-2026 09:40 | 179.736 | 182.214 | 224.4 | 30.369 | 30.1548 | 0.21416 | 180.929 | 29.1 | 29.7236 | -0.62362 |  | 26-03-2026 09:40 | 179.178 | 181.659 | 223.2 | 30.2765 | 30.1548 | 0.12166 | 180.929 | 28.9 | 29.7236 | -0.82362 |  | 26-03-2026 09:40 | 180.729 | 185.866 | 224.8 | 30.9777 | 30.1548 | 0.82283 | 180.929 | 29.2 | 29.7236 | -0.52362 |  | 26-03-2026 09:40 | 171.37 | 173.75 | 213 | 28.9583 | 28.6886 | 0.26974 | 172.1316 | 27.7 | 28.2783 | -0.57835 |  | 26-03-2026 09:40 | 314.5982 | 312.1441 | 2.4541 | 1872.8643 | 301.8 | 307.6804 | -5.8804 | -12.7982
26-03-2026 09:30 | 647 | 51.95 | 227.071 | 230.319 | 261.4 | 38.3865 | 38.0618 | 0.32473 | 228.3706 | 37.7 | 37.5175 | 0.18252 |  | 26-03-2026 09:30 | 228.584 | 232.133 | 263.3 | 38.6888 | 38.0618 | 0.62707 | 228.3706 | 37.5 | 37.5175 | -0.017483 |  | 26-03-2026 09:30 | 225.243 | 230.375 | 259.8 | 38.3958 | 38.0618 | 0.33407 | 228.3706 | 36.8 | 37.5175 | -0.71748 |  | 26-03-2026 09:30 | 228.153 | 231.486 | 262.7 | 38.581 | 38.0618 | 0.51923 | 228.3706 | 37.3 | 37.5175 | -0.21748 |  | 26-03-2026 09:30 | 168.901 | 171.195 | 193.7 | 28.5325 | 28.1939 | 0.3386 | 169.1634 | 27.6 | 27.7907 | -0.19073 |  | 26-03-2026 09:30 | 169.326 | 171.626 | 195.3 | 28.6043 | 28.1939 | 0.41043 | 169.1634 | 27.7 | 27.7907 | -0.090728 |  | 26-03-2026 09:30 | 168.815 | 171.125 | 194.3 | 28.5208 | 28.1939 | 0.32693 | 169.1634 | 27.6 | 27.7907 | -0.19073 |  | 26-03-2026 09:30 | 169.946 | 174.64 | 195.6 | 29.1067 | 28.1939 | 0.91277 | 169.1634 | 27.8 | 27.7907 | 0.0092721 |  | 26-03-2026 09:30 | 160.509 | 162.673 | 185.3 | 27.1122 | 26.823 | 0.28916 | 160.938 | 26.4 | 26.4394 | -0.039436 |  | 26-03-2026 09:30 | 295.9287 | 291.8457 | 4.083 | 1751.074 | 286.4 | 287.6723 | -1.2723 | -9.5287
26-03-2026 09:20 | 622 | 51.95 | 217.504 | 220.525 | 223.7 | 36.7542 | 36.5911 | 0.1631 | 219.5464 | 32.8 | 36.0678 | -3.2678 |  | 26-03-2026 09:20 | 220.482 | 223.59 | 225.8 | 37.265 | 36.5911 | 0.67394 | 219.5464 | 34 | 36.0678 | -2.0678 |  | 26-03-2026 09:20 | 216.616 | 221.018 | 223 | 36.8363 | 36.5911 | 0.24527 | 219.5464 | 33.4 | 36.0678 | -2.6678 |  | 26-03-2026 09:20 | 219.687 | 222.784 | 225.4 | 37.1307 | 36.5911 | 0.5396 | 219.5464 | 33.9 | 36.0678 | -2.1678 |  | 26-03-2026 09:20 | 162.655 | 164.782 | 166.1 | 27.4637 | 27.1045 | 0.35917 | 162.627 | 25.1 | 26.7169 | -1.6169 |  | 26-03-2026 09:20 | 163.005 | 165.169 | 167.6 | 27.5282 | 27.1045 | 0.42367 | 162.627 | 25.2 | 26.7169 | -1.5169 |  | 26-03-2026 09:20 | 162.686 | 164.829 | 166.7 | 27.4715 | 27.1045 | 0.36701 | 162.627 | 25.1 | 26.7169 | -1.6169 |  | 26-03-2026 09:20 | 163.992 | 168.656 | 167.8 | 28.1093 | 27.1045 | 1.0048 | 162.627 | 25.7 | 26.7169 | -1.0169 |  | 26-03-2026 09:20 | 155.2 | 157.26 | 158.9 | 26.21 | 25.7866 | 0.42343 | 154.7194 | 24.3 | 25.4178 | -1.1178 |  | 26-03-2026 09:20 | 284.7688 | 280.5688 | 4.2 | 1683.4127 | 259.5 | 276.5567 | -17.0567 | -25.2688
26-03-2026 09:10 | 541 | 51.66 | 172.943 | 190.356 | 190.9 | 31.726 | 31.8617 | -0.13566 | 191.1699 | 29.4 | 31.406 | -2.006 |  | 26-03-2026 09:10 | 192.795 | 195.414 | 191.8 | 32.569 | 31.8617 | 0.70734 | 191.1699 | 29.7 | 31.406 | -1.706 |  | 26-03-2026 09:10 | 189.64 | 193.315 | 189.6 | 32.2192 | 31.8617 | 0.35751 | 191.1699 | 29.1 | 31.406 | -2.306 |  | 26-03-2026 09:10 | 193.466 | 196.094 | 191.5 | 32.6823 | 31.8617 | 0.82068 | 191.1699 | 29.5 | 31.406 | -1.906 |  | 26-03-2026 09:10 | 142.614 | 144.434 | 141 | 24.0723 | 23.6012 | 0.47111 | 141.6074 | 21.7 | 23.2637 | -1.5637 |  | 26-03-2026 09:10 | 144.204 | 146.059 | 142.4 | 24.3432 | 23.6012 | 0.74194 | 141.6074 | 22.2 | 23.2637 | -1.0637 |  | 26-03-2026 09:10 | 143.997 | 145.849 | 141.6 | 24.3082 | 23.6012 | 0.70694 | 141.6074 | 22.1 | 23.2637 | -1.1637 |  | 26-03-2026 09:10 | 145.004 | 148.894 | 142.1 | 24.8157 | 23.6012 | 1.2144 | 141.6074 | 21.9 | 23.2637 | -1.3637 |  | 26-03-2026 09:10 | 136.524 | 138.294 | 134.6 | 23.049 | 22.4536 | 0.59535 | 134.7219 | 20.7 | 22.1326 | -1.4326 |  | 26-03-2026 09:10 | 249.7848 | 244.3052 | 5.4796 | 1465.8311 | 226.3 | 240.8116 | -14.5116 | -23.4848
26-03-2026 09:00 | 530 | 51.66 | 188.42 | 190.882 | 161.5 | 31.8137 | 31.2138 | 0.59984 | 187.2829 | 26.3 | 30.7675 | -4.4675 |  | 26-03-2026 09:00 | 0 | 192.396 | 162.1 | 32.066 | 31.2138 | 0.85218 | 187.2829 | 26.8 | 30.7675 | -3.9675 |  | 26-03-2026 09:00 | 186.355 | 189.815 | 160.5 | 31.6358 | 31.2138 | 0.42201 | 187.2829 | 26.8 | 30.7675 | -3.9675 |  | 26-03-2026 09:00 | 189.775 | 192.275 | 162 | 32.0458 | 31.2138 | 0.83201 | 187.2829 | 27.2 | 30.7675 | -3.5675 |  | 26-03-2026 09:00 | 139.57 | 141.322 | 119.3 | 23.5537 | 23.1214 | 0.43232 | 138.7281 | 20 | 22.7907 | -2.7907 |  | 26-03-2026 09:00 | 141.213 | 142.957 | 120.2 | 23.8262 | 23.1214 | 0.70482 | 138.7281 | 19.9 | 22.7907 | -2.8907 |  | 26-03-2026 09:00 | 140.314 | 142.09 | 119.5 | 23.6817 | 23.1214 | 0.56032 | 138.7281 | 19.8 | 22.7907 | -2.9907 |  | 26-03-2026 09:00 | 142.161 | 145.931 | 120.2 | 24.3218 | 23.1214 | 1.2005 | 138.7281 | 19.9 | 22.7907 | -2.8907 |  | 26-03-2026 09:00 | 133.456 | 135.132 | 113.9 | 22.522 | 21.9971 | 0.5249 | 131.9826 | 18.8 | 21.6825 | -2.8825 |  | 26-03-2026 09:00 | 245.4667 | 239.3378 | 6.1289 | 1436.0268 | 205.5 | 235.9153 | -30.4153 | -39.9667
26-03-2026 08:50 | 360 | 51.37 | 129.273 | 130.856 | 135.2 | 21.8093 | 21.2256 | 0.58376 | 127.3535 | 18.5 | 20.9221 | -2.4221 |  | 26-03-2026 08:50 | 129.456 | 131.068 | 135.3 | 21.8447 | 21.2256 | 0.61909 | 127.3535 | 18.8 | 20.9221 | -2.1221 |  | 26-03-2026 08:50 | 127.717 | 129.824 | 133.7 | 21.6373 | 21.2256 | 0.41176 | 127.3535 | 17.9 | 20.9221 | -3.0221 |  | 26-03-2026 08:50 | 129.489 | 131.102 | 134.8 | 21.8503 | 21.2256 | 0.62476 | 127.3535 | 18.4 | 20.9221 | -2.5221 |  | 26-03-2026 08:50 | 94.925 | 96.078 | 99.3 | 16.013 | 15.7226 | 0.29035 | 94.3359 | 13.6 | 15.4978 | -1.8978 |  | 26-03-2026 08:50 | 95.693 | 96.836 | 100.3 | 16.1393 | 15.7226 | 0.41668 | 94.3359 | 13.6 | 15.4978 | -1.8978 |  | 26-03-2026 08:50 | 95.156 | 96.283 | 99.7 | 16.0472 | 15.7226 | 0.32452 | 94.3359 | 13.6 | 15.4978 | -1.8978 |  | 26-03-2026 08:50 | 95.288 | 98.164 | 100.3 | 16.3607 | 15.7226 | 0.63802 | 94.3359 | 13.6 | 15.4978 | -1.8978 |  | 26-03-2026 08:50 | 91.036 | 92.151 | 95.1 | 15.3585 | 14.9582 | 0.40035 | 89.7489 | 13 | 14.7443 | -1.7443 |  | 26-03-2026 08:50 | 167.0603 | 162.7511 | 4.3093 | 976.5064 | 141 | 160.4237 | -19.4237 | -26.0603
26-03-2026 08:40 | 283 | 46.78 | 101.111 | 102.349 | 116.7 | 17.0582 | 16.981 | 0.077194 | 101.8858 | 18.3 | 16.7381 | 1.5619 |  | 26-03-2026 08:40 | 104.297 | 102.911 | 116.5 | 17.1518 | 16.981 | 0.17086 | 101.8858 | 18.5 | 16.7381 | 1.7619 |  | 26-03-2026 08:40 | 99.756 | 101.189 | 115.8 | 16.8648 | 16.981 | -0.11614 | 101.8858 | 18.1 | 16.7381 | 1.3619 |  | 26-03-2026 08:40 | 101.566 | 102.853 | 116.4 | 17.1422 | 16.981 | 0.16119 | 101.8858 | 18.1 | 16.7381 | 1.3619 |  | 26-03-2026 08:40 | 74.517 | 75.498 | 85.7 | 12.583 | 12.5785 | 0.0045017 | 75.471 | 13.3 | 12.3986 | 0.90137 |  | 26-03-2026 08:40 | 75.269 | 76.245 | 86.7 | 12.7075 | 12.5785 | 0.129 | 75.471 | 13.6 | 12.3986 | 1.2014 |  | 26-03-2026 08:40 | 74.6 | 75.59 | 86.1 | 12.5983 | 12.5785 | 0.019835 | 75.471 | 13.5 | 12.3986 | 1.1014 |  | 26-03-2026 08:40 | 74.57 | 76.359 | 86.7 | 12.7265 | 12.5785 | 0.148 | 75.471 | 13.6 | 12.3986 | 1.2014 |  | 26-03-2026 08:40 | 71.133 | 72.092 | 82.1 | 12.0153 | 11.9669 | 0.04845 | 71.8013 | 12.9 | 11.7958 | 1.1042 |  | 26-03-2026 08:40 | 130.8477 | 130.2048 | 0.6429 | 781.2286 | 139.9 | 128.3428 | 11.5572 | 9.0523
26-03-2026 08:30 | 286 | 43.62 | 102.615 | 103.726 | 98.4 | 17.2877 | 17.3664 | -0.078779 | 104.1987 | 18.5 | 17.1181 | 1.3819 |  | 26-03-2026 08:30 | 99.577 | 100.817 | 98 | 16.8028 | 17.3664 | -0.56361 | 104.1987 | 18.9 | 17.1181 | 1.7819 |  | 26-03-2026 08:30 | 101.567 | 103.056 | 97.7 | 17.176 | 17.3664 | -0.19045 | 104.1987 | 18.2 | 17.1181 | 1.0819 |  | 26-03-2026 08:30 | 102.626 | 103.894 | 98.3 | 17.3157 | 17.3664 | -0.050779 | 104.1987 | 18.5 | 17.1181 | 1.3819 |  | 26-03-2026 08:30 | 75.77 | 76.768 | 72.4 | 12.7947 | 12.864 | -0.069367 | 77.1842 | 13.6 | 12.6801 | 0.91992 |  | 26-03-2026 08:30 | 75.545 | 76.38 | 73.1 | 12.73 | 12.864 | -0.13403 | 77.1842 | 13.6 | 12.6801 | 0.91992 |  | 26-03-2026 08:30 | 75.434 | 76.412 | 72.6 | 12.7353 | 12.864 | -0.1287 | 77.1842 | 13.5 | 12.6801 | 0.81992 |  | 26-03-2026 08:30 | 75.268 | 77.408 | 73.1 | 12.9013 | 12.864 | 0.037299 | 77.1842 | 13.6 | 12.6801 | 0.91992 |  | 26-03-2026 08:30 | 72.125 | 72.964 | 69.2 | 12.1607 | 12.2385 | -0.077868 | 73.4312 | 12.9 | 12.0635 | 0.83648 |  | 26-03-2026 08:30 | 131.9042 | 133.1605 | -1.2563 | 798.9627 | 141.3 | 131.2563 | 10.0437 | 9.3958
26-03-2026 08:20 | 310 | 43.05 | 110.788 | 112.1 | 79.9 | 18.6833 | 18.8639 | -0.18061 | 113.1836 | 16.7 | 18.5942 | -1.8942 |  | 26-03-2026 08:20 | 95.455 | 101.999 | 79.1 | 16.9998 | 18.8639 | -1.8641 | 113.1836 | 16 | 18.5942 | -2.5942 |  | 26-03-2026 08:20 | 110.009 | 111.624 | 79.5 | 18.604 | 18.8639 | -0.25994 | 113.1836 | 16.3 | 18.5942 | -2.2942 |  | 26-03-2026 08:20 | 110.926 | 112.014 | 79.8 | 18.669 | 18.8639 | -0.19494 | 113.1836 | 16.5 | 18.5942 | -2.0942 |  | 26-03-2026 08:20 | 82.085 | 83.116 | 58.8 | 13.8527 | 13.9733 | -0.12062 | 83.8397 | 12.1 | 13.7735 | -1.6735 |  | 26-03-2026 08:20 | 82.66 | 83.681 | 59.5 | 13.9468 | 13.9733 | -0.026457 | 83.8397 | 12.2 | 13.7735 | -1.5735 |  | 26-03-2026 08:20 | 83.071 | 84.088 | 59.1 | 14.0147 | 13.9733 | 0.041377 | 83.8397 | 12.3 | 13.7735 | -1.4735 |  | 26-03-2026 08:20 | 81.06 | 83.531 | 59.5 | 13.9218 | 13.9733 | -0.051457 | 83.8397 | 12.2 | 13.7735 | -1.5735 |  | 26-03-2026 08:20 | 77.624 | 78.591 | 56.3 | 13.0985 | 13.2939 | -0.19535 | 79.7631 | 11.6 | 13.1038 | -1.5038 |  | 26-03-2026 08:20 | 141.7907 | 144.6428 | -2.8521 | 867.8567 | 125.9 | 142.5744 | -16.6744 | -15.8907
26-03-2026 08:10 | 274 | 36.16 | 97.038 | 98.086 | 63.2 | 16.3477 | 17.1025 | -0.75481 | 102.6149 | 16.2 | 16.8579 | -0.65792 |  | 26-03-2026 08:10 | 97.156 | 98.326 | 63.1 | 16.3877 | 17.1025 | -0.71481 | 102.6149 | 16 | 16.8579 | -0.85792 |  | 26-03-2026 08:10 | 96.917 | 98.293 | 63.2 | 16.3822 | 17.1025 | -0.72031 | 102.6149 | 16 | 16.8579 | -0.85792 |  | 26-03-2026 08:10 | 98.055 | 99.226 | 63.3 | 16.5377 | 17.1025 | -0.56481 | 102.6149 | 16.2 | 16.8579 | -0.65792 |  | 26-03-2026 08:10 | 72.315 | 73.23 | 46.7 | 12.205 | 12.6685 | -0.4635 | 76.011 | 11.9 | 12.4873 | -0.58734 |  | 26-03-2026 08:10 | 72.961 | 73.77 | 47.3 | 12.295 | 12.6685 | -0.3735 | 76.011 | 12 | 12.4873 | -0.48734 |  | 26-03-2026 08:10 | 71.707 | 72.622 | 46.8 | 12.1037 | 12.6685 | -0.56484 | 76.011 | 11.8 | 12.4873 | -0.68734 |  | 26-03-2026 08:10 | 72.697 | 74.678 | 47.3 | 12.4463 | 12.6685 | -0.22217 | 76.011 | 12.1 | 12.4873 | -0.38734 |  | 26-03-2026 08:10 | 68.948 | 69.765 | 44.7 | 11.6275 | 12.0525 | -0.42501 | 72.3151 | 11.4 | 11.8802 | -0.48016 |  | 26-03-2026 08:10 | 126.3327 | 131.1365 | -4.8038 | 786.8187 | 123.6 | 129.2612 | -5.6612 | -2.7327
26-03-2026 08:00 | 228 | 31 | 80.08 | 81.044 | 47 | 13.5073 | 14.4987 | -0.99139 | 86.9923 | 12 | 14.2914 | -2.2914 |  | 26-03-2026 08:00 | 80.866 | 81.865 | 47.1 | 13.6442 | 14.4987 | -0.85456 | 86.9923 | 12.3 | 14.2914 | -1.9914 |  | 26-03-2026 08:00 | 79.87 | 80.848 | 47.2 | 13.4747 | 14.4987 | -1.0241 | 86.9923 | 11.9 | 14.2914 | -2.3914 |  | 26-03-2026 08:00 | 81.049 | 82.042 | 47.1 | 13.6737 | 14.4987 | -0.82506 | 86.9923 | 12 | 14.2914 | -2.2914 |  | 26-03-2026 08:00 | 59.27 | 60.075 | 34.8 | 10.0125 | 10.7398 | -0.7273 | 64.4388 | 8.9 | 10.5862 | -1.6862 |  | 26-03-2026 08:00 | 59.689 | 60.598 | 35.3 | 10.0997 | 10.7398 | -0.64013 | 64.4388 | 9 | 10.5862 | -1.5862 |  | 26-03-2026 08:00 | 59.565 | 60.368 | 35 | 10.0613 | 10.7398 | -0.67846 | 64.4388 | 8.9 | 10.5862 | -1.6862 |  | 26-03-2026 08:00 | 60.003 | 61.747 | 35.2 | 10.2912 | 10.7398 | -0.44863 | 64.4388 | 8.8 | 10.5862 | -1.7862 |  | 26-03-2026 08:00 | 56.907 | 57.703 | 33.3 | 9.6172 | 10.2176 | -0.60042 | 61.3055 | 8.4 | 10.0715 | -1.6715 |  | 26-03-2026 08:00 | 104.3817 | 111.1717 | -6.79 | 667.03 | 92.2 | 109.5819 | -17.3819 | -12.1817
26-03-2026 07:50 | 152 | 28.99 | 54.697 | 55.479 | 35 | 9.2465 | 9.7353 | -0.48877 | 58.4116 | 10.2 | 9.5961 | 0.60394 |  | 26-03-2026 07:50 | 54.881 | 55.694 | 34.8 | 9.2823 | 9.7353 | -0.45294 | 58.4116 | 10.3 | 9.5961 | 0.70394 |  | 26-03-2026 07:50 | 53.903 | 54.696 | 35.3 | 9.116 | 9.7353 | -0.61927 | 58.4116 | 10.2 | 9.5961 | 0.60394 |  | 26-03-2026 07:50 | 54.332 | 55.131 | 35.1 | 9.1885 | 9.7353 | -0.54677 | 58.4116 | 10.3 | 9.5961 | 0.70394 |  | 26-03-2026 07:50 | 39.992 | 40.684 | 25.9 | 6.7807 | 7.2113 | -0.43065 | 43.2679 | 7.4 | 7.1082 | 0.29181 |  | 26-03-2026 07:50 | 40.228 | 40.886 | 26.3 | 6.8143 | 7.2113 | -0.39698 | 43.2679 | 7.9 | 7.1082 | 0.79181 |  | 26-03-2026 07:50 | 39.938 | 40.6 | 26.1 | 6.7667 | 7.2113 | -0.44465 | 43.2679 | 7.6 | 7.1082 | 0.49181 |  | 26-03-2026 07:50 | 40.116 | 41.117 | 26.4 | 6.8528 | 7.2113 | -0.35848 | 43.2679 | 7.7 | 7.1082 | 0.59181 |  | 26-03-2026 07:50 | 38.02 | 38.662 | 24.9 | 6.4437 | 6.8607 | -0.41701 | 41.164 | 7.2 | 6.7626 | 0.43744 |  | 26-03-2026 07:50 | 70.4915 | 74.647 | -4.1555 | 447.8822 | 78.8 | 73.5796 | 5.2204 | 8.3085
26-03-2026 07:40 | 189 | 26.4 | 65.537 | 66.333 | 24.8 | 11.0555 | 12.2163 | -1.1608 | 73.298 | 10.2 | 12.0416 | -1.8416 |  | 26-03-2026 07:40 | 66.032 | 66.854 | 24.5 | 11.1423 | 12.2163 | -1.074 | 73.298 | 9.9 | 12.0416 | -2.1416 |  | 26-03-2026 07:40 | 64.357 | 65.158 | 25.1 | 10.8597 | 12.2163 | -1.3567 | 73.298 | 9.9 | 12.0416 | -2.1416 |  | 26-03-2026 07:40 | 65.282 | 66.088 | 24.8 | 11.0147 | 12.2163 | -1.2017 | 73.298 | 10.1 | 12.0416 | -1.9416 |  | 26-03-2026 07:40 | 47.496 | 48.19 | 18.5 | 8.0317 | 9.0491 | -1.0175 | 54.2948 | 7.5 | 8.9197 | -1.4197 |  | 26-03-2026 07:40 | 49.128 | 49.821 | 18.4 | 8.3035 | 9.0491 | -0.74563 | 54.2948 | 7.2 | 8.9197 | -1.7197 |  | 26-03-2026 07:40 | 48.131 | 48.829 | 18.5 | 8.1382 | 9.0491 | -0.91097 | 54.2948 | 7.4 | 8.9197 | -1.5197 |  | 26-03-2026 07:40 | 48.56 | 49.877 | 18.7 | 8.3128 | 9.0491 | -0.7363 | 54.2948 | 7.5 | 8.9197 | -1.4197 |  | 26-03-2026 07:40 | 46.164 | 46.848 | 17.7 | 7.808 | 8.6091 | -0.80113 | 51.6548 | 7.1 | 8.486 | -1.386 |  | 26-03-2026 07:40 | 84.6663 | 93.671 | -9.0047 | 562.026 | 76.8 | 92.3315 | -15.5315 | -7.8663
26-03-2026 07:30 | 131 | 23.82 | 45.766 | 46.444 | 14.6 | 7.7407 | 8.5442 | -0.80357 | 51.2654 | 6.5 | 8.4221 | -1.9221 |  | 26-03-2026 07:30 | 44.764 | 46.394 | 14.6 | 7.7323 | 8.5442 | -0.81191 | 51.2654 | 6.5 | 8.4221 | -1.9221 |  | 26-03-2026 07:30 | 45.837 | 46.53 | 15.2 | 7.755 | 8.5442 | -0.78924 | 51.2654 | 6.5 | 8.4221 | -1.9221 |  | 26-03-2026 07:30 | 46.272 | 46.977 | 14.7 | 7.8295 | 8.5442 | -0.71474 | 51.2654 | 6.6 | 8.4221 | -1.8221 |  | 26-03-2026 07:30 | 33.628 | 34.162 | 11 | 5.6937 | 6.3291 | -0.6354 | 37.9744 | 4.7 | 6.2386 | -1.5386 |  | 26-03-2026 07:30 | 33.976 | 34.535 | 11.2 | 5.7558 | 6.3291 | -0.57323 | 37.9744 | 4.8 | 6.2386 | -1.4386 |  | 26-03-2026 07:30 | 33.787 | 34.354 | 11.1 | 5.7257 | 6.3291 | -0.6034 | 37.9744 | 4.7 | 6.2386 | -1.5386 |  | 26-03-2026 07:30 | 34.077 | 35.226 | 11.2 | 5.871 | 6.3291 | -0.45807 | 37.9744 | 4.8 | 6.2386 | -1.4386 |  | 26-03-2026 07:30 | 32.284 | 32.832 | 10.6 | 5.472 | 6.0213 | -0.54932 | 36.1279 | 4.7 | 5.9352 | -1.2352 |  | 26-03-2026 07:30 | 59.5757 | 65.5146 | -5.9389 | 393.0874 | 49.8 | 64.5777 | -14.7777 | -9.7757
26-03-2026 07:20 | 94 | 20.95 | 32.515 | 33.057 | 8.1 | 5.5095 | 6.1923 | -0.68281 | 37.1539 | 3.9 | 6.1038 | -2.2038 |  | 26-03-2026 07:20 | 32.239 | 32.809 | 8.1 | 5.4682 | 6.1923 | -0.72415 | 37.1539 | 3.9 | 6.1038 | -2.2038 |  | 26-03-2026 07:20 | 32.125 | 32.674 | 8.7 | 5.4457 | 6.1923 | -0.74665 | 37.1539 | 3.9 | 6.1038 | -2.2038 |  | 26-03-2026 07:20 | 32.443 | 32.997 | 8.1 | 5.4995 | 6.1923 | -0.69281 | 37.1539 | 3.9 | 6.1038 | -2.2038 |  | 26-03-2026 07:20 | 23.825 | 24.321 | 6.3 | 4.0535 | 4.5869 | -0.5334 | 27.5214 | 2.8 | 4.5213 | -1.7213 |  | 26-03-2026 07:20 | 24.148 | 24.638 | 6.4 | 4.1063 | 4.5869 | -0.48057 | 27.5214 | 2.9 | 4.5213 | -1.6213 |  | 26-03-2026 07:20 | 23.976 | 24.473 | 6.4 | 4.0788 | 4.5869 | -0.50807 | 27.5214 | 2.9 | 4.5213 | -1.6213 |  | 26-03-2026 07:20 | 24.081 | 24.842 | 6.4 | 4.1403 | 4.5869 | -0.44657 | 27.5214 | 2.9 | 4.5213 | -1.6213 |  | 26-03-2026 07:20 | 22.544 | 23.028 | 5.9 | 3.838 | 4.3639 | -0.52587 | 26.1832 | 2.6 | 4.3015 | -1.7015 |  | 26-03-2026 07:20 | 42.1398 | 47.4807 | -5.3409 | 284.8844 | 29.7 | 46.8018 | -17.1018 | -12.4398
26-03-2026 07:10 | 44 | 19.23 | 15.601 | 16.001 | 4.2 | 2.6668 | 2.9157 | -0.2489 | 17.4944 | 2.2 | 2.874 | -0.67404 |  | 26-03-2026 07:10 | 15.511 | 16.128 | 4.2 | 2.688 | 2.9157 | -0.22774 | 17.4944 | 2.2 | 2.874 | -0.67404 |  | 26-03-2026 07:10 | 15.499 | 15.903 | 4.8 | 2.6505 | 2.9157 | -0.26524 | 17.4944 | 2.2 | 2.874 | -0.67404 |  | 26-03-2026 07:10 | 15.616 | 16.318 | 4.2 | 2.7197 | 2.9157 | -0.19607 | 17.4944 | 2.2 | 2.874 | -0.67404 |  | 26-03-2026 07:10 | 11.347 | 12.058 | 3.5 | 2.0097 | 2.1598 | -0.15014 | 12.9588 | 1.6 | 2.1289 | -0.52892 |  | 26-03-2026 07:10 | 11.276 | 11.648 | 3.5 | 1.9413 | 2.1598 | -0.21847 | 12.9588 | 1.6 | 2.1289 | -0.52892 |  | 26-03-2026 07:10 | 11.399 | 11.787 | 3.5 | 1.9645 | 2.1598 | -0.1953 | 12.9588 | 1.6 | 2.1289 | -0.52892 |  | 26-03-2026 07:10 | 11.397 | 12.064 | 3.5 | 2.0107 | 2.1598 | -0.14914 | 12.9588 | 1.6 | 2.1289 | -0.52892 |  | 26-03-2026 07:10 | 10.742 | 11.109 | 3.3 | 1.8515 | 2.0548 | -0.20329 | 12.3287 | 1.6 | 2.0254 | -0.4254 |  | 26-03-2026 07:10 | 20.5027 | 22.3569 | -1.8543 | 134.1417 | 16.8 | 22.0372 | -5.2372 | -3.7027
26-03-2026 07:00 | 34 | 18.66 | 12.097 | 12.484 | 2 | 2.0807 | 2.2575 | -0.17681 | 13.5448 | 2 | 2.2252 | -0.22519 |  | 26-03-2026 07:00 | 12.111 | 12.742 | 2 | 2.1237 | 2.2575 | -0.13381 | 13.5448 | 2 | 2.2252 | -0.22519 |  | 26-03-2026 07:00 | 11.965 | 12.358 | 2.6 | 2.0597 | 2.2575 | -0.19781 | 13.5448 | 2.6 | 2.2252 | 0.37481 |  | 26-03-2026 07:00 | 12.134 | 12.997 | 2 | 2.1662 | 2.2575 | -0.091308 | 13.5448 | 2 | 2.2252 | -0.22519 |  | 26-03-2026 07:00 | 8.709 | 9.286 | 1.9 | 1.5477 | 1.6722 | -0.12454 | 10.0332 | 1.9 | 1.6483 | 0.25171 |  | 26-03-2026 07:00 | 8.825 | 9.155 | 1.9 | 1.5258 | 1.6722 | -0.14637 | 10.0332 | 1.9 | 1.6483 | 0.25171 |  | 26-03-2026 07:00 | 8.778 | 9.112 | 1.9 | 1.5187 | 1.6722 | -0.15354 | 10.0332 | 1.9 | 1.6483 | 0.25171 |  | 26-03-2026 07:00 | 8.84 | 9.254 | 1.9 | 1.5423 | 1.6722 | -0.12987 | 10.0332 | 1.9 | 1.6483 | 0.25171 |  | 26-03-2026 07:00 | 8.316 | 8.644 | 1.7 | 1.4407 | 1.5909 | -0.15023 | 9.5454 | 1.7 | 1.5681 | 0.13186 |  | 26-03-2026 07:00 | 16.0053 | 17.3096 | -1.3043 | 103.8576 | 17.9 | 17.0621 | 0.83792 | 1.8947
[110 empty] | Total: - | 17966.3218 | 18540.9271 | -574.6053 |  | 17939.4 | 18275.7919 | -336.3919 | -26.9218
Sum:- | 40679 |  | 13748.897 |  | 91346.4 |  |  |  |  | 2331.5 | 2383.482 | -51.982 | 0.98996 |  | 13709.687 |  | 92049 |  |  |  |  | 2351.5 | 2383.482 | -31.982 | 0.99147 |  | 13600.628 |  | 90731 |  |  |  |  | 2317.8 | 2383.482 | -65.682 | 0.96965 |  | 13713.748 |  | 91354.1 |  |  |  |  | 2331.7 | 2383.482 | -51.782 | 0.98374 |  | 10352.757 |  | 68440.4 |  |  |  |  | 1751 | 1765.5422 | -14.5422 | 0.97632 |  | 10201.233 |  | 67907.8 |  |  |  |  | 1732.8 | 1765.5422 | -32.7422 | 0.97848 |  | 10247.756 |  | 67896.6 |  |  |  |  | 1734 | 1765.5422 | -31.5422 | 0.97967 |  | 10249.218 |  | 68281.6 |  |  |  |  | 1743.2 | 1765.5422 | -22.3422 | 0.96906 |  | 9653.596 |  | 64511.1 |  |  |  |  | 1645.9 | 1679.6948 | -33.7948 | 0.98183 | [8 empty] | -0.1498%

## 27 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
27-03-2026 19:00 | 0 | 42.19 | 0 | 0 | 2397.7 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27-03-2026 19:00 | 0 | 0 | 2396.5 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 27-03-2026 19:00 | 0 | 0 | 1786.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27-03-2026 19:00 | 0 | 0 | 1768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27-03-2026 19:00 | 0 | 0 | 1766.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27-03-2026 19:00 | 0 | 0 | 1776 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 27-03-2026 19:00 | 0 | 0 | 1679.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 27-03-2026 19:00 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.3 | 0.3 | 1 | 98.33%
27-03-2026 18:50 | 1 | 43.34 | 1.398 | 1.47 | 2397.6 | 0.245 | 0.060785 | 0.18421 | 0.36471 | 0.5 | 0.059916 | 0.44008 |  | 27-03-2026 18:50 | 1.686 | 2.105 | 2424.1 | 0.35083 | 0.060785 | 0.29005 | 0.36471 | 0.6 | 0.059916 | 0.54008 |  | 27-03-2026 18:50 | 1.383 | 1.472 | 2378.6 | 0.24533 | 0.060785 | 0.18455 | 0.36471 | 0.6 | 0.059916 | 0.54008 |  | 27-03-2026 18:50 | 1.42 | 1.883 | 2396.4 | 0.31383 | 0.060785 | 0.25305 | 0.36471 | 0.6 | 0.059916 | 0.54008 |  | 27-03-2026 18:50 | 0.878 | 1.081 | 1786.8 | 0.18017 | 0.045026 | 0.13514 | 0.27016 | 0.4 | 0.044382 | 0.35562 |  | 27-03-2026 18:50 | 0.907 | 0.954 | 1768 | 0.159 | 0.045026 | 0.11397 | 0.27016 | 0.4 | 0.044382 | 0.35562 |  | 27-03-2026 18:50 | 0.843 | 0.886 | 1766.5 | 0.14767 | 0.045026 | 0.10264 | 0.27016 | 0.4 | 0.044382 | 0.35562 |  | 27-03-2026 18:50 | 0.97 | 1.256 | 1775.9 | 0.20933 | 0.045026 | 0.16431 | 0.27016 | 0.3 | 0.044382 | 0.25562 |  | 27-03-2026 18:50 | 0.773 | 0.813 | 1679.8 | 0.1355 | 0.042837 | 0.092663 | 0.25702 | 0.4 | 0.042224 | 0.35778 |  | 27-03-2026 18:50 | 1.9867 | 0.46608 | 1.5206 | 2.7965 | 4.2 | 0.45942 | 3.7406 | 2.2133 | 2 | 98.36%
27-03-2026 18:40 | 13 | 44.2 | 5.502 | 5.767 | 2397.1 | 0.96117 | 0.78767 | 0.1735 | 4.726 | 1.3 | 0.77641 | 0.52359 |  | 27-03-2026 18:40 | 5.917 | 6.066 | 2423.5 | 1.011 | 0.78767 | 0.22333 | 4.726 | 1.3 | 0.77641 | 0.52359 |  | 27-03-2026 18:40 | 5.514 | 5.779 | 2378 | 0.96317 | 0.78767 | 0.1755 | 4.726 | 1.2 | 0.77641 | 0.42359 |  | 27-03-2026 18:40 | 5.591 | 6.01 | 2395.8 | 1.0017 | 0.78767 | 0.214 | 4.726 | 1.2 | 0.77641 | 0.42359 |  | 27-03-2026 18:40 | 3.959 | 4.158 | 1786.4 | 0.693 | 0.58346 | 0.10954 | 3.5008 | 0.9 | 0.57512 | 0.32488 |  | 27-03-2026 18:40 | 3.877 | 4.075 | 1767.6 | 0.67917 | 0.58346 | 0.095708 | 3.5008 | 0.8 | 0.57512 | 0.22488 |  | 27-03-2026 18:40 | 3.874 | 4.072 | 1766.1 | 0.67867 | 0.58346 | 0.095208 | 3.5008 | 0.9 | 0.57512 | 0.32488 |  | 27-03-2026 18:40 | 3.912 | 4.226 | 1775.6 | 0.70433 | 0.58346 | 0.12087 | 3.5008 | 0.9 | 0.57512 | 0.32488 |  | 27-03-2026 18:40 | 3.619 | 3.805 | 1679.4 | 0.63417 | 0.55509 | 0.079078 | 3.3305 | 0.8 | 0.54715 | 0.25285 |  | 27-03-2026 18:40 | 7.3263 | 6.0396 | 1.2867 | 36.2376 | 9.3 | 5.9532 | 3.3468 | 1.9737 | 3 | 97.35%
27-03-2026 18:30 | 23 | 45.35 | 9.233 | 9.603 | 2395.8 | 1.6005 | 1.3876 | 0.21294 | 8.3253 | 1.9 | 1.3677 | 0.53229 |  | 27-03-2026 18:30 | 9.612 | 10.136 | 2422.2 | 1.6893 | 1.3876 | 0.30178 | 8.3253 | 2 | 1.3677 | 0.63229 |  | 27-03-2026 18:30 | 9.319 | 9.69 | 2376.8 | 1.615 | 1.3876 | 0.22744 | 8.3253 | 1.9 | 1.3677 | 0.53229 |  | 27-03-2026 18:30 | 9.371 | 9.744 | 2394.6 | 1.624 | 1.3876 | 0.23644 | 8.3253 | 2 | 1.3677 | 0.63229 |  | 27-03-2026 18:30 | 6.853 | 7.159 | 1785.5 | 1.1932 | 1.0278 | 0.16535 | 6.1669 | 1.4 | 1.0131 | 0.38688 |  | 27-03-2026 18:30 | 6.597 | 6.888 | 1766.8 | 1.148 | 1.0278 | 0.12018 | 6.1669 | 1.4 | 1.0131 | 0.38688 |  | 27-03-2026 18:30 | 6.441 | 6.734 | 1765.2 | 1.1223 | 1.0278 | 0.094514 | 6.1669 | 1.4 | 1.0131 | 0.38688 |  | 27-03-2026 18:30 | 6.312 | 6.685 | 1774.7 | 1.1142 | 1.0278 | 0.086347 | 6.1669 | 1.4 | 1.0131 | 0.38688 |  | 27-03-2026 18:30 | 5.985 | 6.262 | 1678.6 | 1.0437 | 0.97784 | 0.065824 | 5.8671 | 1.3 | 0.96386 | 0.33614 |  | 27-03-2026 18:30 | 12.1502 | 10.6393 | 1.5108 | 63.8361 | 14.7 | 10.4872 | 4.2128 | 2.5498 | 4 | 98.32%
27-03-2026 18:20 | 39 | 47.07 | 16.2 | 16.636 | 2393.9 | 2.7727 | 2.3376 | 0.4351 | 14.0254 | 3.6 | 2.3041 | 1.2959 |  | 27-03-2026 18:20 | 16.871 | 17.094 | 2420.2 | 2.849 | 2.3376 | 0.51144 | 14.0254 | 3.6 | 2.3041 | 1.2959 |  | 27-03-2026 18:20 | 16.406 | 16.846 | 2374.9 | 2.8077 | 2.3376 | 0.4701 | 14.0254 | 3.6 | 2.3041 | 1.2959 |  | 27-03-2026 18:20 | 16.608 | 16.971 | 2392.6 | 2.8285 | 2.3376 | 0.49094 | 14.0254 | 3.5 | 2.3041 | 1.1959 |  | 27-03-2026 18:20 | 12.148 | 12.564 | 1784.1 | 2.094 | 1.7315 | 0.36247 | 10.3892 | 2.7 | 1.7068 | 0.99323 |  | 27-03-2026 18:20 | 11.601 | 12.006 | 1765.4 | 2.001 | 1.7315 | 0.26947 | 10.3892 | 2.5 | 1.7068 | 0.79323 |  | 27-03-2026 18:20 | 11.436 | 11.866 | 1763.8 | 1.9777 | 1.7315 | 0.24614 | 10.3892 | 2.4 | 1.7068 | 0.69323 |  | 27-03-2026 18:20 | 10.166 | 10.704 | 1773.3 | 1.784 | 1.7315 | 0.052472 | 10.3892 | 2 | 1.7068 | 0.29323 |  | 27-03-2026 18:20 | 10.055 | 10.441 | 1677.3 | 1.7402 | 1.6473 | 0.092832 | 9.884 | 2.1 | 1.6238 | 0.47622 |  | 27-03-2026 18:20 | 20.8547 | 17.9237 | 2.931 | 107.5422 | 26 | 17.6674 | 8.3326 | 5.1453 | 5 | 98.47%
27-03-2026 18:10 | 56 | 49.36 | 26.065 | 26.616 | 2390.3 | 4.436 | 3.3273 | 1.1087 | 19.9641 | 4.7 | 3.2798 | 1.4202 |  | 27-03-2026 18:10 | 26.566 | 27.141 | 2416.6 | 4.5235 | 3.3273 | 1.1962 | 19.9641 | 5 | 3.2798 | 1.7202 |  | 27-03-2026 18:10 | 26.093 | 26.645 | 2371.3 | 4.4408 | 3.3273 | 1.1135 | 19.9641 | 4.8 | 3.2798 | 1.5202 |  | 27-03-2026 18:10 | 26.032 | 26.593 | 2389.1 | 4.4322 | 3.3273 | 1.1048 | 19.9641 | 4.8 | 3.2798 | 1.5202 |  | 27-03-2026 18:10 | 19.499 | 19.978 | 1781.4 | 3.3297 | 2.4647 | 0.86497 | 14.7882 | 3.6 | 2.4295 | 1.1705 |  | 27-03-2026 18:10 | 18.581 | 19.046 | 1762.9 | 3.1743 | 2.4647 | 0.70963 | 14.7882 | 3.5 | 2.4295 | 1.0705 |  | 27-03-2026 18:10 | 18.271 | 18.734 | 1761.4 | 3.1223 | 2.4647 | 0.65763 | 14.7882 | 3.5 | 2.4295 | 1.0705 |  | 27-03-2026 18:10 | 15.042 | 15.423 | 1771.3 | 2.5705 | 2.4647 | 0.1058 | 14.7882 | 3 | 2.4295 | 0.57054 |  | 27-03-2026 18:10 | 16.785 | 17.221 | 1675.2 | 2.8702 | 2.3449 | 0.52531 | 14.0691 | 3.3 | 2.3113 | 0.98867 |  | 27-03-2026 18:10 | 32.8995 | 25.513 | 7.3865 | 153.0783 | 36.2 | 25.1482 | 11.0518 | 3.3005 | 6 | 98.23%
27-03-2026 18:00 | 63 | 49.94 | 26.748 | 27.313 | 2385.6 | 4.5522 | 3.735 | 0.81721 | 22.4097 | 6.1 | 3.6815 | 2.4185 |  | 27-03-2026 18:00 | 29.044 | 29.591 | 2411.6 | 4.9318 | 3.735 | 1.1969 | 22.4097 | 6.2 | 3.6815 | 2.5185 |  | 27-03-2026 18:00 | 26.203 | 26.781 | 2366.5 | 4.4635 | 3.735 | 0.72854 | 22.4097 | 6.1 | 3.6815 | 2.4185 |  | 27-03-2026 18:00 | 26.332 | 26.911 | 2384.3 | 4.4852 | 3.735 | 0.75021 | 22.4097 | 6.2 | 3.6815 | 2.5185 |  | 27-03-2026 18:00 | 19.84 | 20.336 | 1777.8 | 3.3893 | 2.7666 | 0.6227 | 16.5998 | 4.6 | 2.7271 | 1.8729 |  | 27-03-2026 18:00 | 18.631 | 19.107 | 1759.4 | 3.1845 | 2.7666 | 0.41787 | 16.5998 | 4.4 | 2.7271 | 1.6729 |  | 27-03-2026 18:00 | 18.602 | 19.134 | 1757.9 | 3.189 | 2.7666 | 0.42237 | 16.5998 | 4.4 | 2.7271 | 1.6729 |  | 27-03-2026 18:00 | 17.598 | 18.283 | 1768.3 | 3.0472 | 2.7666 | 0.28053 | 16.5998 | 4.2 | 2.7271 | 1.4729 |  | 27-03-2026 18:00 | 17.162 | 17.611 | 1671.9 | 2.9352 | 2.6321 | 0.30306 | 15.7927 | 4.1 | 2.5945 | 1.5055 |  | 27-03-2026 18:00 | 34.1778 | 28.6385 | 5.5394 | 171.8309 | 46.3 | 28.2289 | 18.0711 | 12.1222 | 7 | 98.2%
27-03-2026 17:50 | 144 | 50.51 | 47.252 | 48.024 | 2379.5 | 8.004 | 8.5184 | -0.51438 | 51.1103 | 8.6 | 8.3966 | 0.20343 |  | 27-03-2026 17:50 | 48.167 | 48.95 | 2405.4 | 8.1583 | 8.5184 | -0.36005 | 51.1103 | 8.6 | 8.3966 | 0.20343 |  | 27-03-2026 17:50 | 47.086 | 47.852 | 2360.4 | 7.9753 | 8.5184 | -0.54305 | 51.1103 | 8.8 | 8.3966 | 0.40343 |  | 27-03-2026 17:50 | 47.201 | 47.968 | 2378.1 | 7.9947 | 8.5184 | -0.52372 | 51.1103 | 8.7 | 8.3966 | 0.30343 |  | 27-03-2026 17:50 | 34.365 | 34.984 | 1773.2 | 5.8307 | 6.3099 | -0.47925 | 37.8595 | 6.5 | 6.2197 | 0.28032 |  | 27-03-2026 17:50 | 33.043 | 33.645 | 1755 | 5.6075 | 6.3099 | -0.70241 | 37.8595 | 6.3 | 6.2197 | 0.080317 |  | 27-03-2026 17:50 | 31.979 | 32.565 | 1753.5 | 5.4275 | 6.3099 | -0.88241 | 37.8595 | 6.3 | 6.2197 | 0.080317 |  | 27-03-2026 17:50 | 32.193 | 33.113 | 1764.1 | 5.5188 | 6.3099 | -0.79108 | 37.8595 | 6.3 | 6.2197 | 0.080317 |  | 27-03-2026 17:50 | 32.003 | 32.586 | 1667.8 | 5.431 | 6.0031 | -0.5721 | 36.0186 | 5.9 | 5.9173 | -0.017258 |  | 27-03-2026 17:50 | 59.9478 | 65.3163 | -5.3685 | 391.8978 | 66 | 64.3823 | 1.6177 | 6.0522 | 8 | 97.12%
27-03-2026 17:40 | 182 | 50.51 | 58.006 | 58.836 | 2370.9 | 9.806 | 10.7663 | -0.96029 | 64.5978 | 11.3 | 10.6123 | 0.68767 |  | 27-03-2026 17:40 | 58.931 | 58.778 | 2396.8 | 9.7963 | 10.7663 | -0.96996 | 64.5978 | 12.1 | 10.6123 | 1.4877 |  | 27-03-2026 17:40 | 57.692 | 58.636 | 2351.6 | 9.7727 | 10.7663 | -0.99363 | 64.5978 | 11.3 | 10.6123 | 0.68767 |  | 27-03-2026 17:40 | 56.86 | 57.714 | 2369.4 | 9.619 | 10.7663 | -1.1473 | 64.5978 | 11.2 | 10.6123 | 0.58767 |  | 27-03-2026 17:40 | 42.808 | 43.517 | 1766.7 | 7.2528 | 7.975 | -0.7222 | 47.8502 | 8.6 | 7.861 | 0.73901 |  | 27-03-2026 17:40 | 41.079 | 41.768 | 1748.7 | 6.9613 | 7.975 | -1.0137 | 47.8502 | 8.3 | 7.861 | 0.43901 |  | 27-03-2026 17:40 | 40.906 | 41.619 | 1747.2 | 6.9365 | 7.975 | -1.0385 | 47.8502 | 8.3 | 7.861 | 0.43901 |  | 27-03-2026 17:40 | 39.568 | 40.506 | 1757.8 | 6.751 | 7.975 | -1.224 | 47.8502 | 8.1 | 7.861 | 0.23901 |  | 27-03-2026 17:40 | 37.431 | 38.09 | 1661.9 | 6.3483 | 7.5873 | -1.2389 | 45.5235 | 7.7 | 7.4788 | 0.22124 |  | 27-03-2026 17:40 | 73.244 | 82.5525 | -9.3085 | 495.3153 | 86.9 | 81.372 | 5.528 | 13.656 | 9 | 98.5%
27-03-2026 17:30 | 240 | 50.51 | 77.139 | 78.123 | 2359.6 | 13.0205 | 14.1973 | -1.1768 | 85.1838 | 11.3 | 13.9943 | -2.6943 |  | 27-03-2026 17:30 | 78.45 | 79.483 | 2384.7 | 13.2472 | 14.1973 | -0.95014 | 85.1838 | 11.5 | 13.9943 | -2.4943 |  | 27-03-2026 17:30 | 77.499 | 78.685 | 2340.3 | 13.1142 | 14.1973 | -1.0831 | 85.1838 | 11 | 13.9943 | -2.9943 |  | 27-03-2026 17:30 | 77.539 | 78.361 | 2358.2 | 13.0602 | 14.1973 | -1.1371 | 85.1838 | 10.7 | 13.9943 | -3.2943 |  | 27-03-2026 17:30 | 58.026 | 58.868 | 1758.1 | 9.8113 | 10.5165 | -0.70519 | 63.0991 | 7.9 | 10.3661 | -2.4661 |  | 27-03-2026 17:30 | 56.011 | 56.835 | 1740.4 | 9.4725 | 10.5165 | -1.044 | 63.0991 | 7.5 | 10.3661 | -2.8661 |  | 27-03-2026 17:30 | 56.264 | 57.092 | 1738.9 | 9.5153 | 10.5165 | -1.0012 | 63.0991 | 7.6 | 10.3661 | -2.7661 |  | 27-03-2026 17:30 | 55.787 | 57.47 | 1749.7 | 9.5783 | 10.5165 | -0.93819 | 63.0991 | 7.7 | 10.3661 | -2.6661 |  | 27-03-2026 17:30 | 52.676 | 53.478 | 1654.2 | 8.913 | 10.0052 | -1.0922 | 60.031 | 7.3 | 9.8621 | -2.5621 |  | 27-03-2026 17:30 | 99.7325 | 108.8605 | -9.128 | 653.163 | 82.5 | 107.3038 | -24.8038 | -17.2325
27-03-2026 17:20 | 296 | 50.51 | 96.577 | 97.75 | 2348.3 | 16.2917 | 17.51 | -1.2183 | 105.0601 | 17.6 | 17.2596 | 0.34038 |  | 27-03-2026 17:20 | 99.841 | 100.862 | 2373.2 | 16.8103 | 17.51 | -0.69968 | 105.0601 | 16.6 | 17.2596 | -0.65962 |  | 27-03-2026 17:20 | 96.764 | 98.35 | 2329.3 | 16.3917 | 17.51 | -1.1183 | 105.0601 | 17.5 | 17.2596 | 0.24038 |  | 27-03-2026 17:20 | 97.051 | 98.26 | 2347.5 | 16.3767 | 17.51 | -1.1333 | 105.0601 | 17.4 | 17.2596 | 0.14038 |  | 27-03-2026 17:20 | 71.691 | 72.643 | 1750.2 | 12.1072 | 12.9704 | -0.86321 | 77.8223 | 13.1 | 12.7849 | 0.3151 |  | 27-03-2026 17:20 | 70.116 | 71.047 | 1732.9 | 11.8412 | 12.9704 | -1.1292 | 77.8223 | 13 | 12.7849 | 0.2151 |  | 27-03-2026 17:20 | 70.037 | 70.981 | 1731.3 | 11.8302 | 12.9704 | -1.1402 | 77.8223 | 12.9 | 12.7849 | 0.1151 |  | 27-03-2026 17:20 | 70.318 | 72.23 | 1742 | 12.0383 | 12.9704 | -0.93205 | 77.8223 | 12.8 | 12.7849 | 0.015096 |  | 27-03-2026 17:20 | 66.38 | 67.295 | 1646.9 | 11.2158 | 12.3397 | -1.1239 | 74.0383 | 12 | 12.1633 | -0.16325 |  | 27-03-2026 17:20 | 124.903 | 134.2613 | -9.3583 | 805.5677 | 132.9 | 132.3413 | 0.55865 | 7.997
27-03-2026 17:10 | 352 | 50.51 | 117.277 | 118.808 | 2330.7 | 19.8013 | 20.8227 | -1.0214 | 124.9363 | 21.1 | 20.525 | 0.57505 |  | 27-03-2026 17:10 | 118.461 | 119.961 | 2356.6 | 19.9935 | 20.8227 | -0.82922 | 124.9363 | 22.1 | 20.525 | 1.575 |  | 27-03-2026 17:10 | 116.957 | 119.176 | 2311.8 | 19.8627 | 20.8227 | -0.96005 | 124.9363 | 21.1 | 20.525 | 0.57505 |  | 27-03-2026 17:10 | 116.709 | 118.198 | 2330.1 | 19.6997 | 20.8227 | -1.1231 | 124.9363 | 21.2 | 20.525 | 0.67505 |  | 27-03-2026 17:10 | 87.515 | 88.687 | 1737.1 | 14.7812 | 15.4242 | -0.64307 | 92.5454 | 16.1 | 15.2037 | 0.89633 |  | 27-03-2026 17:10 | 85.253 | 86.332 | 1719.9 | 14.3887 | 15.4242 | -1.0356 | 92.5454 | 15.4 | 15.2037 | 0.19633 |  | 27-03-2026 17:10 | 85.407 | 86.497 | 1718.4 | 14.4162 | 15.4242 | -1.0081 | 92.5454 | 15.5 | 15.2037 | 0.29633 |  | 27-03-2026 17:10 | 85.127 | 87.582 | 1729.2 | 14.597 | 15.4242 | -0.82724 | 92.5454 | 15.4 | 15.2037 | 0.19633 |  | 27-03-2026 17:10 | 80.315 | 81.373 | 1634.9 | 13.5622 | 14.6743 | -1.1121 | 88.0455 | 14.6 | 14.4644 | 0.13559 |  | 27-03-2026 17:10 | 151.1023 | 159.6621 | -8.5597 | 957.9724 | 162.5 | 157.3789 | 5.1211 | 11.3977
27-03-2026 17:00 | 409 | 50.8 | 137.409 | 139.106 | 2309.6 | 23.1843 | 24.1676 | -0.98328 | 145.0057 | 24.3 | 23.822 | 0.47798 |  | 27-03-2026 17:00 | 139.552 | 141.376 | 2334.5 | 23.5627 | 24.1676 | -0.60495 | 145.0057 | 24.3 | 23.822 | 0.47798 |  | 27-03-2026 17:00 | 136.974 | 139.373 | 2290.7 | 23.2288 | 24.1676 | -0.93878 | 145.0057 | 24.7 | 23.822 | 0.87798 |  | 27-03-2026 17:00 | 136.675 | 138.475 | 2308.9 | 23.0792 | 24.1676 | -1.0884 | 145.0057 | 24.6 | 23.822 | 0.77798 |  | 27-03-2026 17:00 | 102.88 | 104.193 | 1721 | 17.3655 | 17.9019 | -0.53644 | 107.4116 | 18.2 | 17.6459 | 0.55406 |  | 27-03-2026 17:00 | 100.032 | 101.357 | 1704.5 | 16.8928 | 17.9019 | -1.0091 | 107.4116 | 17.8 | 17.6459 | 0.15406 |  | 27-03-2026 17:00 | 100.138 | 101.385 | 1702.9 | 16.8975 | 17.9019 | -1.0044 | 107.4116 | 17.7 | 17.6459 | 0.054061 |  | 27-03-2026 17:00 | 99.869 | 102.656 | 1713.8 | 17.1093 | 17.9019 | -0.7926 | 107.4116 | 17.7 | 17.6459 | 0.054061 |  | 27-03-2026 17:00 | 94.354 | 95.558 | 1620.3 | 15.9263 | 17.0315 | -1.1051 | 102.1889 | 16.7 | 16.7879 | -0.087925 |  | 27-03-2026 17:00 | 177.2465 | 185.3097 | -8.0632 | 1111.8581 | 186 | 182.6597 | 3.3403 | 8.7535
27-03-2026 16:50 | 448 | 51.09 | 152.69 | 154.654 | 2285.3 | 25.7757 | 26.4426 | -0.6669 | 158.6554 | 56.9 | 26.0644 | 30.8356 |  | 27-03-2026 16:50 | 153.502 | 155.508 | 2310.2 | 25.918 | 26.4426 | -0.52457 | 158.6554 | 26.7 | 26.0644 | 0.63556 |  | 27-03-2026 16:50 | 152.409 | 155.447 | 2266 | 25.9078 | 26.4426 | -0.53474 | 158.6554 | 26.4 | 26.0644 | 0.33556 |  | 27-03-2026 16:50 | 151.844 | 153.86 | 2284.3 | 25.6433 | 26.4426 | -0.79924 | 158.6554 | 26.3 | 26.0644 | 0.23556 |  | 27-03-2026 16:50 | 114.613 | 116.076 | 1702.8 | 19.346 | 19.5871 | -0.24109 | 117.5225 | 19.8 | 19.307 | 0.49301 |  | 27-03-2026 16:50 | 111.67 | 113.122 | 1686.7 | 18.8537 | 19.5871 | -0.73342 | 117.5225 | 19.3 | 19.307 | -0.0069928 |  | 27-03-2026 16:50 | 112.422 | 113.845 | 1685.2 | 18.9742 | 19.5871 | -0.61292 | 117.5225 | 19.7 | 19.307 | 0.39301 |  | 27-03-2026 16:50 | 112.878 | 115.896 | 1696.1 | 19.316 | 19.5871 | -0.27109 | 117.5225 | 19.7 | 19.307 | 0.39301 |  | 27-03-2026 16:50 | 106.348 | 107.594 | 1603.6 | 17.9323 | 18.6347 | -0.70236 | 111.8081 | 18.6 | 18.3682 | 0.23179 |  | 27-03-2026 16:50 | 197.667 | 202.7533 | -5.0863 | 1216.5199 | 233.4 | 199.8539 | 33.5461 | 35.733
27-03-2026 16:40 | 490 | 50.8 | 167.1 | 169.284 | 2258.5 | 28.214 | 28.9539 | -0.73987 | 173.7232 | 0 | 28.5398 | -28.5398 |  | 27-03-2026 16:40 | 168.994 | 171.289 | 2283.5 | 28.5482 | 28.9539 | -0.4057 | 173.7232 | 31 | 28.5398 | 2.4602 |  | 27-03-2026 16:40 | 167.016 | 170.622 | 2239.6 | 28.437 | 28.9539 | -0.51687 | 173.7232 | 30 | 28.5398 | 1.4602 |  | 27-03-2026 16:40 | 166.477 | 168.886 | 2258 | 28.1477 | 28.9539 | -0.8062 | 173.7232 | 30.1 | 28.5398 | 1.5602 |  | 27-03-2026 16:40 | 125.039 | 126.728 | 1683 | 21.1213 | 21.4473 | -0.32597 | 128.6838 | 22.4 | 21.1406 | 1.2594 |  | 27-03-2026 16:40 | 122.521 | 124.084 | 1667.4 | 20.6807 | 21.4473 | -0.76664 | 128.6838 | 22 | 21.1406 | 0.85939 |  | 27-03-2026 16:40 | 122.561 | 124.125 | 1665.5 | 20.6875 | 21.4473 | -0.75981 | 128.6838 | 21.7 | 21.1406 | 0.55939 |  | 27-03-2026 16:40 | 122.8 | 126.144 | 1676.4 | 21.024 | 21.4473 | -0.42331 | 128.6838 | 21.7 | 21.1406 | 0.55939 |  | 27-03-2026 16:40 | 116.159 | 117.702 | 1585 | 19.617 | 20.4045 | -0.78746 | 122.4267 | 20.9 | 20.1127 | 0.78733 |  | 27-03-2026 16:40 | 216.4773 | 222.0091 | -5.5318 | 1332.0549 | 199.8 | 218.8344 | -19.0344 | -16.6773
27-03-2026 16:30 | 557 | 50.8 | 193.302 | 195.868 | 2228.4 | 32.6447 | 32.9129 | -0.2682 | 197.4772 | 20.9 | 32.4422 | -11.5422 |  | 27-03-2026 16:30 | 195.768 | 198.427 | 2252.5 | 33.0712 | 32.9129 | 0.1583 | 197.4772 | 20.5 | 32.4422 | -11.9422 |  | 27-03-2026 16:30 | 192.695 | 196.669 | 2209.6 | 32.7782 | 32.9129 | -0.1347 | 197.4772 | 21.1 | 32.4422 | -11.3422 |  | 27-03-2026 16:30 | 191.534 | 194.116 | 2227.9 | 32.3527 | 32.9129 | -0.5602 | 197.4772 | 20.6 | 32.4422 | -11.8422 |  | 27-03-2026 16:30 | 144.417 | 146.29 | 1660.6 | 24.3817 | 24.3799 | 0.0017681 | 146.2794 | 15.9 | 24.0313 | -8.1313 |  | 27-03-2026 16:30 | 141.464 | 143.269 | 1645.4 | 23.8782 | 24.3799 | -0.50173 | 146.2794 | 15.4 | 24.0313 | -8.6313 |  | 27-03-2026 16:30 | 141.615 | 143.489 | 1643.8 | 23.9148 | 24.3799 | -0.46507 | 146.2794 | 15.7 | 24.0313 | -8.3313 |  | 27-03-2026 16:30 | 141.761 | 145.548 | 1654.7 | 24.258 | 24.3799 | -0.1219 | 146.2794 | 15.9 | 24.0313 | -8.1313 |  | 27-03-2026 16:30 | 133.965 | 135.688 | 1564.1 | 22.6147 | 23.1945 | -0.57979 | 139.1667 | 14.5 | 22.8628 | -8.3628 |  | 27-03-2026 16:30 | 249.894 | 252.3655 | -2.4715 | 1514.193 | 160.5 | 248.7567 | -88.2567 | -89.394
27-03-2026 16:20 | 129 | 50.8 | 42.518 | 43.306 | 2207.5 | 7.2177 | 7.6225 | -0.40488 | 45.7353 | 21.6 | 7.5135 | 14.0865 |  | 27-03-2026 16:20 | 44.567 | 45.467 | 2232 | 7.5778 | 7.6225 | -0.044715 | 45.7353 | 22 | 7.5135 | 14.4865 |  | 27-03-2026 16:20 | 42.793 | 43.591 | 2188.5 | 7.2652 | 7.6225 | -0.35738 | 45.7353 | 20.8 | 7.5135 | 13.2865 |  | 27-03-2026 16:20 | 43.751 | 44.576 | 2207.3 | 7.4293 | 7.6225 | -0.19321 | 45.7353 | 21.6 | 7.5135 | 14.0865 |  | 27-03-2026 16:20 | 31.784 | 32.426 | 1644.7 | 5.4043 | 5.6463 | -0.242 | 33.878 | 15.6 | 5.5656 | 10.0344 |  | 27-03-2026 16:20 | 31.864 | 32.498 | 1630 | 5.4163 | 5.6463 | -0.23 | 33.878 | 15.7 | 5.5656 | 10.1344 |  | 27-03-2026 16:20 | 31.25 | 31.881 | 1628.1 | 5.3135 | 5.6463 | -0.33283 | 33.878 | 15.6 | 5.5656 | 10.0344 |  | 27-03-2026 16:20 | 31.517 | 32.364 | 1638.8 | 5.394 | 5.6463 | -0.25233 | 33.878 | 15.8 | 5.5656 | 10.2344 |  | 27-03-2026 16:20 | 29.963 | 30.641 | 1549.6 | 5.1068 | 5.3718 | -0.26495 | 32.2307 | 15.3 | 5.295 | 10.005 |  | 27-03-2026 16:20 | 56.125 | 58.4473 | -2.3223 | 350.6838 | 164 | 57.6115 | 106.3885 | 107.875
27-03-2026 16:10 | 612 | 51.09 | 205.9 | 208.76 | 2185.9 | 34.7933 | 36.1224 | -1.3291 | 216.7346 | 34.5 | 35.6059 | -1.1059 |  | 27-03-2026 16:10 | 211.719 | 214.747 | 2210 | 35.7912 | 36.1224 | -0.33127 | 216.7346 | 34.7 | 35.6059 | -0.90589 |  | 27-03-2026 16:10 | 209.984 | 214.908 | 2167.7 | 35.818 | 36.1224 | -0.30444 | 216.7346 | 34.8 | 35.6059 | -0.80589 |  | 27-03-2026 16:10 | 210.03 | 213.034 | 2185.7 | 35.5057 | 36.1224 | -0.61677 | 216.7346 | 34.7 | 35.6059 | -0.90589 |  | 27-03-2026 16:10 | 157.901 | 160.046 | 1629.1 | 26.6743 | 26.7574 | -0.083028 | 160.5442 | 26 | 26.3747 | -0.37473 |  | 27-03-2026 16:10 | 154.421 | 156.502 | 1614.3 | 26.0837 | 26.7574 | -0.67369 | 160.5442 | 25.5 | 26.3747 | -0.87473 |  | 27-03-2026 16:10 | 154.701 | 157.078 | 1612.5 | 26.1797 | 26.7574 | -0.57769 | 160.5442 | 25.2 | 26.3747 | -1.1747 |  | 27-03-2026 16:10 | 154.695 | 159.056 | 1623 | 26.5093 | 26.7574 | -0.24803 | 160.5442 | 25.2 | 26.3747 | -1.1747 |  | 27-03-2026 16:10 | 146.045 | 148.014 | 1534.3 | 24.669 | 25.4563 | -0.78732 | 152.7379 | 23.8 | 25.0923 | -1.2923 |  | 27-03-2026 16:10 | 272.0242 | 276.9755 | -4.9513 | 1661.8531 | 264.4 | 273.0148 | -8.6148 | -7.6242
27-03-2026 16:00 | 633 | 51.37 | 216.713 | 219.384 | 2151.4 | 36.564 | 37.3216 | -0.75764 | 223.9298 | 36.8 | 36.7879 | 0.01206 |  | 27-03-2026 16:00 | 218.649 | 221.482 | 2175.3 | 36.9137 | 37.3216 | -0.40797 | 223.9298 | 38.1 | 36.7879 | 1.3121 |  | 27-03-2026 16:00 | 215.756 | 221.187 | 2132.9 | 36.8645 | 37.3216 | -0.45714 | 223.9298 | 37.1 | 36.7879 | 0.31206 |  | 27-03-2026 16:00 | 215.974 | 218.821 | 2151 | 36.4702 | 37.3216 | -0.85147 | 223.9298 | 37.9 | 36.7879 | 1.1121 |  | 27-03-2026 16:00 | 161.968 | 164.184 | 1603.1 | 27.364 | 27.6457 | -0.28166 | 165.874 | 28.4 | 27.2503 | 1.1497 |  | 27-03-2026 16:00 | 158.186 | 160.66 | 1588.8 | 26.7767 | 27.6457 | -0.86899 | 165.874 | 27.8 | 27.2503 | 0.54967 |  | 27-03-2026 16:00 | 158.586 | 160.922 | 1587.3 | 26.8203 | 27.6457 | -0.82533 | 165.874 | 28.3 | 27.2503 | 1.0497 |  | 27-03-2026 16:00 | 158.301 | 162.627 | 1597.8 | 27.1045 | 27.6457 | -0.54116 | 165.874 | 28.3 | 27.2503 | 1.0497 |  | 27-03-2026 16:00 | 149.412 | 151.472 | 1510.5 | 25.2453 | 26.3014 | -1.0561 | 157.8085 | 26.7 | 25.9253 | 0.77469 |  | 27-03-2026 16:00 | 280.1232 | 286.1706 | -6.0474 | 1717.0237 | 289.4 | 282.0784 | 7.3216 | 9.2768
27-03-2026 15:50 | 707 | 51.09 | 242.423 | 246.015 | 2114.6 | 41.0025 | 41.7297 | -0.72718 | 250.3781 | 40.7 | 41.1329 | -0.43294 |  | 27-03-2026 15:50 | 245.133 | 248.841 | 2137.2 | 41.4735 | 41.7297 | -0.25618 | 250.3781 | 42.2 | 41.1329 | 1.0671 |  | 27-03-2026 15:50 | 240.917 | 246.891 | 2095.8 | 41.1485 | 41.7297 | -0.58118 | 250.3781 | 40.4 | 41.1329 | -0.73294 |  | 27-03-2026 15:50 | 242.591 | 246.26 | 2113.1 | 41.0433 | 41.7297 | -0.68635 | 250.3781 | 40.7 | 41.1329 | -0.43294 |  | 27-03-2026 15:50 | 181.219 | 183.736 | 1574.7 | 30.6227 | 30.9109 | -0.28821 | 185.4652 | 30.5 | 30.4688 | 0.031152 |  | 27-03-2026 15:50 | 178.515 | 181.463 | 1561 | 30.2438 | 30.9109 | -0.66704 | 185.4652 | 29.9 | 30.4688 | -0.56885 |  | 27-03-2026 15:50 | 178.686 | 181.321 | 1559 | 30.2202 | 30.9109 | -0.69071 | 185.4652 | 29.5 | 30.4688 | -0.96885 |  | 27-03-2026 15:50 | 178.707 | 183.595 | 1569.5 | 30.5992 | 30.9109 | -0.31171 | 185.4652 | 29.9 | 30.4688 | -0.56885 |  | 27-03-2026 15:50 | 169.214 | 171.582 | 1483.8 | 28.597 | 29.4079 | -0.81087 | 176.4472 | 28.3 | 28.9873 | -0.68734 |  | 27-03-2026 15:50 | 314.9507 | 319.9701 | -5.0194 | 1919.8205 | 312.1 | 315.3945 | -3.2945 | -2.8507
27-03-2026 15:40 | 731 | 51.09 | 249.773 | 253.577 | 2073.9 | 42.2628 | 43.1462 | -0.88341 | 258.8775 | 42.3 | 42.5293 | -0.22925 |  | 27-03-2026 15:40 | 252.672 | 256.558 | 2095 | 42.7597 | 43.1462 | -0.38658 | 258.8775 | 41.7 | 42.5293 | -0.82925 |  | 27-03-2026 15:40 | 247.882 | 254.069 | 2055.4 | 42.3448 | 43.1462 | -0.80141 | 258.8775 | 42.2 | 42.5293 | -0.32925 |  | 27-03-2026 15:40 | 248.62 | 252.483 | 2072.4 | 42.0805 | 43.1462 | -1.0657 | 258.8775 | 42.2 | 42.5293 | -0.32925 |  | 27-03-2026 15:40 | 185.907 | 188.528 | 1544.2 | 31.4213 | 31.9602 | -0.53885 | 191.7611 | 31.7 | 31.5032 | 0.19685 |  | 27-03-2026 15:40 | 182.361 | 185.22 | 1531.1 | 30.87 | 31.9602 | -1.0902 | 191.7611 | 31.1 | 31.5032 | -0.40315 |  | 27-03-2026 15:40 | 182.178 | 185.373 | 1529.5 | 30.8955 | 31.9602 | -1.0647 | 191.7611 | 31.1 | 31.5032 | -0.40315 |  | 27-03-2026 15:40 | 182.587 | 187.834 | 1539.6 | 31.3057 | 31.9602 | -0.65452 | 191.7611 | 31.2 | 31.5032 | -0.30315 |  | 27-03-2026 15:40 | 172.789 | 175.242 | 1455.5 | 29.207 | 30.4062 | -1.1992 | 182.4369 | 29.4 | 29.9713 | -0.57135 |  | 27-03-2026 15:40 | 323.1473 | 330.8319 | -7.6845 | 1984.9912 | 322.9 | 326.101 | -3.201 | -0.24733
27-03-2026 15:30 | 751 | 51.09 | 260.163 | 264.157 | 2031.6 | 44.0262 | 44.3267 | -0.30055 | 265.9603 | 42.2 | 43.6928 | -1.4928 |  | 27-03-2026 15:30 | 257.229 | 261.279 | 2053.3 | 43.5465 | 44.3267 | -0.78022 | 265.9603 | 42.3 | 43.6928 | -1.3928 |  | 27-03-2026 15:30 | 255.126 | 261.254 | 2013.2 | 43.5423 | 44.3267 | -0.78438 | 265.9603 | 42.8 | 43.6928 | -0.89285 |  | 27-03-2026 15:30 | 254.899 | 258.912 | 2030.2 | 43.152 | 44.3267 | -1.1747 | 265.9603 | 42.2 | 43.6928 | -1.4928 |  | 27-03-2026 15:30 | 192.366 | 195.117 | 1512.5 | 32.5195 | 32.8346 | -0.31511 | 197.0076 | 31.2 | 32.3651 | -1.1651 |  | 27-03-2026 15:30 | 188 | 191.084 | 1500 | 31.8473 | 32.8346 | -0.98727 | 197.0076 | 30.9 | 32.3651 | -1.4651 |  | 27-03-2026 15:30 | 188.677 | 192.194 | 1498.4 | 32.0323 | 32.8346 | -0.80227 | 197.0076 | 30.7 | 32.3651 | -1.6651 |  | 27-03-2026 15:30 | 188.984 | 194.384 | 1508.4 | 32.3973 | 32.8346 | -0.43727 | 197.0076 | 30.8 | 32.3651 | -1.5651 |  | 27-03-2026 15:30 | 178.058 | 180.605 | 1426.1 | 30.1008 | 31.2381 | -1.1372 | 187.4284 | 29 | 30.7914 | -1.7914 |  | 27-03-2026 15:30 | 333.1643 | 339.8834 | -6.719 | 2039.3001 | 322.1 | 335.023 | -12.923 | -11.0643
27-03-2026 15:20 | 782 | 51.09 | 264.563 | 268.646 | 1989.4 | 44.7743 | 46.1564 | -1.3821 | 276.9387 | 45.6 | 45.4964 | 0.10359 |  | 27-03-2026 15:20 | 270.559 | 272.398 | 2011 | 45.3997 | 46.1564 | -0.75678 | 276.9387 | 48.1 | 45.4964 | 2.6036 |  | 27-03-2026 15:20 | 262.631 | 269.396 | 1970.4 | 44.8993 | 46.1564 | -1.2571 | 276.9387 | 44.1 | 45.4964 | -1.3964 |  | 27-03-2026 15:20 | 265.485 | 269.692 | 1988 | 44.9487 | 46.1564 | -1.2078 | 276.9387 | 45.5 | 45.4964 | 0.0035887 |  | 27-03-2026 15:20 | 199.64 | 202.516 | 1481.3 | 33.7527 | 34.19 | -0.4373 | 205.1398 | 34 | 33.701 | 0.29895 |  | 27-03-2026 15:20 | 195.417 | 198.871 | 1469.1 | 33.1452 | 34.19 | -1.0448 | 205.1398 | 33.5 | 33.701 | -0.20105 |  | 27-03-2026 15:20 | 195.873 | 199.453 | 1467.7 | 33.2422 | 34.19 | -0.9478 | 205.1398 | 33.5 | 33.701 | -0.20105 |  | 27-03-2026 15:20 | 196.08 | 201.722 | 1477.6 | 33.6203 | 34.19 | -0.56963 | 205.1398 | 33.1 | 33.701 | -0.60105 |  | 27-03-2026 15:20 | 185.252 | 187.92 | 1397.1 | 31.32 | 32.5275 | -1.2075 | 195.1651 | 31.8 | 32.0624 | -0.26237 |  | 27-03-2026 15:20 | 345.1023 | 353.9132 | -8.8108 | 2123.4789 | 349.2 | 348.8522 | 0.3478 | 4.0977
27-03-2026 15:10 | 823 | 51.09 | 276.6 | 281.012 | 1943.8 | 46.8353 | 48.5764 | -1.7411 | 291.4585 | 45.9 | 47.8818 | -1.9818 |  | 27-03-2026 15:10 | 282.108 | 285.15 | 1962.9 | 47.525 | 48.5764 | -1.0514 | 291.4585 | 45.1 | 47.8818 | -2.7818 |  | 27-03-2026 15:10 | 275.396 | 282.424 | 1926.3 | 47.0707 | 48.5764 | -1.5057 | 291.4585 | 46.2 | 47.8818 | -1.6818 |  | 27-03-2026 15:10 | 277.579 | 282.064 | 1942.5 | 47.0107 | 48.5764 | -1.5657 | 291.4585 | 46.4 | 47.8818 | -1.4818 |  | 27-03-2026 15:10 | 207.267 | 210.317 | 1447.3 | 35.0528 | 35.9825 | -0.9297 | 215.8952 | 34.8 | 35.468 | -0.66798 |  | 27-03-2026 15:10 | 204.156 | 207.4 | 1435.6 | 34.5667 | 35.9825 | -1.4159 | 215.8952 | 34.1 | 35.468 | -1.368 |  | 27-03-2026 15:10 | 203.68 | 206.941 | 1434.2 | 34.4902 | 35.9825 | -1.4924 | 215.8952 | 34.7 | 35.468 | -0.76798 |  | 27-03-2026 15:10 | 204.729 | 210.163 | 1444.5 | 35.0272 | 35.9825 | -0.95536 | 215.8952 | 34.9 | 35.468 | -0.56798 |  | 27-03-2026 15:10 | 194.213 | 197.051 | 1365.3 | 32.8418 | 34.2329 | -1.3911 | 205.3975 | 32.6 | 33.7434 | -1.1434 |  | 27-03-2026 15:10 | 360.4203 | 372.4687 | -12.0484 | 2234.8122 | 354.7 | 367.1424 | -12.4424 | -5.7203
27-03-2026 15:00 | 836 | 51.09 | 277.865 | 282.297 | 1897.9 | 47.0495 | 49.3437 | -2.2942 | 296.0623 | 47.9 | 48.6381 | -0.73811 | 0.9843 | 27-03-2026 15:00 | 284.319 | 288.942 | 1917.8 | 48.157 | 49.3437 | -1.1867 | 296.0623 | 49.8 | 48.6381 | 1.1619 | 0.984 | 27-03-2026 15:00 | 279.407 | 286.739 | 1880.1 | 47.7898 | 49.3437 | -1.5539 | 296.0623 | 47.5 | 48.6381 | -1.1381 | 0.97443 | 27-03-2026 15:00 | 282.774 | 287.372 | 1896.1 | 47.8953 | 49.3437 | -1.4484 | 296.0623 | 47.6 | 48.6381 | -1.0381 | 0.984 | 27-03-2026 15:00 | 211.552 | 214.686 | 1412.5 | 35.781 | 36.5509 | -0.76991 | 219.3054 | 35.6 | 36.0282 | -0.42823 | 0.9854 | 27-03-2026 15:00 | 208.593 | 212.338 | 1401.5 | 35.3897 | 36.5509 | -1.1612 | 219.3054 | 35.5 | 36.0282 | -0.52823 | 0.98236 | 27-03-2026 15:00 | 208.269 | 211.97 | 1399.5 | 35.3283 | 36.5509 | -1.2226 | 219.3054 | 34.8 | 36.0282 | -1.2282 | 0.98254 | 27-03-2026 15:00 | 209.666 | 215.509 | 1409.6 | 35.9182 | 36.5509 | -0.63274 | 219.3054 | 34.6 | 36.0282 | -1.4282 | 0.97289 | 27-03-2026 15:00 | 199.176 | 202.045 | 1332.7 | 33.6742 | 34.7737 | -1.0995 | 208.642 | 32.7 | 34.2764 | -1.5764 | 0.9858 | 27-03-2026 15:00 | 366.983 | 378.3522 | -11.3692 | 2270.113 | 366 | 372.9417 | -6.9417 | -0.983
27-03-2026 14:50 | 905 | 51.37 | 302.614 | 307.628 | 1850 | 51.2713 | 53.3587 | -2.0874 | 320.1525 | 49.1 | 52.5957 | -3.4957 | 0.9837 | 27-03-2026 14:50 | 306.784 | 311.994 | 1868 | 51.999 | 53.3587 | -1.3597 | 320.1525 | 48.2 | 52.5957 | -4.3957 | 0.9833 | 27-03-2026 14:50 | 300.357 | 308.497 | 1832.6 | 51.4162 | 53.3587 | -1.9426 | 320.1525 | 48.7 | 52.5957 | -3.8957 | 0.97361 | 27-03-2026 14:50 | 302.677 | 307.786 | 1848.5 | 51.2977 | 53.3587 | -2.0611 | 320.1525 | 48.7 | 52.5957 | -3.8957 | 0.9834 | 27-03-2026 14:50 | 226.158 | 229.649 | 1376.9 | 38.2748 | 39.525 | -1.2502 | 237.15 | 36.7 | 38.9598 | -2.2598 | 0.9848 | 27-03-2026 14:50 | 223.068 | 226.77 | 1366 | 37.795 | 39.525 | -1.73 | 237.15 | 35.1 | 38.9598 | -3.8598 | 0.98368 | 27-03-2026 14:50 | 222.513 | 226.289 | 1364.7 | 37.7148 | 39.525 | -1.8102 | 237.15 | 35.4 | 38.9598 | -3.5598 | 0.98331 | 27-03-2026 14:50 | 223.435 | 229.858 | 1375 | 38.3097 | 39.525 | -1.2153 | 237.15 | 35.1 | 38.9598 | -3.8598 | 0.97206 | 27-03-2026 14:50 | 211.627 | 214.806 | 1300 | 35.801 | 37.6031 | -1.8021 | 225.6188 | 33.8 | 37.0654 | -3.2654 | 0.9852 | 27-03-2026 14:50 | 393.8795 | 409.1381 | -15.2586 | 2454.8285 | 370.8 | 403.2874 | -32.4874 | -23.0795
27-03-2026 14:40 | 881 | 51.09 | 296.203 | 301.05 | 1800.9 | 50.175 | 51.9998 | -1.8248 | 311.9987 | 50.6 | 51.2562 | -0.65619 | 0.9839 | 27-03-2026 14:40 | 299.965 | 304.935 | 1819.8 | 50.8225 | 51.9998 | -1.1773 | 311.9987 | 51.1 | 51.2562 | -0.15619 | 0.9837 | 27-03-2026 14:40 | 294.816 | 303.081 | 1783.9 | 50.5135 | 51.9998 | -1.4863 | 311.9987 | 49.6 | 51.2562 | -1.6562 | 0.97273 | 27-03-2026 14:40 | 296.435 | 301.316 | 1799.8 | 50.2193 | 51.9998 | -1.7805 | 311.9987 | 50.1 | 51.2562 | -1.1562 | 0.9838 | 27-03-2026 14:40 | 222.288 | 225.627 | 1340.2 | 37.6045 | 38.5184 | -0.91386 | 231.1102 | 37.8 | 37.9675 | -0.16755 | 0.9852 | 27-03-2026 14:40 | 218.694 | 222.403 | 1330.9 | 37.0672 | 38.5184 | -1.4512 | 231.1102 | 37.4 | 37.9675 | -0.56755 | 0.98332 | 27-03-2026 14:40 | 217.974 | 221.83 | 1329.3 | 36.9717 | 38.5184 | -1.5467 | 231.1102 | 37.3 | 37.9675 | -0.66755 | 0.98262 | 27-03-2026 14:40 | 219.065 | 225.57 | 1339.9 | 37.595 | 38.5184 | -0.92336 | 231.1102 | 37.6 | 37.9675 | -0.36755 | 0.97116 | 27-03-2026 14:40 | 206.623 | 209.518 | 1266.2 | 34.9197 | 36.6454 | -1.7258 | 219.8727 | 35 | 36.1214 | -1.1214 | 0.98618 | 27-03-2026 14:40 | 385.8883 | 398.718 | -12.8297 | 2392.3081 | 386.5 | 393.0164 | -6.5164 | 0.61167
27-03-2026 14:30 | 932 | 51.37 | 311.853 | 317.013 | 1750.3 | 52.8355 | 54.9507 | -2.1152 | 329.704 | 51 | 54.1649 | -3.1649 | 0.98372 | 27-03-2026 14:30 | 315.263 | 320.65 | 1768.7 | 53.4417 | 54.9507 | -1.509 | 329.704 | 51.6 | 54.1649 | -2.5649 | 0.9832 | 27-03-2026 14:30 | 308.024 | 316.488 | 1734.3 | 52.748 | 54.9507 | -2.2027 | 329.704 | 51.2 | 54.1649 | -2.9649 | 0.97326 | 27-03-2026 14:30 | 310.408 | 315.68 | 1749.7 | 52.6133 | 54.9507 | -2.3373 | 329.704 | 51.6 | 54.1649 | -2.5649 | 0.9833 | 27-03-2026 14:30 | 231.984 | 235.589 | 1302.4 | 39.2648 | 40.7042 | -1.4394 | 244.2252 | 38.7 | 40.1221 | -1.4221 | 0.9847 | 27-03-2026 14:30 | 228.365 | 232.556 | 1293.5 | 38.7593 | 40.7042 | -1.9449 | 244.2252 | 38.1 | 40.1221 | -2.0221 | 0.98198 | 27-03-2026 14:30 | 228.614 | 233.098 | 1292 | 38.8497 | 40.7042 | -1.8545 | 244.2252 | 38.1 | 40.1221 | -2.0221 | 0.98076 | 27-03-2026 14:30 | 229.411 | 236.275 | 1302.3 | 39.3792 | 40.7042 | -1.325 | 244.2252 | 38.3 | 40.1221 | -1.8221 | 0.97095 | 27-03-2026 14:30 | 216.935 | 220.216 | 1231.2 | 36.7027 | 38.725 | -2.0223 | 232.35 | 36.2 | 38.1712 | -1.9712 | 0.9851 | 27-03-2026 14:30 | 404.5942 | 421.3444 | -16.7502 | 2528.0664 | 394.8 | 415.3192 | -20.5192 | -9.7942
27-03-2026 14:20 | 923 | 51.66 | 310.976 | 316.129 | 1699.3 | 52.6882 | 54.3592 | -1.671 | 326.155 | 52.4 | 53.5818 | -1.1818 | 0.9837 | 27-03-2026 14:20 | 319.733 | 320.634 | 1717.1 | 53.439 | 54.3592 | -0.92017 | 326.155 | 52.2 | 53.5818 | -1.3818 | 0.99719 | 27-03-2026 14:20 | 307.245 | 315.515 | 1683.1 | 52.5858 | 54.3592 | -1.7733 | 326.155 | 51.4 | 53.5818 | -2.1818 | 0.97379 | 27-03-2026 14:20 | 311.823 | 317.054 | 1698.1 | 52.8423 | 54.3592 | -1.5168 | 326.155 | 50.9 | 53.5818 | -2.6818 | 0.9835 | 27-03-2026 14:20 | 231.606 | 235.157 | 1263.7 | 39.1928 | 40.2661 | -1.0732 | 241.5963 | 38.4 | 39.6902 | -1.2902 | 0.9849 | 27-03-2026 14:20 | 229.224 | 233.251 | 1255.4 | 38.8752 | 40.2661 | -1.3909 | 241.5963 | 37.3 | 39.6902 | -2.3902 | 0.98274 | 27-03-2026 14:20 | 228.337 | 232.423 | 1253.9 | 38.7372 | 40.2661 | -1.5289 | 241.5963 | 37.6 | 39.6902 | -2.0902 | 0.98242 | 27-03-2026 14:20 | 230.667 | 237.356 | 1264 | 39.5593 | 40.2661 | -0.70672 | 241.5963 | 37.4 | 39.6902 | -2.2902 | 0.97182 | 27-03-2026 14:20 | 218.596 | 221.88 | 1195 | 36.98 | 38.3082 | -1.3282 | 229.849 | 35.2 | 37.7604 | -2.5604 | 0.9852 | 27-03-2026 14:20 | 404.8998 | 416.809 | -11.9092 | 2500.8542 | 392.8 | 410.8487 | -18.0487 | -12.0998
27-03-2026 14:10 | 971 | 51.37 | 324.749 | 330.197 | 1646.9 | 55.0328 | 57.2501 | -2.2173 | 343.5006 | 54.1 | 56.4314 | -2.3314 | 0.9835 | 27-03-2026 14:10 | 329.418 | 335.047 | 1664.9 | 55.8412 | 57.2501 | -1.4089 | 343.5006 | 164.1 | 56.4314 | 107.6686 | 0.9832 | 27-03-2026 14:10 | 319.388 | 327.993 | 1631.7 | 54.6655 | 57.2501 | -2.5846 | 343.5006 | 53.7 | 56.4314 | -2.7314 | 0.97376 | 27-03-2026 14:10 | 325.392 | 330.952 | 1647.2 | 55.1587 | 57.2501 | -2.0914 | 343.5006 | 54.3 | 56.4314 | -2.1314 | 0.9832 | 27-03-2026 14:10 | 240.508 | 244.195 | 1225.3 | 40.6992 | 42.4075 | -1.7083 | 254.4449 | 40 | 41.8011 | -1.8011 | 0.9849 | 27-03-2026 14:10 | 239.453 | 243.686 | 1218.1 | 40.6143 | 42.4075 | -1.7931 | 254.4449 | 39.5 | 41.8011 | -2.3011 | 0.98263 | 27-03-2026 14:10 | 236.511 | 240.703 | 1216.3 | 40.1172 | 42.4075 | -2.2903 | 254.4449 | 39.4 | 41.8011 | -2.4011 | 0.98258 | 27-03-2026 14:10 | 237.759 | 244.612 | 1226.6 | 40.7687 | 42.4075 | -1.6388 | 254.4449 | 39.6 | 41.8011 | -2.2011 | 0.97198 | 27-03-2026 14:10 | 227.503 | 230.991 | 1159.8 | 38.4985 | 40.3455 | -1.847 | 242.0728 | 37.6 | 39.7685 | -2.1685 | 0.9849 | 27-03-2026 14:10 | 421.396 | 438.9758 | -17.5798 | 2633.8546 | 522.3 | 432.6984 | 89.6016 | 100.904
27-03-2026 14:00 | 963 | 51.37 | 320.187 | 325.504 | 1592.8 | 54.2507 | 56.7784 | -2.5278 | 340.6705 | 52.6 | 55.9665 | -3.3665 | 0.98367 |  |  |  |  | 0 | 56.7784 | -56.7784 | 340.6705 | 0 | 55.9665 | -55.9665 |  | 27-03-2026 14:00 | 318.076 | 327.25 | 1578 | 54.5417 | 56.7784 | -2.2368 | 340.6705 | 52.7 | 55.9665 | -3.2665 | 0.97197 | 27-03-2026 14:00 | 323.127 | 328.648 | 1592.9 | 54.7747 | 56.7784 | -2.0038 | 340.6705 | 53.7 | 55.9665 | -2.2665 | 0.9832 | 27-03-2026 14:00 | 240.511 | 244.273 | 1185.3 | 40.7122 | 42.0581 | -1.3459 | 252.3485 | 39.8 | 41.4567 | -1.6567 | 0.9846 | 27-03-2026 14:00 | 238.713 | 242.902 | 1178.6 | 40.4837 | 42.0581 | -1.5744 | 252.3485 | 39.6 | 41.4567 | -1.8567 | 0.98275 | 27-03-2026 14:00 | 237.969 | 242.487 | 1176.9 | 40.4145 | 42.0581 | -1.6436 | 252.3485 | 39.3 | 41.4567 | -2.1567 | 0.98137 | 27-03-2026 14:00 | 240.51 | 247.488 | 1187 | 41.248 | 42.0581 | -0.81009 | 252.3485 | 40.3 | 41.4567 | -1.1567 | 0.9718 | 27-03-2026 14:00 | 228.119 | 231.569 | 1122.2 | 38.5948 | 40.0131 | -1.4182 | 240.0784 | 38.2 | 39.4409 | -1.2409 | 0.9851 | 27-03-2026 14:00 | 365.0202 | 435.3591 | -70.3389 | 2612.1545 | 356.2 | 429.1334 | -72.9334 | -8.8202
27-03-2026 13:50 | 941 | 51.37 | 318.748 | 324.194 | 1540.2 | 54.0323 | 55.4813 | -1.449 | 332.8878 | 55.7 | 54.6879 | 1.0121 | 0.9832 |  |  |  |  | 0 | 55.4813 | -55.4813 | 332.8878 | 0 | 54.6879 | -54.6879 |  | 27-03-2026 13:50 | 309.835 | 317.783 | 1525.3 | 52.9638 | 55.4813 | -2.5175 | 332.8878 | 53.7 | 54.6879 | -0.98792 | 0.97499 | 27-03-2026 13:50 | 313.437 | 318.858 | 1539.2 | 53.143 | 55.4813 | -2.3383 | 332.8878 | 54.4 | 54.6879 | -0.28792 | 0.983 | 27-03-2026 13:50 | 231.381 | 235.048 | 1145.5 | 39.1747 | 41.0973 | -1.9226 | 246.5836 | 40.4 | 40.5096 | -0.10957 | 0.9844 | 27-03-2026 13:50 | 231.144 | 235.388 | 1139 | 39.2313 | 41.0973 | -1.8659 | 246.5836 | 40 | 40.5096 | -0.50957 | 0.98197 | 27-03-2026 13:50 | 229.575 | 230.648 | 1137.6 | 38.4413 | 41.0973 | -2.6559 | 246.5836 | 40.4 | 40.5096 | -0.10957 | 0.99535 | 27-03-2026 13:50 | 231.464 | 238.32 | 1146.7 | 39.72 | 41.0973 | -1.3773 | 246.5836 | 40.2 | 40.5096 | -0.30957 | 0.97123 | 27-03-2026 13:50 | 215.772 | 219.036 | 1084 | 36.506 | 39.099 | -2.593 | 234.5937 | 38.1 | 38.5398 | -0.43984 | 0.9851 | 27-03-2026 13:50 | 353.2125 | 425.4132 | -72.2007 | 2552.4791 | 362.9 | 419.3298 | -56.4298 | 9.6875
27-03-2026 13:40 | 986 | 51.09 | 327.363 | 332.991 | 1484.5 | 55.4985 | 58.1973 | -2.6988 | 349.1836 | 55.3 | 57.365 | -2.065 | 0.9831 | 27-03-2026 13:40 | 331.853 | 337.661 | 1500.8 | 56.2768 | 58.1973 | -1.9204 | 349.1836 | 60.9 | 57.365 | 3.535 | 0.9828 | 27-03-2026 13:40 | 325.064 | 334.072 | 1471.6 | 55.6787 | 58.1973 | -2.5186 | 349.1836 | 55.5 | 57.365 | -1.865 | 0.97304 | 27-03-2026 13:40 | 326.831 | 332.551 | 1484.8 | 55.4252 | 58.1973 | -2.7721 | 349.1836 | 56.7 | 57.365 | -0.66504 | 0.9828 | 27-03-2026 13:40 | 244.988 | 248.896 | 1105.1 | 41.4827 | 43.1091 | -1.6264 | 258.6545 | 42.4 | 42.4926 | -0.092622 | 0.9843 | 27-03-2026 13:40 | 241.493 | 245.801 | 1099 | 40.9668 | 43.1091 | -2.1422 | 258.6545 | 41.9 | 42.4926 | -0.59262 | 0.98247 | 27-03-2026 13:40 | 241.365 | 246.266 | 1097.2 | 41.0443 | 43.1091 | -2.0647 | 258.6545 | 41.2 | 42.4926 | -1.2926 | 0.9801 | 27-03-2026 13:40 | 242.797 | 249.98 | 1106.5 | 41.6633 | 43.1091 | -1.4457 | 258.6545 | 41.5 | 42.4926 | -0.99262 | 0.97127 | 27-03-2026 13:40 | 229.368 | 232.979 | 1045.9 | 38.8298 | 41.013 | -2.1831 | 246.0777 | 39.2 | 40.4265 | -1.2265 | 0.9845 | 27-03-2026 13:40 | 426.8662 | 446.2383 | -19.3722 | 2677.43 | 434.6 | 439.8571 | -5.2571 | 7.7338
27-03-2026 13:30 | 1027 | 50.8 | 342.18 | 348.098 | 1429.2 | 58.0163 | 60.6849 | -2.6686 | 364.1096 | 54.5 | 59.8171 | -5.3171 | 0.983 | 27-03-2026 13:30 | 348.579 | 354.679 | 1439.9 | 59.1132 | 60.6849 | -1.5718 | 364.1096 | 51.9 | 59.8171 | -7.9171 | 0.9828 | 27-03-2026 13:30 | 339.302 | 349.038 | 1416.1 | 58.173 | 60.6849 | -2.5119 | 364.1096 | 55.7 | 59.8171 | -4.1171 | 0.97211 | 27-03-2026 13:30 | 342.828 | 348.863 | 1428.1 | 58.1438 | 60.6849 | -2.5411 | 364.1096 | 55.3 | 59.8171 | -4.5171 | 0.9827 | 27-03-2026 13:30 | 255.78 | 259.886 | 1062.7 | 43.3143 | 44.9518 | -1.6375 | 269.7108 | 41.4 | 44.309 | -2.909 | 0.9842 | 27-03-2026 13:30 | 253.199 | 258.479 | 1057.1 | 43.0798 | 44.9518 | -1.872 | 269.7108 | 40.9 | 44.309 | -3.409 | 0.97957 | 27-03-2026 13:30 | 252.852 | 257.869 | 1056 | 42.9782 | 44.9518 | -1.9736 | 269.7108 | 40.9 | 44.309 | -3.409 | 0.98054 | 27-03-2026 13:30 | 255.048 | 262.536 | 1065 | 43.756 | 44.9518 | -1.1958 | 269.7108 | 41.2 | 44.309 | -3.109 | 0.97148 | 27-03-2026 13:30 | 241.206 | 245.004 | 1006.7 | 40.834 | 42.7661 | -1.9321 | 256.5965 | 39 | 42.1545 | -3.1545 | 0.9845 | 27-03-2026 13:30 | 447.4087 | 465.3131 | -17.9044 | 2791.8783 | 420.8 | 458.6591 | -37.8591 | -26.6087
27-03-2026 13:20 | 996 | 50.23 | 330.114 | 335.857 | 1374.7 | 55.9762 | 58.9822 | -3.0061 | 353.8934 | 55.8 | 58.1388 | -2.3388 | 0.9829 | 27-03-2026 13:20 | 335.858 | 341.771 | 1388 | 56.9618 | 58.9822 | -2.0204 | 353.8934 | 57.6 | 58.1388 | -0.53878 | 0.9827 | 27-03-2026 13:20 | 327.61 | 337.034 | 1360.4 | 56.1723 | 58.9822 | -2.8099 | 353.8934 | 54.6 | 58.1388 | -3.5388 | 0.97204 | 27-03-2026 13:20 | 331.042 | 336.801 | 1372.8 | 56.1335 | 58.9822 | -2.8487 | 353.8934 | 55.3 | 58.1388 | -2.8388 | 0.9829 | 27-03-2026 13:20 | 246.095 | 250.071 | 1021.3 | 41.6785 | 43.6905 | -2.012 | 262.1432 | 41.1 | 43.0658 | -1.9658 | 0.9841 | 27-03-2026 13:20 | 244.157 | 248.835 | 1016.2 | 41.4725 | 43.6905 | -2.218 | 262.1432 | 40.7 | 43.0658 | -2.3658 | 0.9812 | 27-03-2026 13:20 | 243.311 | 248.21 | 1015.1 | 41.3683 | 43.6905 | -2.3222 | 262.1432 | 40.5 | 43.0658 | -2.5658 | 0.98026 | 27-03-2026 13:20 | 245.467 | 252.752 | 1023.8 | 42.1253 | 43.6905 | -1.5652 | 262.1432 | 40.7 | 43.0658 | -2.3658 | 0.97118 | 27-03-2026 13:20 | 232.511 | 236.148 | 967.7 | 39.358 | 41.5661 | -2.2081 | 249.3968 | 39.2 | 40.9717 | -1.7717 | 0.9846 | 27-03-2026 13:20 | 431.2465 | 452.2572 | -21.0107 | 2713.5433 | 425.5 | 445.7899 | -20.2899 | -5.7465
27-03-2026 13:10 | 1039 | 50.51 | 345.025 | 351.063 | 1318.9 | 58.5105 | 61.4625 | -2.952 | 368.7751 | 56.8 | 60.5836 | -3.7836 | 0.9828 | 27-03-2026 13:10 | 350.002 | 356.272 | 1330.4 | 59.3787 | 61.4625 | -2.0838 | 368.7751 | 57.6 | 60.5836 | -2.9836 | 0.9824 | 27-03-2026 13:10 | 339.961 | 349.75 | 1305.8 | 58.2917 | 61.4625 | -3.1708 | 368.7751 | 56.5 | 60.5836 | -4.0836 | 0.97201 | 27-03-2026 13:10 | 343.987 | 350.114 | 1317.5 | 58.3523 | 61.4625 | -3.1102 | 368.7751 | 56.9 | 60.5836 | -3.6836 | 0.9825 | 27-03-2026 13:10 | 255.729 | 259.861 | 980.2 | 43.3102 | 45.5278 | -2.2176 | 273.1667 | 42.6 | 44.8767 | -2.2767 | 0.9841 | 27-03-2026 13:10 | 252.781 | 257.733 | 975.5 | 42.9555 | 45.5278 | -2.5723 | 273.1667 | 42.1 | 44.8767 | -2.7767 | 0.98079 | 27-03-2026 13:10 | 252.503 | 257.586 | 974.6 | 42.931 | 45.5278 | -2.5968 | 273.1667 | 42.1 | 44.8767 | -2.7767 | 0.98027 | 27-03-2026 13:10 | 253.65 | 261.298 | 983.1 | 43.5497 | 45.5278 | -1.9781 | 273.1667 | 42.3 | 44.8767 | -2.5767 | 0.97073 | 27-03-2026 13:10 | 240.205 | 244.036 | 928.5 | 40.6727 | 43.3141 | -2.6414 | 259.8843 | 39.9 | 42.6947 | -2.7947 | 0.9843 | 27-03-2026 13:10 | 447.9522 | 471.2752 | -23.3231 | 2827.6515 | 436.8 | 464.536 | -27.736 | -11.1522
27-03-2026 13:00 | 1033 | 50.23 | 341.162 | 347.168 | 1262.1 | 57.8613 | 61.1733 | -3.312 | 367.04 | 57.2 | 60.2986 | -3.0986 | 0.9827 | 27-03-2026 13:00 | 345.318 | 351.504 | 1272.8 | 58.584 | 61.1733 | -2.5893 | 367.04 | 57.9 | 60.2986 | -2.3986 | 0.9824 | 27-03-2026 13:00 | 339.389 | 349.159 | 1249.3 | 58.1932 | 61.1733 | -2.9802 | 367.04 | 56.8 | 60.2986 | -3.4986 | 0.97202 | 27-03-2026 13:00 | 341.027 | 347.137 | 1260.6 | 57.8562 | 61.1733 | -3.3172 | 367.04 | 57.2 | 60.2986 | -3.0986 | 0.9824 | 27-03-2026 13:00 | 256.159 | 260.271 | 937.6 | 43.3785 | 45.3136 | -1.9351 | 271.8815 | 42.9 | 44.6656 | -1.7656 | 0.9842 | 27-03-2026 13:00 | 251.673 | 256.617 | 933.4 | 42.7695 | 45.3136 | -2.5441 | 271.8815 | 42.1 | 44.6656 | -2.5656 | 0.98073 | 27-03-2026 13:00 | 252.663 | 258.256 | 932.5 | 43.0427 | 45.3136 | -2.2709 | 271.8815 | 42.2 | 44.6656 | -2.4656 | 0.97834 | 27-03-2026 13:00 | 253.009 | 260.903 | 940.8 | 43.4838 | 45.3136 | -1.8297 | 271.8815 | 42.4 | 44.6656 | -2.2656 | 0.96974 | 27-03-2026 13:00 | 238.997 | 242.834 | 888.6 | 40.4723 | 43.1103 | -2.6379 | 258.6616 | 40.1 | 42.4938 | -2.3938 | 0.9842 | 27-03-2026 13:00 | 445.6415 | 469.0579 | -23.4164 | 2814.3476 | 438.8 | 462.3504 | -23.5504 | -6.8415
27-03-2026 12:50 | 1030 | 50.51 | 341.671 | 347.656 | 1204.9 | 57.9427 | 60.9301 | -2.9874 | 365.5807 | 58.6 | 60.0588 | -1.4588 | 0.98278 | 27-03-2026 12:50 | 345.845 | 352.627 | 1214.9 | 58.7712 | 60.9301 | -2.1589 | 365.5807 | 57.5 | 60.0588 | -2.5588 | 0.98077 | 27-03-2026 12:50 | 339.009 | 348.539 | 1192.5 | 58.0898 | 60.9301 | -2.8403 | 365.5807 | 57.3 | 60.0588 | -2.7588 | 0.97266 | 27-03-2026 12:50 | 341.178 | 347.29 | 1203.4 | 57.8817 | 60.9301 | -3.0484 | 365.5807 | 57.7 | 60.0588 | -2.3588 | 0.9824 | 27-03-2026 12:50 | 255.422 | 259.405 | 894.7 | 43.2342 | 45.1334 | -1.8993 | 270.8005 | 43.2 | 44.488 | -1.288 | 0.98465 | 27-03-2026 12:50 | 251.853 | 257.146 | 891.3 | 42.8577 | 45.1334 | -2.2758 | 270.8005 | 42.6 | 44.488 | -1.888 | 0.97942 | 27-03-2026 12:50 | 252.048 | 257.579 | 890.3 | 42.9298 | 45.1334 | -2.2036 | 270.8005 | 42.7 | 44.488 | -1.788 | 0.97853 | 27-03-2026 12:50 | 253.389 | 260.875 | 898.4 | 43.4792 | 45.1334 | -1.6543 | 270.8005 | 43.3 | 44.488 | -1.188 | 0.9713 | 27-03-2026 12:50 | 239.704 | 243.503 | 848.5 | 40.5838 | 42.9389 | -2.355 | 257.6331 | 40.4 | 42.3248 | -1.9248 | 0.9844 | 27-03-2026 12:50 | 445.77 | 467.193 | -21.423 | 2803.1579 | 443.3 | 460.5121 | -17.2121 | -2.47
27-03-2026 12:40 | 1048 | 50.8 | 348.678 | 354.78 | 1146.3 | 59.13 | 61.9258 | -2.7958 | 371.5549 | 58.9 | 61.0403 | -2.1403 | 0.9828 | 27-03-2026 12:40 | 351.832 | 358.026 | 1157.4 | 59.671 | 61.9258 | -2.2548 | 371.5549 | 57 | 61.0403 | -4.0403 | 0.9827 | 27-03-2026 12:40 | 344.829 | 354.706 | 1135.2 | 59.1177 | 61.9258 | -2.8082 | 371.5549 | 55.9 | 61.0403 | -5.1403 | 0.97215 | 27-03-2026 12:40 | 345.634 | 351.826 | 1145.7 | 58.6377 | 61.9258 | -3.2882 | 371.5549 | 57.2 | 61.0403 | -3.8403 | 0.9824 | 27-03-2026 12:40 | 259.264 | 263.453 | 851.5 | 43.9088 | 45.871 | -1.9621 | 275.2259 | 42.7 | 45.215 | -2.515 | 0.9841 | 27-03-2026 12:40 | 254.919 | 259.853 | 848.7 | 43.3088 | 45.871 | -2.5621 | 275.2259 | 42.2 | 45.215 | -3.015 | 0.98101 | 27-03-2026 12:40 | 255.73 | 261.162 | 847.6 | 43.527 | 45.871 | -2.344 | 275.2259 | 42.2 | 45.215 | -3.015 | 0.9792 | 27-03-2026 12:40 | 256.192 | 263.723 | 855.1 | 43.9538 | 45.871 | -1.9171 | 275.2259 | 41.9 | 45.215 | -3.315 | 0.97144 | 27-03-2026 12:40 | 241.785 | 245.642 | 808.1 | 40.9403 | 43.6406 | -2.7002 | 261.8433 | 39.6 | 43.0165 | -3.4165 | 0.9843 | 27-03-2026 12:40 | 452.1952 | 474.8277 | -22.6326 | 2848.9664 | 437.6 | 468.0377 | -30.4377 | -14.5952
27-03-2026 12:30 | 1034 | 50.8 | 338.325 | 344.361 | 1087.4 | 57.3935 | 61.0986 | -3.7051 | 366.5914 | 54.2 | 60.2249 | -6.0249 | 0.98247 | 27-03-2026 12:30 | 343.851 | 350.082 | 1100.4 | 58.347 | 61.0986 | -2.7516 | 366.5914 | 58 | 60.2249 | -2.2249 | 0.9822 | 27-03-2026 12:30 | 336.929 | 346.781 | 1079.3 | 57.7968 | 61.0986 | -3.3017 | 366.5914 | 56.7 | 60.2249 | -3.5249 | 0.97159 | 27-03-2026 12:30 | 339.919 | 346.009 | 1088.5 | 57.6682 | 61.0986 | -3.4304 | 366.5914 | 56.4 | 60.2249 | -3.8249 | 0.9824 | 27-03-2026 12:30 | 254.074 | 258.232 | 808.8 | 43.0387 | 45.2582 | -2.2195 | 271.5492 | 42.2 | 44.611 | -2.411 | 0.9839 | 27-03-2026 12:30 | 251.171 | 256.522 | 806.5 | 42.7537 | 45.2582 | -2.5045 | 271.5492 | 41.7 | 44.611 | -2.911 | 0.97914 | 27-03-2026 12:30 | 251.259 | 256.452 | 805.4 | 42.742 | 45.2582 | -2.5162 | 271.5492 | 41.7 | 44.611 | -2.911 | 0.97975 | 27-03-2026 12:30 | 252.832 | 260.387 | 813.2 | 43.3978 | 45.2582 | -1.8604 | 271.5492 | 42 | 44.611 | -2.611 | 0.97099 | 27-03-2026 12:30 | 238.837 | 242.721 | 768.5 | 40.4535 | 43.0576 | -2.6041 | 258.3454 | 40.3 | 42.4418 | -2.1418 | 0.984 | 27-03-2026 12:30 | 443.5912 | 468.4846 | -24.8934 | 2810.9077 | 433.2 | 461.7853 | -28.5853 | -10.3912
27-03-2026 12:20 | 1043 | 50.51 | 346.79 | 352.895 | 1033.2 | 58.8158 | 61.6991 | -2.8833 | 370.1948 | 57.2 | 60.8168 | -3.6168 | 0.9827 | 27-03-2026 12:20 | 351.145 | 357.363 | 1042.4 | 59.5605 | 61.6991 | -2.1386 | 370.1948 | 57.7 | 60.8168 | -3.1168 | 0.9826 | 27-03-2026 12:20 | 342.128 | 352.202 | 1022.6 | 58.7003 | 61.6991 | -2.9988 | 370.1948 | 56.8 | 60.8168 | -4.0168 | 0.9714 | 27-03-2026 12:20 | 346.022 | 352.185 | 1032.1 | 58.6975 | 61.6991 | -3.0016 | 370.1948 | 57.1 | 60.8168 | -3.7168 | 0.9825 | 27-03-2026 12:20 | 256.949 | 261.074 | 766.6 | 43.5123 | 45.7031 | -2.1907 | 274.2184 | 43.4 | 45.0495 | -1.6495 | 0.9842 | 27-03-2026 12:20 | 254.715 | 259.161 | 764.8 | 43.1935 | 45.7031 | -2.5096 | 274.2184 | 42.9 | 45.0495 | -2.1495 | 0.98284 | 27-03-2026 12:20 | 253.503 | 258.513 | 763.7 | 43.0855 | 45.7031 | -2.6176 | 274.2184 | 43 | 45.0495 | -2.0495 | 0.98062 | 27-03-2026 12:20 | 254.504 | 262.248 | 771.2 | 43.708 | 45.7031 | -1.9951 | 274.2184 | 43.2 | 45.0495 | -1.8495 | 0.97047 | 27-03-2026 12:20 | 242.495 | 246.338 | 728.2 | 41.0563 | 43.4808 | -2.4245 | 260.8848 | 40.1 | 42.859 | -2.759 | 0.9844 | 27-03-2026 12:20 | 450.3298 | 473.0896 | -22.7598 | 2838.5375 | 441.4 | 466.3244 | -24.9244 | -8.9298
27-03-2026 12:10 | 1011 | 51.09 | 337.687 | 343.527 | 976 | 57.2545 | 59.6729 | -2.4184 | 358.0371 | 56.7 | 58.8195 | -2.1195 | 0.983 | 27-03-2026 12:10 | 342.2 | 348.115 | 984.7 | 58.0192 | 59.6729 | -1.6537 | 358.0371 | 59.1 | 58.8195 | 0.28047 | 0.98301 | 27-03-2026 12:10 | 334.774 | 343.998 | 965.8 | 57.333 | 59.6729 | -2.3399 | 358.0371 | 57 | 58.8195 | -1.8195 | 0.97319 | 27-03-2026 12:10 | 337.427 | 343.332 | 975 | 57.222 | 59.6729 | -2.4509 | 358.0371 | 57.7 | 58.8195 | -1.1195 | 0.9828 | 27-03-2026 12:10 | 252.435 | 256.435 | 723.2 | 42.7392 | 44.2021 | -1.4629 | 265.2127 | 42.3 | 43.57 | -1.27 | 0.9844 | 27-03-2026 12:10 | 249.081 | 253.866 | 721.9 | 42.311 | 44.2021 | -1.8911 | 265.2127 | 41.8 | 43.57 | -1.77 | 0.98115 | 27-03-2026 12:10 | 250.028 | 255 | 720.7 | 42.5 | 44.2021 | -1.7021 | 265.2127 | 41.8 | 43.57 | -1.77 | 0.9805 | 27-03-2026 12:10 | 250.616 | 258.392 | 728 | 43.0653 | 44.2021 | -1.1368 | 265.2127 | 42.1 | 43.57 | -1.47 | 0.96991 | 27-03-2026 12:10 | 236.487 | 240.19 | 688.1 | 40.0317 | 42.0528 | -2.0212 | 252.317 | 40 | 41.4515 | -1.4515 | 0.98458 | 27-03-2026 12:10 | 440.4758 | 457.5527 | -17.0769 | 2745.3161 | 438.5 | 451.0097 | -12.5097 | -1.9758
27-03-2026 12:00 | 1008 | 50.8 | 338.85 | 344.745 | 919.3 | 57.4575 | 59.5622 | -2.1047 | 357.3734 | 60 | 58.7105 | 1.2895 | 0.9829 | 27-03-2026 12:00 | 339.313 | 343.834 | 925.6 | 57.3057 | 59.5622 | -2.2566 | 357.3734 | 56.7 | 58.7105 | -2.0105 | 0.98685 | 27-03-2026 12:00 | 334.751 | 344.369 | 908.8 | 57.3948 | 59.5622 | -2.1674 | 357.3734 | 55.4 | 58.7105 | -3.3105 | 0.97207 | 27-03-2026 12:00 | 335.718 | 341.593 | 917.3 | 56.9322 | 59.5622 | -2.6301 | 357.3734 | 55.9 | 58.7105 | -2.8105 | 0.9828 | 27-03-2026 12:00 | 252.955 | 257.016 | 680.9 | 42.836 | 44.1202 | -1.2842 | 264.7211 | 42.3 | 43.4893 | -1.1893 | 0.9842 | 27-03-2026 12:00 | 249.586 | 254.169 | 680.1 | 42.3615 | 44.1202 | -1.7587 | 264.7211 | 41.9 | 43.4893 | -1.5893 | 0.98197 | 27-03-2026 12:00 | 249.973 | 255.077 | 678.9 | 42.5128 | 44.1202 | -1.6073 | 264.7211 | 41.9 | 43.4893 | -1.5893 | 0.97999 | 27-03-2026 12:00 | 252.72 | 260.472 | 685.9 | 43.412 | 44.1202 | -0.70818 | 264.7211 | 42.2 | 43.4893 | -1.2893 | 0.97024 | 27-03-2026 12:00 | 239.234 | 243.001 | 648.1 | 40.5002 | 41.9749 | -1.4747 | 251.8493 | 39.9 | 41.3746 | -1.4746 | 0.9845 | 27-03-2026 12:00 | 440.7127 | 456.7045 | -15.9919 | 2740.2272 | 436.2 | 450.1737 | -13.9737 | -4.5127
27-03-2026 11:50 | 1027 | 50.51 | 339.825 | 345.737 | 859.3 | 57.6228 | 60.7526 | -3.1298 | 364.5159 | 52.2 | 59.8839 | -7.6839 | 0.9829 | 27-03-2026 11:50 | 347.268 | 353.417 | 868.9 | 58.9028 | 60.7526 | -1.8498 | 364.5159 | 55.7 | 59.8839 | -4.1839 | 0.9826 | 27-03-2026 11:50 | 334.927 | 344.064 | 853.4 | 57.344 | 60.7526 | -3.4086 | 364.5159 | 55.5 | 59.8839 | -4.3839 | 0.97344 | 27-03-2026 11:50 | 339.109 | 345.079 | 861.4 | 57.5132 | 60.7526 | -3.2395 | 364.5159 | 55.7 | 59.8839 | -4.1839 | 0.9827 | 27-03-2026 11:50 | 252.97 | 256.983 | 638.6 | 42.8305 | 45.002 | -2.1715 | 270.0118 | 41.2 | 44.3584 | -3.1584 | 0.98438 | 27-03-2026 11:50 | 250.376 | 255.336 | 638.2 | 42.556 | 45.002 | -2.446 | 270.0118 | 40.7 | 44.3584 | -3.6584 | 0.98057 | 27-03-2026 11:50 | 251.735 | 256.93 | 637 | 42.8217 | 45.002 | -2.1803 | 270.0118 | 40.9 | 44.3584 | -3.4584 | 0.97978 | 27-03-2026 11:50 | 255.455 | 263.353 | 643.7 | 43.8922 | 45.002 | -1.1098 | 270.0118 | 41.2 | 44.3584 | -3.1584 | 0.97001 | 27-03-2026 11:50 | 241.044 | 244.864 | 608.2 | 40.8107 | 42.8138 | -2.0031 | 256.8828 | 38.8 | 42.2016 | -3.4016 | 0.9844 | 27-03-2026 11:50 | 444.2938 | 465.8322 | -21.5384 | 2794.9933 | 421.9 | 459.1708 | -37.2708 | -22.3938
27-03-2026 11:40 | 994 | 50.51 | 328.732 | 334.451 | 807.1 | 55.7418 | 58.8005 | -3.0587 | 352.8031 | 54.1 | 57.9597 | -3.8597 | 0.9829 | 27-03-2026 11:40 | 334.09 | 339.972 | 813.2 | 56.662 | 58.8005 | -2.1385 | 352.8031 | 54.6 | 57.9597 | -3.3597 | 0.9827 | 27-03-2026 11:40 | 324.869 | 333.985 | 797.9 | 55.6642 | 58.8005 | -3.1364 | 352.8031 | 52.6 | 57.9597 | -5.3597 | 0.97271 | 27-03-2026 11:40 | 329.291 | 335.088 | 805.7 | 55.848 | 58.8005 | -2.9525 | 352.8031 | 53.1 | 57.9597 | -4.8597 | 0.9827 | 27-03-2026 11:40 | 245.109 | 249.044 | 597.4 | 41.5073 | 43.5559 | -2.0486 | 261.3356 | 39.7 | 42.9331 | -3.2331 | 0.9842 | 27-03-2026 11:40 | 242.753 | 247.345 | 597.5 | 41.2242 | 43.5559 | -2.3318 | 261.3356 | 39.3 | 42.9331 | -3.6331 | 0.98143 | 27-03-2026 11:40 | 243.01 | 247.831 | 596.1 | 41.3052 | 43.5559 | -2.2508 | 261.3356 | 39.9 | 42.9331 | -3.0331 | 0.98055 | 27-03-2026 11:40 | 244.601 | 251.682 | 602.5 | 41.947 | 43.5559 | -1.6089 | 261.3356 | 40.1 | 42.9331 | -2.8331 | 0.97187 | 27-03-2026 11:40 | 230.762 | 234.419 | 569.4 | 39.0698 | 41.4381 | -2.3682 | 248.6285 | 37.9 | 40.8455 | -2.9455 | 0.9844 | 27-03-2026 11:40 | 428.9695 | 450.8639 | -21.8944 | 2705.1834 | 411.3 | 444.4166 | -33.1166 | -17.6695
27-03-2026 11:30 | 957 | 50.8 | 322.202 | 327.774 | 753 | 54.629 | 56.5487 | -1.9197 | 339.292 | 55.5 | 55.74 | -0.24003 | 0.983 | 27-03-2026 11:30 | 323.466 | 329.094 | 758.6 | 54.849 | 56.5487 | -1.6997 | 339.292 | 52.2 | 55.74 | -3.54 | 0.9829 | 27-03-2026 11:30 | 317.087 | 325.787 | 745.3 | 54.2978 | 56.5487 | -2.2508 | 339.292 | 51.9 | 55.74 | -3.84 | 0.9733 | 27-03-2026 11:30 | 317.038 | 322.587 | 752.6 | 53.7645 | 56.5487 | -2.7842 | 339.292 | 53.1 | 55.74 | -2.64 | 0.9828 | 27-03-2026 11:30 | 238.098 | 241.822 | 557.7 | 40.3037 | 41.8879 | -1.5842 | 251.3274 | 39.5 | 41.2889 | -1.7889 | 0.9846 | 27-03-2026 11:30 | 233.803 | 238.111 | 558.2 | 39.6852 | 41.8879 | -2.2027 | 251.3274 | 39.2 | 41.2889 | -2.0889 | 0.98191 | 27-03-2026 11:30 | 235.707 | 240.122 | 556.2 | 40.0203 | 41.8879 | -1.8676 | 251.3274 | 38.6 | 41.2889 | -2.6889 | 0.98161 | 27-03-2026 11:30 | 236.396 | 243.381 | 562.4 | 40.5635 | 41.8879 | -1.3244 | 251.3274 | 38.8 | 41.2889 | -2.4889 | 0.9713 | 27-03-2026 11:30 | 222.094 | 225.522 | 531.5 | 37.587 | 39.8512 | -2.2642 | 239.1069 | 36.7 | 39.2813 | -2.5813 | 0.9848 | 27-03-2026 11:30 | 415.7 | 433.5975 | -17.8975 | 2601.5847 | 405.5 | 427.397 | -21.897 | -10.2
27-03-2026 11:20 | 964 | 51.09 | 323.513 | 329.074 | 697.5 | 54.8457 | 56.8987 | -2.0531 | 341.3925 | 50.6 | 56.0851 | -5.4851 | 0.9831 | 27-03-2026 11:20 | 328.799 | 334.205 | 706.4 | 55.7008 | 56.8987 | -1.1979 | 341.3925 | 54.7 | 56.0851 | -1.3851 | 0.98382 | 27-03-2026 11:20 | 315.93 | 324.778 | 693.4 | 54.1297 | 56.8987 | -2.7691 | 341.3925 | 53.1 | 56.0851 | -2.9851 | 0.97276 | 27-03-2026 11:20 | 320.836 | 326.451 | 699.5 | 54.4085 | 56.8987 | -2.4902 | 341.3925 | 52.5 | 56.0851 | -3.5851 | 0.9828 | 27-03-2026 11:20 | 237.093 | 240.826 | 518.2 | 40.1377 | 42.1472 | -2.0095 | 252.8833 | 39.8 | 41.5445 | -1.7445 | 0.9845 | 27-03-2026 11:20 | 236.224 | 240.413 | 519 | 40.0688 | 42.1472 | -2.0784 | 252.8833 | 39.4 | 41.5445 | -2.1445 | 0.98258 | 27-03-2026 11:20 | 235.167 | 239.529 | 517.6 | 39.9215 | 42.1472 | -2.2257 | 252.8833 | 39.5 | 41.5445 | -2.0445 | 0.98179 | 27-03-2026 11:20 | 236.41 | 243.632 | 523.6 | 40.6053 | 42.1472 | -1.5419 | 252.8833 | 39.8 | 41.5445 | -1.7445 | 0.97036 | 27-03-2026 11:20 | 224.606 | 228.096 | 494.8 | 38.016 | 40.0979 | -2.0819 | 240.5871 | 37.6 | 39.5245 | -1.9245 | 0.9847 | 27-03-2026 11:20 | 417.834 | 436.2817 | -18.4477 | 2617.6901 | 407 | 430.0429 | -23.0429 | -10.834
27-03-2026 11:10 | 942 | 51.09 | 315.297 | 320.619 | 646.9 | 53.4365 | 55.6002 | -2.1637 | 333.6013 | 54 | 54.8051 | -0.80514 | 0.9834 | 27-03-2026 11:10 | 316.152 | 321.62 | 651.7 | 53.6033 | 55.6002 | -1.9969 | 333.6013 | 53 | 54.8051 | -1.8051 | 0.983 | 27-03-2026 11:10 | 313.082 | 321.594 | 640.3 | 53.599 | 55.6002 | -2.0012 | 333.6013 | 51.3 | 54.8051 | -3.5051 | 0.97353 | 27-03-2026 11:10 | 315.579 | 321.004 | 647 | 53.5007 | 55.6002 | -2.0996 | 333.6013 | 51.7 | 54.8051 | -3.1051 | 0.9831 | 27-03-2026 11:10 | 236.378 | 240.075 | 478.4 | 40.0125 | 41.1854 | -1.1729 | 247.1121 | 38.1 | 40.5964 | -2.4964 | 0.9846 | 27-03-2026 11:10 | 233.748 | 238.043 | 479.6 | 39.6738 | 41.1854 | -1.5115 | 247.1121 | 37.8 | 40.5964 | -2.7964 | 0.98196 | 27-03-2026 11:10 | 235.358 | 239.53 | 478.1 | 39.9217 | 41.1854 | -1.2637 | 247.1121 | 38.4 | 40.5964 | -2.1964 | 0.98258 | 27-03-2026 11:10 | 237.172 | 244.492 | 483.8 | 40.7487 | 41.1854 | -0.43668 | 247.1121 | 38.6 | 40.5964 | -1.9964 | 0.97006 | 27-03-2026 11:10 | 222.841 | 226.239 | 457.2 | 37.7065 | 39.1828 | -1.4763 | 235.0966 | 36.5 | 38.6224 | -2.1224 | 0.98498 | 27-03-2026 11:10 | 412.2027 | 426.3251 | -14.1224 | 2557.9503 | 399.4 | 420.2286 | -20.8286 | -12.8027
27-03-2026 11:00 | 897 | 51.37 | 300.764 | 305.748 | 592.9 | 50.958 | 52.8871 | -1.9291 | 317.3224 | 49.7 | 52.1308 | -2.4308 | 0.9837 | 27-03-2026 11:00 | 305.299 | 310.389 | 598.7 | 51.7315 | 52.8871 | -1.1556 | 317.3224 | 50.3 | 52.1308 | -1.8308 | 0.9836 | 27-03-2026 11:00 | 301.219 | 309.259 | 589 | 51.5432 | 52.8871 | -1.3439 | 317.3224 | 50.4 | 52.1308 | -1.7308 | 0.974 | 27-03-2026 11:00 | 303.236 | 308.323 | 595.3 | 51.3872 | 52.8871 | -1.4999 | 317.3224 | 51.1 | 52.1308 | -1.0308 | 0.9835 | 27-03-2026 11:00 | 226.963 | 230.489 | 440.3 | 38.4148 | 39.1756 | -0.76077 | 235.0536 | 37.8 | 38.6154 | -0.81539 | 0.9847 | 27-03-2026 11:00 | 224.94 | 228.902 | 441.8 | 38.1503 | 39.1756 | -1.0253 | 235.0536 | 37.7 | 38.6154 | -0.91539 | 0.98269 | 27-03-2026 11:00 | 225.304 | 229.541 | 439.7 | 38.2568 | 39.1756 | -0.91877 | 235.0536 | 37 | 38.6154 | -1.6154 | 0.98154 | 27-03-2026 11:00 | 227.13 | 233.894 | 445.2 | 38.9823 | 39.1756 | -0.19327 | 235.0536 | 37.8 | 38.6154 | -0.81539 | 0.97108 | 27-03-2026 11:00 | 214.767 | 217.847 | 420.7 | 36.3078 | 37.2707 | -0.9629 | 223.6244 | 35.9 | 36.7378 | -0.83776 | 0.98586 | 27-03-2026 11:00 | 395.732 | 405.5214 | -9.7894 | 2433.1283 | 387.7 | 399.7224 | -12.0224 | -8.032
27-03-2026 10:50 | 905 | 51.09 | 304.887 | 309.876 | 543.2 | 51.646 | 53.4164 | -1.7704 | 320.4981 | 49.4 | 52.6525 | -3.2525 | 0.9839 | 27-03-2026 10:50 | 307.895 | 313.061 | 548.4 | 52.1768 | 53.4164 | -1.2395 | 320.4981 | 51.1 | 52.6525 | -1.5525 | 0.9835 | 27-03-2026 10:50 | 302.105 | 310.114 | 538.6 | 51.6857 | 53.4164 | -1.7307 | 320.4981 | 49.6 | 52.6525 | -3.0525 | 0.97417 | 27-03-2026 10:50 | 305.361 | 310.484 | 544.2 | 51.7473 | 53.4164 | -1.669 | 320.4981 | 49.8 | 52.6525 | -2.8525 | 0.9835 | 27-03-2026 10:50 | 226.391 | 229.885 | 402.5 | 38.3142 | 39.5677 | -1.2535 | 237.406 | 37.2 | 39.0018 | -1.8018 | 0.9848 | 27-03-2026 10:50 | 225.981 | 229.724 | 404.1 | 38.2873 | 39.5677 | -1.2803 | 237.406 | 36.9 | 39.0018 | -2.1018 | 0.98371 | 27-03-2026 10:50 | 224.819 | 228.824 | 402.7 | 38.1373 | 39.5677 | -1.4303 | 237.406 | 36.8 | 39.0018 | -2.2018 | 0.9825 | 27-03-2026 10:50 | 226.364 | 233.27 | 407.4 | 38.8783 | 39.5677 | -0.68933 | 237.406 | 36.7 | 39.0018 | -2.3018 | 0.97039 | 27-03-2026 10:50 | 215.255 | 218.489 | 384.8 | 36.4148 | 37.6437 | -1.2289 | 225.8624 | 34.5 | 37.1054 | -2.6054 | 0.9852 | 27-03-2026 10:50 | 397.2878 | 409.5798 | -12.292 | 2457.4788 | 382 | 403.7228 | -21.7228 | -15.2878
27-03-2026 10:40 | 863 | 50.51 | 293.065 | 297.83 | 493.8 | 49.6383 | 51.0512 | -1.4128 | 306.3069 | 47.9 | 50.3211 | -2.4211 | 0.984 | 27-03-2026 10:40 | 295.539 | 300.436 | 497.3 | 50.0727 | 51.0512 | -0.97849 | 306.3069 | 48.3 | 50.3211 | -2.0211 | 0.9837 | 27-03-2026 10:40 | 291.552 | 299.033 | 489 | 49.8388 | 51.0512 | -1.2123 | 306.3069 | 47.4 | 50.3211 | -2.9211 | 0.97498 | 27-03-2026 10:40 | 296.662 | 301.547 | 494.4 | 50.2578 | 51.0512 | -0.79332 | 306.3069 | 48 | 50.3211 | -2.3211 | 0.9838 | 27-03-2026 10:40 | 219.35 | 222.69 | 365.3 | 37.115 | 37.8157 | -0.70067 | 226.894 | 35.5 | 37.2749 | -1.7749 | 0.985 | 27-03-2026 10:40 | 220.323 | 224.096 | 367.2 | 37.3493 | 37.8157 | -0.46634 | 226.894 | 35.5 | 37.2749 | -1.7749 | 0.98316 | 27-03-2026 10:40 | 218.716 | 222.626 | 365.9 | 37.1043 | 37.8157 | -0.71134 | 226.894 | 35.8 | 37.2749 | -1.4749 | 0.98244 | 27-03-2026 10:40 | 221.533 | 228.116 | 370.7 | 38.0193 | 37.8157 | 0.20366 | 226.894 | 36.5 | 37.2749 | -0.77491 | 0.97114 | 27-03-2026 10:40 | 209.64 | 212.725 | 350.3 | 35.4542 | 35.9769 | -0.52276 | 215.8616 | 34.4 | 35.4625 | -1.0625 | 0.9855 | 27-03-2026 10:40 | 384.8498 | 391.4442 | -6.5944 | 2348.6653 | 369.3 | 385.8466 | -16.5466 | -15.5498
27-03-2026 10:30 | 843 | 50.51 | 286.627 | 291.169 | 445.9 | 48.5282 | 49.868 | -1.3399 | 299.2083 | 46.5 | 49.1549 | -2.6549 | 0.9844 | 27-03-2026 10:30 | 289.376 | 294.452 | 449 | 49.0753 | 49.868 | -0.79271 | 299.2083 | 47.3 | 49.1549 | -1.8549 | 0.98276 | 27-03-2026 10:30 | 283.527 | 290.462 | 441.6 | 48.4103 | 49.868 | -1.4577 | 299.2083 | 46.2 | 49.1549 | -2.9549 | 0.97612 | 27-03-2026 10:30 | 286.935 | 291.63 | 446.4 | 48.605 | 49.868 | -1.263 | 299.2083 | 47.3 | 49.1549 | -1.8549 | 0.9839 | 27-03-2026 10:30 | 212.655 | 215.761 | 329.8 | 35.9602 | 36.9393 | -0.97913 | 221.6358 | 35.1 | 36.4111 | -1.3111 | 0.9856 | 27-03-2026 10:30 | 212.314 | 215.65 | 331.7 | 35.9417 | 36.9393 | -0.99763 | 221.6358 | 35 | 36.4111 | -1.4111 | 0.98453 | 27-03-2026 10:30 | 211.14 | 214.631 | 330.1 | 35.7718 | 36.9393 | -1.1675 | 221.6358 | 34.4 | 36.4111 | -2.0111 | 0.98373 | 27-03-2026 10:30 | 211.135 | 217.135 | 334.2 | 36.1892 | 36.9393 | -0.75013 | 221.6358 | 34 | 36.4111 | -2.4111 | 0.97237 | 27-03-2026 10:30 | 200.952 | 203.909 | 315.9 | 33.9848 | 35.1432 | -1.1583 | 210.859 | 32.7 | 34.6406 | -1.9406 | 0.9855 | 27-03-2026 10:30 | 372.4665 | 382.3725 | -9.906 | 2294.235 | 358.5 | 376.9046 | -18.4046 | -13.9665
27-03-2026 10:20 | 805 | 50.8 | 277.209 | 281.578 | 399.4 | 46.9297 | 47.5671 | -0.6374 | 285.4024 | 45.7 | 46.8869 | -1.1869 | 0.98448 | 27-03-2026 10:20 | 278.865 | 283.996 | 401.7 | 47.3327 | 47.5671 | -0.2344 | 285.4024 | 44.8 | 46.8869 | -2.0869 | 0.98193 | 27-03-2026 10:20 | 273.643 | 280.349 | 395.4 | 46.7248 | 47.5671 | -0.84223 | 285.4024 | 45.1 | 46.8869 | -1.7869 | 0.97608 | 27-03-2026 10:20 | 276.259 | 280.694 | 399.1 | 46.7823 | 47.5671 | -0.78473 | 285.4024 | 44.9 | 46.8869 | -1.9869 | 0.9842 | 27-03-2026 10:20 | 204.596 | 207.606 | 294.7 | 34.601 | 35.2349 | -0.63386 | 211.4092 | 33.3 | 34.731 | -1.431 | 0.9855 | 27-03-2026 10:20 | 204.398 | 207.373 | 296.7 | 34.5622 | 35.2349 | -0.6727 | 211.4092 | 33.2 | 34.731 | -1.531 | 0.98565 | 27-03-2026 10:20 | 203.208 | 206.459 | 295.7 | 34.4098 | 35.2349 | -0.82503 | 211.4092 | 33.2 | 34.731 | -1.531 | 0.98425 | 27-03-2026 10:20 | 204.101 | 209.917 | 300.2 | 34.9862 | 35.2349 | -0.2487 | 211.4092 | 33.3 | 34.731 | -1.431 | 0.97229 | 27-03-2026 10:20 | 193.434 | 196.28 | 283.2 | 32.7133 | 33.5216 | -0.80827 | 201.1296 | 31.6 | 33.0422 | -1.4422 | 0.9855 | 27-03-2026 10:20 | 359.042 | 364.7293 | -5.6873 | 2188.3759 | 345.1 | 359.5137 | -14.4137 | -13.942
27-03-2026 10:10 | 768 | 50.51 | 266.815 | 271.425 | 353.7 | 45.2375 | 45.4314 | -0.19389 | 272.5883 | 43.8 | 44.7817 | -0.98172 | 0.98302 | 27-03-2026 10:10 | 270.504 | 274.758 | 356.9 | 45.793 | 45.4314 | 0.36161 | 272.5883 | 44.3 | 44.7817 | -0.48172 | 0.98452 | 27-03-2026 10:10 | 264.695 | 271.009 | 350.3 | 45.1682 | 45.4314 | -0.26322 | 272.5883 | 42.9 | 44.7817 | -1.8817 | 0.9767 | 27-03-2026 10:10 | 267.234 | 271.414 | 354.2 | 45.2357 | 45.4314 | -0.19572 | 272.5883 | 43.4 | 44.7817 | -1.3817 | 0.9846 | 27-03-2026 10:10 | 198.118 | 200.951 | 261.4 | 33.4918 | 33.6529 | -0.16104 | 201.9173 | 32.5 | 33.1716 | -0.67164 | 0.9859 | 27-03-2026 10:10 | 197.622 | 200.614 | 263.5 | 33.4357 | 33.6529 | -0.21721 | 201.9173 | 32.5 | 33.1716 | -0.67164 | 0.98509 | 27-03-2026 10:10 | 197.155 | 200.18 | 262.5 | 33.3633 | 33.6529 | -0.28954 | 201.9173 | 32.3 | 33.1716 | -0.87164 | 0.98489 | 27-03-2026 10:10 | 197.653 | 203.316 | 266.9 | 33.886 | 33.6529 | 0.23312 | 201.9173 | 32.5 | 33.1716 | -0.67164 | 0.97215 | 27-03-2026 10:10 | 187.539 | 190.24 | 251.6 | 31.7067 | 32.0165 | -0.30988 | 192.0993 | 30.9 | 31.5587 | -0.65871 | 0.9858 | 27-03-2026 10:10 | 347.3178 | 348.3536 | -1.0358 | 2090.1216 | 335.1 | 343.3721 | -8.2721 | -12.2178
27-03-2026 10:00 | 746 | 50.8 | 255.105 | 259.7 | 309.9 | 43.2833 | 44.0808 | -0.79745 | 264.4847 | 41.7 | 43.4504 | -1.7504 | 0.98231 | 27-03-2026 10:00 | 259.081 | 263.053 | 312.6 | 43.8422 | 44.0808 | -0.23862 | 264.4847 | 42.1 | 43.4504 | -1.3504 | 0.9849 | 27-03-2026 10:00 | 253.805 | 259.517 | 307.4 | 43.2528 | 44.0808 | -0.82795 | 264.4847 | 41.2 | 43.4504 | -2.2504 | 0.97799 | 27-03-2026 10:00 | 257.811 | 261.79 | 310.8 | 43.6317 | 44.0808 | -0.44912 | 264.4847 | 42.3 | 43.4504 | -1.1504 | 0.9848 | 27-03-2026 10:00 | 189.405 | 192.075 | 228.9 | 32.0125 | 32.6524 | -0.63993 | 195.9146 | 30.8 | 32.1855 | -1.3855 | 0.9861 | 27-03-2026 10:00 | 190.415 | 193.137 | 231 | 32.1895 | 32.6524 | -0.46293 | 195.9146 | 31 | 32.1855 | -1.1855 | 0.98591 | 27-03-2026 10:00 | 188.832 | 191.513 | 230.2 | 31.9188 | 32.6524 | -0.7336 | 195.9146 | 30.7 | 32.1855 | -1.4855 | 0.986 | 27-03-2026 10:00 | 190.197 | 195.736 | 234.4 | 32.6227 | 32.6524 | -0.029765 | 195.9146 | 31 | 32.1855 | -1.1855 | 0.9717 | 27-03-2026 10:00 | 181.455 | 183.994 | 220.7 | 30.6657 | 31.0647 | -0.39908 | 186.3885 | 29.5 | 30.6205 | -1.1205 | 0.9862 | 27-03-2026 10:00 | 333.4192 | 337.9976 | -4.5784 | 2027.9856 | 320.3 | 333.1642 | -12.8642 | -13.1192
27-03-2026 09:50 | 707 | 51.09 | 223.201 | 226.026 | 268.2 | 37.671 | 41.7297 | -4.0587 | 250.3781 | 5.7 | 41.1329 | -35.4329 |  | 27-03-2026 09:50 | 206.323 | 209.803 | 270.5 | 34.9672 | 41.7297 | -6.7625 | 250.3781 | 6.3 | 41.1329 | -34.8329 |  | 27-03-2026 09:50 | 240.162 | 245.414 | 266.2 | 40.9023 | 41.7297 | -0.82735 | 250.3781 | 6.4 | 41.1329 | -34.7329 |  | 27-03-2026 09:50 | 243.304 | 247.034 | 268.5 | 41.1723 | 41.7297 | -0.55735 | 250.3781 | 5.8 | 41.1329 | -35.3329 |  | 27-03-2026 09:50 | 179.516 | 182.021 | 198.1 | 30.3368 | 30.9109 | -0.57404 | 185.4652 | 5.2 | 30.4688 | -25.2688 |  | 27-03-2026 09:50 | 180.593 | 183.179 | 200 | 30.5298 | 30.9109 | -0.38104 | 185.4652 | 5.3 | 30.4688 | -25.1688 |  | 27-03-2026 09:50 | 178.866 | 181.387 | 199.5 | 30.2312 | 30.9109 | -0.67971 | 185.4652 | 5.3 | 30.4688 | -25.1688 |  | 27-03-2026 09:50 | 180.24 | 185.552 | 203.4 | 30.9253 | 30.9109 | 0.01446 | 185.4652 | 6.9 | 30.4688 | -23.5688 |  | 27-03-2026 09:50 | 171.932 | 174.356 | 191.2 | 29.0593 | 29.4079 | -0.34853 | 176.4472 | 5.3 | 28.9873 | -23.6873 |  | 27-03-2026 09:50 | 305.7953 | 319.9701 | -14.1747 | 1919.8205 | 52.2 | 315.3945 | -263.1945 | -253.5953
27-03-2026 09:40 | 666 | 51.09 | 0 | 0 | 262.5 | 0 | 39.3097 | -39.3097 | 235.8583 | 31.6 | 38.7476 | -7.1476 |  | 27-03-2026 09:40 | 0 | 0 | 264.2 | 0 | 39.3097 | -39.3097 | 235.8583 | 0 | 38.7476 | -38.7476 |  | 27-03-2026 09:40 | 0 | 0 | 259.8 | 0 | 39.3097 | -39.3097 | 235.8583 | 0 | 38.7476 | -38.7476 |  | 27-03-2026 09:40 | 0 | 0 | 262.7 | 0 | 39.3097 | -39.3097 | 235.8583 | 0 | 38.7476 | -38.7476 |  | 27-03-2026 09:40 | 0 | 0 | 192.9 | 0 | 29.1183 | -29.1183 | 174.7098 | 0 | 28.7019 | -28.7019 |  | 27-03-2026 09:40 | 0 | 0 | 194.7 | 0 | 29.1183 | -29.1183 | 174.7098 | 0 | 28.7019 | -28.7019 |  | 27-03-2026 09:40 | 0 | 0 | 194.2 | 0 | 29.1183 | -29.1183 | 174.7098 | 0 | 28.7019 | -28.7019 |  | 27-03-2026 09:40 | 0 | 0 | 196.5 | 0 | 29.1183 | -29.1183 | 174.7098 | 0 | 28.7019 | -28.7019 |  | 27-03-2026 09:40 | 0 | 0 | 185.9 | 0 | 27.7025 | -27.7025 | 166.2148 | 0 | 27.3063 | -27.3063 |  | 27-03-2026 09:40 | 0 | 301.4145 | -301.4145 | 1808.4872 | 31.6 | 297.1043 | -265.5043 | 31.6
27-03-2026 09:30 | 625 | 50.23 |  |  |  | 0 | 37.0119 | -37.0119 | 222.0716 | 0 | 36.4827 | -36.4827 |  | 27-03-2026 09:30 | 0 | 0 | 264.2 | 0 | 37.0119 | -37.0119 | 222.0716 | 31.7 | 36.4827 | -4.7827 |  | 27-03-2026 09:30 | 0 | 0 | 259.8 | 0 | 37.0119 | -37.0119 | 222.0716 | 31 | 36.4827 | -5.4827 |  | 27-03-2026 09:30 | 0 | 0 | 262.7 | 0 | 37.0119 | -37.0119 | 222.0716 | 31.3 | 36.4827 | -5.1827 |  | 27-03-2026 09:30 | 0 | 0 | 192.9 | 0 | 27.4163 | -27.4163 | 164.4975 | 23.5 | 27.0242 | -3.5242 |  | 27-03-2026 09:30 | 0 | 0 | 194.7 | 0 | 27.4163 | -27.4163 | 164.4975 | 23.1 | 27.0242 | -3.9242 |  | 27-03-2026 09:30 | 0 | 0 | 194.2 | 0 | 27.4163 | -27.4163 | 164.4975 | 23 | 27.0242 | -4.0242 |  | 27-03-2026 09:30 | 0 | 0 | 196.5 | 0 | 27.4163 | -27.4163 | 164.4975 | 23.2 | 27.0242 | -3.8242 |  | 27-03-2026 09:30 | 0 | 0 | 185.9 | 0 | 26.0832 | -26.0832 | 156.499 | 22.3 | 25.7102 | -3.4102 |  | 27-03-2026 09:30 | 0 | 283.7959 | -283.7959 | 1702.7757 | 209.1 | 279.7377 | -70.6377 | 209.1
27-03-2026 09:20 | 583 | 47.07 | 206.456 | 209.531 | 230.9 | 34.9218 | 34.9436 | -0.021734 | 209.6614 | 33.2 | 34.4439 | -1.2439 |  | 27-03-2026 09:20 | 208.344 | 211.152 | 232.5 | 35.192 | 34.9436 | 0.24843 | 209.6614 | 33.9 | 34.4439 | -0.54387 |  | 27-03-2026 09:20 | 205.18 | 209.33 | 228.8 | 34.8883 | 34.9436 | -0.055234 | 209.6614 | 32.9 | 34.4439 | -1.5439 |  | 27-03-2026 09:20 | 207.21 | 210.024 | 231.4 | 35.004 | 34.9436 | 0.060433 | 209.6614 | 33.7 | 34.4439 | -0.74387 |  | 27-03-2026 09:20 | 152.579 | 154.542 | 169.4 | 25.757 | 25.8841 | -0.12712 | 155.3047 | 24.4 | 25.514 | -1.114 |  | 27-03-2026 09:20 | 153.551 | 155.495 | 171.6 | 25.9158 | 25.8841 | 0.03171 | 155.3047 | 24.9 | 25.514 | -0.61398 |  | 27-03-2026 09:20 | 153.095 | 155.033 | 171.2 | 25.8388 | 25.8841 | -0.04529 | 155.3047 | 24.8 | 25.514 | -0.71398 |  | 27-03-2026 09:20 | 154.552 | 158.938 | 173.3 | 26.4897 | 25.8841 | 0.60554 | 155.3047 | 25 | 25.514 | -0.51398 |  | 27-03-2026 09:20 | 146.568 | 148.423 | 163.6 | 24.7372 | 24.6255 | 0.11163 | 147.7532 | 23.4 | 24.2734 | -0.87339 |  | 27-03-2026 09:20 | 268.7447 | 267.9363 | 0.80837 | 1607.6178 | 256.2 | 264.1048 | -7.9048 | -12.5447
27-03-2026 09:10 | 544 | 44.2 | 194.618 | 197.121 | 197.7 | 32.8535 | 32.9609 | -0.10745 | 197.7657 | 32.1 | 32.4896 | -0.38961 |  | 27-03-2026 09:10 | 194.854 | 197.44 | 198.6 | 32.9067 | 32.9609 | -0.054283 | 197.7657 | 31.6 | 32.4896 | -0.88961 |  | 27-03-2026 09:10 | 191.669 | 195.359 | 195.9 | 32.5598 | 32.9609 | -0.40112 | 197.7657 | 31.1 | 32.4896 | -1.3896 |  | 27-03-2026 09:10 | 193.518 | 196.067 | 197.7 | 32.6778 | 32.9609 | -0.28312 | 197.7657 | 31 | 32.4896 | -1.4896 |  | 27-03-2026 09:10 | 142.58 | 144.356 | 145 | 24.0593 | 24.4155 | -0.35618 | 146.4931 | 22.8 | 24.0664 | -1.2664 |  | 27-03-2026 09:10 | 143.661 | 145.421 | 146.7 | 24.2368 | 24.4155 | -0.17868 | 146.4931 | 23 | 24.0664 | -1.0664 |  | 27-03-2026 09:10 | 143.044 | 144.793 | 146.4 | 24.1322 | 24.4155 | -0.28335 | 146.4931 | 22.9 | 24.0664 | -1.1664 |  | 27-03-2026 09:10 | 144.456 | 148.614 | 148.3 | 24.769 | 24.4155 | 0.35348 | 146.4931 | 23.1 | 24.0664 | -0.96638 |  | 27-03-2026 09:10 | 137.194 | 138.903 | 140.2 | 23.1505 | 23.2283 | -0.077841 | 139.37 | 22 | 22.8962 | -0.89618 |  | 27-03-2026 09:10 | 251.3457 | 252.7342 | -1.3885 | 1516.4053 | 239.6 | 249.1201 | -9.5201 | -11.7457
27-03-2026 09:00 | 505 | 42.19 | 179.792 | 182.049 | 165.6 | 30.3415 | 30.8287 | -0.4872 | 184.9722 | 27.4 | 30.3879 | -2.9879 |  | 27-03-2026 09:00 | 180.936 | 183.263 | 167 | 30.5438 | 30.8287 | -0.28487 | 184.9722 | 28.5 | 30.3879 | -1.8879 |  | 27-03-2026 09:00 | 178.168 | 181.474 | 164.8 | 30.2457 | 30.8287 | -0.58304 | 184.9722 | 28.1 | 30.3879 | -2.2879 |  | 27-03-2026 09:00 | 179.732 | 182.026 | 166.7 | 30.3377 | 30.8287 | -0.49104 | 184.9722 | 28.3 | 30.3879 | -2.0879 |  | 27-03-2026 09:00 | 132.473 | 134.082 | 122.2 | 22.347 | 22.8361 | -0.48908 | 137.0165 | 20.9 | 22.5095 | -1.6095 |  | 27-03-2026 09:00 | 133.619 | 135.242 | 123.7 | 22.5403 | 22.8361 | -0.29574 | 137.0165 | 21.1 | 22.5095 | -1.4095 |  | 27-03-2026 09:00 | 132.937 | 134.552 | 123.5 | 22.4253 | 22.8361 | -0.41074 | 137.0165 | 21 | 22.5095 | -1.5095 |  | 27-03-2026 09:00 | 134.271 | 138.144 | 125.2 | 23.024 | 22.8361 | 0.18792 | 137.0165 | 21.2 | 22.5095 | -1.3095 |  | 27-03-2026 09:00 | 127.634 | 129.197 | 118.2 | 21.5328 | 21.7257 | -0.19287 | 130.3542 | 20.1 | 21.415 | -1.315 |  | 27-03-2026 09:00 | 233.3382 | 236.3848 | -3.0467 | 1418.3089 | 216.6 | 233.0045 | -16.4045 | -16.7382
27-03-2026 08:50 | 456 | 40.47 | 160.92 | 162.843 | 138.2 | 27.1405 | 28.0157 | -0.87521 | 168.0943 | 25.6 | 27.6151 | -2.0151 |  | 27-03-2026 08:50 | 162.235 | 164.22 | 138.5 | 27.37 | 28.0157 | -0.64571 | 168.0943 | 25.2 | 27.6151 | -2.4151 |  | 27-03-2026 08:50 | 159.728 | 162.522 | 136.7 | 27.087 | 28.0157 | -0.92871 | 168.0943 | 25.1 | 27.6151 | -2.5151 |  | 27-03-2026 08:50 | 161.325 | 163.317 | 138.4 | 27.2195 | 28.0157 | -0.79621 | 168.0943 | 25.8 | 27.6151 | -1.8151 |  | 27-03-2026 08:50 | 118.57 | 119.998 | 101.3 | 19.9997 | 20.7524 | -0.75271 | 124.5143 | 18.9 | 20.4556 | -1.5556 |  | 27-03-2026 08:50 | 119.575 | 120.991 | 102.6 | 20.1652 | 20.7524 | -0.58721 | 124.5143 | 19.1 | 20.4556 | -1.3556 |  | 27-03-2026 08:50 | 119.318 | 120.743 | 102.5 | 20.1238 | 20.7524 | -0.62855 | 124.5143 | 19 | 20.4556 | -1.4556 |  | 27-03-2026 08:50 | 120.57 | 123.838 | 104 | 20.6397 | 20.7524 | -0.11271 | 124.5143 | 19.2 | 20.4556 | -1.2556 |  | 27-03-2026 08:50 | 114.267 | 115.631 | 98.1 | 19.2718 | 19.7433 | -0.47149 | 118.4599 | 18.2 | 19.461 | -1.261 |  | 27-03-2026 08:50 | 209.0172 | 214.8157 | -5.7985 | 1288.8941 | 196.1 | 211.7438 | -15.6438 | -12.9172
27-03-2026 08:40 | 414 | 38.46 | 143.418 | 146.958 | 112.6 | 24.493 | 25.6245 | -1.1315 | 153.747 | 22.8 | 25.2581 | -2.4581 |  | 27-03-2026 08:40 | 146.967 | 148.767 | 113.3 | 24.7945 | 25.6245 | -0.83 | 153.747 | 23 | 25.2581 | -2.2581 |  | 27-03-2026 08:40 | 144.456 | 146.644 | 111.6 | 24.4407 | 25.6245 | -1.1838 | 153.747 | 22.9 | 25.2581 | -2.3581 |  | 27-03-2026 08:40 | 145.783 | 147.526 | 112.6 | 24.5877 | 25.6245 | -1.0368 | 153.747 | 22.8 | 25.2581 | -2.4581 |  | 27-03-2026 08:40 | 106.83 | 108.095 | 82.4 | 18.0158 | 18.9811 | -0.96528 | 113.8867 | 16.7 | 18.7097 | -2.0097 |  | 27-03-2026 08:40 | 107.887 | 109.142 | 83.5 | 18.1903 | 18.9811 | -0.79078 | 113.8867 | 16.9 | 18.7097 | -1.8097 |  | 27-03-2026 08:40 | 107.413 | 108.685 | 83.5 | 18.1142 | 18.9811 | -0.86694 | 113.8867 | 16.8 | 18.7097 | -1.9097 |  | 27-03-2026 08:40 | 108.522 | 111.429 | 84.8 | 18.5715 | 18.9811 | -0.40961 | 113.8867 | 17.1 | 18.7097 | -1.6097 |  | 27-03-2026 08:40 | 103.029 | 104.249 | 79.9 | 17.3748 | 18.0582 | -0.68334 | 108.3491 | 16.1 | 17.7999 | -1.6999 |  | 27-03-2026 08:40 | 188.5825 | 196.4806 | -7.8981 | 1178.8837 | 175.1 | 193.6709 | -18.5709 | -13.4825
27-03-2026 08:30 | 366 | 35.59 | 127.705 | 129.191 | 89.8 | 21.5318 | 22.8923 | -1.3605 | 137.3541 | 19.7 | 22.565 | -2.865 |  | 27-03-2026 08:30 | 126.48 | 130.634 | 90.3 | 21.7723 | 22.8923 | -1.12 | 137.3541 | 19.9 | 22.565 | -2.665 |  | 27-03-2026 08:30 | 126.59 | 128.652 | 88.7 | 21.442 | 22.8923 | -1.4503 | 137.3541 | 19.6 | 22.565 | -2.965 |  | 27-03-2026 08:30 | 128.02 | 129.509 | 89.8 | 21.5848 | 22.8923 | -1.3075 | 137.3541 | 19.7 | 22.565 | -2.865 |  | 27-03-2026 08:30 | 93.854 | 94.955 | 65.7 | 15.8258 | 16.9573 | -1.1315 | 101.7438 | 14.5 | 16.7148 | -2.2148 |  | 27-03-2026 08:30 | 95.177 | 96.245 | 66.6 | 16.0408 | 16.9573 | -0.91646 | 101.7438 | 14.7 | 16.7148 | -2.0148 |  | 27-03-2026 08:30 | 94.629 | 95.73 | 66.7 | 15.955 | 16.9573 | -1.0023 | 101.7438 | 14.6 | 16.7148 | -2.1148 |  | 27-03-2026 08:30 | 95.923 | 98.466 | 67.7 | 16.411 | 16.9573 | -0.54629 | 101.7438 | 14.8 | 16.7148 | -1.9148 |  | 27-03-2026 08:30 | 90.848 | 91.94 | 63.8 | 15.3233 | 16.1328 | -0.80943 | 96.7966 | 14.1 | 15.9021 | -1.8021 |  | 27-03-2026 08:30 | 165.887 | 175.5313 | -9.6443 | 1053.188 | 151.6 | 173.0212 | -21.4212 | -14.287
27-03-2026 08:20 | 318 | 33.87 | 109.115 | 110.64 | 70.1 | 18.44 | 20.0144 | -1.5744 | 120.0865 | 16.8 | 19.7282 | -2.9282 |  | 27-03-2026 08:20 | 111.057 | 112.338 | 70.4 | 18.723 | 20.0144 | -1.2914 | 120.0865 | 17.3 | 19.7282 | -2.4282 |  | 27-03-2026 08:20 | 108.782 | 110.077 | 69.1 | 18.3462 | 20.0144 | -1.6683 | 120.0865 | 16.4 | 19.7282 | -3.3282 |  | 27-03-2026 08:20 | 110.146 | 111.416 | 70.1 | 18.5693 | 20.0144 | -1.4451 | 120.0865 | 17 | 19.7282 | -2.7282 |  | 27-03-2026 08:20 | 80.695 | 81.667 | 51.2 | 13.6112 | 14.8255 | -1.2143 | 88.953 | 12.3 | 14.6135 | -2.3135 |  | 27-03-2026 08:20 | 81.71 | 82.661 | 51.9 | 13.7768 | 14.8255 | -1.0487 | 88.953 | 12.5 | 14.6135 | -2.1135 |  | 27-03-2026 08:20 | 81.431 | 82.403 | 52.1 | 13.7338 | 14.8255 | -1.0917 | 88.953 | 12.6 | 14.6135 | -2.0135 |  | 27-03-2026 08:20 | 82.568 | 84.804 | 52.9 | 14.134 | 14.8255 | -0.6915 | 88.953 | 12.7 | 14.6135 | -1.9135 |  | 27-03-2026 08:20 | 78.22 | 79.162 | 49.7 | 13.1937 | 14.1046 | -0.91096 | 84.6277 | 12 | 13.9029 | -1.9029 |  | 27-03-2026 08:20 | 142.528 | 153.4643 | -10.9363 | 920.7857 | 129.6 | 151.2697 | -21.6697 | -12.928
27-03-2026 08:10 | 271 | 33 | 91.581 | 92.609 | 53.3 | 15.4348 | 17.1099 | -1.6751 | 102.6595 | 14.3 | 16.8652 | -2.5652 |  | 27-03-2026 08:10 | 92.968 | 94.031 | 53.1 | 15.6718 | 17.1099 | -1.4381 | 102.6595 | 14.2 | 16.8652 | -2.6652 |  | 27-03-2026 08:10 | 91.482 | 92.721 | 52.7 | 15.4535 | 17.1099 | -1.6564 | 102.6595 | 14 | 16.8652 | -2.8652 |  | 27-03-2026 08:10 | 92.46 | 93.507 | 53.1 | 15.5845 | 17.1099 | -1.5254 | 102.6595 | 14 | 16.8652 | -2.8652 |  | 27-03-2026 08:10 | 67.538 | 68.379 | 38.9 | 11.3965 | 12.674 | -1.2775 | 76.0441 | 10.3 | 12.4928 | -2.1928 |  | 27-03-2026 08:10 | 68.562 | 69.395 | 39.4 | 11.5658 | 12.674 | -1.1082 | 76.0441 | 10.4 | 12.4928 | -2.0928 |  | 27-03-2026 08:10 | 68.124 | 69.149 | 39.5 | 11.5248 | 12.674 | -1.1492 | 76.0441 | 10.4 | 12.4928 | -2.0928 |  | 27-03-2026 08:10 | 69.287 | 71.242 | 40.2 | 11.8737 | 12.674 | -0.80034 | 76.0441 | 10.6 | 12.4928 | -1.8928 |  | 27-03-2026 08:10 | 65.768 | 66.587 | 37.7 | 11.0978 | 12.0578 | -0.95992 | 72.3465 | 10 | 11.8853 | -1.8853 |  | 27-03-2026 08:10 | 119.6033 | 131.1934 | -11.5901 | 787.1607 | 108.2 | 129.3174 | -21.1174 | -11.4033
27-03-2026 08:00 | 228 | 31.28 | 75.609 | 76.496 | 39 | 12.7493 | 14.4842 | -1.7349 | 86.9053 | 11.3 | 14.2771 | -2.9771 |  | 27-03-2026 08:00 | 75.153 | 76.05 | 38.9 | 12.675 | 14.4842 | -1.8092 | 86.9053 | 11.6 | 14.2771 | -2.6771 |  | 27-03-2026 08:00 | 75.828 | 76.642 | 38.7 | 12.7737 | 14.4842 | -1.7105 | 86.9053 | 11.5 | 14.2771 | -2.7771 |  | 27-03-2026 08:00 | 76.622 | 77.485 | 39.1 | 12.9142 | 14.4842 | -1.57 | 86.9053 | 11.6 | 14.2771 | -2.6771 |  | 27-03-2026 08:00 | 55.886 | 56.639 | 28.6 | 9.4398 | 10.729 | -1.2892 | 64.3743 | 8.5 | 10.5756 | -2.0756 |  | 27-03-2026 08:00 | 56.928 | 57.666 | 29 | 9.611 | 10.729 | -1.118 | 64.3743 | 8.7 | 10.5756 | -1.8756 |  | 27-03-2026 08:00 | 56.663 | 57.421 | 29.1 | 9.5702 | 10.729 | -1.1589 | 64.3743 | 8.6 | 10.5756 | -1.9756 |  | 27-03-2026 08:00 | 57.538 | 59.15 | 29.6 | 9.8583 | 10.729 | -0.87071 | 64.3743 | 8.7 | 10.5756 | -1.8756 |  | 27-03-2026 08:00 | 54.431 | 55.17 | 27.7 | 9.195 | 10.2074 | -1.0124 | 61.2441 | 8.3 | 10.0614 | -1.7614 |  | 27-03-2026 08:00 | 98.7865 | 111.0604 | -12.2739 | 666.3623 | 88.8 | 109.4722 | -20.6722 | -9.9865
27-03-2026 07:50 | 189 | 27.84 | 62.012 | 62.778 | 27.7 | 10.463 | 12.1545 | -1.6915 | 72.9267 | 9.3 | 11.9806 | -2.6806 |  | 27-03-2026 07:50 | 60.948 | 61.726 | 27.3 | 10.2877 | 12.1545 | -1.8668 | 72.9267 | 9 | 11.9806 | -2.9806 |  | 27-03-2026 07:50 | 61.093 | 61.854 | 27.2 | 10.309 | 12.1545 | -1.8455 | 72.9267 | 9 | 11.9806 | -2.9806 |  | 27-03-2026 07:50 | 62.004 | 62.789 | 27.5 | 10.4648 | 12.1545 | -1.6896 | 72.9267 | 9.1 | 11.9806 | -2.8806 |  | 27-03-2026 07:50 | 45.149 | 45.823 | 20.1 | 7.6372 | 9.0033 | -1.3661 | 54.0198 | 6.6 | 8.8746 | -2.2746 |  | 27-03-2026 07:50 | 46.104 | 46.778 | 20.3 | 7.7963 | 9.0033 | -1.207 | 54.0198 | 6.7 | 8.8746 | -2.1746 |  | 27-03-2026 07:50 | 45.959 | 46.635 | 20.5 | 7.7725 | 9.0033 | -1.2308 | 54.0198 | 6.7 | 8.8746 | -2.1746 |  | 27-03-2026 07:50 | 46.666 | 47.981 | 20.9 | 7.9968 | 9.0033 | -1.0065 | 54.0198 | 6.8 | 8.8746 | -2.0746 |  | 27-03-2026 07:50 | 44.273 | 44.943 | 19.4 | 7.4905 | 8.5655 | -1.075 | 51.3932 | 6.5 | 8.443 | -1.943 |  | 27-03-2026 07:50 | 80.2178 | 93.1966 | -12.9787 | 559.1794 | 69.7 | 91.8639 | -22.1639 | -10.5178
27-03-2026 07:40 | 149 | 25.83 | 47.213 | 47.893 | 18.4 | 7.9822 | 9.6502 | -1.668 | 57.901 | 7 | 9.5122 | -2.5122 |  | 27-03-2026 07:40 | 46.991 | 48.105 | 18.3 | 8.0175 | 9.6502 | -1.6327 | 57.901 | 6.8 | 9.5122 | -2.7122 |  | 27-03-2026 07:40 | 47.315 | 48.011 | 18.2 | 8.0018 | 9.6502 | -1.6483 | 57.901 | 6.7 | 9.5122 | -2.8122 |  | 27-03-2026 07:40 | 47.928 | 48.633 | 18.4 | 8.1055 | 9.6502 | -1.5447 | 57.901 | 6.9 | 9.5122 | -2.6122 |  | 27-03-2026 07:40 | 34.827 | 35.404 | 13.5 | 5.9007 | 7.1483 | -1.2476 | 42.8897 | 4.9 | 7.0461 | -2.1461 |  | 27-03-2026 07:40 | 35.58 | 36.155 | 13.6 | 6.0258 | 7.1483 | -1.1224 | 42.8897 | 5.2 | 7.0461 | -1.8461 |  | 27-03-2026 07:40 | 35.543 | 36.128 | 13.8 | 6.0213 | 7.1483 | -1.1269 | 42.8897 | 5.1 | 7.0461 | -1.9461 |  | 27-03-2026 07:40 | 36.054 | 37.124 | 14.1 | 6.1873 | 7.1483 | -0.96094 | 42.8897 | 5.2 | 7.0461 | -1.8461 |  | 27-03-2026 07:40 | 34.109 | 34.674 | 12.9 | 5.779 | 6.8007 | -1.0217 | 40.8042 | 4.9 | 6.7034 | -1.8034 |  | 27-03-2026 07:40 | 62.0212 | 73.9945 | -11.9733 | 443.967 | 52.7 | 72.9364 | -20.2364 | -9.3212
27-03-2026 07:30 | 110 | 23.53 | 34.696 | 35.264 | 11.4 | 5.8773 | 7.1818 | -1.3045 | 43.0908 | 4.8 | 7.0791 | -2.2791 |  | 27-03-2026 07:30 | 34.21 | 35.371 | 11.5 | 5.8952 | 7.1818 | -1.2866 | 43.0908 | 4.8 | 7.0791 | -2.2791 |  | 27-03-2026 07:30 | 34.617 | 35.187 | 11.5 | 5.8645 | 7.1818 | -1.3173 | 43.0908 | 5 | 7.0791 | -2.0791 |  | 27-03-2026 07:30 | 35.034 | 35.622 | 11.5 | 5.937 | 7.1818 | -1.2448 | 43.0908 | 4.9 | 7.0791 | -2.1791 |  | 27-03-2026 07:30 | 25.334 | 25.84 | 8.6 | 4.3067 | 5.3199 | -1.0132 | 31.9191 | 3.6 | 5.2438 | -1.6438 |  | 27-03-2026 07:30 | 25.902 | 26.398 | 8.4 | 4.3997 | 5.3199 | -0.92019 | 31.9191 | 3.6 | 5.2438 | -1.6438 |  | 27-03-2026 07:30 | 25.842 | 26.348 | 8.7 | 4.3913 | 5.3199 | -0.92852 | 31.9191 | 3.7 | 5.2438 | -1.5438 |  | 27-03-2026 07:30 | 26.323 | 27.232 | 8.9 | 4.5387 | 5.3199 | -0.78119 | 31.9191 | 3.7 | 5.2438 | -1.5438 |  | 27-03-2026 07:30 | 24.743 | 25.245 | 8 | 4.2075 | 5.0612 | -0.85368 | 30.3671 | 3.5 | 4.9888 | -1.4888 |  | 27-03-2026 07:30 | 45.4178 | 55.0678 | -9.65 | 330.407 | 37.6 | 54.2804 | -16.6804 | -7.8178
27-03-2026 07:20 | 77 | 22.1 | 24.515 | 25.144 | 6.6 | 4.1907 | 5.0523 | -0.86163 | 30.3138 | 3.3 | 4.98 | -1.68 |  | 27-03-2026 07:20 | 23.872 | 24.695 | 6.7 | 4.1158 | 5.0523 | -0.93646 | 30.3138 | 3.5 | 4.98 | -1.48 |  | 27-03-2026 07:20 | 24.266 | 24.745 | 6.5 | 4.1242 | 5.0523 | -0.92813 | 30.3138 | 3.2 | 4.98 | -1.78 |  | 27-03-2026 07:20 | 24.434 | 24.992 | 6.6 | 4.1653 | 5.0523 | -0.88696 | 30.3138 | 3.3 | 4.98 | -1.68 |  | 27-03-2026 07:20 | 17.656 | 18.263 | 5 | 3.0438 | 3.7424 | -0.69861 | 22.4547 | 2.5 | 3.6889 | -1.1889 |  | 27-03-2026 07:20 | 18.113 | 18.541 | 4.8 | 3.0902 | 3.7424 | -0.65228 | 22.4547 | 2.5 | 3.6889 | -1.1889 |  | 27-03-2026 07:20 | 17.902 | 18.335 | 5 | 3.0558 | 3.7424 | -0.68661 | 22.4547 | 2.4 | 3.6889 | -1.2889 |  | 27-03-2026 07:20 | 18.451 | 19.352 | 5.2 | 3.2253 | 3.7424 | -0.51711 | 22.4547 | 2.6 | 3.6889 | -1.0889 |  | 27-03-2026 07:20 | 17.232 | 17.65 | 4.5 | 2.9417 | 3.5605 | -0.6188 | 21.3628 | 2.3 | 3.5096 | -1.2096 |  | 27-03-2026 07:20 | 31.9528 | 38.7394 | -6.7866 | 232.4366 | 25.6 | 38.1855 | -12.5855 | -6.3528
27-03-2026 07:10 | 42 | 20.66 | 16.148 | 16.554 | 3.3 | 2.759 | 2.7695 | -0.010548 | 16.6173 | 2.1 | 2.7299 | -0.62994 |  | 27-03-2026 07:10 | 15.674 | 16.647 | 3.2 | 2.7745 | 2.7695 | 0.004952 | 16.6173 | 2 | 2.7299 | -0.72994 |  | 27-03-2026 07:10 | 15.952 | 16.358 | 3.3 | 2.7263 | 2.7695 | -0.043215 | 16.6173 | 2.1 | 2.7299 | -0.62994 |  | 27-03-2026 07:10 | 16.016 | 16.775 | 3.3 | 2.7958 | 2.7695 | 0.026285 | 16.6173 | 2.1 | 2.7299 | -0.62994 |  | 27-03-2026 07:10 | 11.485 | 12.143 | 2.5 | 2.0238 | 2.0515 | -0.027684 | 12.3091 | 1.4 | 2.0222 | -0.62218 |  | 27-03-2026 07:10 | 11.732 | 12.105 | 2.3 | 2.0175 | 2.0515 | -0.034017 | 12.3091 | 1.5 | 2.0222 | -0.52218 |  | 27-03-2026 07:10 | 11.762 | 12.145 | 2.6 | 2.0242 | 2.0515 | -0.02735 | 12.3091 | 1.6 | 2.0222 | -0.42218 |  | 27-03-2026 07:10 | 12.01 | 12.693 | 2.6 | 2.1155 | 2.0515 | 0.063983 | 12.3091 | 1.5 | 2.0222 | -0.52218 |  | 27-03-2026 07:10 | 11.116 | 11.493 | 2.2 | 1.9155 | 1.9518 | -0.036264 | 11.7106 | 1.5 | 1.9239 | -0.42385 |  | 27-03-2026 07:10 | 21.1522 | 21.236 | -0.083858 | 127.4161 | 15.8 | 20.9323 | -5.1323 | -5.3522
27-03-2026 07:00 | 25 | 19.8 | 9.252 | 9.594 | 1.2 | 1.599 | 1.6534 | -0.054428 | 9.9206 | 1.2 | 1.6298 | -0.42978 |  | 27-03-2026 07:00 | 9.369 | 9.976 | 1.2 | 1.6627 | 1.6534 | 0.0092383 | 9.9206 | 1.2 | 1.6298 | -0.42978 |  | 27-03-2026 07:00 | 9.245 | 9.593 | 1.2 | 1.5988 | 1.6534 | -0.054595 | 9.9206 | 1.2 | 1.6298 | -0.42978 |  | 27-03-2026 07:00 | 9.278 | 10.084 | 1.2 | 1.6807 | 1.6534 | 0.027238 | 9.9206 | 1.2 | 1.6298 | -0.42978 |  | 27-03-2026 07:00 | 6.687 | 7.33 | 1.1 | 1.2217 | 1.2248 | -0.0030951 | 7.3486 | 1.1 | 1.2072 | -0.10725 |  | 27-03-2026 07:00 | 6.69 | 6.972 | 0.8 | 1.162 | 1.2248 | -0.062762 | 7.3486 | 0.8 | 1.2072 | -0.40725 |  | 27-03-2026 07:00 | 6.711 | 6.995 | 1 | 1.1658 | 1.2248 | -0.058928 | 7.3486 | 1 | 1.2072 | -0.20725 |  | 27-03-2026 07:00 | 6.845 | 7.326 | 1.1 | 1.221 | 1.2248 | -0.0037617 | 7.3486 | 1.1 | 1.2072 | -0.10725 |  | 27-03-2026 07:00 | 6.35 | 6.623 | 0.7 | 1.1038 | 1.1652 | -0.061376 | 6.9913 | 0.7 | 1.1485 | -0.44855 |  | 27-03-2026 07:00 | 12.4155 | 12.678 | -0.26247 | 76.0678 | 9.5 | 12.4967 | -2.9967 | -2.9155
[110 empty] | Total: - | 18658.651 | 20059.6676 | -1401.0166 |  | 18374 | 19772.8143 | -1398.8143 | -284.651
Sum:- | 44074 |  | 14411.883 |  | 89940.8 |  |  |  |  | 2397.7 | 2578.7199 | -181.0199 | 0.98329 |  | 13927.991 |  | 85539 |  |  |  |  | 2424.1 | 2578.7199 | -154.6199 | 0.98365 |  | 14312.363 |  | 87034.3 |  |  |  |  | 2378.6 | 2578.7199 | -200.1199 | 0.9735 |  | 14432.024 |  | 90171.1 |  |  |  |  | 2396.5 | 2578.7199 | -182.2199 | 0.98317 |  | 10747.206 |  | 67115.4 |  |  |  |  | 1786.8 | 1910.1629 | -123.3629 | 0.98468 |  | 10644.466 |  | 66649.5 |  |  |  |  | 1768 | 1910.1629 | -142.1629 | 0.98229 |  | 10628.814 |  | 66568.8 |  |  |  |  | 1766.5 | 1910.1629 | -143.6629 | 0.98196 |  | 10684.525 |  | 67070.4 |  |  |  |  | 1776 | 1910.1629 | -134.1629 | 0.97121 |  | 10116.239 |  | 63398.8 |  |  |  |  | 1679.8 | 1817.2834 | -137.4834 | 0.98496 | [8 empty] | -1.526%

## 28 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
28-03-2026 19:00 | 0 | 42.48 | 0 | 0 | 2358.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 2378.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 2340.3 | 0 | 0 | 0 | 0 | 423.4 | 0 | 423.4 |  | 28-03-2026 19:00 | 0 | 0 | 2361.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 1766.2 | 0 | 0 | 0 | 0 | 319.3 | 0 | 319.3 |  | 28-03-2026 19:00 | 0 | 0 | 1749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 1753.7 | 0 | 0 | 0 | 0 | 314.2 | 0 | 314.2 |  | 28-03-2026 19:00 | 0 | 0 | 1763.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 1662.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 28-03-2026 19:00 | 0 | 0 | 0 | 0 | 1056.9 | 0 | 1056.9 | 1056.9 | 1 | 98.34%
28-03-2026 18:50 | 4 | 42.48 | 0 | 0 | 2358.4 | 0 | 0.24392 | -0.24392 | 1.4635 | 0.4 | 0.24044 | 0.15956 |  | 28-03-2026 18:50 | 0 | 0 | 2378.6 | 0 | 0.24392 | -0.24392 | 1.4635 | 0.4 | 0.24044 | 0.15956 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:50 | 0 | 0 | 2361.6 | 0 | 0.24392 | -0.24392 | 1.4635 | 0.4 | 0.24044 | 0.15956 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:50 | 0 | 0 | 1749 | 0 | 0.18068 | -0.18068 | 1.0841 | 0.2 | 0.1781 | 0.021899 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:50 | 0 | 0 | 1763.3 | 0 | 0.18068 | -0.18068 | 1.0841 | 0.3 | 0.1781 | 0.1219 |  | 28-03-2026 18:50 | 0 | 0 | 1662.9 | 0 | 0.1719 | -0.1719 | 1.0314 | 0.2 | 0.16944 | 0.030559 |  | 28-03-2026 18:50 | 0 | 1.265 | -1.265 | 7.5902 | 1.9 | 1.2469 | 0.65305 | 1.9 | 2 | 99.18%
28-03-2026 18:40 | 12 | 43.34 | 4.379 | 4.599 | 2358 | 0.7665 | 0.72943 | 0.037074 | 4.3766 | 1 | 0.719 | 0.281 |  | 28-03-2026 18:40 | 4.448 | 4.982 | 2378.2 | 0.83033 | 0.72943 | 0.10091 | 4.3766 | 1 | 0.719 | 0.281 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:40 | 4.358 | 4.692 | 2361.2 | 0.782 | 0.72943 | 0.052574 | 4.3766 | 1 | 0.719 | 0.281 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:40 | 2.946 | 3.097 | 1748.8 | 0.51617 | 0.54032 | -0.024149 | 3.2419 | 0.7 | 0.53259 | 0.16741 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:40 | 3.07 | 3.285 | 1763 | 0.5475 | 0.54032 | 0.0071845 | 3.2419 | 0.6 | 0.53259 | 0.067411 |  | 28-03-2026 18:40 | 2.789 | 2.932 | 1662.7 | 0.48867 | 0.51404 | -0.025377 | 3.0843 | 0.6 | 0.50669 | 0.093308 |  | 28-03-2026 18:40 | 3.9312 | 3.783 | 0.14821 | 22.6977 | 4.9 | 3.7289 | 1.1711 | 0.96883 | 3 | 97.3%
28-03-2026 18:30 | 22 | 44.48 | 9.706 | 8.685 | 2357 | 1.4475 | 1.3316 | 0.11592 | 7.9895 | 4.9 | 1.3125 | 3.5875 |  | 28-03-2026 18:30 | 8.067 | 8.541 | 2377.2 | 1.4235 | 1.3316 | 0.091921 | 7.9895 | 5.1 | 1.3125 | 3.7875 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:30 | 7.921 | 8.296 | 2360.2 | 1.3827 | 1.3316 | 0.051088 | 7.9895 | 5.1 | 1.3125 | 3.7875 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:30 | 5.563 | 5.825 | 1748.1 | 0.97083 | 0.98635 | -0.015522 | 5.9181 | 3.7 | 0.97225 | 2.7277 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:30 | 5.564 | 5.994 | 1762.4 | 0.999 | 0.98635 | 0.012645 | 5.9181 | 3.4 | 0.97225 | 2.4277 |  | 28-03-2026 18:30 | 5.185 | 5.443 | 1662.1 | 0.90717 | 0.93839 | -0.031228 | 5.6304 | 3.3 | 0.92498 | 2.375 |  | 28-03-2026 18:30 | 7.1307 | 6.9058 | 0.22482 | 41.4351 | 25.5 | 6.8071 | 18.6929 | 18.3693 | 4 | 98.35%
28-03-2026 18:20 | 40 | 45.63 |  |  |  | 0 | 2.4106 | -2.4106 | 14.4636 | 0 | 2.3761 | -2.3761 | [5 empty] | 0 | 2.4106 | -2.4106 | 14.4636 | 0 | 2.3761 | -2.3761 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 2.4106 | -2.4106 | 14.4636 | 0 | 2.3761 | -2.3761 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 1.7856 | -1.7856 | 10.7138 | 0 | 1.7601 | -1.7601 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 | 1.7856 | -1.7856 | 10.7138 | 0 | 1.7601 | -1.7601 | [5 empty] | 0 | 1.6988 | -1.6988 | 10.1928 | 0 | 1.6745 | -1.6745 |  | 28-03-2026 18:20 | 0 | 12.5018 | -12.5018 | 75.011 | 0 | 12.3231 | -12.3231 | 0 | 5 | 98.4%
28-03-2026 18:10 | 53 | 47.07 | 22.524 | 23.058 | 2352.1 | 3.843 | 3.1767 | 0.66631 | 19.0601 | 4.5 | 3.1313 | 1.3687 |  | 28-03-2026 18:10 | 23.178 | 23.719 | 2372.1 | 3.9532 | 3.1767 | 0.77648 | 19.0601 | 4.7 | 3.1313 | 1.5687 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:10 | 23.061 | 23.611 | 2355.1 | 3.9352 | 3.1767 | 0.75848 | 19.0601 | 4.5 | 3.1313 | 1.3687 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:10 | 16.435 | 16.87 | 1744.4 | 2.8117 | 2.3531 | 0.45856 | 14.1186 | 3.2 | 2.3195 | 0.88055 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:10 | 13.829 | 14.406 | 1759 | 2.401 | 2.3531 | 0.047898 | 14.1186 | 2.8 | 2.3195 | 0.48055 |  | 28-03-2026 18:10 | 14.963 | 15.389 | 1658.8 | 2.5648 | 2.2387 | 0.32615 | 13.4321 | 3.1 | 2.2067 | 0.89333 |  | 28-03-2026 18:10 | 19.5088 | 16.475 | 3.0339 | 98.8497 | 22.8 | 16.2394 | 6.5606 | 3.2912 | 6 | 98.22%
28-03-2026 18:00 | 72 | 48.22 | 33.477 | 33.946 | 2347.6 | 5.6577 | 4.2967 | 1.361 | 25.7801 | 6.7 | 4.2352 | 2.4648 |  | 28-03-2026 18:00 | 34.336 | 34.98 | 2367.4 | 5.83 | 4.2967 | 1.5333 | 25.7801 | 6.7 | 4.2352 | 2.4648 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:00 | 33.97 | 34.596 | 2350.6 | 5.766 | 4.2967 | 1.4693 | 25.7801 | 6.8 | 4.2352 | 2.5648 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:00 | 24.482 | 25.025 | 1741.2 | 4.1708 | 3.1827 | 0.98811 | 19.0963 | 4.9 | 3.1372 | 1.7628 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 18:00 | 22.358 | 23.265 | 1756.2 | 3.8775 | 3.1827 | 0.69478 | 19.0963 | 4.6 | 3.1372 | 1.4628 |  | 28-03-2026 18:00 | 22.923 | 23.443 | 1655.7 | 3.9072 | 3.028 | 0.8792 | 18.1678 | 4.5 | 2.9847 | 1.5153 |  | 28-03-2026 18:00 | 29.2092 | 22.2834 | 6.9257 | 133.7007 | 34.2 | 21.9648 | 12.2352 | 4.9908 | 7 | 98.1%
28-03-2026 17:50 | 139 | 49.08 | 45.648 | 46.381 | 2340.9 | 7.7302 | 8.2678 | -0.53763 | 49.6068 | 8.9 | 8.1496 | 0.75043 |  | 28-03-2026 17:50 | 46.041 | 46.813 | 2360.7 | 7.8022 | 8.2678 | -0.46563 | 49.6068 | 8.9 | 8.1496 | 0.75043 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:50 | 46.194 | 46.955 | 2343.8 | 7.8258 | 8.2678 | -0.44196 | 49.6068 | 8.8 | 8.1496 | 0.65043 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:50 | 33.387 | 33.996 | 1736.3 | 5.666 | 6.1243 | -0.45829 | 36.7458 | 6.4 | 6.0367 | 0.36328 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:50 | 33.079 | 33.827 | 1751.6 | 5.6378 | 6.1243 | -0.48646 | 36.7458 | 6.4 | 6.0367 | 0.36328 |  | 28-03-2026 17:50 | 31.358 | 31.936 | 1651.2 | 5.3227 | 5.8265 | -0.50384 | 34.959 | 6 | 5.7432 | 0.25681 |  | 28-03-2026 17:50 | 39.9847 | 42.8785 | -2.8938 | 257.2709 | 45.4 | 42.2653 | 3.1347 | 5.4153 | 8 | 97.09%
28-03-2026 17:40 | 154 | 49.36 | 41.842 | 42.566 | 2332 | 7.0943 | 9.1502 | -2.0559 | 54.9012 | 11 | 9.0194 | 1.9806 |  | 28-03-2026 17:40 | 48.848 | 49.793 | 2351.8 | 8.2988 | 9.1502 | -0.85137 | 54.9012 | 11.1 | 9.0194 | 2.0806 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:40 | 54.407 | 55.258 | 2335 | 9.2097 | 9.1502 | 0.059465 | 54.9012 | 11 | 9.0194 | 1.9806 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:40 | 40.306 | 40.995 | 1729.9 | 6.8325 | 6.7779 | 0.054573 | 40.6676 | 7.9 | 6.681 | 1.219 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:40 | 39.104 | 40.502 | 1745.2 | 6.7503 | 6.7779 | -0.027594 | 40.6676 | 7.8 | 6.681 | 1.119 |  | 28-03-2026 17:40 | 36.652 | 37.309 | 1645.2 | 6.2182 | 6.4484 | -0.23019 | 38.6901 | 7.6 | 6.3561 | 1.2439 |  | 28-03-2026 17:40 | 44.4038 | 47.4548 | -3.051 | 284.7289 | 56.4 | 46.7762 | 9.6238 | 11.9962 | 9 | 98.67%
28-03-2026 17:30 | 237 | 49.65 | 7.761 | 8.037 | 2321 | 1.3395 | 14.0662 | -12.7267 | 84.3971 | 0 | 13.865 | -13.865 |  | 28-03-2026 17:30 | 45.596 | 46.795 | 2340.7 | 7.7992 | 14.0662 | -6.267 | 84.3971 | 0.2 | 13.865 | -13.665 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:30 | 46.423 | 48.541 | 2324 | 8.0902 | 14.0662 | -5.976 | 84.3971 | 0.1 | 13.865 | -13.765 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:30 | 51.792 | 52.715 | 1722 | 8.7858 | 10.4194 | -1.6336 | 62.5163 | 0.2 | 10.2704 | -10.0704 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:30 | 55.15 | 56.706 | 1737.4 | 9.451 | 10.4194 | -0.96839 | 62.5163 | 0.5 | 10.2704 | -9.7704 |  | 28-03-2026 17:30 | 42.745 | 44.204 | 1637.6 | 7.3673 | 9.9128 | -2.5454 | 59.4766 | 0.1 | 9.771 | -9.671 |  | 28-03-2026 17:30 | 42.833 | 72.9501 | -30.1171 | 437.7005 | 1.1 | 71.9069 | -70.8069 | -41.733
28-03-2026 17:20 | 288 | 49.65 | 0 | 0 | 2321 | 0 | 17.0931 | -17.0931 | 102.5585 | 0 | 16.8486 | -16.8486 |  | 28-03-2026 17:20 | 0 | 0 | 2340.5 | 0 | 17.0931 | -17.0931 | 102.5585 | 0 | 16.8486 | -16.8486 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:20 | 0 | 0 | 2323.9 | 0 | 17.0931 | -17.0931 | 102.5585 | 0 | 16.8486 | -16.8486 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:20 | 0 | 0 | 1721.8 | 0 | 12.6615 | -12.6615 | 75.9692 | 0 | 12.4805 | -12.4805 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:20 | 0 | 0 | 1736.9 | 0 | 12.6615 | -12.6615 | 75.9692 | 0 | 12.4805 | -12.4805 |  | 28-03-2026 17:20 | 0 | 0 | 1637.5 | 0 | 12.0459 | -12.0459 | 72.2753 | 0 | 11.8736 | -11.8736 |  | 28-03-2026 17:20 | 0 | 88.6482 | -88.6482 | 531.8892 | 0 | 87.3805 | -87.3805 | 0
28-03-2026 17:10 | 332 | 49.65 | 0 | 0 | 2321 | 0 | 19.7045 | -19.7045 | 118.2271 | 0 | 19.4227 | -19.4227 |  | 28-03-2026 17:10 | 0 | 0 | 2340.5 | 0 | 19.7045 | -19.7045 | 118.2271 | 0 | 19.4227 | -19.4227 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:10 | 0 | 0 | 2323.9 | 0 | 19.7045 | -19.7045 | 118.2271 | 0 | 19.4227 | -19.4227 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:10 | 0 | 0 | 1721.8 | 0 | 14.5959 | -14.5959 | 87.5756 | 0 | 14.3872 | -14.3872 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:10 | 0 | 0 | 1736.9 | 0 | 14.5959 | -14.5959 | 87.5756 | 0 | 14.3872 | -14.3872 |  | 28-03-2026 17:10 | 0 | 0 | 1637.5 | 0 | 13.8862 | -13.8862 | 83.3174 | 0 | 13.6877 | -13.6877 |  | 28-03-2026 17:10 | 0 | 102.1917 | -102.1917 | 613.15 | 0 | 100.7303 | -100.7303 | 0
28-03-2026 17:00 | 371 | 49.94 | 0 | 0 | 2321 | 0 | 21.9947 | -21.9947 | 131.9685 | 0 | 21.6802 | -21.6802 |  | 28-03-2026 17:00 | 0 | 0 | 2340.5 | 0 | 21.9947 | -21.9947 | 131.9685 | 0 | 21.6802 | -21.6802 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:00 | 0 | 0 | 2323.9 | 0 | 21.9947 | -21.9947 | 131.9685 | 0 | 21.6802 | -21.6802 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:00 | 0 | 0 | 1721.8 | 0 | 16.2924 | -16.2924 | 97.7544 | 0 | 16.0594 | -16.0594 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 17:00 | 0 | 0 | 1736.9 | 0 | 16.2924 | -16.2924 | 97.7544 | 0 | 16.0594 | -16.0594 |  | 28-03-2026 17:00 | 0 | 0 | 1637.5 | 0 | 15.5002 | -15.5002 | 93.0012 | 0 | 15.2786 | -15.2786 |  | 28-03-2026 17:00 | 0 | 114.0693 | -114.0693 | 684.4156 | 0 | 112.4381 | -112.4381 | 0
28-03-2026 16:50 | 410 | 50.23 | 0 | 0 | 2321 | 0 | 24.2798 | -24.2798 | 145.679 | 0 | 23.9326 | -23.9326 |  | 28-03-2026 16:50 | 0 | 0 | 2340.5 | 0 | 24.2798 | -24.2798 | 145.679 | 0 | 23.9326 | -23.9326 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:50 | 0 | 0 | 2323.9 | 0 | 24.2798 | -24.2798 | 145.679 | 0 | 23.9326 | -23.9326 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:50 | 0 | 0 | 1721.8 | 0 | 17.9851 | -17.9851 | 107.9104 | 0 | 17.7279 | -17.7279 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:50 | 0 | 0 | 1736.9 | 0 | 17.9851 | -17.9851 | 107.9104 | 0 | 17.7279 | -17.7279 |  | 28-03-2026 16:50 | 0 | 0 | 1637.5 | 0 | 17.1106 | -17.1106 | 102.6634 | 0 | 16.8659 | -16.8659 |  | 28-03-2026 16:50 | 0 | 125.9202 | -125.9202 | 755.5211 | 0 | 124.1195 | -124.1195 | 0
28-03-2026 16:40 | 467 | 50.51 | 0 | 0 | 2321 | 0 | 27.6256 | -27.6256 | 165.7536 | 0 | 27.2305 | -27.2305 |  | 28-03-2026 16:40 | 0 | 0 | 2340.5 | 0 | 27.6256 | -27.6256 | 165.7536 | 0 | 27.2305 | -27.2305 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:40 | 0 | 0 | 2323.9 | 0 | 27.6256 | -27.6256 | 165.7536 | 0 | 27.2305 | -27.2305 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:40 | 0 | 0 | 1721.8 | 0 | 20.4634 | -20.4634 | 122.7804 | 0 | 20.1708 | -20.1708 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:40 | 0 | 0 | 1736.9 | 0 | 20.4634 | -20.4634 | 122.7804 | 0 | 20.1708 | -20.1708 |  | 28-03-2026 16:40 | 0 | 0 | 1637.5 | 0 | 19.4684 | -19.4684 | 116.8104 | 0 | 19.19 | -19.19 |  | 28-03-2026 16:40 | 0 | 143.272 | -143.272 | 859.6319 | 0 | 141.2232 | -141.2232 | 0
28-03-2026 16:30 | 517 | 49.94 | 0 | 0 | 2321 | 0 | 30.6504 | -30.6504 | 183.9022 | 0 | 30.2121 | -30.2121 |  | 28-03-2026 16:30 | 0 | 0 | 2340.5 | 0 | 30.6504 | -30.6504 | 183.9022 | 0 | 30.2121 | -30.2121 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:30 | 0 | 0 | 2323.9 | 0 | 30.6504 | -30.6504 | 183.9022 | 0 | 30.2121 | -30.2121 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:30 | 0 | 0 | 1721.8 | 0 | 22.704 | -22.704 | 136.2238 | 0 | 22.3793 | -22.3793 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:30 | 0 | 0 | 1736.9 | 0 | 22.704 | -22.704 | 136.2238 | 0 | 22.3793 | -22.3793 |  | 28-03-2026 16:30 | 0 | 0 | 1637.5 | 0 | 21.6 | -21.6 | 129.6001 | 0 | 21.2911 | -21.2911 |  | 28-03-2026 16:30 | 0 | 158.9591 | -158.9591 | 953.7543 | 0 | 156.6859 | -156.6859 | 0
28-03-2026 16:20 | 147 | 49.65 | 0 | 0 | 2321 | 0 | 8.7246 | -8.7246 | 52.3476 | 23.3 | 8.5998 | 14.7002 |  | 28-03-2026 16:20 | 0 | 0 | 2340.5 | 0 | 8.7246 | -8.7246 | 52.3476 | 23.4 | 8.5998 | 14.8002 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:20 | 0 | 0 | 2323.9 | 0 | 8.7246 | -8.7246 | 52.3476 | 23.1 | 8.5998 | 14.5002 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:20 | 0 | 0 | 1721.8 | 0 | 6.4627 | -6.4627 | 38.776 | 17 | 6.3702 | 10.6298 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:20 | 0 | 0 | 1736.9 | 0 | 6.4627 | -6.4627 | 38.776 | 16.7 | 6.3702 | 10.3298 |  | 28-03-2026 16:20 | 0 | 0 | 1637.5 | 0 | 6.1484 | -6.1484 | 36.8905 | 16.2 | 6.0605 | 10.1395 |  | 28-03-2026 16:20 | 0 | 45.2475 | -45.2475 | 271.4851 | 119.7 | 44.6005 | 75.0995 | 119.7
28-03-2026 16:10 | 596 | 50.23 | 203.431 | 206.278 | 2297.7 | 34.3797 | 35.2946 | -0.91492 | 211.7675 | 35.3 | 34.7899 | 0.51013 |  | 28-03-2026 16:10 | 205.567 | 208.528 | 2317.1 | 34.7547 | 35.2946 | -0.53992 | 211.7675 | 35.7 | 34.7899 | 0.91013 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:10 | 203.897 | 206.813 | 2300.8 | 34.4688 | 35.2946 | -0.82575 | 211.7675 | 36 | 34.7899 | 1.2101 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:10 | 150.004 | 152.122 | 1704.8 | 25.3537 | 26.1441 | -0.79047 | 156.8648 | 26.4 | 25.7703 | 0.62972 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:10 | 150.288 | 154.302 | 1720.2 | 25.717 | 26.1441 | -0.42714 | 156.8648 | 26.5 | 25.7703 | 0.72972 |  | 28-03-2026 16:10 | 142.35 | 144.283 | 1621.3 | 24.0472 | 24.8729 | -0.82574 | 149.2375 | 25 | 24.5172 | 0.48277 |  | 28-03-2026 16:10 | 178.721 | 183.0449 | -4.3239 | 1098.2697 | 184.9 | 180.4274 | 4.4726 | 6.179
28-03-2026 16:00 | 641 | 50.51 | 221.153 | 224.29 | 2262.4 | 37.3817 | 37.9186 | -0.53698 | 227.5119 | 34.6 | 37.3764 | -2.7764 |  | 28-03-2026 16:00 | 223.03 | 226.266 | 2281.4 | 37.711 | 37.9186 | -0.20764 | 227.5119 | 34.6 | 37.3764 | -2.7764 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:00 | 220.828 | 224.009 | 2264.8 | 37.3348 | 37.9186 | -0.58381 | 227.5119 | 33.5 | 37.3764 | -3.8764 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:00 | 162.744 | 165.368 | 1678.4 | 27.5613 | 28.0879 | -0.52655 | 168.5273 | 24.7 | 27.6862 | -2.9862 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 16:00 | 163.647 | 168.098 | 1693.7 | 28.0163 | 28.0879 | -0.071551 | 168.5273 | 25.2 | 27.6862 | -2.4862 |  | 28-03-2026 16:00 | 154.183 | 156.277 | 1596.3 | 26.0462 | 26.7221 | -0.67598 | 160.3329 | 23.4 | 26.34 | -2.94 |  | 28-03-2026 16:00 | 194.0513 | 196.6538 | -2.6025 | 1179.923 | 176 | 193.8417 | -17.8417 | -18.0513
28-03-2026 15:50 | 679 | 50.23 | 233.85 | 237.291 | 2227.8 | 39.5485 | 40.2098 | -0.66127 | 241.2586 | 39.4 | 39.6348 | -0.23477 |  | 28-03-2026 15:50 | 234.9 | 238.453 | 2246.8 | 39.7422 | 40.2098 | -0.46761 | 241.2586 | 39.8 | 39.6348 | 0.16523 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:50 | 230.965 | 234.387 | 2231.3 | 39.0645 | 40.2098 | -1.1453 | 241.2586 | 39.8 | 39.6348 | 0.16523 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:50 | 170.992 | 173.701 | 1653.7 | 28.9502 | 29.785 | -0.83485 | 178.7101 | 29.5 | 29.3591 | 0.14091 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:50 | 159.67 | 167.214 | 1668.5 | 27.869 | 29.785 | -1.916 | 178.7101 | 29.5 | 29.3591 | 0.14091 |  | 28-03-2026 15:50 | 128.089 | 135.251 | 1572.9 | 22.5418 | 28.3368 | -5.7949 | 170.0205 | 27.8 | 27.9315 | -0.13154 |  | 28-03-2026 15:50 | 197.7162 | 208.5361 | -10.8199 | 1251.2166 | 205.8 | 205.554 | 0.24596 | 8.0838
28-03-2026 15:40 | 724 | 49.94 | 250.538 | 254.198 | 2188.4 | 42.3663 | 42.9224 | -0.55603 | 257.5342 | 38 | 42.3086 | -4.3086 |  | 28-03-2026 15:40 | 252.399 | 256.217 | 2207 | 42.7028 | 42.9224 | -0.21953 | 257.5342 | 38.6 | 42.3086 | -3.7086 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:40 | 249.366 | 253.112 | 2191.5 | 42.1853 | 42.9224 | -0.73703 | 257.5342 | 38 | 42.3086 | -4.3086 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:40 | 184.208 | 187.135 | 1624.2 | 31.1892 | 31.7943 | -0.60518 | 190.7661 | 28.2 | 31.3397 | -3.1397 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:40 | 185.213 | 190.048 | 1639 | 31.6747 | 31.7943 | -0.11968 | 190.7661 | 28.9 | 31.3397 | -2.4397 |  | 28-03-2026 15:40 | 174.226 | 176.61 | 1545.1 | 29.435 | 30.2484 | -0.81338 | 181.4903 | 27.3 | 29.8158 | -2.5158 |  | 28-03-2026 15:40 | 219.5533 | 222.6042 | -3.0508 | 1335.625 | 199 | 219.4209 | -20.4209 | -20.5533
28-03-2026 15:30 | 769 | 49.94 | 262.981 | 267.118 | 2150.4 | 44.5197 | 45.5902 | -1.0705 | 273.5412 | 40.9 | 44.9383 | -4.0383 |  | 28-03-2026 15:30 | 266.035 | 270.196 | 2168.4 | 45.0327 | 45.5902 | -0.55753 | 273.5412 | 41.3 | 44.9383 | -3.6383 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:30 | 263.745 | 267.87 | 2153.5 | 44.645 | 45.5902 | -0.94519 | 273.5412 | 40.7 | 44.9383 | -4.2383 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:30 | 194.772 | 197.948 | 1596 | 32.9913 | 33.7705 | -0.77918 | 202.6231 | 30.2 | 33.2876 | -3.0876 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:30 | 196.085 | 201.603 | 1610.1 | 33.6005 | 33.7705 | -0.17001 | 202.6231 | 29.2 | 33.2876 | -4.0876 |  | 28-03-2026 15:30 | 185.415 | 188.048 | 1517.8 | 31.3413 | 32.1285 | -0.78713 | 192.7708 | 27.8 | 31.669 | -3.869 |  | 28-03-2026 15:30 | 232.1305 | 236.4401 | -4.3096 | 1418.6404 | 210.1 | 233.059 | -22.959 | -22.0305
28-03-2026 15:20 | 786 | 49.65 | 267.946 | 272.082 | 2109.5 | 45.347 | 46.6499 | -1.3029 | 279.8991 | 42.4 | 45.9828 | -3.5828 |  | 28-03-2026 15:20 | 271.026 | 275.321 | 2127.1 | 45.8868 | 46.6499 | -0.76302 | 279.8991 | 44 | 45.9828 | -1.9828 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:20 | 268.929 | 273.163 | 2112.8 | 45.5272 | 46.6499 | -1.1227 | 279.8991 | 42.4 | 45.9828 | -3.5828 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:20 | 198.172 | 201.37 | 1565.8 | 33.5617 | 34.5555 | -0.99378 | 207.3327 | 31.1 | 34.0613 | -2.9613 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:20 | 199.036 | 204.473 | 1580.9 | 34.0788 | 34.5555 | -0.47662 | 207.3327 | 31.5 | 34.0613 | -2.5613 |  | 28-03-2026 15:20 | 188.162 | 190.853 | 1490 | 31.8088 | 32.8752 | -1.0664 | 197.2514 | 29.6 | 32.4051 | -2.8051 |  | 28-03-2026 15:20 | 236.2103 | 241.9357 | -5.7254 | 1451.6142 | 221 | 238.476 | -17.476 | -15.2103
28-03-2026 15:10 | 826 | 49.65 | 280.838 | 285.272 | 2067.1 | 47.5453 | 49.0239 | -1.4786 | 294.1434 | 44.9 | 48.3229 | -3.4229 |  | 28-03-2026 15:10 | 284.327 | 288.95 | 2083.1 | 48.1583 | 49.0239 | -0.86556 | 294.1434 | 44.8 | 48.3229 | -3.5229 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:10 | 280.315 | 284.844 | 2070.4 | 47.474 | 49.0239 | -1.5499 | 294.1434 | 45.9 | 48.3229 | -2.4229 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:10 | 207.02 | 210.628 | 1534.7 | 35.1047 | 36.314 | -1.2093 | 217.884 | 33.7 | 35.7947 | -2.0947 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:10 | 208.015 | 214.003 | 1549.4 | 35.6672 | 36.314 | -0.64683 | 217.884 | 34.7 | 35.7947 | -1.0947 |  | 28-03-2026 15:10 | 197.307 | 200.269 | 1460.4 | 33.3782 | 34.5483 | -1.1701 | 207.2896 | 32.5 | 34.0542 | -1.5542 |  | 28-03-2026 15:10 | 247.3277 | 254.248 | -6.9203 | 1525.4877 | 236.5 | 250.6122 | -14.1122 | -10.8277
28-03-2026 15:00 | 561 | 49.65 | 185.918 | 194.627 | 2022.2 | 32.4378 | 33.2959 | -0.85806 | 199.7753 | 48.2 | 32.8198 | 15.3802 | 0.9842 | 28-03-2026 15:00 | 188.761 | 191.48 | 2038.3 | 31.9133 | 33.2959 | -1.3826 | 199.7753 | 48.6 | 32.8198 | 15.7802 | 0.9839 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:00 | 222.213 | 229.497 | 2024.5 | 38.2495 | 33.2959 | 4.9536 | 199.7753 | 48.8 | 32.8198 | 15.9802 | 0.9838 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:00 | 94.062 | 99.351 | 1501 | 16.5585 | 24.6636 | -8.1051 | 147.9817 | 36.2 | 24.3109 | 11.8891 | 0.9833 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 15:00 | 213.863 | 225.535 | 1514.7 | 37.5892 | 24.6636 | 12.9255 | 147.9817 | 36.4 | 24.3109 | 12.0891 | 0.97189 | 28-03-2026 15:00 | 116.791 | 128.226 | 1427.9 | 21.371 | 23.4644 | -2.0934 | 140.7863 | 34.2 | 23.1288 | 11.0712 | 0.98894 | 28-03-2026 15:00 | 178.1193 | 172.6793 | 5.44 | 1036.0758 | 252.4 | 170.21 | 82.19 | 74.2807
28-03-2026 14:50 | 886 | 50.23 | 300.99 | 305.822 | 1974 | 50.9703 | 52.4681 | -1.4978 | 314.8088 | 40.1 | 51.7178 | -11.6178 | 0.9837 | 28-03-2026 14:50 | 304.366 | 309.346 | 1989.7 | 51.5577 | 52.4681 | -0.91046 | 314.8088 | 41.3 | 51.7178 | -10.4178 | 0.97841 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 14:50 | 302.271 | 307.248 | 1975.7 | 51.208 | 52.4681 | -1.2601 | 314.8088 | 39.4 | 51.7178 | -12.3178 | 0.9835 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 14:50 | 223.25 | 227.042 | 1464.8 | 37.8403 | 38.8653 | -1.0249 | 233.1917 | 28.7 | 38.3095 | -9.6095 | 0.98207 |  |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 28-03-2026 14:50 | 224.649 | 231.146 | 1478.3 | 38.5243 | 38.8653 | -0.34095 | 233.1917 | 29.1 | 38.3095 | -9.2095 | 0.97182 | 28-03-2026 14:50 | 212.714 | 215.092 | 1393.7 | 35.8487 | 36.9755 | -1.1268 | 221.853 | 27.1 | 36.4468 | -9.3468 | 0.9853 | 28-03-2026 14:50 | 265.9493 | 272.1104 | -6.1611 | 1632.6627 | 205.7 | 268.2193 | -62.5193 | -60.2493
28-03-2026 14:40 | 914 | 50.51 | 307.061 | 312.149 | 1933.9 | 52.0248 | 54.0681 | -2.0432 | 324.4085 | 51.8 | 53.2949 | -1.4949 | 0.9837 | 28-03-2026 14:40 | 308.543 | 315.35 | 1948.4 | 52.5583 | 54.0681 | -1.5097 | 324.4085 | 50.9 | 53.2949 | -2.3949 | 0.9832 | 28-03-2026 14:40 | 304.979 | 313.522 | 1916.9 | 52.2537 | 54.0681 | -1.8144 | 324.4085 | 52.2 | 53.2949 | -1.0949 | 0.97275 | 28-03-2026 14:40 | 307.248 | 312.403 | 1936.3 | 52.0672 | 54.0681 | -2.0009 | 324.4085 | 52 | 53.2949 | -1.2949 | 0.98339 | 28-03-2026 14:40 | 231.069 | 234.612 | 1446.9 | 39.102 | 40.0504 | -0.94843 | 240.3026 | 39 | 39.4777 | -0.47771 | 0.9849 | 28-03-2026 14:40 | 227.089 | 231.235 | 1436.1 | 38.5392 | 40.0504 | -1.5113 | 240.3026 | 38.4 | 39.4777 | -1.0777 | 0.98159 | 28-03-2026 14:40 | 228.008 | 232.39 | 1439.5 | 38.7317 | 40.0504 | -1.3188 | 240.3026 | 38.5 | 39.4777 | -0.97771 | 0.98114 | 28-03-2026 14:40 | 229.185 | 235.831 | 1449.2 | 39.3052 | 40.0504 | -0.74526 | 240.3026 | 38.8 | 39.4777 | -0.67771 | 0.97082 | 28-03-2026 14:40 | 215.702 | 218.92 | 1366.6 | 36.4867 | 38.103 | -1.6164 | 228.6181 | 36.5 | 37.5582 | -1.0582 | 0.98515 | 28-03-2026 14:40 | 401.0687 | 414.5771 | -13.5084 | 2487.4624 | 398.1 | 408.6486 | -10.5486 | -2.9687
28-03-2026 14:30 | 927 | 50.51 | 311.136 | 316.292 | 1882.1 | 52.7153 | 54.8371 | -2.1218 | 329.0226 | 51.2 | 54.0529 | -2.8529 | 0.9837 | 28-03-2026 14:30 | 314.851 | 320.231 | 1897.5 | 53.3718 | 54.8371 | -1.4653 | 329.0226 | 53.5 | 54.0529 | -0.55293 | 0.97931 | 28-03-2026 14:30 | 308.942 | 317.604 | 1864.7 | 52.934 | 54.8371 | -1.9031 | 329.0226 | 49.9 | 54.0529 | -4.1529 | 0.97273 | 28-03-2026 14:30 | 311.344 | 316.603 | 1884.3 | 52.7672 | 54.8371 | -2.0699 | 329.0226 | 51.1 | 54.0529 | -2.9529 | 0.9833 | 28-03-2026 14:30 | 234.246 | 237.837 | 1407.9 | 39.6395 | 40.6201 | -0.98058 | 243.7205 | 38.2 | 40.0392 | -1.8392 | 0.9849 | 28-03-2026 14:30 | 229.611 | 233.918 | 1397.7 | 38.9863 | 40.6201 | -1.6337 | 243.7205 | 37.4 | 40.0392 | -2.6392 | 0.98233 | 28-03-2026 14:30 | 231.318 | 236.065 | 1401 | 39.3442 | 40.6201 | -1.2759 | 243.7205 | 38.3 | 40.0392 | -1.7392 | 0.97989 | 28-03-2026 14:30 | 232.225 | 239.204 | 1410.4 | 39.8673 | 40.6201 | -0.75274 | 243.7205 | 38.5 | 40.0392 | -1.5392 | 0.97137 | 28-03-2026 14:30 | 218.477 | 221.77 | 1330.1 | 36.9617 | 38.645 | -1.6833 | 231.8698 | 36 | 38.0923 | -2.0923 | 0.98531 | 28-03-2026 14:30 | 406.5873 | 420.4737 | -13.8863 | 2522.8421 | 394.1 | 414.4609 | -20.3609 | -12.4873
28-03-2026 14:20 | 945 | 50.23 | 319.065 | 324.352 | 1830.9 | 54.0587 | 55.9621 | -1.9034 | 335.7723 | 41.8 | 55.1618 | -13.3618 | 0.9859 | 28-03-2026 14:20 | 321.39 | 328.179 | 1844 | 54.6965 | 55.9621 | -1.2656 | 335.7723 | 40.8 | 55.1618 | -14.3618 | 1.2506 | 28-03-2026 14:20 | 316.983 | 325.712 | 1814.8 | 54.2853 | 55.9621 | -1.6767 | 335.7723 | 41.3 | 55.1618 | -13.8618 | 0.9732 | 28-03-2026 14:20 | 319.705 | 325.135 | 1833.2 | 54.1892 | 55.9621 | -1.7729 | 335.7723 | 41 | 55.1618 | -14.1618 | 0.9863 | 28-03-2026 14:20 | 239.751 | 243.451 | 1369.7 | 40.5752 | 41.4534 | -0.87821 | 248.7202 | 31.3 | 40.8606 | -9.5606 | 0.9848 | 28-03-2026 14:20 | 235.715 | 239.956 | 1360.3 | 39.9927 | 41.4534 | -1.4607 | 248.7202 | 30.7 | 40.8606 | -10.1606 | 0.9857 | 28-03-2026 14:20 | 236.572 | 241.282 | 1362.7 | 40.2137 | 41.4534 | -1.2397 | 248.7202 | 30.7 | 40.8606 | -10.1606 | 0.98048 | 28-03-2026 14:20 | 237.612 | 244.616 | 1371.9 | 40.7693 | 41.4534 | -0.68404 | 248.7202 | 30.9 | 40.8606 | -9.9606 | 0.95768 | 28-03-2026 14:20 | 223.883 | 227.221 | 1294.1 | 37.8702 | 39.4378 | -1.5676 | 236.6265 | 28.9 | 38.8738 | -9.9738 | 1.0333 | 28-03-2026 14:20 | 416.6507 | 429.0995 | -12.4488 | 2574.5968 | 317.4 | 422.9633 | -105.5633 | -99.2507
28-03-2026 14:10 | 298 | 50.8 | 141.971 | 144.001 | 1789.1 | 24.0002 | 17.6087 | 6.3915 | 105.6521 | 54.4 | 17.3569 | 37.0431 | 0.9834 | 28-03-2026 14:10 | 133.696 | 106.906 | 1803.2 | 17.8177 | 17.6087 | 0.20899 | 105.6521 | 55.3 | 17.3569 | 37.9431 | 0.9828 | 28-03-2026 14:10 | 82.854 | 84.905 | 1773.5 | 14.1508 | 17.6087 | -3.4578 | 105.6521 | 52.8 | 17.3569 | 35.4431 | 0.97584 | 28-03-2026 14:10 | 94.699 | 96.014 | 1792.2 | 16.0023 | 17.6087 | -1.6063 | 105.6521 | 53.7 | 17.3569 | 36.3431 | 0.983 | 28-03-2026 14:10 | 61.353 | 63.909 | 1338.4 | 10.6515 | 13.0435 | -2.392 | 78.2608 | 40 | 12.8569 | 27.1431 | 0.96001 | 28-03-2026 14:10 | 154.467 | 156.708 | 1329.6 | 26.118 | 13.0435 | 13.0745 | 78.2608 | 39.4 | 12.8569 | 26.5431 | 0.9817 | 28-03-2026 14:10 | 58.211 | 59.2 | 1332 | 9.8667 | 13.0435 | -3.1768 | 78.2608 | 39.3 | 12.8569 | 26.4431 | 0.98329 | 28-03-2026 14:10 | 66.823 | 69.776 | 1341 | 11.6293 | 13.0435 | -1.4141 | 78.2608 | 40.3 | 12.8569 | 27.4431 | 0.97097 | 28-03-2026 14:10 | 98.995 | 95.805 | 1265.2 | 15.9675 | 12.4092 | 3.5583 | 74.4554 | 38.1 | 12.2318 | 25.8682 | 0.9847 | 28-03-2026 14:10 | 146.204 | 135.0178 | 11.1862 | 810.1068 | 413.3 | 133.0871 | 280.2129 | 267.096
28-03-2026 14:00 | 972 | 50.51 | 325.663 | 331.16 | 1734.7 | 55.1933 | 57.4991 | -2.3058 | 344.9946 | 53.2 | 56.6769 | -3.4769 | 0.9833 | 28-03-2026 14:00 | 330.429 | 336.211 | 1747.9 | 56.0352 | 57.4991 | -1.4639 | 344.9946 | 53.8 | 56.6769 | -2.8769 | 0.98319 | 28-03-2026 14:00 | 323.128 | 332.221 | 1720.7 | 55.3702 | 57.4991 | -2.1289 | 344.9946 | 55.2 | 56.6769 | -1.4769 | 0.97263 | 28-03-2026 14:00 | 325.434 | 331.062 | 1738.5 | 55.177 | 57.4991 | -2.3221 | 344.9946 | 55.5 | 56.6769 | -1.1769 | 0.9831 | 28-03-2026 14:00 | 244.312 | 248.133 | 1298.4 | 41.3555 | 42.5919 | -1.2364 | 255.5515 | 41.7 | 41.9829 | -0.28286 | 0.9846 | 28-03-2026 14:00 | 240.765 | 245.252 | 1290.2 | 40.8753 | 42.5919 | -1.7166 | 255.5515 | 41 | 41.9829 | -0.98286 | 0.98097 | 28-03-2026 14:00 | 241.788 | 246.561 | 1292.7 | 41.0935 | 42.5919 | -1.4984 | 255.5515 | 41.3 | 41.9829 | -0.68286 | 0.98064 | 28-03-2026 14:00 | 244.217 | 251.519 | 1300.7 | 41.9198 | 42.5919 | -0.67209 | 255.5515 | 41 | 41.9829 | -0.98286 | 0.97258 | 28-03-2026 14:00 | 229.919 | 233.491 | 1227.1 | 38.9152 | 40.5209 | -1.6058 | 243.1256 | 38.5 | 39.9415 | -1.4415 | 0.9848 | 28-03-2026 14:00 | 425.935 | 440.885 | -14.95 | 2645.3102 | 421.2 | 434.5804 | -13.3804 | -4.735
28-03-2026 13:50 | 987 | 50.8 | 331.743 | 337.377 | 1681.5 | 56.2295 | 58.3214 | -2.0919 | 349.9281 | 57 | 57.4874 | -0.48736 | 0.98141 | 28-03-2026 13:50 | 335.131 | 340.862 | 1694.1 | 56.8103 | 58.3214 | -1.511 | 349.9281 | 60.2 | 57.4874 | 2.7126 | 0.98304 | 28-03-2026 13:50 | 329.35 | 338.623 | 1665.5 | 56.4372 | 58.3214 | -1.8842 | 349.9281 | 55.3 | 57.4874 | -2.1874 | 0.97262 | 28-03-2026 13:50 | 331.7 | 337.402 | 1683 | 56.2337 | 58.3214 | -2.0877 | 349.9281 | 55.7 | 57.4874 | -1.7874 | 0.983 | 28-03-2026 13:50 | 249.321 | 253.221 | 1256.7 | 42.2035 | 43.201 | -0.99751 | 259.206 | 41.9 | 42.5832 | -0.68323 | 0.9846 | 28-03-2026 13:50 | 245.138 | 249.894 | 1249.2 | 41.649 | 43.201 | -1.552 | 259.206 | 41.7 | 42.5832 | -0.88323 | 0.98088 | 28-03-2026 13:50 | 246.621 | 251.316 | 1251.4 | 41.886 | 43.201 | -1.315 | 259.206 | 41.9 | 42.5832 | -0.68323 | 0.98132 | 28-03-2026 13:50 | 248.513 | 255.519 | 1259.7 | 42.5865 | 43.201 | -0.61451 | 259.206 | 42.1 | 42.5832 | -0.48323 | 0.97196 | 28-03-2026 13:50 | 233.131 | 236.73 | 1188.6 | 39.455 | 41.1004 | -1.6454 | 246.6024 | 39.6 | 40.5127 | -0.91267 | 0.9846 | 28-03-2026 13:50 | 433.4907 | 447.1899 | -13.6992 | 2683.1391 | 435.4 | 440.795 | -5.395 | 1.9093
28-03-2026 13:40 | 1011 | 50.51 | 336.723 | 343.103 | 1624.5 | 57.1838 | 59.8062 | -2.6223 | 358.837 | 55.4 | 58.9509 | -3.5509 | 0.9831 | 28-03-2026 13:40 | 340.867 | 346.749 | 1633.9 | 57.7915 | 59.8062 | -2.0147 | 358.837 | 53.6 | 58.9509 | -5.3509 | 0.983 | 28-03-2026 13:40 | 336.123 | 345.556 | 1610.2 | 57.5927 | 59.8062 | -2.2135 | 358.837 | 55.7 | 58.9509 | -3.2509 | 0.9727 | 28-03-2026 13:40 | 338.217 | 344.066 | 1627.3 | 57.3443 | 59.8062 | -2.4618 | 358.837 | 56.9 | 58.9509 | -2.0509 | 0.9827 | 28-03-2026 13:40 | 254.137 | 258.121 | 1214.8 | 43.0202 | 44.3009 | -1.2807 | 265.8052 | 42.8 | 43.6674 | -0.86736 | 0.98457 | 28-03-2026 13:40 | 249.649 | 254.516 | 1207.5 | 42.4193 | 44.3009 | -1.8815 | 265.8052 | 41.6 | 43.6674 | -2.0674 | 0.98094 | 28-03-2026 13:40 | 251.476 | 256.715 | 1209.5 | 42.7858 | 44.3009 | -1.515 | 265.8052 | 41.8 | 43.6674 | -1.8674 | 0.97959 | 28-03-2026 13:40 | 253.039 | 260.338 | 1217.6 | 43.3897 | 44.3009 | -0.91119 | 265.8052 | 42.1 | 43.6674 | -1.5674 | 0.97166 | 28-03-2026 13:40 | 237.762 | 241.481 | 1149 | 40.2468 | 42.1468 | -1.8999 | 252.8807 | 39.6 | 41.5441 | -1.9441 | 0.9846 | 28-03-2026 13:40 | 441.7742 | 458.5749 | -16.8007 | 2751.4491 | 429.5 | 452.0172 | -22.5172 | -12.2742
28-03-2026 13:30 | 1011 | 51.95 | 337.675 | 343.48 | 1569.1 | 57.2467 | 59.4752 | -2.2285 | 356.8511 | 59.2 | 58.6247 | 0.57531 | 0.9829 | 28-03-2026 13:30 | 341.532 | 347.438 | 1580.3 | 57.9063 | 59.4752 | -1.5689 | 356.8511 | 58.9 | 58.6247 | 0.27531 | 0.9841 | 28-03-2026 13:30 | 335.891 | 345.64 | 1554.5 | 57.6067 | 59.4752 | -1.8685 | 356.8511 | 56.6 | 58.6247 | -2.0247 | 0.97179 | 28-03-2026 13:30 | 339.226 | 345.198 | 1570.4 | 57.533 | 59.4752 | -1.9422 | 356.8511 | 56.3 | 58.6247 | -2.3247 | 0.9827 | 28-03-2026 13:30 | 254.495 | 258.528 | 1172 | 43.088 | 44.0557 | -0.96769 | 264.3342 | 42.3 | 43.4257 | -1.1257 | 0.9844 | 28-03-2026 13:30 | 250.753 | 255.624 | 1165.9 | 42.604 | 44.0557 | -1.4517 | 264.3342 | 41.6 | 43.4257 | -1.8257 | 0.98009 | 28-03-2026 13:30 | 251.234 | 256.356 | 1167.7 | 42.726 | 44.0557 | -1.3297 | 264.3342 | 41.9 | 43.4257 | -1.5257 | 0.98002 | 28-03-2026 13:30 | 252.834 | 260.209 | 1175.5 | 43.3682 | 44.0557 | -0.68753 | 264.3342 | 42.1 | 43.4257 | -1.3257 | 0.97108 | 28-03-2026 13:30 | 238.428 | 242.157 | 1109.4 | 40.3595 | 41.9135 | -1.554 | 251.4812 | 40.1 | 41.3142 | -1.2142 | 0.9845 | 28-03-2026 13:30 | 442.4383 | 456.0371 | -13.5987 | 2736.2223 | 439 | 449.5157 | -10.5157 | -3.4383
28-03-2026 13:20 | 1027 | 51.37 | 344.261 | 350.25 | 1509.9 | 58.375 | 60.5519 | -2.1769 | 363.3111 | 55.8 | 59.686 | -3.886 | 0.9831 | 28-03-2026 13:20 | 339.846 | 345.337 | 1521.4 | 57.5562 | 60.5519 | -2.9957 | 363.3111 | 56.1 | 59.686 | -3.586 | 0.98325 | 28-03-2026 13:20 | 340.757 | 350.624 | 1497.9 | 58.4373 | 60.5519 | -2.1145 | 363.3111 | 57 | 59.686 | -2.686 | 0.97186 | 28-03-2026 13:20 | 344.047 | 350.104 | 1514.1 | 58.3507 | 60.5519 | -2.2012 | 363.3111 | 57.2 | 59.686 | -2.486 | 0.9842 | 28-03-2026 13:20 | 258.205 | 262.27 | 1129.7 | 43.7117 | 44.8532 | -1.1416 | 269.1194 | 43.8 | 44.2118 | -0.41182 | 0.9845 | 28-03-2026 13:20 | 254.569 | 259.74 | 1124.3 | 43.29 | 44.8532 | -1.5632 | 269.1194 | 43.2 | 44.2118 | -1.0118 | 0.98048 | 28-03-2026 13:20 | 256.246 | 261.639 | 1125.8 | 43.6065 | 44.8532 | -1.2467 | 269.1194 | 43.3 | 44.2118 | -0.91182 | 0.97939 | 28-03-2026 13:20 | 257.888 | 265.568 | 1133.4 | 44.2613 | 44.8532 | -0.59189 | 269.1194 | 43.5 | 44.2118 | -0.71182 | 0.97005 | 28-03-2026 13:20 | 243.057 | 246.884 | 1069.3 | 41.1473 | 42.6723 | -1.525 | 256.0337 | 40.5 | 42.0621 | -1.5621 | 0.9845 | 28-03-2026 13:20 | 448.736 | 464.2926 | -15.5566 | 2785.7556 | 440.4 | 457.6532 | -17.2532 | -8.336
28-03-2026 13:10 | 1043 | 50.8 | 349.611 | 355.621 | 1454.1 | 59.2702 | 61.6304 | -2.3602 | 369.7822 | 58.1 | 60.7491 | -2.6491 | 0.983 | 28-03-2026 13:10 | 352.274 | 358.274 | 1465.3 | 59.7123 | 61.6304 | -1.918 | 369.7822 | 60.9 | 60.7491 | 0.15094 | 0.9826 | 28-03-2026 13:10 | 346.936 | 356.929 | 1440.9 | 59.4882 | 61.6304 | -2.1422 | 369.7822 | 57.9 | 60.7491 | -2.8491 | 0.972 | 28-03-2026 13:10 | 341.661 | 347.146 | 1456.9 | 57.8577 | 61.6304 | -3.7727 | 369.7822 | 58.2 | 60.7491 | -2.5491 | 0.9825 | 28-03-2026 13:10 | 263.049 | 267.218 | 1085.9 | 44.5363 | 45.6521 | -1.1158 | 273.9128 | 43.2 | 44.9993 | -1.7993 | 0.9844 | 28-03-2026 13:10 | 258.999 | 264.155 | 1081.1 | 44.0258 | 45.6521 | -1.6263 | 273.9128 | 42.4 | 44.9993 | -2.5993 | 0.97919 | 28-03-2026 13:10 | 260.323 | 265.772 | 1082.5 | 44.2953 | 45.6521 | -1.3568 | 273.9128 | 42.7 | 44.9993 | -2.2993 | 0.9795 | 28-03-2026 13:10 | 261.641 | 269.718 | 1089.9 | 44.953 | 45.6521 | -0.69913 | 273.9128 | 43 | 44.9993 | -1.9993 | 0.97017 | 28-03-2026 13:10 | 246.228 | 250.105 | 1028.8 | 41.6842 | 43.4323 | -1.7482 | 260.5941 | 40.9 | 42.8113 | -1.9113 | 0.9844 | 28-03-2026 13:10 | 455.823 | 472.5623 | -16.7393 | 2835.374 | 447.3 | 465.8047 | -18.5047 | -8.523
28-03-2026 13:00 | 1041 | 50.8 | 347.217 | 353.222 | 1396 | 58.8703 | 61.5122 | -2.6419 | 369.0731 | 57.5 | 60.6326 | -3.1326 | 0.9829 | 28-03-2026 13:00 | 350.452 | 356.658 | 1404.4 | 59.443 | 61.5122 | -2.0692 | 369.0731 | 58.8 | 60.6326 | -1.8326 | 0.9826 | 28-03-2026 13:00 | 344.621 | 354.673 | 1383 | 59.1122 | 61.5122 | -2.4 | 369.0731 | 57.1 | 60.6326 | -3.5326 | 0.97166 | 28-03-2026 13:00 | 347.574 | 353.765 | 1398.7 | 58.9608 | 61.5122 | -2.5514 | 369.0731 | 58.3 | 60.6326 | -2.3326 | 0.9825 | 28-03-2026 13:00 | 260.604 | 264.788 | 1042.7 | 44.1313 | 45.5646 | -1.4333 | 273.3875 | 43.2 | 44.913 | -1.713 | 0.9842 | 28-03-2026 13:00 | 256.73 | 262.185 | 1038.7 | 43.6975 | 45.5646 | -1.8671 | 273.3875 | 43.1 | 44.913 | -1.813 | 0.9817 | 28-03-2026 13:00 | 257.853 | 263.145 | 1039.8 | 43.8575 | 45.5646 | -1.7071 | 273.3875 | 43.3 | 44.913 | -1.613 | 0.97989 | 28-03-2026 13:00 | 259.335 | 267.308 | 1046.9 | 44.5513 | 45.5646 | -1.0133 | 273.3875 | 43.5 | 44.913 | -1.413 | 0.97042 | 28-03-2026 13:00 | 244.225 | 248.095 | 987.9 | 41.3492 | 43.3491 | -1.9999 | 260.0944 | 40.5 | 42.7292 | -2.2292 | 0.9844 | 28-03-2026 13:00 | 453.9732 | 471.6562 | -17.683 | 2829.937 | 445.3 | 464.9115 | -19.6115 | -8.6732
28-03-2026 12:50 | 1049 | 51.95 | 349.777 | 355.862 | 1338.5 | 59.3103 | 61.7107 | -2.4003 | 370.2639 | 58 | 60.8282 | -2.8282 | 0.983 | 28-03-2026 12:50 | 352.817 | 359.065 | 1345.6 | 59.8442 | 61.7107 | -1.8665 | 370.2639 | 55.7 | 60.8282 | -5.1282 | 0.98217 | 28-03-2026 12:50 | 348.832 | 358.917 | 1325.9 | 59.8195 | 61.7107 | -1.8912 | 370.2639 | 57.8 | 60.8282 | -3.0282 | 0.9719 | 28-03-2026 12:50 | 350.807 | 357.055 | 1340.4 | 59.5092 | 61.7107 | -2.2015 | 370.2639 | 56.9 | 60.8282 | -3.9282 | 0.9826 | 28-03-2026 12:50 | 263.954 | 268.232 | 999.5 | 44.7053 | 45.7116 | -1.0063 | 274.2696 | 44.2 | 45.0579 | -0.85792 | 0.98405 | 28-03-2026 12:50 | 259.796 | 264.64 | 995.6 | 44.1067 | 45.7116 | -1.6049 | 274.2696 | 43.1 | 45.0579 | -1.9579 | 0.98076 | 28-03-2026 12:50 | 261.071 | 266.311 | 996.5 | 44.3852 | 45.7116 | -1.3264 | 274.2696 | 43.4 | 45.0579 | -1.6579 | 0.98032 | 28-03-2026 12:50 | 262.643 | 270.65 | 1003.4 | 45.1083 | 45.7116 | -0.60326 | 274.2696 | 43.6 | 45.0579 | -1.4579 | 0.96992 | 28-03-2026 12:50 | 247.105 | 251.021 | 947.4 | 41.8368 | 43.4889 | -1.6521 | 260.9335 | 41.1 | 42.867 | -1.767 | 0.9845 | 28-03-2026 12:50 | 458.6255 | 473.1779 | -14.5524 | 2839.0675 | 443.8 | 466.4115 | -22.6115 | -14.8255
28-03-2026 12:40 | 1043 | 51.09 | 349.57 | 355.615 | 1280.5 | 59.2692 | 61.5616 | -2.2924 | 369.3696 | 58.5 | 60.6813 | -2.1813 | 0.9829 | 28-03-2026 12:40 | 352.777 | 359.18 | 1289.9 | 59.8633 | 61.5616 | -1.6983 | 369.3696 | 58.3 | 60.6813 | -2.3813 | 0.9827 | 28-03-2026 12:40 | 347.618 | 357.384 | 1268.1 | 59.564 | 61.5616 | -1.9976 | 369.3696 | 57.9 | 60.6813 | -2.7813 | 0.97267 | 28-03-2026 12:40 | 350.152 | 356.353 | 1283.5 | 59.3922 | 61.5616 | -2.1694 | 369.3696 | 58.4 | 60.6813 | -2.2813 | 0.98473 | 28-03-2026 12:40 | 263.424 | 267.571 | 955.3 | 44.5952 | 45.6012 | -1.006 | 273.6071 | 43.4 | 44.9491 | -1.5491 | 0.9845 | 28-03-2026 12:40 | 259.042 | 264.124 | 952.5 | 44.0207 | 45.6012 | -1.5805 | 273.6071 | 42.7 | 44.9491 | -2.2491 | 0.98072 | 28-03-2026 12:40 | 261.385 | 266.358 | 953.1 | 44.393 | 45.6012 | -1.2082 | 273.6071 | 43 | 44.9491 | -1.9491 | 0.98133 | 28-03-2026 12:40 | 262.814 | 270.966 | 959.8 | 45.161 | 45.6012 | -0.44019 | 273.6071 | 43.3 | 44.9491 | -1.6491 | 0.97195 | 28-03-2026 12:40 | 247.097 | 250.987 | 906.3 | 41.8312 | 43.3839 | -1.5527 | 260.3033 | 41.3 | 42.7635 | -1.4635 | 0.98442 | 28-03-2026 12:40 | 458.0897 | 472.0351 | -13.9454 | 2832.2104 | 446.8 | 465.285 | -18.485 | -11.2897
28-03-2026 12:30 | 1039 | 50.8 | 347.253 | 353.294 | 1222 | 58.8823 | 61.394 | -2.5117 | 368.3641 | 56.6 | 60.5161 | -3.9161 | 0.9832 | 28-03-2026 12:30 | 350.627 | 356.8 | 1231.6 | 59.4667 | 61.394 | -1.9273 | 368.3641 | 58.8 | 60.5161 | -1.7161 | 0.98265 | 28-03-2026 12:30 | 344.798 | 355.021 | 1210.2 | 59.1702 | 61.394 | -2.2238 | 368.3641 | 57 | 60.5161 | -3.5161 | 0.9712 | 28-03-2026 12:30 | 339.689 | 344.958 | 1225.1 | 57.493 | 61.394 | -3.901 | 368.3641 | 58.3 | 60.5161 | -2.2161 | 0.9826 | 28-03-2026 12:30 | 261.274 | 265.468 | 911.9 | 44.2447 | 45.477 | -1.2324 | 272.8623 | 43.9 | 44.8267 | -0.92672 | 0.9842 | 28-03-2026 12:30 | 257.334 | 262.393 | 909.8 | 43.7322 | 45.477 | -1.7449 | 272.8623 | 42.8 | 44.8267 | -2.0267 | 0.98179 | 28-03-2026 12:30 | 259.162 | 264.414 | 910.1 | 44.069 | 45.477 | -1.408 | 272.8623 | 42.9 | 44.8267 | -1.9267 | 0.98014 | 28-03-2026 12:30 | 260.589 | 268.11 | 916.5 | 44.685 | 45.477 | -0.79205 | 272.8623 | 43.1 | 44.8267 | -1.7267 | 0.97019 | 28-03-2026 12:30 | 245.22 | 249.1 | 865 | 41.5167 | 43.2658 | -1.7491 | 259.5947 | 40.6 | 42.6471 | -2.0471 | 0.9845 | 28-03-2026 12:30 | 453.2597 | 470.75 | -17.4903 | 2824.5001 | 444 | 464.0183 | -20.0183 | -9.2597
28-03-2026 12:20 | 1034 | 50.8 | 345.759 | 351.667 | 1165.4 | 58.6112 | 61.0986 | -2.4874 | 366.5914 | 57.5 | 60.2249 | -2.7249 | 0.9828 | 28-03-2026 12:20 | 349.805 | 355.983 | 1172.8 | 59.3305 | 61.0986 | -1.7681 | 366.5914 | 57.2 | 60.2249 | -3.0249 | 0.9825 | 28-03-2026 12:20 | 343.615 | 353.836 | 1153.2 | 58.9727 | 61.0986 | -2.1259 | 366.5914 | 56.9 | 60.2249 | -3.3249 | 0.97111 | 28-03-2026 12:20 | 346.447 | 352.582 | 1166.8 | 58.7637 | 61.0986 | -2.3349 | 366.5914 | 56.7 | 60.2249 | -3.5249 | 0.9826 | 28-03-2026 12:20 | 260.402 | 264.502 | 868 | 44.0837 | 45.2582 | -1.1745 | 271.5492 | 43.2 | 44.611 | -1.411 | 0.9845 | 28-03-2026 12:20 | 256.897 | 261.662 | 867 | 43.6103 | 45.2582 | -1.6479 | 271.5492 | 43.2 | 44.611 | -1.411 | 0.98172 | 28-03-2026 12:20 | 258.372 | 263.372 | 867.2 | 43.8953 | 45.2582 | -1.3629 | 271.5492 | 43.3 | 44.611 | -1.311 | 0.98102 | 28-03-2026 12:20 | 259.683 | 267.661 | 873.4 | 44.6102 | 45.2582 | -0.64803 | 271.5492 | 43.7 | 44.611 | -0.911 | 0.97202 | 28-03-2026 12:20 | 244.445 | 248.294 | 824.4 | 41.3823 | 43.0576 | -1.6752 | 258.3454 | 40.6 | 42.4418 | -1.8418 | 0.9844 | 28-03-2026 12:20 | 453.2598 | 468.4846 | -15.2248 | 2810.9077 | 442.3 | 461.7853 | -19.4853 | -10.9598
28-03-2026 12:10 | 1030 | 50.51 | 342.299 | 348.29 | 1107.9 | 58.0483 | 60.9301 | -2.8818 | 365.5807 | 57.7 | 60.0588 | -2.3588 | 0.98143 | 28-03-2026 12:10 | 346.997 | 353.178 | 1115.6 | 58.863 | 60.9301 | -2.0671 | 365.5807 | 59.4 | 60.0588 | -0.65881 | 0.9828 | 28-03-2026 12:10 | 340.16 | 349.826 | 1096.3 | 58.3043 | 60.9301 | -2.6258 | 365.5807 | 57.5 | 60.0588 | -2.5588 | 0.97237 | 28-03-2026 12:10 | 344.227 | 350.323 | 1110.1 | 58.3872 | 60.9301 | -2.5429 | 365.5807 | 58.1 | 60.0588 | -1.9588 | 0.9827 | 28-03-2026 12:10 | 257.2 | 261.302 | 824.8 | 43.5503 | 45.1334 | -1.5831 | 270.8005 | 42.8 | 44.488 | -1.688 | 0.9843 | 28-03-2026 12:10 | 254.935 | 259.681 | 823.8 | 43.2802 | 45.1334 | -1.8533 | 270.8005 | 42.3 | 44.488 | -2.188 | 0.98205 | 28-03-2026 12:10 | 255.07 | 259.961 | 823.9 | 43.3268 | 45.1334 | -1.8066 | 270.8005 | 42.5 | 44.488 | -1.988 | 0.98119 | 28-03-2026 12:10 | 257.149 | 264.55 | 829.7 | 44.0917 | 45.1334 | -1.0418 | 270.8005 | 42.7 | 44.488 | -1.788 | 0.97129 | 28-03-2026 12:10 | 242.713 | 246.559 | 783.8 | 41.0932 | 42.9389 | -1.8457 | 257.6331 | 40.9 | 42.3248 | -1.4248 | 0.9847 | 28-03-2026 12:10 | 448.945 | 467.193 | -18.248 | 2803.1579 | 443.9 | 460.5121 | -16.6121 | -5.045
28-03-2026 12:00 | 1024 | 51.66 | 343.287 | 349.783 | 1050.2 | 58.2972 | 60.3075 | -2.0103 | 361.8448 | 57.3 | 59.4451 | -2.1451 | 0.9832 | 28-03-2026 12:00 | 347.054 | 353.128 | 1056.2 | 58.8547 | 60.3075 | -1.4528 | 361.8448 | 57.9 | 59.4451 | -1.5451 | 0.98118 | 28-03-2026 12:00 | 340.579 | 350.674 | 1038.8 | 58.4457 | 60.3075 | -1.8618 | 361.8448 | 56.1 | 59.4451 | -3.3451 | 0.97121 | 28-03-2026 12:00 | 343.896 | 349.95 | 1052 | 58.325 | 60.3075 | -1.9825 | 361.8448 | 57.4 | 59.4451 | -2.0451 | 0.9828 | 28-03-2026 12:00 | 258.283 | 262.349 | 782 | 43.7248 | 44.6722 | -0.94736 | 268.0332 | 43 | 44.0334 | -1.0334 | 0.9845 | 28-03-2026 12:00 | 255.022 | 259.684 | 781.5 | 43.2807 | 44.6722 | -1.3915 | 268.0332 | 42.6 | 44.0334 | -1.4334 | 0.98215 | 28-03-2026 12:00 | 255.69 | 261.056 | 781.4 | 43.5093 | 44.6722 | -1.1629 | 268.0332 | 42.6 | 44.0334 | -1.4334 | 0.97945 | 28-03-2026 12:00 | 257.35 | 264.956 | 787 | 44.1593 | 44.6722 | -0.51286 | 268.0332 | 42.9 | 44.0334 | -1.1334 | 0.97107 | 28-03-2026 12:00 | 242.647 | 246.417 | 742.9 | 41.0695 | 42.5001 | -1.4306 | 255.0004 | 39.9 | 41.8923 | -1.9923 | 0.9846 | 28-03-2026 12:00 | 449.6662 | 462.4187 | -12.7525 | 2774.5121 | 439.7 | 455.8061 | -16.1061 | -9.9662
28-03-2026 11:50 | 1012 | 50.8 | 339.306 | 345.104 | 992.9 | 57.5173 | 59.7986 | -2.2813 | 358.7916 | 57.6 | 58.9435 | -1.3435 | 0.98356 | 28-03-2026 11:50 | 343.263 | 349.848 | 998.3 | 58.308 | 59.7986 | -1.4906 | 358.7916 | 56.7 | 58.9435 | -2.2435 | 0.9828 | 28-03-2026 11:50 | 336.827 | 346.407 | 982.7 | 57.7345 | 59.7986 | -2.0641 | 358.7916 | 56.4 | 58.9435 | -2.5435 | 0.97234 | 28-03-2026 11:50 | 340.998 | 346.966 | 994.6 | 57.8277 | 59.7986 | -1.9709 | 358.7916 | 56.3 | 58.9435 | -2.6435 | 0.9828 | 28-03-2026 11:50 | 255.826 | 259.827 | 739 | 43.3045 | 44.2953 | -0.99076 | 265.7715 | 42.2 | 43.6618 | -1.4618 | 0.9846 | 28-03-2026 11:50 | 252.738 | 257.332 | 738.9 | 42.8887 | 44.2953 | -1.4066 | 265.7715 | 41.7 | 43.6618 | -1.9618 | 0.98031 | 28-03-2026 11:50 | 253.378 | 258.516 | 738.8 | 43.086 | 44.2953 | -1.2093 | 265.7715 | 41.7 | 43.6618 | -1.9618 | 0.98013 | 28-03-2026 11:50 | 254.792 | 262.383 | 744.1 | 43.7305 | 44.2953 | -0.56476 | 265.7715 | 42.6 | 43.6618 | -1.0618 | 0.97026 | 28-03-2026 11:50 | 240.617 | 244.38 | 703 | 40.73 | 42.1414 | -1.4114 | 252.8487 | 40.2 | 41.5388 | -1.3388 | 0.9846 | 28-03-2026 11:50 | 445.1272 | 458.5169 | -13.3897 | 2751.1011 | 435.4 | 451.9601 | -16.5601 | -9.7272
28-03-2026 11:40 | 1005 | 51.09 | 337.459 | 343.101 | 935.3 | 57.1835 | 59.3187 | -2.1352 | 355.9123 | 54.7 | 58.4705 | -3.7705 | 0.98271 | 28-03-2026 11:40 | 341.051 | 347.02 | 941.6 | 57.8367 | 59.3187 | -1.482 | 355.9123 | 56.8 | 58.4705 | -1.6705 |  | 28-03-2026 11:40 | 334.727 | 344.676 | 926.3 | 57.446 | 59.3187 | -1.8727 | 355.9123 | 55.8 | 58.4705 | -2.6705 | 0.97114 | 28-03-2026 11:40 | 337.886 | 343.799 | 938.3 | 57.2998 | 59.3187 | -2.0189 | 355.9123 | 56.3 | 58.4705 | -2.1705 | 0.983 | 28-03-2026 11:40 | 253.613 | 257.58 | 696.8 | 42.93 | 43.9398 | -1.0098 | 263.6387 | 42.1 | 43.3114 | -1.2114 | 0.9846 | 28-03-2026 11:40 | 250.169 | 255.194 | 697.2 | 42.5323 | 43.9398 | -1.4075 | 263.6387 | 41.7 | 43.3114 | -1.6114 | 0.98053 | 28-03-2026 11:40 | 251.644 | 256.722 | 697.1 | 42.787 | 43.9398 | -1.1528 | 263.6387 | 41.8 | 43.3114 | -1.5114 | 0.98022 | 28-03-2026 11:40 | 252.705 | 260.45 | 701.5 | 43.4083 | 43.9398 | -0.53145 | 263.6387 | 41.5 | 43.3114 | -1.8114 | 0.9713 | 28-03-2026 11:40 | 238.424 | 242.153 | 662.8 | 40.3588 | 41.8033 | -1.4444 | 250.8196 | 39.2 | 41.2055 | -2.0055 | 0.9848 | 28-03-2026 11:40 | 441.7825 | 454.8372 | -13.0547 | 2729.0234 | 429.9 | 448.3331 | -18.4331 | -11.8825
28-03-2026 11:30 | 995 | 50.8 | 335.399 | 341.301 | 880.6 | 56.8835 | 58.7941 | -1.9106 | 352.7644 | 55.9 | 57.9533 | -2.0533 | 0.9835 | 28-03-2026 11:30 | 338.791 | 344.685 | 884.8 | 57.4475 | 58.7941 | -1.3466 | 352.7644 | 55.5 | 57.9533 | -2.4533 | 0.9831 | 28-03-2026 11:30 | 333.176 | 342.529 | 870.5 | 57.0882 | 58.7941 | -1.7059 | 352.7644 | 54.6 | 57.9533 | -3.3533 | 0.97269 | 28-03-2026 11:30 | 336.227 | 342.042 | 882 | 57.007 | 58.7941 | -1.7871 | 352.7644 | 55.2 | 57.9533 | -2.7533 | 0.9832 | 28-03-2026 11:30 | 252.016 | 255.984 | 654.7 | 42.664 | 43.5512 | -0.88717 | 261.307 | 41.3 | 42.9284 | -1.6284 | 0.9845 | 28-03-2026 11:30 | 249.286 | 254.235 | 655.5 | 42.3725 | 43.5512 | -1.1787 | 261.307 | 40.8 | 42.9284 | -2.1284 | 0.98076 | 28-03-2026 11:30 | 249.973 | 254.752 | 655.3 | 42.4587 | 43.5512 | -1.0925 | 261.307 | 41 | 42.9284 | -1.9284 | 0.98124 | 28-03-2026 11:30 | 251.84 | 259.282 | 660 | 43.2137 | 43.5512 | -0.3375 | 261.307 | 41.9 | 42.9284 | -1.0284 | 0.97188 | 28-03-2026 11:30 | 237.319 | 240.982 | 623.6 | 40.1637 | 41.4335 | -1.2699 | 248.6012 | 39.3 | 40.841 | -1.541 | 0.9849 | 28-03-2026 11:30 | 439.2987 | 450.8145 | -11.5158 | 2704.887 | 425.5 | 444.3678 | -18.8678 | -13.7987
28-03-2026 11:20 | 980 | 50.8 | 331.165 | 336.721 | 824.7 | 56.1202 | 57.9077 | -1.7876 | 347.4464 | 53.4 | 57.0796 | -3.6796 | 0.9836 | 28-03-2026 11:20 | 333.881 | 339.621 | 829.3 | 56.6035 | 57.9077 | -1.3042 | 347.4464 | 54.9 | 57.0796 | -2.1796 | 0.9832 | 28-03-2026 11:20 | 327.92 | 336.917 | 815.9 | 56.1528 | 57.9077 | -1.7549 | 347.4464 | 53.7 | 57.0796 | -3.3796 | 0.9733 | 28-03-2026 11:20 | 331.134 | 336.792 | 826.8 | 56.132 | 57.9077 | -1.7757 | 347.4464 | 54.2 | 57.0796 | -2.8796 | 0.9833 | 28-03-2026 11:20 | 247.681 | 251.504 | 613.4 | 41.9173 | 42.8946 | -0.97728 | 257.3677 | 41.2 | 42.2812 | -1.0812 | 0.9848 | 28-03-2026 11:20 | 245.111 | 249.919 | 614.7 | 41.6532 | 42.8946 | -1.2414 | 257.3677 | 40.8 | 42.2812 | -1.4812 | 0.98243 | 28-03-2026 11:20 | 246.294 | 251.156 | 614.3 | 41.8593 | 42.8946 | -1.0353 | 257.3677 | 41 | 42.2812 | -1.2812 | 0.98064 | 28-03-2026 11:20 | 248.22 | 255.403 | 618.1 | 42.5672 | 42.8946 | -0.32745 | 257.3677 | 40.7 | 42.2812 | -1.5812 | 0.97132 | 28-03-2026 11:20 | 233.578 | 237.159 | 584.3 | 39.5265 | 40.8089 | -1.2824 | 244.8535 | 38.3 | 40.2253 | -1.9253 | 0.985 | 28-03-2026 11:20 | 432.532 | 444.0183 | -11.4863 | 2664.1098 | 418.2 | 437.6688 | -19.4688 | -14.332
28-03-2026 11:10 | 957 | 51.37 | 323.643 | 329.039 | 771.3 | 54.8398 | 56.4247 | -1.5848 | 338.548 | 54.8 | 55.6178 | -0.81779 | 0.9835 | 28-03-2026 11:10 | 326.222 | 331.796 | 774.4 | 55.2993 | 56.4247 | -1.1253 | 338.548 | 53.7 | 55.6178 | -1.9178 | 0.9832 | 28-03-2026 11:10 | 321.321 | 330.098 | 762.2 | 55.0163 | 56.4247 | -1.4083 | 338.548 | 52.9 | 55.6178 | -2.7178 | 0.97341 | 28-03-2026 11:10 | 324.23 | 329.737 | 772.6 | 54.9562 | 56.4247 | -1.4685 | 338.548 | 53.5 | 55.6178 | -2.1178 | 0.9836 | 28-03-2026 11:10 | 242.868 | 246.617 | 572.2 | 41.1028 | 41.796 | -0.69321 | 250.7763 | 39.4 | 41.1984 | -1.7984 | 0.9848 | 28-03-2026 11:10 | 240.042 | 244.336 | 573.9 | 40.7227 | 41.796 | -1.0734 | 250.7763 | 39 | 41.1984 | -2.1984 | 0.98244 | 28-03-2026 11:10 | 241.534 | 246.293 | 573.3 | 41.0488 | 41.796 | -0.74721 | 250.7763 | 40.2 | 41.1984 | -0.99836 | 0.98068 | 28-03-2026 11:10 | 243.421 | 250.608 | 577.4 | 41.768 | 41.796 | -0.028043 | 250.7763 | 39.5 | 41.1984 | -1.6984 | 0.97107 | 28-03-2026 11:10 | 228.812 | 232.296 | 546 | 38.716 | 39.7638 | -1.0478 | 238.5826 | 37.8 | 39.1951 | -1.3951 | 0.985 | 28-03-2026 11:10 | 423.47 | 432.6466 | -9.1766 | 2595.8794 | 410.8 | 426.4597 | -15.6597 | -12.67
28-03-2026 11:00 | 933 | 51.09 | 313.806 | 319.071 | 716.5 | 53.1785 | 55.069 | -1.8905 | 330.4141 | 50.4 | 54.2815 | -3.8815 | 0.9838 | 28-03-2026 11:00 | 316.8 | 322.213 | 720.7 | 53.7022 | 55.069 | -1.3668 | 330.4141 | 51.5 | 54.2815 | -2.7815 | 0.9834 | 28-03-2026 11:00 | 311.867 | 320.333 | 709.3 | 53.3888 | 55.069 | -1.6802 | 330.4141 | 51.2 | 54.2815 | -3.0815 | 0.97357 | 28-03-2026 11:00 | 314.819 | 320.067 | 719.1 | 53.3445 | 55.069 | -1.7245 | 330.4141 | 51.8 | 54.2815 | -2.4815 | 0.9834 | 28-03-2026 11:00 | 236.17 | 239.815 | 532.8 | 39.9692 | 40.7919 | -0.82269 | 244.7512 | 38.7 | 40.2085 | -1.5085 | 0.9848 | 28-03-2026 11:00 | 233.982 | 238.165 | 534.9 | 39.6942 | 40.7919 | -1.0977 | 244.7512 | 38.5 | 40.2085 | -1.7085 | 0.98422 | 28-03-2026 11:00 | 234.12 | 238.326 | 533.1 | 39.721 | 40.7919 | -1.0709 | 244.7512 | 38.1 | 40.2085 | -2.1085 | 0.98235 | 28-03-2026 11:00 | 236.178 | 243.214 | 537.9 | 40.5357 | 40.7919 | -0.25619 | 244.7512 | 39.4 | 40.2085 | -0.80854 | 0.97129 | 28-03-2026 11:00 | 222.407 | 225.794 | 508.2 | 37.6323 | 38.8084 | -1.1761 | 232.8504 | 36.8 | 38.2534 | -1.4534 | 0.9852 | 28-03-2026 11:00 | 411.1663 | 422.2519 | -11.0856 | 2533.5113 | 396.4 | 416.2137 | -19.8137 | -14.7663
28-03-2026 10:50 | 913 | 54.53 | 308.769 | 313.853 | 666.1 | 52.3088 | 53.1745 | -0.86569 | 319.0471 | 50.9 | 52.4141 | -1.5141 | 0.98371 | 28-03-2026 10:50 | 311.826 | 317.09 | 669.2 | 52.8483 | 53.1745 | -0.32619 | 319.0471 | 53.5 | 52.4141 | 1.0859 | 0.98417 | 28-03-2026 10:50 | 306.105 | 314.302 | 658.1 | 52.3837 | 53.1745 | -0.79085 | 319.0471 | 50.6 | 52.4141 | -1.8141 | 0.97392 | 28-03-2026 10:50 | 309.525 | 314.75 | 667.3 | 52.4583 | 53.1745 | -0.71619 | 319.0471 | 51.3 | 52.4141 | -1.1141 | 0.9839 | 28-03-2026 10:50 | 231.216 | 234.761 | 494.1 | 39.1268 | 39.3885 | -0.2617 | 236.3312 | 38.3 | 38.8253 | -0.52528 | 0.9849 | 28-03-2026 10:50 | 229.837 | 233.522 | 496.4 | 38.9203 | 39.3885 | -0.4682 | 236.3312 | 38.1 | 38.8253 | -0.72528 | 0.98301 | 28-03-2026 10:50 | 229.642 | 233.629 | 495 | 38.9382 | 39.3885 | -0.45037 | 236.3312 | 37.5 | 38.8253 | -1.3253 | 0.98293 | 28-03-2026 10:50 | 230.93 | 237.757 | 498.5 | 39.6262 | 39.3885 | 0.23763 | 236.3312 | 38.2 | 38.8253 | -0.62528 | 0.97213 | 28-03-2026 10:50 | 218.695 | 221.98 | 471.4 | 36.9967 | 37.4733 | -0.47664 | 224.8399 | 36.2 | 36.9374 | -0.73744 | 0.9855 | 28-03-2026 10:50 | 403.6073 | 407.7255 | -4.1182 | 2446.3532 | 394.6 | 401.8951 | -7.2951 | -9.0073
28-03-2026 10:40 | 886 | 54.24 | 302.81 | 307.825 | 615.2 | 51.3042 | 51.6604 | -0.35625 | 309.9625 | 50.5 | 50.9217 | -0.42167 | 0.9843 | 28-03-2026 10:40 | 305.849 | 310.769 | 615.7 | 51.7948 | 51.6604 | 0.13442 | 309.9625 | 48.3 | 50.9217 | -2.6217 | 0.9842 | 28-03-2026 10:40 | 300.929 | 309.169 | 607.5 | 51.5282 | 51.6604 | -0.13225 | 309.9625 | 49.5 | 50.9217 | -1.4217 | 0.97335 | 28-03-2026 10:40 | 304.968 | 309.958 | 616 | 51.6597 | 51.6604 | -0.00074565 | 309.9625 | 50 | 50.9217 | -0.92167 | 0.9841 | 28-03-2026 10:40 | 227.498 | 230.822 | 455.8 | 38.4703 | 38.267 | 0.20336 | 229.6018 | 37.4 | 37.7198 | -0.31975 | 0.9856 | 28-03-2026 10:40 | 226.294 | 230.206 | 458.3 | 38.3677 | 38.267 | 0.10069 | 229.6018 | 37.2 | 37.7198 | -0.51975 | 0.98359 | 28-03-2026 10:40 | 226.013 | 229.995 | 457.5 | 38.3325 | 38.267 | 0.065528 | 229.6018 | 37.7 | 37.7198 | -0.019754 | 0.98269 | 28-03-2026 10:40 | 227.266 | 233.781 | 460.3 | 38.9635 | 38.267 | 0.69653 | 229.6018 | 37.3 | 37.7198 | -0.41975 | 0.97153 | 28-03-2026 10:40 | 215.281 | 218.449 | 435.2 | 36.4082 | 36.4063 | 0.0018822 | 218.4377 | 35.3 | 35.8857 | -0.58567 | 0.9855 | 28-03-2026 10:40 | 396.829 | 396.1158 | 0.71318 | 2376.6949 | 383.2 | 390.4514 | -7.2514 | -13.629
28-03-2026 10:30 | 861 | 52.23 | 296.293 | 301.019 | 564.7 | 50.1698 | 50.5962 | -0.42633 | 303.577 | 49.1 | 49.8726 | -0.77264 | 0.9846 | 28-03-2026 10:30 | 299.43 | 304.237 | 567.4 | 50.7062 | 50.5962 | 0.11 | 303.577 | 48.7 | 49.8726 | -1.1726 | 0.9843 | 28-03-2026 10:30 | 294.277 | 301.701 | 558 | 50.2835 | 50.5962 | -0.31267 | 303.577 | 48.7 | 49.8726 | -1.1726 | 0.97539 | 28-03-2026 10:30 | 297.169 | 301.97 | 566 | 50.3283 | 50.5962 | -0.26783 | 303.577 | 49.3 | 49.8726 | -0.57264 | 0.9842 | 28-03-2026 10:30 | 221.846 | 225.064 | 418.4 | 37.5107 | 37.4786 | 0.032025 | 224.8719 | 36.7 | 36.9427 | -0.2427 | 0.9857 | 28-03-2026 10:30 | 220.491 | 224.169 | 421.1 | 37.3615 | 37.4786 | -0.11714 | 224.8719 | 36.5 | 36.9427 | -0.4427 | 0.98497 | 28-03-2026 10:30 | 220.601 | 224.344 | 419.8 | 37.3907 | 37.4786 | -0.087975 | 224.8719 | 36.1 | 36.9427 | -0.8427 | 0.98332 | 28-03-2026 10:30 | 222.096 | 228.604 | 423 | 38.1007 | 37.4786 | 0.62202 | 224.8719 | 36.2 | 36.9427 | -0.7427 | 0.97193 | 28-03-2026 10:30 | 210.188 | 213.281 | 399.9 | 35.5468 | 35.6563 | -0.10945 | 213.9377 | 34.3 | 35.1464 | -0.8464 | 0.9858 | 28-03-2026 10:30 | 387.3982 | 387.9555 | -0.55735 | 2327.7331 | 375.6 | 382.4078 | -6.8078 | -11.7982
28-03-2026 10:20 | 832 | 52.23 | 287.81 | 292.312 | 515.6 | 48.7187 | 48.892 | -0.17333 | 293.352 | 46.9 | 48.1928 | -1.2928 | 0.98216 | 28-03-2026 10:20 | 290.255 | 294.885 | 518.7 | 49.1475 | 48.892 | 0.2555 | 293.352 | 49.8 | 48.1928 | 1.6072 | 0.98285 | 28-03-2026 10:20 | 285.386 | 292.569 | 509.3 | 48.7615 | 48.892 | -0.1305 | 293.352 | 46.4 | 48.1928 | -1.7928 | 0.97545 | 28-03-2026 10:20 | 288.411 | 293.041 | 516.7 | 48.8402 | 48.892 | -0.051832 | 293.352 | 46.9 | 48.1928 | -1.2928 | 0.9844 | 28-03-2026 10:20 | 215.049 | 218.101 | 381.7 | 36.3502 | 36.2163 | 0.13387 | 217.2978 | 35.3 | 35.6984 | -0.3984 | 0.98601 | 28-03-2026 10:20 | 214.267 | 217.536 | 384.6 | 36.256 | 36.2163 | 0.039705 | 217.2978 | 35.2 | 35.6984 | -0.4984 | 0.98492 | 28-03-2026 10:20 | 214.521 | 218.508 | 383.7 | 36.418 | 36.2163 | 0.2017 | 217.2978 | 35.2 | 35.6984 | -0.4984 | 0.98175 | 28-03-2026 10:20 | 216.022 | 222.26 | 386.8 | 37.0433 | 36.2163 | 0.82704 | 217.2978 | 35.6 | 35.6984 | -0.098402 | 0.97134 | 28-03-2026 10:20 | 204.518 | 207.464 | 365.6 | 34.5773 | 34.4553 | 0.12201 | 206.7319 | 33.6 | 33.9626 | -0.36261 | 0.9859 | 28-03-2026 10:20 | 376.1127 | 374.8885 | 1.2242 | 2249.331 | 364.9 | 369.5276 | -4.6276 | -11.2127
28-03-2026 10:10 | 805 | 52.81 | 279.071 | 284.141 | 468.7 | 47.3568 | 47.1992 | 0.15762 | 283.1953 | 46 | 46.5243 | -0.52426 | 0.9851 | 28-03-2026 10:10 | 280.533 | 285.427 | 468.9 | 47.5712 | 47.1992 | 0.37195 | 283.1953 | 46.2 | 46.5243 | -0.32426 | 0.98526 | 28-03-2026 10:10 | 277.347 | 284.39 | 462.9 | 47.3983 | 47.1992 | 0.19912 | 283.1953 | 45.5 | 46.5243 | -1.0243 | 0.97523 | 28-03-2026 10:10 | 280.195 | 284.635 | 469.8 | 47.4392 | 47.1992 | 0.23995 | 283.1953 | 46 | 46.5243 | -0.52426 | 0.9848 | 28-03-2026 10:10 | 208.707 | 211.67 | 346.4 | 35.2783 | 34.9624 | 0.31595 | 209.7743 | 33.9 | 34.4624 | -0.56242 | 0.986 | 28-03-2026 10:10 | 207.577 | 210.756 | 349.4 | 35.126 | 34.9624 | 0.16362 | 209.7743 | 33.8 | 34.4624 | -0.66242 | 0.98556 | 28-03-2026 10:10 | 208.259 | 211.909 | 348.5 | 35.3182 | 34.9624 | 0.35579 | 209.7743 | 34.1 | 34.4624 | -0.36242 | 0.98278 | 28-03-2026 10:10 | 210.133 | 216.333 | 351.2 | 36.0555 | 34.9624 | 1.0931 | 209.7743 | 34.4 | 34.4624 | -0.062418 | 0.97177 | 28-03-2026 10:10 | 198.423 | 201.261 | 332 | 33.5435 | 33.2624 | 0.28113 | 199.5742 | 32.6 | 32.7867 | -0.18672 | 0.9862 | 28-03-2026 10:10 | 365.087 | 361.9087 | 3.1783 | 2171.4525 | 352.5 | 356.7335 | -4.2335 | -12.587
28-03-2026 10:00 | 771 | 52.52 | 269.479 | 273.555 | 422.7 | 45.5925 | 45.2565 | 0.33596 | 271.5392 | 43.3 | 44.6094 | -1.3094 | 0.98546 | 28-03-2026 10:00 | 270.339 | 274.384 | 422.7 | 45.7307 | 45.2565 | 0.47413 | 271.5392 | 42.5 | 44.6094 | -2.1094 | 0.98429 | 28-03-2026 10:00 | 267.578 | 273.915 | 417.4 | 45.6525 | 45.2565 | 0.39596 | 271.5392 | 43.5 | 44.6094 | -1.1094 | 0.97687 | 28-03-2026 10:00 | 269.901 | 274.067 | 423.8 | 45.6778 | 45.2565 | 0.4213 | 271.5392 | 44.7 | 44.6094 | 0.090631 | 0.9852 | 28-03-2026 10:00 | 201.14 | 203.913 | 312.5 | 33.9855 | 33.5234 | 0.46214 | 201.1402 | 33.2 | 33.044 | 0.15602 | 0.9864 | 28-03-2026 10:00 | 200.704 | 203.645 | 315.6 | 33.9408 | 33.5234 | 0.41747 | 201.1402 | 33.2 | 33.044 | 0.15602 | 0.9865 | 28-03-2026 10:00 | 200.73 | 204.232 | 314.4 | 34.0387 | 33.5234 | 0.51531 | 201.1402 | 32.8 | 33.044 | -0.24398 | 0.98285 | 28-03-2026 10:00 | 202.492 | 208.375 | 316.8 | 34.7292 | 33.5234 | 1.2058 | 201.1402 | 33.1 | 33.044 | 0.056023 | 0.9725 | 28-03-2026 10:00 | 191.398 | 194.076 | 299.4 | 32.346 | 31.8933 | 0.45267 | 191.36 | 31.3 | 31.4373 | -0.13725 | 0.9864 | 28-03-2026 10:00 | 351.6937 | 347.0129 | 4.6807 | 2082.0775 | 337.6 | 342.0506 | -4.4506 | -14.0937
28-03-2026 09:50 | 741 | 52.23 | 260.544 | 264.388 | 379.4 | 44.0647 | 43.5444 | 0.52023 | 261.2666 | 43.2 | 42.9218 | 0.27825 |  | 28-03-2026 09:50 | 261.886 | 266.065 | 380.2 | 44.3442 | 43.5444 | 0.79973 | 261.2666 | 44.5 | 42.9218 | 1.5782 |  | 28-03-2026 09:50 | 257.809 | 263.948 | 373.9 | 43.9913 | 43.5444 | 0.4469 | 261.2666 | 42.1 | 42.9218 | -0.82175 |  | 28-03-2026 09:50 | 260.963 | 264.883 | 379.1 | 44.1472 | 43.5444 | 0.60273 | 261.2666 | 42 | 42.9218 | -0.92175 |  | 28-03-2026 09:50 | 193.917 | 196.571 | 279.3 | 32.7618 | 32.2551 | 0.5067 | 193.5308 | 31.2 | 31.7939 | -0.59389 |  | 28-03-2026 09:50 | 193.826 | 196.478 | 282.4 | 32.7463 | 32.2551 | 0.4912 | 193.5308 | 31.2 | 31.7939 | -0.59389 |  | 28-03-2026 09:50 | 193.793 | 196.543 | 281.6 | 32.7572 | 32.2551 | 0.50203 | 193.5308 | 32 | 31.7939 | 0.20611 |  | 28-03-2026 09:50 | 195.525 | 201.054 | 283.7 | 33.509 | 32.2551 | 1.2539 | 193.5308 | 31.8 | 31.7939 | 0.0061106 |  | 28-03-2026 09:50 | 184.962 | 187.512 | 268.1 | 31.252 | 30.6868 | 0.56523 | 184.1206 | 30.2 | 30.2479 | -0.047948 |  | 28-03-2026 09:50 | 339.5737 | 333.8851 | 5.6886 | 2003.3104 | 328.2 | 329.1105 | -0.91051 | -11.3737
28-03-2026 09:40 | 705 | 51.95 | 248.348 | 251.925 | 336.2 | 41.9875 | 41.4738 | 0.51371 | 248.8428 | 40 | 40.8807 | -0.88072 |  | 28-03-2026 09:40 | 249.463 | 253.133 | 335.7 | 42.1888 | 41.4738 | 0.71504 | 248.8428 | 39.6 | 40.8807 | -1.2807 |  | 28-03-2026 09:40 | 245.853 | 251.37 | 331.8 | 41.895 | 41.4738 | 0.42121 | 248.8428 | 40.2 | 40.8807 | -0.68072 |  | 28-03-2026 09:40 | 248.968 | 252.631 | 337.1 | 42.1052 | 41.4738 | 0.63137 | 248.8428 | 40.7 | 40.8807 | -0.18072 |  | 28-03-2026 09:40 | 184.801 | 187.273 | 248.1 | 31.2122 | 30.7213 | 0.49084 | 184.328 | 30.1 | 30.282 | -0.18201 |  | 28-03-2026 09:40 | 184.742 | 187.251 | 251.2 | 31.2085 | 30.7213 | 0.48717 | 184.328 | 30.2 | 30.282 | -0.082014 |  | 28-03-2026 09:40 | 184.062 | 186.744 | 249.6 | 31.124 | 30.7213 | 0.40267 | 184.328 | 29.3 | 30.282 | -0.98201 |  | 28-03-2026 09:40 | 185.969 | 191.173 | 251.9 | 31.8622 | 30.7213 | 1.1408 | 184.328 | 30 | 30.282 | -0.28201 |  | 28-03-2026 09:40 | 176.218 | 178.63 | 237.9 | 29.7717 | 29.2275 | 0.54413 | 175.3652 | 28.8 | 28.8096 | -0.0095859 |  | 28-03-2026 09:40 | 323.355 | 318.008 | 5.347 | 1908.0482 | 308.9 | 313.4605 | -4.5605 | -14.455
28-03-2026 09:30 | 662 | 51.95 | 232.266 | 235.516 | 296.2 | 39.2527 | 38.9442 | 0.30848 | 233.6651 | 39.7 | 38.3873 | 1.3127 |  | 28-03-2026 09:30 | 233.073 | 236.725 | 296.1 | 39.4542 | 38.9442 | 0.50998 | 233.6651 | 38.9 | 38.3873 | 0.51271 |  | 28-03-2026 09:30 | 230.938 | 236.395 | 291.6 | 39.3992 | 38.9442 | 0.45498 | 233.6651 | 37.7 | 38.3873 | -0.68729 |  | 28-03-2026 09:30 | 233.078 | 236.339 | 296.4 | 39.3898 | 38.9442 | 0.44565 | 233.6651 | 38.2 | 38.3873 | -0.18729 |  | 28-03-2026 09:30 | 173.012 | 175.85 | 218 | 29.3083 | 28.8475 | 0.46079 | 173.0853 | 28.3 | 28.435 | -0.13503 |  | 28-03-2026 09:30 | 173.651 | 176.054 | 221 | 29.3423 | 28.8475 | 0.49479 | 173.0853 | 28.4 | 28.435 | -0.035026 |  | 28-03-2026 09:30 | 173.95 | 176.723 | 220.3 | 29.4538 | 28.8475 | 0.60629 | 173.0853 | 28.5 | 28.435 | 0.064974 |  | 28-03-2026 09:30 | 175.083 | 179.894 | 221.9 | 29.9823 | 28.8475 | 1.1348 | 173.0853 | 28.7 | 28.435 | 0.26497 |  | 28-03-2026 09:30 | 165.14 | 167.315 | 209.1 | 27.8858 | 27.4449 | 0.44097 | 164.6692 | 26.8 | 27.0524 | -0.25241 |  | 28-03-2026 09:30 | 303.4685 | 298.6118 | 4.8567 | 1791.6708 | 295.2 | 294.3417 | 0.85835 | -8.2685
28-03-2026 09:20 | 628 | 52.23 | 221.937 | 224.951 | 256.5 | 37.4918 | 36.9041 | 0.58778 | 221.4243 | 33.9 | 36.3763 | -2.4763 |  | 28-03-2026 09:20 | 223.153 | 226.332 | 257.2 | 37.722 | 36.9041 | 0.81794 | 221.4243 | 36.5 | 36.3763 | 0.12367 |  | 28-03-2026 09:20 | 218.956 | 223.53 | 253.9 | 37.255 | 36.9041 | 0.35094 | 221.4243 | 35.5 | 36.3763 | -0.87633 |  | 28-03-2026 09:20 | 222.282 | 225.37 | 258.2 | 37.5617 | 36.9041 | 0.65761 | 221.4243 | 36 | 36.3763 | -0.37633 |  | 28-03-2026 09:20 | 164.552 | 166.665 | 189.7 | 27.7775 | 27.3363 | 0.44116 | 164.018 | 26.7 | 26.9454 | -0.24543 |  | 28-03-2026 09:20 | 165.331 | 167.463 | 192.6 | 27.9105 | 27.3363 | 0.57416 | 164.018 | 26.8 | 26.9454 | -0.14543 |  | 28-03-2026 09:20 | 165.057 | 167.34 | 191.8 | 27.89 | 27.3363 | 0.55366 | 164.018 | 26.7 | 26.9454 | -0.24543 |  | 28-03-2026 09:20 | 166.554 | 171.255 | 193.2 | 28.5425 | 27.3363 | 1.2062 | 164.018 | 26.9 | 26.9454 | -0.045429 |  | 28-03-2026 09:20 | 158.014 | 160.095 | 182.3 | 26.6825 | 26.0071 | 0.67536 | 156.0428 | 25.5 | 25.6352 | -0.13524 |  | 28-03-2026 09:20 | 288.8335 | 282.9687 | 5.8648 | 1697.8123 | 274.5 | 278.9223 | -4.4223 | -14.3335
28-03-2026 09:10 | 590 | 52.52 | 209.062 | 211.837 | 222.6 | 35.3062 | 34.6321 | 0.67406 | 207.7927 | 34.5 | 34.1369 | 0.36313 |  | 28-03-2026 09:10 | 209.608 | 212.412 | 220.7 | 35.402 | 34.6321 | 0.76989 | 207.7927 | 32.2 | 34.1369 | -1.9369 |  | 28-03-2026 09:10 | 206.376 | 210.558 | 218.4 | 35.093 | 34.6321 | 0.46089 | 207.7927 | 33 | 34.1369 | -1.1369 |  | 28-03-2026 09:10 | 209.574 | 212.42 | 222.2 | 35.4033 | 34.6321 | 0.77122 | 207.7927 | 33.5 | 34.1369 | -0.63687 |  | 28-03-2026 09:10 | 154.612 | 156.582 | 163 | 26.097 | 25.6534 | 0.44359 | 153.9205 | 24.7 | 25.2866 | -0.58657 |  | 28-03-2026 09:10 | 155.82 | 157.808 | 165.8 | 26.3013 | 25.6534 | 0.64792 | 153.9205 | 25.3 | 25.2866 | 0.013429 |  | 28-03-2026 09:10 | 155.279 | 157.245 | 165.1 | 26.2075 | 25.6534 | 0.55409 | 153.9205 | 25.2 | 25.2866 | -0.086571 |  | 28-03-2026 09:10 | 155.972 | 160.254 | 166.3 | 26.709 | 25.6534 | 1.0556 | 153.9205 | 25.4 | 25.2866 | 0.11343 |  | 28-03-2026 09:10 | 148.925 | 150.825 | 156.8 | 25.1375 | 24.406 | 0.73145 | 146.4363 | 24 | 24.057 | -0.057041 |  | 28-03-2026 09:10 | 271.6568 | 265.5481 | 6.1087 | 1593.2889 | 257.8 | 261.7508 | -3.9508 | -13.8568
28-03-2026 09:00 | 552 | 48.79 | 195.271 | 197.763 | 188.1 | 32.9605 | 32.8697 | 0.090844 | 197.2179 | 30.9 | 32.3996 | -1.4996 |  | 28-03-2026 09:00 | 196.387 | 198.916 | 188.5 | 33.1527 | 32.8697 | 0.28301 | 197.2179 | 31.3 | 32.3996 | -1.0996 |  | 28-03-2026 09:00 | 193.208 | 196.836 | 185.4 | 32.806 | 32.8697 | -0.063656 | 197.2179 | 30.8 | 32.3996 | -1.5996 |  | 28-03-2026 09:00 | 195.949 | 198.53 | 188.7 | 33.0883 | 32.8697 | 0.21868 | 197.2179 | 31.6 | 32.3996 | -0.79962 |  | 28-03-2026 09:00 | 144.772 | 146.56 | 138.3 | 24.4267 | 24.3479 | 0.078773 | 146.0874 | 23.3 | 23.9997 | -0.69972 |  | 28-03-2026 09:00 | 145.525 | 147.337 | 140.5 | 24.5562 | 24.3479 | 0.20827 | 146.0874 | 23.5 | 23.9997 | -0.49972 |  | 28-03-2026 09:00 | 145.555 | 147.353 | 139.9 | 24.5588 | 24.3479 | 0.21094 | 146.0874 | 23.2 | 23.9997 | -0.79972 |  | 28-03-2026 09:00 | 145.216 | 149.246 | 140.9 | 24.8743 | 24.3479 | 0.52644 | 146.0874 | 23.2 | 23.9997 | -0.79972 |  | 28-03-2026 09:00 | 138.705 | 140.461 | 132.8 | 23.4102 | 23.164 | 0.24616 | 138.984 | 22.7 | 22.8328 | -0.13276 |  | 28-03-2026 09:00 | 253.8337 | 252.0342 | 1.7995 | 1512.2052 | 240.5 | 248.4301 | -7.9301 | -13.3337
28-03-2026 08:50 | 508 | 44.77 | 179.761 | 182 | 157.2 | 30.3333 | 30.7139 | -0.38055 | 184.2833 | 28.7 | 30.2747 | -1.5747 |  | 28-03-2026 08:50 | 179.533 | 182.513 | 157.2 | 30.4188 | 30.7139 | -0.29505 | 184.2833 | 29 | 30.2747 | -1.2747 |  | 28-03-2026 08:50 | 177.583 | 180.851 | 154.6 | 30.1418 | 30.7139 | -0.57205 | 184.2833 | 28.2 | 30.2747 | -2.0747 |  | 28-03-2026 08:50 | 179.305 | 181.575 | 157.1 | 30.2625 | 30.7139 | -0.45138 | 184.2833 | 28.6 | 30.2747 | -1.6747 |  | 28-03-2026 08:50 | 132.602 | 134.213 | 115 | 22.3688 | 22.751 | -0.38219 | 136.5061 | 21.1 | 22.4257 | -1.3257 |  | 28-03-2026 08:50 | 133.407 | 135.014 | 117 | 22.5023 | 22.751 | -0.24869 | 136.5061 | 21 | 22.4257 | -1.4257 |  | 28-03-2026 08:50 | 133.621 | 135.23 | 116.7 | 22.5383 | 22.751 | -0.21269 | 136.5061 | 21.2 | 22.4257 | -1.2257 |  | 28-03-2026 08:50 | 133.51 | 137.403 | 117.7 | 22.9005 | 22.751 | 0.14948 | 136.5061 | 21.3 | 22.4257 | -1.1257 |  | 28-03-2026 08:50 | 126.977 | 128.506 | 110.1 | 21.4177 | 21.6448 | -0.22711 | 129.8687 | 19.5 | 21.3353 | -1.8353 |  | 28-03-2026 08:50 | 232.8842 | 235.5044 | -2.6202 | 1413.0264 | 218.6 | 232.1367 | -13.5367 | -14.2842
28-03-2026 08:40 | 465 | 42.19 | 162.978 | 164.941 | 128.5 | 27.4902 | 28.3868 | -0.89666 | 170.321 | 25.4 | 27.9809 | -2.5809 |  | 28-03-2026 08:40 | 163.387 | 165.405 | 128.2 | 27.5675 | 28.3868 | -0.81933 | 170.321 | 25.4 | 27.9809 | -2.5809 |  | 28-03-2026 08:40 | 160.566 | 163.13 | 126.4 | 27.1883 | 28.3868 | -1.1985 | 170.321 | 25.4 | 27.9809 | -2.5809 |  | 28-03-2026 08:40 | 163.205 | 165.221 | 128.5 | 27.5368 | 28.3868 | -0.84999 | 170.321 | 25.5 | 27.9809 | -2.4809 |  | 28-03-2026 08:40 | 120.109 | 121.531 | 93.9 | 20.2552 | 21.0273 | -0.77211 | 126.1637 | 18.7 | 20.7266 | -2.0266 |  | 28-03-2026 08:40 | 121.833 | 123.275 | 96 | 20.5458 | 21.0273 | -0.48145 | 126.1637 | 19 | 20.7266 | -1.7266 |  | 28-03-2026 08:40 | 121.438 | 122.863 | 95.5 | 20.4772 | 21.0273 | -0.55011 | 126.1637 | 18.9 | 20.7266 | -1.8266 |  | 28-03-2026 08:40 | 122.116 | 125.283 | 96.4 | 20.8805 | 21.0273 | -0.14678 | 126.1637 | 19 | 20.7266 | -1.7266 |  | 28-03-2026 08:40 | 114.931 | 116.303 | 90.6 | 19.3838 | 20.0049 | -0.62102 | 120.0291 | 18.2 | 19.7188 | -1.5188 |  | 28-03-2026 08:40 | 211.3253 | 217.6613 | -6.3359 | 1305.9676 | 195.5 | 214.5487 | -19.0487 | -15.8253
28-03-2026 08:30 | 419 | 39.32 | 145.576 | 147.285 | 103.1 | 24.5475 | 25.8521 | -1.3046 | 155.1123 | 22.3 | 25.4824 | -3.1824 |  | 28-03-2026 08:30 | 145.043 | 147.586 | 102.8 | 24.5977 | 25.8521 | -1.2544 | 155.1123 | 23 | 25.4824 | -2.4824 |  | 28-03-2026 08:30 | 143.331 | 145.565 | 101 | 24.2608 | 25.8521 | -1.5912 | 155.1123 | 22.2 | 25.4824 | -3.2824 |  | 28-03-2026 08:30 | 146.008 | 147.751 | 103 | 24.6252 | 25.8521 | -1.2269 | 155.1123 | 22.7 | 25.4824 | -2.7824 |  | 28-03-2026 08:30 | 107.136 | 108.371 | 75.2 | 18.0618 | 19.1497 | -1.0878 | 114.898 | 16.7 | 18.8758 | -2.1758 |  | 28-03-2026 08:30 | 108.927 | 110.183 | 77 | 18.3638 | 19.1497 | -0.78584 | 114.898 | 17 | 18.8758 | -1.8758 |  | 28-03-2026 08:30 | 108.505 | 109.767 | 76.6 | 18.2945 | 19.1497 | -0.85517 | 114.898 | 16.9 | 18.8758 | -1.9758 |  | 28-03-2026 08:30 | 109.253 | 112.164 | 77.4 | 18.694 | 19.1497 | -0.45567 | 114.898 | 17 | 18.8758 | -1.8758 |  | 28-03-2026 08:30 | 102.664 | 103.869 | 72.4 | 17.3115 | 18.2185 | -0.90704 | 109.3112 | 15.8 | 17.958 | -2.158 |  | 28-03-2026 08:30 | 188.7568 | 198.2254 | -9.4686 | 1189.3526 | 173.6 | 195.3908 | -21.7908 | -15.1568
28-03-2026 08:20 | 376 | 37.31 | 129.019 | 130.485 | 80.8 | 21.7475 | 23.3708 | -1.6233 | 140.2248 | 18 | 23.0366 | -5.0366 |  | 28-03-2026 08:20 | 128.515 | 130.023 | 79.8 | 21.6705 | 23.3708 | -1.7003 | 140.2248 | 17.4 | 23.0366 | -5.6366 |  | 28-03-2026 08:20 | 126.099 | 127.933 | 78.8 | 21.3222 | 23.3708 | -2.0486 | 140.2248 | 17.4 | 23.0366 | -5.6366 |  | 28-03-2026 08:20 | 128.856 | 130.368 | 80.3 | 21.728 | 23.3708 | -1.6428 | 140.2248 | 17.7 | 23.0366 | -5.3366 |  | 28-03-2026 08:20 | 94.144 | 95.23 | 58.5 | 15.8717 | 17.3117 | -1.44 | 103.8702 | 13 | 17.0641 | -4.0641 |  | 28-03-2026 08:20 | 96.064 | 97.142 | 60 | 16.1903 | 17.3117 | -1.1214 | 103.8702 | 13.4 | 17.0641 | -3.6641 |  | 28-03-2026 08:20 | 95.723 | 96.817 | 59.7 | 16.1362 | 17.3117 | -1.1755 | 103.8702 | 13.4 | 17.0641 | -3.6641 |  | 28-03-2026 08:20 | 96.4 | 98.95 | 60.4 | 16.4917 | 17.3117 | -0.82003 | 103.8702 | 13.5 | 17.0641 | -3.5641 |  | 28-03-2026 08:20 | 90.72 | 91.757 | 56.6 | 15.2928 | 16.4699 | -1.1771 | 98.8196 | 12.7 | 16.2344 | -3.5344 |  | 28-03-2026 08:20 | 166.4508 | 179.1999 | -12.7491 | 1075.1995 | 136.5 | 176.6374 | -40.1374 | -29.9508
28-03-2026 08:10 | 212 | 36.45 | 73.081 | 73.976 | 62.8 | 12.3293 | 13.2186 | -0.88927 | 79.3116 | 15.3 | 13.0296 | 2.2704 |  | 28-03-2026 08:10 | 71.545 | 72.465 | 62.4 | 12.0775 | 13.2186 | -1.1411 | 79.3116 | 15.1 | 13.0296 | 2.0704 |  | 28-03-2026 08:10 | 69.383 | 70.268 | 61.4 | 11.7113 | 13.2186 | -1.5073 | 79.3116 | 15 | 13.0296 | 1.9704 |  | 28-03-2026 08:10 | 70.726 | 71.629 | 62.6 | 11.9382 | 13.2186 | -1.2804 | 79.3116 | 15.4 | 13.0296 | 2.3704 |  | 28-03-2026 08:10 | 50.977 | 51.743 | 45.5 | 8.6238 | 9.7916 | -1.1677 | 58.7493 | 11.2 | 9.6515 | 1.5485 |  | 28-03-2026 08:10 | 53.585 | 54.34 | 46.6 | 9.0567 | 9.7916 | -0.73489 | 58.7493 | 11.3 | 9.6515 | 1.6485 |  | 28-03-2026 08:10 | 52.871 | 53.633 | 46.3 | 8.9388 | 9.7916 | -0.85272 | 58.7493 | 11.3 | 9.6515 | 1.6485 |  | 28-03-2026 08:10 | 51.847 | 52.912 | 46.9 | 8.8187 | 9.7916 | -0.97289 | 58.7493 | 11.2 | 9.6515 | 1.5485 |  | 28-03-2026 08:10 | 50.363 | 51.12 | 43.9 | 8.52 | 9.3155 | -0.79545 | 55.8927 | 10.6 | 9.1822 | 1.4178 |  | 28-03-2026 08:10 | 92.0143 | 101.3561 | -9.3417 | 608.1364 | 116.4 | 99.9067 | 16.4933 | 24.3857
28-03-2026 08:00 | 297 | 36.16 | 97.801 | 98.869 | 47.5 | 16.4782 | 18.5381 | -2.0599 | 111.2285 | 13 | 18.273 | -5.273 |  | 28-03-2026 08:00 | 97.979 | 99.089 | 47.3 | 16.5148 | 18.5381 | -2.0233 | 111.2285 | 13.4 | 18.273 | -4.873 |  | 28-03-2026 08:00 | 95.701 | 96.798 | 46.4 | 16.133 | 18.5381 | -2.4051 | 111.2285 | 12.9 | 18.273 | -5.373 |  | 28-03-2026 08:00 | 97.898 | 99.007 | 47.2 | 16.5012 | 18.5381 | -2.0369 | 111.2285 | 13.2 | 18.273 | -5.073 |  | 28-03-2026 08:00 | 71.321 | 72.187 | 34.3 | 12.0312 | 13.7319 | -1.7008 | 82.3915 | 9.6 | 13.5356 | -3.9356 |  | 28-03-2026 08:00 | 73.178 | 74.012 | 35.3 | 12.3353 | 13.7319 | -1.3966 | 82.3915 | 9.9 | 13.5356 | -3.6356 |  | 28-03-2026 08:00 | 72.347 | 73.058 | 35 | 12.1763 | 13.7319 | -1.5556 | 82.3915 | 9.7 | 13.5356 | -3.8356 |  | 28-03-2026 08:00 | 73.195 | 75.222 | 35.7 | 12.537 | 13.7319 | -1.1949 | 82.3915 | 9.9 | 13.5356 | -3.6356 |  | 28-03-2026 08:00 | 69.558 | 70.41 | 33.3 | 11.735 | 13.0642 | -1.3292 | 78.3853 | 9.4 | 12.8774 | -3.4774 |  | 28-03-2026 08:00 | 126.442 | 142.1443 | -15.7023 | 852.8655 | 101 | 140.1116 | -39.1116 | -25.442
28-03-2026 07:50 | 244 | 34.15 | 78.747 | 79.655 | 34.5 | 13.2758 | 15.3414 | -2.0656 | 92.0487 | 11.5 | 15.1221 | -3.6221 |  | 28-03-2026 07:50 | 76.978 | 77.889 | 33.9 | 12.9815 | 15.3414 | -2.3599 | 92.0487 | 11.2 | 15.1221 | -3.9221 |  | 28-03-2026 07:50 | 76.906 | 77.809 | 33.5 | 12.9682 | 15.3414 | -2.3733 | 92.0487 | 11.2 | 15.1221 | -3.9221 |  | 28-03-2026 07:50 | 78.709 | 79.633 | 34 | 13.2722 | 15.3414 | -2.0693 | 92.0487 | 11.5 | 15.1221 | -3.6221 |  | 28-03-2026 07:50 | 57.027 | 57.79 | 24.7 | 9.6317 | 11.364 | -1.7324 | 68.1842 | 8.3 | 11.2015 | -2.9015 |  | 28-03-2026 07:50 | 57.846 | 58.59 | 25.4 | 9.765 | 11.364 | -1.599 | 68.1842 | 8.5 | 11.2015 | -2.7015 |  | 28-03-2026 07:50 | 58.338 | 59.113 | 25.3 | 9.8522 | 11.364 | -1.5119 | 68.1842 | 8.5 | 11.2015 | -2.7015 |  | 28-03-2026 07:50 | 58.928 | 60.355 | 25.8 | 10.0592 | 11.364 | -1.3049 | 68.1842 | 8.7 | 11.2015 | -2.5015 |  | 28-03-2026 07:50 | 55.872 | 56.619 | 23.9 | 9.4365 | 10.8115 | -1.375 | 64.8688 | 8.2 | 10.6569 | -2.4569 |  | 28-03-2026 07:50 | 101.2422 | 117.6334 | -16.3912 | 705.8003 | 87.6 | 115.9512 | -28.3512 | -13.6422
28-03-2026 07:40 | 192 | 27.84 | 59.615 | 60.382 | 23 | 10.0637 | 12.3474 | -2.2837 | 74.0843 | 8.7 | 12.1708 | -3.4708 |  | 28-03-2026 07:40 | 58.859 | 60.112 | 22.7 | 10.0187 | 12.3474 | -2.3287 | 74.0843 | 14.7 | 12.1708 | 2.5292 |  | 28-03-2026 07:40 | 58.183 | 58.943 | 22.3 | 9.8238 | 12.3474 | -2.5236 | 74.0843 | 8.4 | 12.1708 | -3.7708 |  | 28-03-2026 07:40 | 59.407 | 60.183 | 22.5 | 10.0305 | 12.3474 | -2.3169 | 74.0843 | 8.5 | 12.1708 | -3.6708 |  | 28-03-2026 07:40 | 43.393 | 44.014 | 16.4 | 7.3357 | 9.1462 | -1.8105 | 54.8773 | 6.2 | 9.0154 | -2.8154 |  | 28-03-2026 07:40 | 44.02 | 44.659 | 16.9 | 7.4432 | 9.1462 | -1.703 | 54.8773 | 6.4 | 9.0154 | -2.6154 |  | 28-03-2026 07:40 | 44.345 | 45.007 | 16.8 | 7.5012 | 9.1462 | -1.645 | 54.8773 | 6.4 | 9.0154 | -2.6154 |  | 28-03-2026 07:40 | 44.979 | 46.189 | 17.1 | 7.6982 | 9.1462 | -1.448 | 54.8773 | 6.4 | 9.0154 | -2.6154 |  | 28-03-2026 07:40 | 42.627 | 43.276 | 15.7 | 7.2127 | 8.7015 | -1.4888 | 52.2089 | 6.1 | 8.5771 | -2.4771 |  | 28-03-2026 07:40 | 77.1275 | 94.6759 | -17.5484 | 568.0553 | 71.8 | 93.322 | -21.522 | -5.3275
28-03-2026 07:30 | 145 | 26.12 | 43.247 | 43.888 | 14.3 | 7.3147 | 9.3815 | -2.0669 | 56.2893 | 6 | 9.2474 | -3.2474 | [5 empty] | 0 | 9.3815 | -9.3815 | 56.2893 | 0 | 9.2474 | -9.2474 |  | 28-03-2026 07:30 | 42.327 | 42.972 | 13.9 | 7.162 | 9.3815 | -2.2195 | 56.2893 | 5.8 | 9.2474 | -3.4474 |  | 28-03-2026 07:30 | 43.369 | 44.029 | 14 | 7.3382 | 9.3815 | -2.0434 | 56.2893 | 5.9 | 9.2474 | -3.3474 |  | 28-03-2026 07:30 | 31.438 | 31.975 | 10.2 | 5.3292 | 6.9493 | -1.6201 | 41.6958 | 4.4 | 6.8499 | -2.4499 |  | 28-03-2026 07:30 | 32.478 | 33.006 | 10.5 | 5.501 | 6.9493 | -1.4483 | 41.6958 | 4.5 | 6.8499 | -2.3499 |  | 28-03-2026 07:30 | 31.918 | 32.732 | 10.4 | 5.4553 | 6.9493 | -1.494 | 41.6958 | 4.4 | 6.8499 | -2.4499 |  | 28-03-2026 07:30 | 32.916 | 33.742 | 10.7 | 5.6237 | 6.9493 | -1.3256 | 41.6958 | 4.6 | 6.8499 | -2.2499 |  | 28-03-2026 07:30 | 30.961 | 31.463 | 9.6 | 5.2438 | 6.6114 | -1.3676 | 39.6684 | 4.2 | 6.5169 | -2.3169 |  | 28-03-2026 07:30 | 48.9678 | 71.9348 | -22.9669 | 431.6086 | 39.8 | 70.9061 | -31.1061 | -9.1678
28-03-2026 07:20 | 99 | 23.82 | 29.128 | 29.644 | 8.3 | 4.9407 | 6.4571 | -1.5164 | 38.7426 | 4 | 6.3648 | -2.3648 |  | 28-03-2026 07:20 | 28.271 | 28.965 | 8 | 4.8275 | 6.4571 | -1.6296 | 38.7426 | 3.7 | 6.3648 | -2.6648 |  | 28-03-2026 07:20 | 28.507 | 29.021 | 8.1 | 4.8368 | 6.4571 | -1.6203 | 38.7426 | 3.8 | 6.3648 | -2.5648 |  | 28-03-2026 07:20 | 28.701 | 29.227 | 8.1 | 4.8712 | 6.4571 | -1.5859 | 38.7426 | 3.9 | 6.3648 | -2.4648 |  | 28-03-2026 07:20 | 20.775 | 21.234 | 5.8 | 3.539 | 4.783 | -1.244 | 28.6982 | 2.8 | 4.7146 | -1.9146 |  | 28-03-2026 07:20 | 21.53 | 21.99 | 6 | 3.665 | 4.783 | -1.118 | 28.6982 | 2.9 | 4.7146 | -1.8146 |  | 28-03-2026 07:20 | 21.396 | 21.862 | 6 | 3.6437 | 4.783 | -1.1394 | 28.6982 | 2.9 | 4.7146 | -1.8146 |  | 28-03-2026 07:20 | 21.854 | 22.529 | 6.1 | 3.7548 | 4.783 | -1.0282 | 28.6982 | 2.9 | 4.7146 | -1.8146 |  | 28-03-2026 07:20 | 20.262 | 20.653 | 5.4 | 3.4422 | 4.5505 | -1.1083 | 27.3028 | 2.7 | 4.4854 | -1.7854 |  | 28-03-2026 07:20 | 37.5208 | 49.511 | -11.9902 | 297.066 | 29.6 | 48.803 | -19.203 | -7.9208
28-03-2026 07:10 | 46 | 23.53 | 18.479 | 18.916 | 4.3 | 3.1527 | 3.0033 | 0.14937 | 18.0198 | 2.4 | 2.9604 | -0.56035 |  | 28-03-2026 07:10 | 18.147 | 18.938 | 4.3 | 3.1563 | 3.0033 | 0.15303 | 18.0198 | 2.4 | 2.9604 | -0.56035 |  | 28-03-2026 07:10 | 18.155 | 18.59 | 4.3 | 3.0983 | 3.0033 | 0.095033 | 18.0198 | 2.4 | 2.9604 | -0.56035 |  | 28-03-2026 07:10 | 17.961 | 18.696 | 4.2 | 3.116 | 3.0033 | 0.1127 | 18.0198 | 2.3 | 2.9604 | -0.66035 |  | 28-03-2026 07:10 | 13.157 | 13.754 | 3 | 2.2923 | 2.2247 | 0.067666 | 13.348 | 1.7 | 2.1929 | -0.49285 |  | 28-03-2026 07:10 | 13.518 | 13.902 | 3.1 | 2.317 | 2.2247 | 0.092333 | 13.348 | 1.8 | 2.1929 | -0.39285 |  | 28-03-2026 07:10 | 13.578 | 13.966 | 3.1 | 2.3277 | 2.2247 | 0.103 | 13.348 | 1.8 | 2.1929 | -0.39285 |  | 28-03-2026 07:10 | 13.863 | 14.367 | 3.2 | 2.3945 | 2.2247 | 0.16983 | 13.348 | 1.8 | 2.1929 | -0.39285 |  | 28-03-2026 07:10 | 12.633 | 13.018 | 2.7 | 2.1697 | 2.1165 | 0.053171 | 12.699 | 1.7 | 2.0862 | -0.38623 |  | 28-03-2026 07:10 | 24.0245 | 23.0284 | 0.99613 | 138.1702 | 18.3 | 22.6991 | -4.3991 | -5.7245
28-03-2026 07:00 | 29 | 22.96 | 10.933 | 11.306 | 1.9 | 1.8843 | 1.8971 | -0.01281 | 11.3829 | 1.9 | 1.87 | 0.029986 |  | 28-03-2026 07:00 | 10.58 | 11.397 | 1.9 | 1.8995 | 1.8971 | 0.0023568 | 11.3829 | 1.9 | 1.87 | 0.029986 |  | 28-03-2026 07:00 | 10.597 | 10.963 | 1.9 | 1.8272 | 1.8971 | -0.069977 | 11.3829 | 1.9 | 1.87 | 0.029986 |  | 28-03-2026 07:00 | 10.513 | 11.205 | 1.9 | 1.8675 | 1.8971 | -0.029643 | 11.3829 | 1.9 | 1.87 | 0.029986 |  | 28-03-2026 07:00 | 7.698 | 8.258 | 1.3 | 1.3763 | 1.4053 | -0.028958 | 8.4317 | 1.3 | 1.3852 | -0.085196 |  | 28-03-2026 07:00 | 7.83 | 8.142 | 1.3 | 1.357 | 1.4053 | -0.048291 | 8.4317 | 1.3 | 1.3852 | -0.085196 |  | 28-03-2026 07:00 | 7.867 | 8.182 | 1.3 | 1.3637 | 1.4053 | -0.041625 | 8.4317 | 1.3 | 1.3852 | -0.085196 |  | 28-03-2026 07:00 | 8.068 | 8.598 | 1.4 | 1.433 | 1.4053 | 0.027709 | 8.4317 | 1.4 | 1.3852 | 0.014804 |  | 28-03-2026 07:00 | 7.319 | 7.616 | 1 | 1.2693 | 1.337 | -0.067627 | 8.0218 | 1 | 1.3178 | -0.31784 |  | 28-03-2026 07:00 | 14.2778 | 14.5467 | -0.26887 | 87.2802 | 13.9 | 14.3387 | -0.43868 | -0.37783
[110 empty] | Total: - | 17307.167 | 18552.6528 | -1245.4858 |  | 18134 | 18287.3499 | -153.3499 | 826.833
Sum:- | 43988 |  | 14023.856 |  | 92961.7 |  |  |  |  | 2358.4 | 2569.0907 | -210.6907 | 0.98345 |  | 14120.66 |  | 93638.4 |  |  |  |  | 2378.6 | 2569.0907 | -190.4907 | 0.99183 |  | 11494.104 |  | 38263.1 |  |  |  |  | 2340.3 | 2000.2244 | 340.0756 | 0.973 |  | 14065.871 |  | 93096.6 |  |  |  |  | 2361.6 | 2569.0907 | -207.4907 | 0.98348 |  | 8674.152 |  | 28808.8 |  |  |  |  | 1766.2 | 1481.6477 | 284.5523 | 0.98395 |  | 10460.255 |  | 69044.6 |  |  |  |  | 1749 | 1903.0302 | -154.0302 | 0.98224 |  | 8626.752 |  | 28762.3 |  |  |  |  | 1753.7 | 1481.6477 | 272.0523 | 0.98104 |  | 10563.503 |  | 69612.8 |  |  |  |  | 1763.3 | 1903.0302 | -139.7302 | 0.97088 |  | 9891.397 |  | 65656.5 |  |  |  |  | 1662.9 | 1810.4975 | -147.5975 | 0.98666 | [8 empty] | 4.777%

## 29 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
29-03-2026 19:00 | 0 | 42.19 | 0 | 0 | 2455.8 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29-03-2026 19:00 | 0 | 0 | 2442.1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 29-03-2026 19:00 | 0 | 0 | 2449.5 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 29-03-2026 19:00 | 0 | 0 | 1839.1 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 29-03-2026 19:00 | 0 | 0 | 1818.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29-03-2026 19:00 | 0 | 0 | 1822.5 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  | 29-03-2026 19:00 | 0 | 0 | 1825.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29-03-2026 19:00 | 0 | 0 | 1722.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29-03-2026 19:00 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0.5 | 0.5 | 1 | 99.15%
29-03-2026 18:50 | 3 | 42.48 | 1.519 | 1.597 | 2455.7 | 0.26617 | 0.18294 | 0.083224 | 1.0977 | 0.7 | 0.18033 | 0.51967 |  | 29-03-2026 18:50 | 1.758 | 2.316 | 2468 | 0.386 | 0.18294 | 0.20306 | 1.0977 | 0.7 | 0.18033 | 0.51967 |  | 29-03-2026 18:50 | 1.554 | 1.634 | 2442 | 0.27233 | 0.18294 | 0.08939 | 1.0977 | 0.7 | 0.18033 | 0.51967 |  | 29-03-2026 18:50 | 1.446 | 2.166 | 2449.4 | 0.361 | 0.18294 | 0.17806 | 1.0977 | 0.7 | 0.18033 | 0.51967 |  | 29-03-2026 18:50 | 1.093 | 1.177 | 1839 | 0.19617 | 0.13551 | 0.060653 | 0.81308 | 0.4 | 0.13358 | 0.26642 |  | 29-03-2026 18:50 | 1.01 | 1.062 | 1818.5 | 0.177 | 0.13551 | 0.041487 | 0.81308 | 0.5 | 0.13358 | 0.36642 |  | 29-03-2026 18:50 | 0.958 | 1.015 | 1822.4 | 0.16917 | 0.13551 | 0.033653 | 0.81308 | 0.5 | 0.13358 | 0.36642 | [5 empty] | 0 | 0.13551 | -0.13551 | 0.81308 | 0 | 0.13358 | -0.13358 |  | 29-03-2026 18:50 | 0 | 0 | 1722.1 | 0 | 0.12892 | -0.12892 | 0.77355 | 0 | 0.12708 | -0.12708 |  | 29-03-2026 18:50 | 1.8278 | 1.4027 | 0.42508 | 8.4165 | 4.2 | 1.3827 | 2.8173 | 2.3722 | 2 | 98.39%
29-03-2026 18:40 | 17 | 43.34 | 6.222 | 6.507 | 2455 | 1.0845 | 1.0334 | 0.051147 | 6.2001 | 1.2 | 1.0186 | 0.18142 |  | 29-03-2026 18:40 | 6.405 | 7.006 | 2467.3 | 1.1677 | 1.0334 | 0.13431 | 6.2001 | 1.3 | 1.0186 | 0.28142 |  | 29-03-2026 18:40 | 6.207 | 6.499 | 2441.3 | 1.0832 | 1.0334 | 0.049813 | 6.2001 | 1.2 | 1.0186 | 0.18142 |  | 29-03-2026 18:40 | 6.285 | 6.86 | 2448.7 | 1.1433 | 1.0334 | 0.10998 | 6.2001 | 1.2 | 1.0186 | 0.18142 |  | 29-03-2026 18:40 | 4.487 | 4.711 | 1838.6 | 0.78517 | 0.76545 | 0.01972 | 4.5927 | 0.9 | 0.7545 | 0.1455 |  | 29-03-2026 18:40 | 4.277 | 4.491 | 1818 | 0.7485 | 0.76545 | -0.016947 | 4.5927 | 0.8 | 0.7545 | 0.045499 |  | 29-03-2026 18:40 | 4.408 | 4.635 | 1821.9 | 0.7725 | 0.76545 | 0.007053 | 4.5927 | 0.8 | 0.7545 | 0.045499 |  | 29-03-2026 18:40 | 0 | 0 | 1825.1 | 0 | 0.76545 | -0.76545 | 4.5927 | 0 | 0.7545 | -0.7545 | [5 empty] | 0 | 0.72823 | -0.72823 | 4.3694 | 0 | 0.71781 | -0.71781 |  | 29-03-2026 18:40 | 6.7848 | 7.9234 | -1.1386 | 47.5406 | 7.4 | 7.8101 | -0.41012 | 0.61517 | 3 | 97.33%
29-03-2026 18:30 | 24 | 43.91 | 8.805 | 9.169 | 2453.8 | 1.5282 | 1.4557 | 0.072425 | 8.7345 | 2 | 1.4349 | 0.56508 |  | 29-03-2026 18:30 | 9.136 | 9.83 | 2466 | 1.6383 | 1.4557 | 0.18259 | 8.7345 | 2 | 1.4349 | 0.56508 |  | 29-03-2026 18:30 | 8.774 | 9.138 | 2440.1 | 1.523 | 1.4557 | 0.067258 | 8.7345 | 2 | 1.4349 | 0.56508 |  | 29-03-2026 18:30 | 8.885 | 9.254 | 2447.5 | 1.5423 | 1.4557 | 0.086592 | 8.7345 | 2.1 | 1.4349 | 0.66508 |  | 29-03-2026 18:30 | 6.38 | 6.67 | 1837.7 | 1.1117 | 1.0783 | 0.033339 | 6.47 | 1.5 | 1.0629 | 0.43709 |  | 29-03-2026 18:30 | 6.251 | 6.535 | 1817.2 | 1.0892 | 1.0783 | 0.010839 | 6.47 | 1.5 | 1.0629 | 0.43709 |  | 29-03-2026 18:30 | 6.29 | 6.584 | 1821.1 | 1.0973 | 1.0783 | 0.019006 | 6.47 | 1.5 | 1.0629 | 0.43709 |  | 29-03-2026 18:30 | 0 | 0 | 1825.1 | 0 | 1.0783 | -1.0783 | 6.47 | 0 | 1.0629 | -1.0629 | [5 empty] | 0 | 1.0259 | -1.0259 | 6.1554 | 0 | 1.0112 | -1.0112 |  | 29-03-2026 18:30 | 9.53 | 11.1622 | -1.6322 | 66.973 | 12.6 | 11.0026 | 1.5974 | 3.07 | 4 | 98.38%
29-03-2026 18:20 | 44 | 44.77 | 15.885 | 16.329 | 2451.8 | 2.7215 | 2.6603 | 0.061243 | 15.9615 | 3 | 2.6222 | 0.37778 |  | 29-03-2026 18:20 | 16.125 | 16.751 | 2464 | 2.7918 | 2.6603 | 0.13158 | 15.9615 | 3 | 2.6222 | 0.37778 |  | 29-03-2026 18:20 | 15.887 | 16.336 | 2438.1 | 2.7227 | 2.6603 | 0.062409 | 15.9615 | 2.9 | 2.6222 | 0.27778 |  | 29-03-2026 18:20 | 16.083 | 16.536 | 2445.4 | 2.756 | 2.6603 | 0.095743 | 15.9615 | 2.9 | 2.6222 | 0.27778 |  | 29-03-2026 18:20 | 11.713 | 12.135 | 1836.2 | 2.0225 | 1.9706 | 0.051939 | 11.8234 | 2.2 | 1.9424 | 0.25762 |  | 29-03-2026 18:20 | 11.459 | 11.87 | 1815.7 | 1.9783 | 1.9706 | 0.0077723 | 11.8234 | 2.1 | 1.9424 | 0.15762 |  | 29-03-2026 18:20 | 11.505 | 11.914 | 1819.6 | 1.9857 | 1.9706 | 0.015106 | 11.8234 | 2.1 | 1.9424 | 0.15762 |  | 29-03-2026 18:20 | 0 | 0 | 1825.1 | 0 | 1.9706 | -1.9706 | 11.8234 | 0 | 1.9424 | -1.9424 |  | 29-03-2026 18:20 | 0 | 0 | 1722.1 | 0 | 1.8747 | -1.8747 | 11.2485 | 0 | 1.8479 | -1.8479 |  | 29-03-2026 18:20 | 16.9785 | 20.398 | -3.4195 | 122.3881 | 18.2 | 20.1063 | -1.9063 | 1.2215 | 5 | 98.39%
29-03-2026 18:10 | 55 | 45.06 | 19.734 | 20.238 | 2448.8 | 3.373 | 3.3217 | 0.051304 | 19.9302 | 3.4 | 3.2742 | 0.1258 |  | 29-03-2026 18:10 | 20.021 | 20.543 | 2461 | 3.4238 | 3.3217 | 0.10214 | 19.9302 | 3.5 | 3.2742 | 0.2258 |  | 29-03-2026 18:10 | 19.531 | 20.038 | 2435.2 | 3.3397 | 3.3217 | 0.017971 | 19.9302 | 3.5 | 3.2742 | 0.2258 |  | 29-03-2026 18:10 | 19.676 | 20.189 | 2442.5 | 3.3648 | 3.3217 | 0.043138 | 19.9302 | 3.5 | 3.2742 | 0.2258 |  | 29-03-2026 18:10 | 14.433 | 14.878 | 1834 | 2.4797 | 2.4605 | 0.019151 | 14.7631 | 2.5 | 2.4253 | 0.07467 |  | 29-03-2026 18:10 | 14.264 | 14.648 | 1813.6 | 2.4413 | 2.4605 | -0.019182 | 14.7631 | 2.5 | 2.4253 | 0.07467 |  | 29-03-2026 18:10 | 14.225 | 14.666 | 1817.5 | 2.4443 | 2.4605 | -0.016182 | 14.7631 | 2.4 | 2.4253 | -0.02533 |  | 29-03-2026 18:10 | 0 | 0 | 1825.1 | 0 | 2.4605 | -2.4605 | 14.7631 | 0 | 2.4253 | -2.4253 |  | 29-03-2026 18:10 | 0 | 0 | 1722.1 | 0 | 2.3409 | -2.3409 | 14.0453 | 0 | 2.3074 | -2.3074 |  | 29-03-2026 18:10 | 20.8667 | 25.4697 | -4.6031 | 152.8183 | 21.3 | 25.1055 | -3.8055 | 0.43333 | 6 | 98.14%
29-03-2026 18:00 | 60 | 45.92 | 21.616 | 22.15 | 2445.4 | 3.6917 | 3.6119 | 0.07973 | 21.6716 | 4 | 3.5603 | 0.43971 |  | 29-03-2026 18:00 | 21.88 | 22.427 | 2457.5 | 3.7378 | 3.6119 | 0.1259 | 21.6716 | 4.2 | 3.5603 | 0.63971 |  | 29-03-2026 18:00 | 21.508 | 22.044 | 2431.7 | 3.674 | 3.6119 | 0.062063 | 21.6716 | 4.1 | 3.5603 | 0.53971 |  | 29-03-2026 18:00 | 21.685 | 22.225 | 2439 | 3.7042 | 3.6119 | 0.09223 | 21.6716 | 4.1 | 3.5603 | 0.53971 |  | 29-03-2026 18:00 | 15.782 | 16.227 | 1831.5 | 2.7045 | 2.6755 | 0.028991 | 16.0531 | 3 | 2.6372 | 0.36275 |  | 29-03-2026 18:00 | 15.595 | 16.029 | 1811.1 | 2.6715 | 2.6755 | -0.0040089 | 16.0531 | 3 | 2.6372 | 0.36275 |  | 29-03-2026 18:00 | 15.597 | 16.033 | 1815.1 | 2.6722 | 2.6755 | -0.0033423 | 16.0531 | 3 | 2.6372 | 0.36275 |  | 29-03-2026 18:00 | 0 | 0 | 1825.1 | 0 | 2.6755 | -2.6755 | 16.0531 | 1.2 | 2.6372 | -1.4372 |  | 29-03-2026 18:00 | 0 | 0 | 1722.1 | 0 | 2.5454 | -2.5454 | 15.2725 | 1.1 | 2.509 | -1.409 |  | 29-03-2026 18:00 | 22.8558 | 27.6952 | -4.8394 | 166.1712 | 27.7 | 27.2992 | 0.40084 | 4.8442 | 7 | 98.22%
29-03-2026 17:50 | 82 | 47.07 | 29.046 | 29.639 | 2441.4 | 4.9398 | 4.9149 | 0.024958 | 29.4893 | 5.2 | 4.8446 | 0.35541 |  | 29-03-2026 17:50 | 29.608 | 30.242 | 2453.3 | 5.0403 | 4.9149 | 0.12546 | 29.4893 | 5.1 | 4.8446 | 0.25541 |  | 29-03-2026 17:50 | 29.098 | 29.704 | 2427.6 | 4.9507 | 4.9149 | 0.035791 | 29.4893 | 5 | 4.8446 | 0.15541 |  | 29-03-2026 17:50 | 29.109 | 29.721 | 2434.9 | 4.9535 | 4.9149 | 0.038624 | 29.4893 | 5 | 4.8446 | 0.15541 |  | 29-03-2026 17:50 | 21.56 | 22.088 | 1828.5 | 3.6813 | 3.6406 | 0.040685 | 21.8439 | 3.7 | 3.5886 | 0.11141 |  | 29-03-2026 17:50 | 21.137 | 21.659 | 1808.1 | 3.6098 | 3.6406 | -0.030815 | 21.8439 | 3.6 | 3.5886 | 0.011413 |  | 29-03-2026 17:50 | 21.079 | 21.6 | 1812.1 | 3.6 | 3.6406 | -0.040649 | 21.8439 | 3.7 | 3.5886 | 0.11141 |  | 29-03-2026 17:50 | 21.226 | 22.034 | 1823.9 | 3.6723 | 3.6406 | 0.031685 | 21.8439 | 3.7 | 3.5886 | 0.11141 |  | 29-03-2026 17:50 | 19.943 | 20.463 | 1721 | 3.4105 | 3.4636 | -0.053126 | 20.7818 | 3.5 | 3.4141 | 0.085904 |  | 29-03-2026 17:50 | 37.8583 | 37.6857 | 0.17261 | 226.1143 | 38.5 | 37.1468 | 1.3532 | 0.64167 | 8 | 97.14%
29-03-2026 17:40 | 96 | 48.22 | 34.855 | 35.512 | 2436.2 | 5.9187 | 5.7289 | 0.18976 | 34.3734 | 7 | 5.647 | 1.353 |  | 29-03-2026 17:40 | 34.463 | 35.13 | 2448.2 | 5.855 | 5.7289 | 0.1261 | 34.3734 | 7.1 | 5.647 | 1.453 |  | 29-03-2026 17:40 | 33.835 | 34.487 | 2422.6 | 5.7478 | 5.7289 | 0.018931 | 34.3734 | 7 | 5.647 | 1.353 |  | 29-03-2026 17:40 | 33.831 | 34.483 | 2429.9 | 5.7472 | 5.7289 | 0.018265 | 34.3734 | 7 | 5.647 | 1.353 |  | 29-03-2026 17:40 | 25.119 | 25.687 | 1824.8 | 4.2812 | 4.2436 | 0.037535 | 25.4618 | 5.2 | 4.1829 | 1.0171 |  | 29-03-2026 17:40 | 24.67 | 25.228 | 1804.5 | 4.2047 | 4.2436 | -0.038965 | 25.4618 | 5.1 | 4.1829 | 0.91705 |  | 29-03-2026 17:40 | 24.695 | 25.258 | 1808.4 | 4.2097 | 4.2436 | -0.033965 | 25.4618 | 5 | 4.1829 | 0.81705 |  | 29-03-2026 17:40 | 24.812 | 25.682 | 1820.2 | 4.2803 | 4.2436 | 0.036702 | 25.4618 | 5 | 4.1829 | 0.81705 |  | 29-03-2026 17:40 | 23.38 | 23.928 | 1717.5 | 3.988 | 4.0373 | -0.04929 | 24.2237 | 4.8 | 3.9796 | 0.82044 |  | 29-03-2026 17:40 | 44.2325 | 43.9274 | 0.30508 | 263.5645 | 53.2 | 43.2993 | 9.9007 | 8.9675 | 9 | 98.47%
29-03-2026 17:30 | 131 | 48.5 | 46.211 | 46.996 | 2429.2 | 7.8327 | 7.8092 | 0.023441 | 46.8554 | 8 | 7.6976 | 0.30245 |  | 29-03-2026 17:30 | 46.367 | 47.169 | 2441.1 | 7.8615 | 7.8092 | 0.052275 | 46.8554 | 7.8 | 7.6976 | 0.10245 |  | 29-03-2026 17:30 | 46.12 | 46.908 | 2415.6 | 7.818 | 7.8092 | 0.0087745 | 46.8554 | 7.8 | 7.6976 | 0.10245 |  | 29-03-2026 17:30 | 46.016 | 46.812 | 2422.9 | 7.802 | 7.8092 | -0.0072255 | 46.8554 | 7.9 | 7.6976 | 0.20245 |  | 29-03-2026 17:30 | 34.361 | 35.002 | 1819.6 | 5.8337 | 5.7846 | 0.049055 | 34.7077 | 5.9 | 5.7019 | 0.19811 |  | 29-03-2026 17:30 | 33.622 | 34.249 | 1799.4 | 5.7082 | 5.7846 | -0.076445 | 34.7077 | 5.8 | 5.7019 | 0.098108 |  | 29-03-2026 17:30 | 33.647 | 34.252 | 1803.4 | 5.7087 | 5.7846 | -0.075945 | 34.7077 | 5.9 | 5.7019 | 0.19811 |  | 29-03-2026 17:30 | 33.712 | 34.794 | 1815.2 | 5.799 | 5.7846 | 0.014389 | 34.7077 | 5.8 | 5.7019 | 0.098108 |  | 29-03-2026 17:30 | 31.618 | 32.227 | 1712.7 | 5.3712 | 5.5033 | -0.13217 | 33.02 | 5.4 | 5.4246 | -0.024644 |  | 29-03-2026 17:30 | 59.7348 | 59.8787 | -0.14386 | 359.2721 | 60.3 | 59.0224 | 1.2776 | 0.56517
29-03-2026 17:20 | 140 | 48.79 | 49.603 | 50.297 | 2421.2 | 8.3828 | 8.3365 | 0.046326 | 50.019 | 8.8 | 8.2173 | 0.58271 |  | 29-03-2026 17:20 | 49.871 | 50.708 | 2433.3 | 8.4513 | 8.3365 | 0.11483 | 50.019 | 9.2 | 8.2173 | 0.98271 |  | 29-03-2026 17:20 | 49.296 | 50.304 | 2407.8 | 8.384 | 8.3365 | 0.047493 | 50.019 | 9 | 8.2173 | 0.78271 |  | 29-03-2026 17:20 | 49.271 | 50.103 | 2415 | 8.3505 | 8.3365 | 0.013993 | 50.019 | 9 | 8.2173 | 0.78271 |  | 29-03-2026 17:20 | 36.691 | 37.418 | 1813.7 | 6.2363 | 6.1752 | 0.061143 | 37.0511 | 6.7 | 6.0869 | 0.61311 |  | 29-03-2026 17:20 | 36.091 | 36.756 | 1793.6 | 6.126 | 6.1752 | -0.04919 | 37.0511 | 6.6 | 6.0869 | 0.51311 |  | 29-03-2026 17:20 | 36.045 | 36.709 | 1797.5 | 6.1182 | 6.1752 | -0.057024 | 37.0511 | 6.5 | 6.0869 | 0.41311 |  | 29-03-2026 17:20 | 36.103 | 36.983 | 1809.4 | 6.1638 | 6.1752 | -0.011357 | 37.0511 | 6.6 | 6.0869 | 0.51311 |  | 29-03-2026 17:20 | 34.013 | 34.654 | 1707.3 | 5.7757 | 5.8749 | -0.099262 | 35.2496 | 6.2 | 5.7909 | 0.40908 |  | 29-03-2026 17:20 | 63.9887 | 63.9217 | 0.066948 | 383.5303 | 68.6 | 63.0076 | 5.5924 | 4.6113
29-03-2026 17:10 | 149 | 49.08 | 52.675 | 53.515 | 2412.4 | 8.9192 | 8.8626 | 0.056565 | 53.1756 | 9.6 | 8.7359 | 0.86413 |  | 29-03-2026 17:10 | 52.881 | 53.878 | 2424.1 | 8.9797 | 8.8626 | 0.11706 | 53.1756 | 9.4 | 8.7359 | 0.66413 |  | 29-03-2026 17:10 | 52.501 | 53.454 | 2398.8 | 8.909 | 8.8626 | 0.046398 | 53.1756 | 9.2 | 8.7359 | 0.46413 |  | 29-03-2026 17:10 | 52.263 | 53.129 | 2406 | 8.8548 | 8.8626 | -0.0077686 | 53.1756 | 9.1 | 8.7359 | 0.36413 |  | 29-03-2026 17:10 | 38.981 | 39.683 | 1807 | 6.6138 | 6.5649 | 0.048943 | 39.3893 | 6.8 | 6.471 | 0.32899 |  | 29-03-2026 17:10 | 38.226 | 38.923 | 1787 | 6.4872 | 6.5649 | -0.077724 | 39.3893 | 6.6 | 6.471 | 0.12899 |  | 29-03-2026 17:10 | 38.222 | 38.911 | 1791 | 6.4852 | 6.5649 | -0.079724 | 39.3893 | 6.7 | 6.471 | 0.22899 |  | 29-03-2026 17:10 | 38.257 | 39.361 | 1802.8 | 6.5602 | 6.5649 | -0.0047236 | 39.3893 | 6.7 | 6.471 | 0.22899 |  | 29-03-2026 17:10 | 36.148 | 36.822 | 1701.1 | 6.137 | 6.2457 | -0.10868 | 37.4741 | 6.4 | 6.1564 | 0.24363 |  | 29-03-2026 17:10 | 67.946 | 67.9556 | -0.0096487 | 407.7339 | 70.5 | 66.9839 | 3.5161 | 2.554
29-03-2026 17:00 | 184 | 49.36 | 65.221 | 66.134 | 2402.8 | 11.0223 | 10.9327 | 0.089625 | 65.5963 | 14.5 | 10.7764 | 3.7236 |  | 29-03-2026 17:00 | 67.227 | 67.991 | 2414.7 | 11.3318 | 10.9327 | 0.39912 | 65.5963 | 14.7 | 10.7764 | 3.9236 |  | 29-03-2026 17:00 | 64.17 | 65.243 | 2389.6 | 10.8738 | 10.9327 | -0.058875 | 65.5963 | 14.7 | 10.7764 | 3.9236 |  | 29-03-2026 17:00 | 64.17 | 65.114 | 2396.9 | 10.8523 | 10.9327 | -0.080375 | 65.5963 | 14.7 | 10.7764 | 3.9236 |  | 29-03-2026 17:00 | 47.47 | 48.286 | 1800.2 | 8.0477 | 8.0983 | -0.050636 | 48.5898 | 10.9 | 7.9825 | 2.9175 |  | 29-03-2026 17:00 | 46.752 | 47.541 | 1780.4 | 7.9235 | 8.0983 | -0.1748 | 48.5898 | 10.8 | 7.9825 | 2.8175 |  | 29-03-2026 17:00 | 46.414 | 47.202 | 1784.3 | 7.867 | 8.0983 | -0.2313 | 48.5898 | 10.7 | 7.9825 | 2.7175 |  | 29-03-2026 17:00 | 46.39 | 47.821 | 1796.1 | 7.9702 | 8.0983 | -0.12814 | 48.5898 | 10.9 | 7.9825 | 2.9175 |  | 29-03-2026 17:00 | 44.048 | 44.847 | 1694.7 | 7.4745 | 7.7045 | -0.23003 | 46.2272 | 10.2 | 7.5944 | 2.6056 |  | 29-03-2026 17:00 | 83.3632 | 83.8286 | -0.46541 | 502.9715 | 112.1 | 82.6298 | 29.4702 | 28.7368
29-03-2026 16:50 | 268 | 49.65 | 94.905 | 96.087 | 2388.3 | 16.0145 | 15.9061 | 0.10844 | 95.4364 | 31.1 | 15.6786 | 15.4214 |  | 29-03-2026 16:50 | 97.585 | 97.063 | 2400 | 16.1772 | 15.9061 | 0.27111 | 95.4364 | 15 | 15.6786 | -0.6786 |  | 29-03-2026 16:50 | 93.846 | 95.556 | 2374.9 | 15.926 | 15.9061 | 0.019942 | 95.4364 | 14.8 | 15.6786 | -0.8786 |  | 29-03-2026 16:50 | 93.943 | 95.132 | 2382.2 | 15.8553 | 15.9061 | -0.050725 | 95.4364 | 14.8 | 15.6786 | -0.8786 |  | 29-03-2026 16:50 | 69.655 | 70.601 | 1789.3 | 11.7668 | 11.7823 | -0.015432 | 70.6936 | 11.2 | 11.6138 | -0.41378 |  | 29-03-2026 16:50 | 68.681 | 69.718 | 1769.6 | 11.6197 | 11.7823 | -0.1626 | 70.6936 | 10.9 | 11.6138 | -0.71378 |  | 29-03-2026 16:50 | 67.963 | 68.893 | 1773.6 | 11.4822 | 11.7823 | -0.3001 | 70.6936 | 10.9 | 11.6138 | -0.71378 |  | 29-03-2026 16:50 | 68.888 | 70.691 | 1785.2 | 11.7818 | 11.7823 | -0.0004322 | 70.6936 | 10.7 | 11.6138 | -0.91378 |  | 29-03-2026 16:50 | 65.332 | 66.292 | 1684.5 | 11.0487 | 11.2094 | -0.1607 | 67.2562 | 10.2 | 11.0491 | -0.84907 |  | 29-03-2026 16:50 | 121.6722 | 121.9627 | -0.2905 | 731.776 | 129.6 | 120.2186 | 9.3814 | 7.9278
29-03-2026 16:40 | 239 | 49.36 | 82.107 | 83.197 | 2373 | 13.8662 | 14.2006 | -0.33447 | 85.2038 | 0 | 13.9976 | -13.9976 |  | 29-03-2026 16:40 | 84.745 | 85.896 | 2385 | 14.316 | 14.2006 | 0.11536 | 85.2038 | 17.2 | 13.9976 | 3.2024 |  | 29-03-2026 16:40 | 83.876 | 85.54 | 2360.1 | 14.2567 | 14.2006 | 0.056029 | 85.2038 | 16.3 | 13.9976 | 2.3024 |  | 29-03-2026 16:40 | 83.214 | 84.327 | 2367.4 | 14.0545 | 14.2006 | -0.14614 | 85.2038 | 16.2 | 13.9976 | 2.2024 |  | 29-03-2026 16:40 | 62.709 | 63.606 | 1778.1 | 10.601 | 10.519 | 0.082009 | 63.1139 | 12 | 10.3686 | 1.6314 |  | 29-03-2026 16:40 | 61.208 | 62.077 | 1758.7 | 10.3462 | 10.519 | -0.17282 | 63.1139 | 11.8 | 10.3686 | 1.4314 |  | 29-03-2026 16:40 | 61.332 | 62.203 | 1762.7 | 10.3672 | 10.519 | -0.15182 | 63.1139 | 12 | 10.3686 | 1.6314 |  | 29-03-2026 16:40 | 61.272 | 62.99 | 1774.5 | 10.4983 | 10.519 | -0.020657 | 63.1139 | 12 | 10.3686 | 1.6314 |  | 29-03-2026 16:40 | 57.766 | 58.664 | 1674.3 | 9.7773 | 10.0075 | -0.23018 | 60.0451 | 11.3 | 9.8644 | 1.4356 |  | 29-03-2026 16:40 | 108.0833 | 108.886 | -0.8027 | 653.3162 | 108.8 | 107.329 | 1.471 | 0.71667
29-03-2026 16:30 | 316 | 49.36 | 109.991 | 111.395 | 2357.2 | 18.5658 | 18.7757 | -0.20991 | 112.6544 | 25.5 | 18.5072 | 6.9928 |  | 29-03-2026 16:30 | 111.874 | 113.359 | 2367.8 | 18.8932 | 18.7757 | 0.11743 | 112.6544 | 25.4 | 18.5072 | 6.8928 |  | 29-03-2026 16:30 | 111.193 | 113.481 | 2343.8 | 18.9135 | 18.7757 | 0.13776 | 112.6544 | 25.6 | 18.5072 | 7.0928 |  | 29-03-2026 16:30 | 110.188 | 111.628 | 2351.2 | 18.6047 | 18.7757 | -0.17107 | 112.6544 | 25.6 | 18.5072 | 7.0928 |  | 29-03-2026 16:30 | 84.392 | 85.512 | 1766.1 | 14.252 | 13.908 | 0.34405 | 83.4477 | 19.3 | 13.7091 | 5.5909 |  | 29-03-2026 16:30 | 82.281 | 83.569 | 1746.9 | 13.9282 | 13.908 | 0.020212 | 83.4477 | 18.9 | 13.7091 | 5.1909 |  | 29-03-2026 16:30 | 86.383 | 87.53 | 1750.7 | 14.5883 | 13.908 | 0.68038 | 83.4477 | 19.1 | 13.7091 | 5.3909 |  | 29-03-2026 16:30 | 87.67 | 89.992 | 1762.5 | 14.9987 | 13.908 | 1.0907 | 83.4477 | 19.2 | 13.7091 | 5.4909 |  | 29-03-2026 16:30 | 81.165 | 82.267 | 1663 | 13.7112 | 13.2317 | 0.47947 | 79.3902 | 18 | 13.0425 | 4.9575 |  | 29-03-2026 16:30 | 146.4555 | 143.9665 | 2.489 | 863.7988 | 196.6 | 141.9077 | 54.6923 | 50.1445
29-03-2026 16:20 | 499 | 49.65 | 173.523 | 175.826 | 2331.7 | 29.3043 | 29.6161 | -0.3118 | 177.6968 | 32.3 | 29.1926 | 3.1074 |  | 29-03-2026 16:20 | 175.603 | 176.518 | 2342.4 | 29.4197 | 29.6161 | -0.19646 | 177.6968 | 30.9 | 29.1926 | 1.7074 |  | 29-03-2026 16:20 | 173.102 | 176.907 | 2318.2 | 29.4845 | 29.6161 | -0.13163 | 177.6968 | 30.5 | 29.1926 | 1.3074 |  | 29-03-2026 16:20 | 172.472 | 174.807 | 2325.6 | 29.1345 | 29.6161 | -0.48163 | 177.6968 | 30.8 | 29.1926 | 1.6074 |  | 29-03-2026 16:20 | 129.74 | 131.37 | 1746.8 | 21.895 | 21.9379 | -0.042875 | 131.6273 | 23.1 | 21.6242 | 1.4758 |  | 29-03-2026 16:20 | 126.73 | 128.386 | 1728 | 21.3977 | 21.9379 | -0.54021 | 131.6273 | 22.6 | 21.6242 | 0.97584 |  | 29-03-2026 16:20 | 127.178 | 129.063 | 1731.6 | 21.5105 | 21.9379 | -0.42738 | 131.6273 | 22.4 | 21.6242 | 0.77584 |  | 29-03-2026 16:20 | 127.377 | 131.009 | 1743.3 | 21.8348 | 21.9379 | -0.10304 | 131.6273 | 22.5 | 21.6242 | 0.87584 |  | 29-03-2026 16:20 | 120.08 | 121.649 | 1645 | 20.2748 | 20.8712 | -0.59634 | 125.227 | 21.2 | 20.5727 | 0.62729 |  | 29-03-2026 16:20 | 224.2558 | 227.0872 | -2.8314 | 1362.5232 | 236.3 | 223.8398 | 12.4602 | 12.0442
29-03-2026 16:10 | 563 | 49.94 | 196.08 | 198.763 | 2299.4 | 33.1272 | 33.3775 | -0.25031 | 200.2648 | 31.9 | 32.9002 | -1.0002 |  | 29-03-2026 16:10 | 197.149 | 199.908 | 2311.5 | 33.318 | 33.3775 | -0.059475 | 200.2648 | 34.1 | 32.9002 | 1.1998 |  | 29-03-2026 16:10 | 194.685 | 199.317 | 2287.7 | 33.2195 | 33.3775 | -0.15797 | 200.2648 | 33.6 | 32.9002 | 0.69982 |  | 29-03-2026 16:10 | 194.569 | 197.272 | 2294.8 | 32.8787 | 33.3775 | -0.49881 | 200.2648 | 33.2 | 32.9002 | 0.29982 |  | 29-03-2026 16:10 | 145.725 | 147.644 | 1723.7 | 24.6073 | 24.7241 | -0.11672 | 148.3443 | 24.8 | 24.3705 | 0.4295 |  | 29-03-2026 16:10 | 142.807 | 144.676 | 1705.4 | 24.1127 | 24.7241 | -0.61139 | 148.3443 | 24.8 | 24.3705 | 0.4295 |  | 29-03-2026 16:10 | 143.114 | 145.127 | 1709.2 | 24.1878 | 24.7241 | -0.53622 | 148.3443 | 24.7 | 24.3705 | 0.3295 |  | 29-03-2026 16:10 | 143.344 | 147.247 | 1720.8 | 24.5412 | 24.7241 | -0.18289 | 148.3443 | 24.7 | 24.3705 | 0.3295 |  | 29-03-2026 16:10 | 135.103 | 136.896 | 1623.8 | 22.816 | 23.5219 | -0.70588 | 141.1313 | 23.4 | 23.1855 | 0.21449 |  | 29-03-2026 16:10 | 252.8083 | 255.928 | -3.1197 | 1535.568 | 255.2 | 252.2682 | 2.9318 | 2.3917
29-03-2026 16:00 | 605 | 49.94 | 213.469 | 216.478 | 2267.5 | 36.0797 | 35.8674 | 0.21222 | 215.2047 | 36.8 | 35.3545 | 1.4455 |  | 29-03-2026 16:00 | 211.605 | 214.631 | 2277.4 | 35.7718 | 35.8674 | -0.095613 | 215.2047 | 36 | 35.3545 | 0.64546 |  | 29-03-2026 16:00 | 208.659 | 213.595 | 2254.1 | 35.5992 | 35.8674 | -0.26828 | 215.2047 | 36.1 | 35.3545 | 0.74546 |  | 29-03-2026 16:00 | 208.619 | 211.603 | 2261.6 | 35.2672 | 35.8674 | -0.60028 | 215.2047 | 36.1 | 35.3545 | 0.74546 |  | 29-03-2026 16:00 | 156.68 | 158.792 | 1698.9 | 26.4653 | 26.5685 | -0.10315 | 159.4109 | 27.5 | 26.1885 | 1.3115 |  | 29-03-2026 16:00 | 153.431 | 155.82 | 1680.6 | 25.97 | 26.5685 | -0.59848 | 159.4109 | 26.5 | 26.1885 | 0.31145 |  | 29-03-2026 16:00 | 153.667 | 155.81 | 1684.5 | 25.9683 | 26.5685 | -0.60015 | 159.4109 | 26.6 | 26.1885 | 0.41145 |  | 29-03-2026 16:00 | 154.202 | 158.699 | 1696.1 | 26.4498 | 26.5685 | -0.11865 | 159.4109 | 26.7 | 26.1885 | 0.51145 |  | 29-03-2026 16:00 | 145.602 | 147.565 | 1600.4 | 24.5942 | 25.2766 | -0.68245 | 151.6597 | 25.1 | 24.9152 | 0.18484 |  | 29-03-2026 16:00 | 272.1655 | 275.0203 | -2.8548 | 1650.1219 | 277.4 | 271.0875 | 6.3125 | 5.2345
29-03-2026 15:50 | 650 | 50.23 | 226.899 | 230.167 | 2230.7 | 38.3612 | 38.4924 | -0.13125 | 230.9545 | 39.1 | 37.942 | 1.158 |  | 29-03-2026 15:50 | 226.76 | 230.267 | 2241.4 | 38.3778 | 38.4924 | -0.11459 | 230.9545 | 38.4 | 37.942 | 0.45802 |  | 29-03-2026 15:50 | 223.737 | 229.261 | 2218 | 38.2102 | 38.4924 | -0.28225 | 230.9545 | 37.5 | 37.942 | -0.44198 |  | 29-03-2026 15:50 | 224.005 | 227.255 | 2225.5 | 37.8758 | 38.4924 | -0.61659 | 230.9545 | 37.5 | 37.942 | -0.44198 |  | 29-03-2026 15:50 | 168.51 | 170.799 | 1671.4 | 28.4665 | 28.5129 | -0.046403 | 171.0774 | 28.1 | 28.1052 | -0.0051683 |  | 29-03-2026 15:50 | 165.377 | 167.936 | 1654.1 | 27.9893 | 28.5129 | -0.52357 | 171.0774 | 27.6 | 28.1052 | -0.50517 |  | 29-03-2026 15:50 | 165.825 | 168.434 | 1657.9 | 28.0723 | 28.5129 | -0.44057 | 171.0774 | 27.8 | 28.1052 | -0.30517 |  | 29-03-2026 15:50 | 166.363 | 171.028 | 1669.4 | 28.5047 | 28.5129 | -0.0082362 | 171.0774 | 27.8 | 28.1052 | -0.30517 |  | 29-03-2026 15:50 | 156.81 | 158.986 | 1575.3 | 26.4977 | 27.1265 | -0.62883 | 162.759 | 26.2 | 26.7386 | -0.53859 |  | 29-03-2026 15:50 | 292.3555 | 295.1478 | -2.7923 | 1770.8867 | 290 | 290.9272 | -0.92717 | -2.3555
29-03-2026 15:40 | 652 | 49.94 | 221.836 | 225.009 | 2191.6 | 37.5015 | 38.6538 | -1.1523 | 231.9231 | 37.6 | 38.1011 | -0.50109 |  | 29-03-2026 15:40 | 225.009 | 228.366 | 2203 | 38.061 | 38.6538 | -0.59284 | 231.9231 | 39.5 | 38.1011 | 1.3989 |  | 29-03-2026 15:40 | 226.431 | 231.709 | 2180.5 | 38.6182 | 38.6538 | -0.035676 | 231.9231 | 38.8 | 38.1011 | 0.69891 |  | 29-03-2026 15:40 | 224.571 | 227.852 | 2188 | 37.9753 | 38.6538 | -0.67851 | 231.9231 | 38.9 | 38.1011 | 0.79891 |  | 29-03-2026 15:40 | 168.762 | 171.071 | 1643.3 | 28.5118 | 28.6325 | -0.12064 | 171.7949 | 28.9 | 28.223 | 0.67697 |  | 29-03-2026 15:40 | 164.8 | 167.407 | 1626.5 | 27.9012 | 28.6325 | -0.73131 | 171.7949 | 28.3 | 28.223 | 0.076968 |  | 29-03-2026 15:40 | 166.816 | 169.773 | 1630.1 | 28.2955 | 28.6325 | -0.33698 | 171.7949 | 28.3 | 28.223 | 0.076968 |  | 29-03-2026 15:40 | 167.74 | 172.655 | 1641.6 | 28.7758 | 28.6325 | 0.14336 | 171.7949 | 28.8 | 28.223 | 0.57697 |  | 29-03-2026 15:40 | 157.202 | 159.369 | 1549.1 | 26.5615 | 27.2403 | -0.67875 | 163.4415 | 27.2 | 26.8507 | 0.34928 |  | 29-03-2026 15:40 | 292.2018 | 296.3855 | -4.1837 | 1778.3132 | 296.3 | 292.1472 | 4.1528 | 4.0982
29-03-2026 15:30 | 723 | 49.94 | 249.631 | 253.407 | 2154 | 42.2345 | 42.8631 | -0.62858 | 257.1785 | 42.4 | 42.2501 | 0.14986 |  | 29-03-2026 15:30 | 251.507 | 255.489 | 2163.5 | 42.5815 | 42.8631 | -0.28158 | 257.1785 | 42.2 | 42.2501 | -0.050138 |  | 29-03-2026 15:30 | 247.381 | 253.851 | 2141.7 | 42.3085 | 42.8631 | -0.55458 | 257.1785 | 42.1 | 42.2501 | -0.15014 |  | 29-03-2026 15:30 | 247.914 | 251.715 | 2149.1 | 41.9525 | 42.8631 | -0.91058 | 257.1785 | 42.2 | 42.2501 | -0.050138 |  | 29-03-2026 15:30 | 185.708 | 188.395 | 1614.4 | 31.3992 | 31.7504 | -0.35126 | 190.5026 | 31.5 | 31.2964 | 0.2036 |  | 29-03-2026 15:30 | 182.537 | 185.591 | 1598.2 | 30.9318 | 31.7504 | -0.8186 | 190.5026 | 31 | 31.2964 | -0.2964 |  | 29-03-2026 15:30 | 182.661 | 185.637 | 1601.8 | 30.9395 | 31.7504 | -0.81093 | 190.5026 | 31.1 | 31.2964 | -0.1964 |  | 29-03-2026 15:30 | 183.263 | 188.277 | 1612.8 | 31.3795 | 31.7504 | -0.37093 | 190.5026 | 31.3 | 31.2964 | 0.0036012 |  | 29-03-2026 15:30 | 173.105 | 175.527 | 1521.9 | 29.2545 | 30.2066 | -0.9521 | 181.2396 | 29.5 | 29.7746 | -0.27465 |  | 29-03-2026 15:30 | 322.9815 | 328.6606 | -5.6791 | 1971.9639 | 323.3 | 323.9608 | -0.6608 | 0.3185
29-03-2026 15:20 | 757 | 49.94 | 260.851 | 264.796 | 2111.6 | 44.1327 | 44.8788 | -0.7461 | 269.2726 | 42.9 | 44.237 | -1.337 |  | 29-03-2026 15:20 | 263.403 | 267.496 | 2121.3 | 44.5827 | 44.8788 | -0.2961 | 269.2726 | 43.9 | 44.237 | -0.33701 |  | 29-03-2026 15:20 | 258.469 | 264.987 | 2099.6 | 44.1645 | 44.8788 | -0.71427 | 269.2726 | 42.7 | 44.237 | -1.537 |  | 29-03-2026 15:20 | 259.913 | 263.925 | 2106.9 | 43.9875 | 44.8788 | -0.89127 | 269.2726 | 42.8 | 44.237 | -1.437 |  | 29-03-2026 15:20 | 193.903 | 196.676 | 1582.9 | 32.7793 | 33.2435 | -0.4642 | 199.4612 | 32.1 | 32.7682 | -0.66815 |  | 29-03-2026 15:20 | 190.725 | 193.88 | 1567.2 | 32.3133 | 33.2435 | -0.9302 | 199.4612 | 31.5 | 32.7682 | -1.2682 |  | 29-03-2026 15:20 | 190.689 | 193.998 | 1570.7 | 32.333 | 33.2435 | -0.91053 | 199.4612 | 31.6 | 32.7682 | -1.1682 |  | 29-03-2026 15:20 | 191.817 | 197.255 | 1581.5 | 32.8758 | 33.2435 | -0.3677 | 199.4612 | 31.6 | 32.7682 | -1.1682 |  | 29-03-2026 15:20 | 181.119 | 183.691 | 1492.4 | 30.6152 | 31.6271 | -1.0119 | 189.7626 | 29.8 | 31.1748 | -1.3748 |  | 29-03-2026 15:20 | 337.784 | 344.1163 | -6.3323 | 2064.698 | 328.9 | 339.1955 | -10.2955 | -8.884
29-03-2026 15:10 | 745 | 49.94 | 256.658 | 260.567 | 2068.7 | 43.4278 | 44.1674 | -0.73952 | 265.0041 | 45.4 | 43.5358 | 1.8642 |  | 29-03-2026 15:10 | 259.253 | 263.254 | 2077.4 | 43.8757 | 44.1674 | -0.29168 | 265.0041 | 45.4 | 43.5358 | 1.8642 |  | 29-03-2026 15:10 | 253.548 | 260.208 | 2056.9 | 43.368 | 44.1674 | -0.79935 | 265.0041 | 45.2 | 43.5358 | 1.6642 |  | 29-03-2026 15:10 | 254.872 | 258.832 | 2064.1 | 43.1387 | 44.1674 | -1.0287 | 265.0041 | 45.3 | 43.5358 | 1.7642 |  | 29-03-2026 15:10 | 189.667 | 192.302 | 1550.8 | 32.0503 | 32.7166 | -0.66622 | 196.2993 | 34 | 32.2487 | 1.7513 |  | 29-03-2026 15:10 | 187.076 | 189.581 | 1535.7 | 31.5968 | 32.7166 | -1.1197 | 196.2993 | 33.9 | 32.2487 | 1.6513 |  | 29-03-2026 15:10 | 187.097 | 190.298 | 1539.1 | 31.7163 | 32.7166 | -1.0002 | 196.2993 | 34 | 32.2487 | 1.7513 |  | 29-03-2026 15:10 | 187.58 | 193.318 | 1549.9 | 32.2197 | 32.7166 | -0.49689 | 196.2993 | 33.7 | 32.2487 | 1.4513 |  | 29-03-2026 15:10 | 177.516 | 180.018 | 1462.6 | 30.003 | 31.1258 | -1.1228 | 186.7545 | 31.8 | 30.6807 | 1.1193 |  | 29-03-2026 15:10 | 331.3963 | 338.6614 | -7.265 | 2031.9683 | 348.7 | 333.8185 | 14.8815 | 17.3037
29-03-2026 15:00 | 838 | 49.94 | 284.808 | 289.292 | 2023.3 | 48.2153 | 49.6809 | -1.4655 | 298.0852 | 48.8 | 48.9704 | -0.17042 | 0.9845 | 29-03-2026 15:00 | 288.732 | 293.397 | 2032 | 48.8995 | 49.6809 | -0.78136 | 298.0852 | 48.7 | 48.9704 | -0.27042 | 0.9841 | 29-03-2026 15:00 | 283.397 | 290.875 | 2011.7 | 48.4792 | 49.6809 | -1.2017 | 298.0852 | 47.9 | 48.9704 | -1.0704 | 0.97429 | 29-03-2026 15:00 | 284.352 | 288.946 | 2018.8 | 48.1577 | 49.6809 | -1.5232 | 298.0852 | 48.1 | 48.9704 | -0.87042 | 0.9841 | 29-03-2026 15:00 | 212.972 | 216.062 | 1516.8 | 36.0103 | 36.8006 | -0.7903 | 220.8038 | 36.7 | 36.2744 | 0.42561 | 0.9857 | 29-03-2026 15:00 | 209.297 | 212.996 | 1501.8 | 35.4993 | 36.8006 | -1.3013 | 220.8038 | 35.5 | 36.2744 | -0.77439 | 0.98263 | 29-03-2026 15:00 | 209.859 | 213.739 | 1505.1 | 35.6232 | 36.8006 | -1.1775 | 220.8038 | 35.6 | 36.2744 | -0.67439 | 0.98185 | 29-03-2026 15:00 | 210.963 | 216.932 | 1516.2 | 36.1553 | 36.8006 | -0.6453 | 220.8038 | 35.8 | 36.2744 | -0.47439 | 0.97248 | 29-03-2026 15:00 | 199.152 | 202.021 | 1430.8 | 33.6702 | 35.0112 | -1.3411 | 210.0675 | 33.8 | 34.5106 | -0.71059 | 0.9858 | 29-03-2026 15:00 | 370.71 | 380.9372 | -10.2272 | 2285.6234 | 370.9 | 375.4898 | -4.5898 | 0.19
29-03-2026 14:50 | 863 | 49.65 | 293.615 | 298.359 | 1974.5 | 49.7265 | 51.2199 | -1.4934 | 307.3193 | 46 | 50.4874 | -4.4874 | 0.9841 | 29-03-2026 14:50 | 297.306 | 302.11 | 1983.3 | 50.3517 | 51.2199 | -0.86822 | 307.3193 | 48.6 | 50.4874 | -1.8874 | 0.9841 | 29-03-2026 14:50 | 292.239 | 300.073 | 1963.8 | 50.0122 | 51.2199 | -1.2077 | 307.3193 | 47.8 | 50.4874 | -2.6874 | 0.97389 | 29-03-2026 14:50 | 293.36 | 298.13 | 1970.7 | 49.6883 | 51.2199 | -1.5315 | 307.3193 | 48 | 50.4874 | -2.4874 | 0.984 | 29-03-2026 14:50 | 220.281 | 223.499 | 1480.1 | 37.2498 | 37.9407 | -0.69082 | 227.6439 | 35.5 | 37.3981 | -1.8981 | 0.9856 | 29-03-2026 14:50 | 216.11 | 220.085 | 1466.3 | 36.6808 | 37.9407 | -1.2598 | 227.6439 | 34.8 | 37.3981 | -2.5981 | 0.98194 | 29-03-2026 14:50 | 217.12 | 221.259 | 1469.5 | 36.8765 | 37.9407 | -1.0642 | 227.6439 | 34.9 | 37.3981 | -2.4981 | 0.98129 | 29-03-2026 14:50 | 217.822 | 224.099 | 1480.4 | 37.3498 | 37.9407 | -0.59082 | 227.6439 | 35.1 | 37.3981 | -2.2981 | 0.97199 | 29-03-2026 14:50 | 205.68 | 208.664 | 1397 | 34.7773 | 36.0958 | -1.3185 | 216.575 | 33.1 | 35.5797 | -2.4797 | 0.9857 | 29-03-2026 14:50 | 382.713 | 392.738 | -10.025 | 2356.4279 | 363.8 | 387.1218 | -23.3218 | -18.913
29-03-2026 14:40 | 828 | 49.65 | 282.954 | 287.409 | 1928.5 | 47.9015 | 49.1426 | -1.2411 | 294.8556 | 45.2 | 48.4399 | -3.2399 | 0.9845 | 29-03-2026 14:40 | 278.962 | 283.44 | 1934.7 | 47.24 | 49.1426 | -1.9026 | 294.8556 | 45.5 | 48.4399 | -2.9399 | 0.9842 | 29-03-2026 14:40 | 281.379 | 288.933 | 1916 | 48.1555 | 49.1426 | -0.9871 | 294.8556 | 44.2 | 48.4399 | -4.2399 | 0.97386 | 29-03-2026 14:40 | 281.552 | 286.043 | 1922.7 | 47.6738 | 49.1426 | -1.4688 | 294.8556 | 44.3 | 48.4399 | -4.1399 | 0.9843 | 29-03-2026 14:40 | 211.412 | 214.501 | 1444.6 | 35.7502 | 36.4019 | -0.65176 | 218.4115 | 33.2 | 35.8814 | -2.6814 | 0.9856 | 29-03-2026 14:40 | 207.29 | 210.889 | 1431.5 | 35.1482 | 36.4019 | -1.2538 | 218.4115 | 32.6 | 35.8814 | -3.2814 | 0.98293 | 29-03-2026 14:40 | 208.09 | 211.925 | 1434.6 | 35.3208 | 36.4019 | -1.0811 | 218.4115 | 32.8 | 35.8814 | -3.0814 | 0.9819 | 29-03-2026 14:40 | 208.068 | 213.976 | 1445.3 | 35.6627 | 36.4019 | -0.73926 | 218.4115 | 33.4 | 35.8814 | -2.4814 | 0.97239 | 29-03-2026 14:40 | 196.807 | 199.682 | 1363.9 | 33.2803 | 34.6319 | -1.3516 | 207.7915 | 31.4 | 34.1367 | -2.7367 | 0.9856 | 29-03-2026 14:40 | 366.133 | 376.81 | -10.677 | 2260.8601 | 342.6 | 371.4216 | -28.8216 | -23.533
29-03-2026 14:30 | 785 | 49.94 | 265.078 | 269.251 | 1883.3 | 44.8752 | 46.5388 | -1.6636 | 279.2325 | 53.6 | 45.8732 | 7.7268 | 0.9845 | 29-03-2026 14:30 | 283.665 | 288.277 | 1889.2 | 48.0462 | 46.5388 | 1.5074 | 279.2325 | 52.9 | 45.8732 | 7.0268 | 0.984 | 29-03-2026 14:30 | 262.081 | 269.008 | 1871.8 | 44.8347 | 46.5388 | -1.7041 | 279.2325 | 52.1 | 45.8732 | 6.2268 | 0.97425 | 29-03-2026 14:30 | 266.66 | 270.968 | 1878.4 | 45.1613 | 46.5388 | -1.3774 | 279.2325 | 52.8 | 45.8732 | 6.9268 | 0.9841 | 29-03-2026 14:30 | 198.36 | 201.299 | 1411.4 | 33.5498 | 34.4732 | -0.92332 | 206.8389 | 39.7 | 33.9802 | 5.7198 | 0.9854 | 29-03-2026 14:30 | 195.32 | 198.174 | 1398.9 | 33.029 | 34.4732 | -1.4442 | 206.8389 | 38.9 | 33.9802 | 4.9198 | 0.9856 | 29-03-2026 14:30 | 204.892 | 199.311 | 1401.8 | 33.2185 | 34.4732 | -1.2547 | 206.8389 | 39.1 | 33.9802 | 5.1198 | 1.028 | 29-03-2026 14:30 | 208.14 | 212.975 | 1411.9 | 35.4958 | 34.4732 | 1.0227 | 206.8389 | 38.8 | 33.9802 | 4.8198 | 0.9773 | 29-03-2026 14:30 | 193.392 | 197.764 | 1332.5 | 32.9607 | 32.7969 | 0.16373 | 196.7816 | 36.6 | 32.3279 | 4.2721 | 0.97789 | 29-03-2026 14:30 | 351.1712 | 356.8445 | -5.6734 | 2141.0673 | 404.5 | 351.7417 | 52.7583 | 53.3288
29-03-2026 14:20 | 920 | 49.94 | 286.881 | 291.516 | 1829.7 | 48.586 | 54.5422 | -5.9562 | 327.2534 | 52 | 53.7623 | -1.7623 | 0.9841 | 29-03-2026 14:20 | 303.313 | 306.901 | 1836.3 | 51.1502 | 54.5422 | -3.3921 | 327.2534 | 55.7 | 53.7623 | 1.9377 | 0.98831 | 29-03-2026 14:20 | 308.738 | 317.591 | 1819.7 | 52.9318 | 54.5422 | -1.6104 | 327.2534 | 53.7 | 53.7623 | -0.062278 | 0.97212 | 29-03-2026 14:20 | 300.197 | 303.908 | 1825.6 | 50.6513 | 54.5422 | -3.8909 | 327.2534 | 53.4 | 53.7623 | -0.36228 | 0.98779 | 29-03-2026 14:20 | 227.469 | 231.257 | 1371.7 | 38.5428 | 40.4017 | -1.8588 | 242.4099 | 40.1 | 39.8239 | 0.27609 | 0.98362 | 29-03-2026 14:20 | 221.643 | 226.336 | 1360 | 37.7227 | 40.4017 | -2.679 | 242.4099 | 39.4 | 39.8239 | -0.42391 | 0.97927 | 29-03-2026 14:20 | 225.087 | 230.573 | 1362.7 | 38.4288 | 40.4017 | -1.9728 | 242.4099 | 39.6 | 39.8239 | -0.22391 | 0.97621 | 29-03-2026 14:20 | 225.366 | 232.108 | 1373.1 | 38.6847 | 40.4017 | -1.717 | 242.4099 | 39.8 | 39.8239 | -0.02391 | 0.97095 | 29-03-2026 14:20 | 211.82 | 215.002 | 1295.9 | 35.8337 | 38.4372 | -2.6035 | 230.623 | 37.4 | 37.8875 | -0.48752 | 0.9852 | 29-03-2026 14:20 | 392.532 | 418.2127 | -25.6807 | 2509.2763 | 411.1 | 412.2323 | -1.1323 | 18.568
29-03-2026 14:10 | 977 | 49.65 | 327.251 | 332.775 | 1777.7 | 55.4625 | 57.9859 | -2.5234 | 347.9154 | 55.5 | 57.1567 | -1.6567 | 0.9834 | 29-03-2026 14:10 | 331.51 | 337.209 | 1780.6 | 56.2015 | 57.9859 | -1.7844 | 347.9154 | 53.8 | 57.1567 | -3.3567 | 0.9831 | 29-03-2026 14:10 | 326.096 | 335.57 | 1766 | 55.9283 | 57.9859 | -2.0576 | 347.9154 | 54.5 | 57.1567 | -2.6567 | 0.97177 | 29-03-2026 14:10 | 327.649 | 333.281 | 1772.2 | 55.5468 | 57.9859 | -2.4391 | 347.9154 | 55.6 | 57.1567 | -1.5567 | 0.9831 | 29-03-2026 14:10 | 245.81 | 249.629 | 1331.6 | 41.6048 | 42.9525 | -1.3477 | 257.7151 | 41.8 | 42.3383 | -0.53829 | 0.9847 | 29-03-2026 14:10 | 241.282 | 245.702 | 1320.6 | 40.9503 | 42.9525 | -2.0022 | 257.7151 | 40.9 | 42.3383 | -1.4383 | 0.98201 | 29-03-2026 14:10 | 242.539 | 247.253 | 1323.1 | 41.2088 | 42.9525 | -1.7437 | 257.7151 | 41.1 | 42.3383 | -1.2383 | 0.98093 | 29-03-2026 14:10 | 243.56 | 250.804 | 1333.3 | 41.8007 | 42.9525 | -1.1518 | 257.7151 | 41.3 | 42.3383 | -1.0383 | 0.97112 | 29-03-2026 14:10 | 229.439 | 232.933 | 1258.5 | 38.8222 | 40.864 | -2.0418 | 245.184 | 39 | 40.2796 | -1.2796 | 0.985 | 29-03-2026 14:10 | 427.526 | 444.6176 | -17.0916 | 2667.7057 | 423.5 | 438.2596 | -14.7596 | -4.026
29-03-2026 14:00 | 1002 | 49.65 | 334.496 | 340.212 | 1722.2 | 56.702 | 59.4697 | -2.7677 | 356.818 | 56.5 | 58.6193 | -2.1193 | 0.9832 | 29-03-2026 14:00 | 339.273 | 345.211 | 1726.8 | 57.5352 | 59.4697 | -1.9345 | 356.818 | 57.1 | 58.6193 | -1.5193 | 0.9828 | 29-03-2026 14:00 | 331.927 | 341.739 | 1711.5 | 56.9565 | 59.4697 | -2.5132 | 356.818 | 56 | 58.6193 | -2.6193 | 0.97129 | 29-03-2026 14:00 | 335.023 | 340.817 | 1716.6 | 56.8028 | 59.4697 | -2.6668 | 356.818 | 55.5 | 58.6193 | -3.1193 | 0.983 | 29-03-2026 14:00 | 251.943 | 255.858 | 1289.8 | 42.643 | 44.0516 | -1.4086 | 264.3096 | 42.4 | 43.4217 | -1.0217 | 0.9847 | 29-03-2026 14:00 | 247.232 | 252.015 | 1279.7 | 42.0025 | 44.0516 | -2.0491 | 264.3096 | 41.6 | 43.4217 | -1.8217 | 0.98102 | 29-03-2026 14:00 | 248.11 | 253.32 | 1282 | 42.22 | 44.0516 | -1.8316 | 264.3096 | 41.9 | 43.4217 | -1.5217 | 0.97943 | 29-03-2026 14:00 | 249.172 | 256.404 | 1292 | 42.734 | 44.0516 | -1.3176 | 264.3096 | 42.6 | 43.4217 | -0.82167 | 0.97179 | 29-03-2026 14:00 | 235.195 | 238.825 | 1219.5 | 39.8042 | 41.9096 | -2.1055 | 251.4579 | 39.7 | 41.3103 | -1.6103 | 0.9848 | 29-03-2026 14:00 | 437.4002 | 455.9947 | -18.5946 | 2735.9684 | 433.3 | 449.474 | -16.174 | -4.1002
29-03-2026 13:50 | 1021 | 49.94 | 343.19 | 346.84 | 1665.7 | 57.8067 | 60.53 | -2.7234 | 363.1801 | 57.7 | 59.6644 | -1.9644 | 0.98948 | 29-03-2026 13:50 | 338.272 | 343.807 | 1669.7 | 57.3012 | 60.53 | -3.2289 | 363.1801 | 57.3 | 59.6644 | -2.3644 | 0.9839 | 29-03-2026 13:50 | 338.952 | 348.87 | 1655.5 | 58.145 | 60.53 | -2.385 | 363.1801 | 56.6 | 59.6644 | -3.0644 | 0.97157 | 29-03-2026 13:50 | 340.709 | 346.672 | 1661.1 | 57.7787 | 60.53 | -2.7514 | 363.1801 | 56.7 | 59.6644 | -2.9644 | 0.9828 | 29-03-2026 13:50 | 256.157 | 260.19 | 1247.4 | 43.365 | 44.8371 | -1.4721 | 269.0223 | 42 | 44.1959 | -2.1959 | 0.9845 | 29-03-2026 13:50 | 251.235 | 256.249 | 1238.1 | 42.7082 | 44.8371 | -2.1289 | 269.0223 | 41.3 | 44.1959 | -2.8959 | 0.98043 | 29-03-2026 13:50 | 252.718 | 257.842 | 1240.1 | 42.9737 | 44.8371 | -1.8634 | 269.0223 | 42.1 | 44.1959 | -2.0959 | 0.98013 | 29-03-2026 13:50 | 253.709 | 261.446 | 1249.4 | 43.5743 | 44.8371 | -1.2627 | 269.0223 | 41.9 | 44.1959 | -2.2959 | 0.97041 | 29-03-2026 13:50 | 239.179 | 242.787 | 1179.8 | 40.4645 | 42.6569 | -2.1924 | 255.9414 | 39.9 | 42.0469 | -2.1469 | 0.98514 | 29-03-2026 13:50 | 444.1172 | 464.1252 | -20.008 | 2784.7512 | 435.5 | 457.4882 | -21.9882 | -8.6172
29-03-2026 13:40 | 1043 | 49.94 | 347.886 | 353.8 | 1608 | 58.9667 | 61.8343 | -2.8676 | 371.0057 | 56.7 | 60.9501 | -4.2501 | 0.98328 | 29-03-2026 13:40 | 349.653 | 355.519 | 1612.4 | 59.2532 | 61.8343 | -2.5811 | 371.0057 | 59.8 | 60.9501 | -1.1501 | 0.9835 | 29-03-2026 13:40 | 345.783 | 355.886 | 1598.9 | 59.3143 | 61.8343 | -2.52 | 371.0057 | 57.2 | 60.9501 | -3.7501 | 0.97161 | 29-03-2026 13:40 | 342.41 | 347.942 | 1604.4 | 57.9903 | 61.8343 | -3.844 | 371.0057 | 58.1 | 60.9501 | -2.8501 | 0.9841 | 29-03-2026 13:40 | 261.133 | 265.271 | 1205.4 | 44.2118 | 45.8032 | -1.5913 | 274.8191 | 43.9 | 45.1482 | -1.2482 | 0.9844 | 29-03-2026 13:40 | 256.124 | 261.21 | 1196.8 | 43.535 | 45.8032 | -2.2682 | 274.8191 | 43.1 | 45.1482 | -2.0482 | 0.98053 | 29-03-2026 13:40 | 257.596 | 263.163 | 1198 | 43.8605 | 45.8032 | -1.9427 | 274.8191 | 42.7 | 45.1482 | -2.4482 | 0.97885 | 29-03-2026 13:40 | 259.05 | 266.95 | 1207.5 | 44.4917 | 45.8032 | -1.3115 | 274.8191 | 42.9 | 45.1482 | -2.2482 | 0.97041 | 29-03-2026 13:40 | 243.659 | 247.486 | 1139.9 | 41.2477 | 43.5761 | -2.3284 | 261.4563 | 40.4 | 42.9529 | -2.5529 | 0.98454 | 29-03-2026 13:40 | 452.8712 | 474.1259 | -21.2548 | 2844.7556 | 444.8 | 467.3459 | -22.5459 | -8.0712
29-03-2026 13:30 | 1051 | 49.94 | 352.006 | 358.057 | 1551.3 | 59.6762 | 62.3086 | -2.6324 | 373.8514 | 59.2 | 61.4176 | -2.2176 | 0.9831 | 29-03-2026 13:30 | 352.833 | 358.511 | 1552.6 | 59.7518 | 62.3086 | -2.5567 | 373.8514 | 56 | 61.4176 | -5.4176 | 0.98416 | 29-03-2026 13:30 | 349.919 | 359.779 | 1541.7 | 59.9632 | 62.3086 | -2.3454 | 373.8514 | 58.7 | 61.4176 | -2.7176 | 0.97259 | 29-03-2026 13:30 | 352.171 | 358.387 | 1546.3 | 59.7312 | 62.3086 | -2.5774 | 373.8514 | 57.7 | 61.4176 | -3.7176 | 0.98266 | 29-03-2026 13:30 | 264.406 | 268.596 | 1161.5 | 44.766 | 46.1545 | -1.3885 | 276.927 | 43.7 | 45.4945 | -1.7945 | 0.9844 | 29-03-2026 13:30 | 259.971 | 265.156 | 1153.7 | 44.1927 | 46.1545 | -1.9618 | 276.927 | 42.9 | 45.4945 | -2.5945 | 0.98045 | 29-03-2026 13:30 | 261.259 | 266.728 | 1155.3 | 44.4547 | 46.1545 | -1.6998 | 276.927 | 43.9 | 45.4945 | -1.5945 | 0.9795 | 29-03-2026 13:30 | 262.569 | 270.071 | 1164.6 | 45.0118 | 46.1545 | -1.1427 | 276.927 | 44.1 | 45.4945 | -1.3945 | 0.97222 | 29-03-2026 13:30 | 247.472 | 251.343 | 1099.5 | 41.8905 | 43.9103 | -2.0198 | 263.4617 | 41.5 | 43.2824 | -1.7824 | 0.9846 | 29-03-2026 13:30 | 459.438 | 477.7626 | -18.3246 | 2866.5754 | 447.7 | 470.9306 | -23.2306 | -11.738
29-03-2026 13:20 | 1061 | 50.23 | 352.698 | 358.365 | 1492.1 | 59.7275 | 62.8315 | -3.104 | 376.9888 | 59.3 | 61.933 | -2.633 | 0.98419 | 29-03-2026 13:20 | 352.897 | 358.599 | 1496.6 | 59.7665 | 62.8315 | -3.065 | 376.9888 | 58.5 | 61.933 | -3.433 | 0.9841 | 29-03-2026 13:20 | 352.582 | 362.842 | 1483 | 60.4737 | 62.8315 | -2.3578 | 376.9888 | 58.6 | 61.933 | -3.333 | 0.97172 | 29-03-2026 13:20 | 352.36 | 358.162 | 1488.6 | 59.6937 | 62.8315 | -3.1378 | 376.9888 | 58.2 | 61.933 | -3.733 | 0.9838 | 29-03-2026 13:20 | 266.353 | 270.546 | 1117.8 | 45.091 | 46.5418 | -1.4508 | 279.251 | 44.8 | 45.8763 | -1.0763 | 0.9845 | 29-03-2026 13:20 | 262.084 | 267.318 | 1110.8 | 44.553 | 46.5418 | -1.9888 | 279.251 | 44.1 | 45.8763 | -1.7763 | 0.98042 | 29-03-2026 13:20 | 263.328 | 268.94 | 1111.4 | 44.8233 | 46.5418 | -1.7185 | 279.251 | 44 | 45.8763 | -1.8763 | 0.97913 | 29-03-2026 13:20 | 264.811 | 272.431 | 1120.5 | 45.4052 | 46.5418 | -1.1367 | 279.251 | 44.3 | 45.8763 | -1.5763 | 0.97203 | 29-03-2026 13:20 | 249.572 | 253.476 | 1058 | 42.246 | 44.2788 | -2.0328 | 265.6727 | 41.8 | 43.6456 | -1.8456 | 0.9846 | 29-03-2026 13:20 | 461.7798 | 481.772 | -19.9922 | 2890.632 | 453.6 | 474.8827 | -21.2827 | -8.1798
29-03-2026 13:10 | 1033 | 50.51 | 336.867 | 346.181 | 1432.8 | 57.6968 | 61.1076 | -3.4107 | 366.6455 | 58 | 60.2337 | -2.2337 | 0.97309 | 29-03-2026 13:10 | 350.443 | 356.721 | 1438.1 | 59.4535 | 61.1076 | -1.6541 | 366.6455 | 59.6 | 60.2337 | -0.63374 | 0.9824 | 29-03-2026 13:10 | 343.671 | 354.153 | 1424.4 | 59.0255 | 61.1076 | -2.0821 | 366.6455 | 57.9 | 60.2337 | -2.3337 | 0.9704 | 29-03-2026 13:10 | 345.319 | 351.327 | 1430.4 | 58.5545 | 61.1076 | -2.5531 | 366.6455 | 58 | 60.2337 | -2.2337 | 0.9829 | 29-03-2026 13:10 | 258.827 | 262.902 | 1073 | 43.817 | 45.2649 | -1.4479 | 271.5892 | 44.1 | 44.6176 | -0.51759 | 0.9845 | 29-03-2026 13:10 | 251.123 | 259.91 | 1066.7 | 43.3183 | 45.2649 | -1.9465 | 271.5892 | 43.5 | 44.6176 | -1.1176 | 0.96619 | 29-03-2026 13:10 | 252.7 | 256.626 | 1067.4 | 42.771 | 45.2649 | -2.4939 | 271.5892 | 43 | 44.6176 | -1.6176 | 0.9847 | 29-03-2026 13:10 | 257.505 | 261.506 | 1076.2 | 43.5843 | 45.2649 | -1.6805 | 271.5892 | 43.2 | 44.6176 | -1.4176 | 0.9847 | 29-03-2026 13:10 | 245.218 | 249.053 | 1016.2 | 41.5088 | 43.0639 | -1.5551 | 258.3835 | 40.8 | 42.4481 | -1.6481 | 0.9846 | 29-03-2026 13:10 | 449.7298 | 468.5537 | -18.8239 | 2811.3224 | 448.1 | 461.8534 | -13.7534 | -1.6298
29-03-2026 13:00 | 1082 | 50.23 | 352.887 | 358.516 | 1374.8 | 59.7527 | 64.0751 | -4.3224 | 384.4504 | 61.1 | 63.1588 | -2.0588 | 0.9843 | 29-03-2026 13:00 | 352.846 | 358.51 | 1378.5 | 59.7517 | 64.0751 | -4.3234 | 384.4504 | 57.3 | 63.1588 | -5.8588 | 0.9842 | 29-03-2026 13:00 | 352.573 | 362.883 | 1366.5 | 60.4805 | 64.0751 | -3.5946 | 384.4504 | 58.6 | 63.1588 | -4.5588 | 0.97159 | 29-03-2026 13:00 | 352.637 | 358.335 | 1372.4 | 59.7225 | 64.0751 | -4.3526 | 384.4504 | 58.4 | 63.1588 | -4.7588 | 0.9841 | 29-03-2026 13:00 | 270.891 | 275.212 | 1028.9 | 45.8687 | 47.463 | -1.5944 | 284.7781 | 44.7 | 46.7843 | -2.0843 | 0.9843 | 29-03-2026 13:00 | 266.444 | 271.766 | 1023.2 | 45.2943 | 47.463 | -2.1687 | 284.7781 | 43.9 | 46.7843 | -2.8843 | 0.98042 | 29-03-2026 13:00 | 267.624 | 273.198 | 1024.4 | 45.533 | 47.463 | -1.93 | 284.7781 | 44.2 | 46.7843 | -2.5843 | 0.9796 | 29-03-2026 13:00 | 269.477 | 277.475 | 1033 | 46.2458 | 47.463 | -1.2172 | 284.7781 | 44.5 | 46.7843 | -2.2843 | 0.97118 | 29-03-2026 13:00 | 253.96 | 257.985 | 975.4 | 42.9975 | 45.1552 | -2.1577 | 270.9311 | 41.8 | 44.5095 | -2.7095 | 0.9844 | 29-03-2026 13:00 | 465.6467 | 491.3075 | -25.6609 | 2947.8452 | 454.5 | 484.2818 | -29.7818 | -11.1467
29-03-2026 12:50 | 1077 | 49.94 | 352.017 | 357.705 | 1313.7 | 59.6175 | 63.85 | -4.2325 | 383.0999 | 55.1 | 62.9369 | -7.8369 | 0.9841 | 29-03-2026 12:50 | 352.881 | 358.582 | 1321.2 | 59.7637 | 63.85 | -4.0863 | 383.0999 | 59.1 | 62.9369 | -3.8369 | 0.9841 | 29-03-2026 12:50 | 352.308 | 362.376 | 1307.9 | 60.396 | 63.85 | -3.454 | 383.0999 | 58.3 | 62.9369 | -4.6369 | 0.97222 | 29-03-2026 12:50 | 348.619 | 354.252 | 1314 | 59.042 | 63.85 | -4.808 | 383.0999 | 58.5 | 62.9369 | -4.4369 | 0.9841 | 29-03-2026 12:50 | 269.631 | 273.904 | 984.2 | 45.6507 | 47.2963 | -1.6456 | 283.7777 | 45.4 | 46.6199 | -1.2199 | 0.9844 | 29-03-2026 12:50 | 264.758 | 269.831 | 979.3 | 44.9718 | 47.2963 | -2.3245 | 283.7777 | 44.7 | 46.6199 | -1.9199 | 0.9812 | 29-03-2026 12:50 | 266.514 | 272.291 | 980.2 | 45.3818 | 47.2963 | -1.9145 | 283.7777 | 44.9 | 46.6199 | -1.7199 | 0.97878 | 29-03-2026 12:50 | 268.17 | 275.843 | 988.5 | 45.9738 | 47.2963 | -1.3225 | 283.7777 | 45.2 | 46.6199 | -1.4199 | 0.97218 | 29-03-2026 12:50 | 252.452 | 256.453 | 933.6 | 42.7422 | 44.9966 | -2.2544 | 269.9793 | 42.6 | 44.3531 | -1.7531 | 0.9844 | 29-03-2026 12:50 | 463.5395 | 489.5816 | -26.0421 | 2937.4897 | 453.8 | 482.5806 | -28.7806 | -9.7395
29-03-2026 12:40 | 1091 | 50.23 | 352.799 | 358.426 | 1258.6 | 59.7377 | 64.608 | -4.8704 | 387.6483 | 60.2 | 63.6841 | -3.4841 | 0.9843 | 29-03-2026 12:40 | 352.879 | 358.508 | 1262.1 | 59.7513 | 64.608 | -4.8567 | 387.6483 | 58.4 | 63.6841 | -5.2841 | 0.9843 | 29-03-2026 12:40 | 352.23 | 362.86 | 1249.6 | 60.4767 | 64.608 | -4.1314 | 387.6483 | 59.2 | 63.6841 | -4.4841 | 0.9707 | 29-03-2026 12:40 | 347.288 | 352.756 | 1255.5 | 58.7927 | 64.608 | -5.8154 | 387.6483 | 57.9 | 63.6841 | -5.7841 | 0.9845 | 29-03-2026 12:40 | 271.66 | 275.993 | 938.8 | 45.9988 | 47.8578 | -1.859 | 287.1469 | 44.9 | 47.1734 | -2.2734 | 0.9843 | 29-03-2026 12:40 | 267.554 | 272.904 | 934.6 | 45.484 | 47.8578 | -2.3738 | 287.1469 | 44.2 | 47.1734 | -2.9734 | 0.9804 | 29-03-2026 12:40 | 268.252 | 273.76 | 935.3 | 45.6267 | 47.8578 | -2.2311 | 287.1469 | 44.4 | 47.1734 | -2.7734 | 0.97988 | 29-03-2026 12:40 | 269.545 | 277.684 | 943.3 | 46.2807 | 47.8578 | -1.5771 | 287.1469 | 44.6 | 47.1734 | -2.5734 | 0.97069 | 29-03-2026 12:40 | 254.378 | 258.409 | 891 | 43.0682 | 45.5308 | -2.4626 | 273.1847 | 42.7 | 44.8797 | -2.1797 | 0.9844 | 29-03-2026 12:40 | 465.2167 | 495.3942 | -30.1775 | 2972.3652 | 456.5 | 488.3101 | -31.8101 | -8.7167
29-03-2026 12:30 | 1080 | 50.51 | 352.771 | 358.398 | 1198.4 | 59.733 | 63.8879 | -4.1549 | 383.3273 | 58.2 | 62.9743 | -4.7743 | 0.9843 | 29-03-2026 12:30 | 352.891 | 358.483 | 1203.7 | 59.7472 | 63.8879 | -4.1407 | 383.3273 | 57.5 | 62.9743 | -5.4743 | 0.9844 | 29-03-2026 12:30 | 352.134 | 362.627 | 1190.4 | 60.4378 | 63.8879 | -3.4501 | 383.3273 | 59 | 62.9743 | -3.9743 | 0.97106 | 29-03-2026 12:30 | 348.399 | 353.92 | 1197.6 | 58.9867 | 63.8879 | -4.9012 | 383.3273 | 59 | 62.9743 | -3.9743 | 0.9844 | 29-03-2026 12:30 | 270.867 | 275.187 | 893.9 | 45.8645 | 47.3244 | -1.4599 | 283.9462 | 45.2 | 46.6476 | -1.4476 | 0.9843 | 29-03-2026 12:30 | 267.102 | 272.394 | 890.4 | 45.399 | 47.3244 | -1.9254 | 283.9462 | 44.6 | 46.6476 | -2.0476 | 0.98057 | 29-03-2026 12:30 | 267.721 | 273.326 | 890.9 | 45.5543 | 47.3244 | -1.77 | 283.9462 | 44.7 | 46.6476 | -1.9476 | 0.97949 | 29-03-2026 12:30 | 269.314 | 277.328 | 898.7 | 46.2213 | 47.3244 | -1.103 | 283.9462 | 45 | 46.6476 | -1.6476 | 0.9711 | 29-03-2026 12:30 | 254.043 | 258.069 | 848.3 | 43.0115 | 45.0233 | -2.0118 | 270.1396 | 41.8 | 44.3794 | -2.5794 | 0.9844 | 29-03-2026 12:30 | 464.9553 | 489.8723 | -24.9169 | 2939.2335 | 455 | 482.8671 | -27.8671 | -9.9553
29-03-2026 12:20 | 1086 | 50.51 | 352.86 | 358.514 | 1140.2 | 59.7523 | 64.2428 | -4.4905 | 385.4569 | 57.5 | 63.3241 | -5.8241 | 0.98423 | 29-03-2026 12:20 | 352.868 | 358.441 | 1146.2 | 59.7402 | 64.2428 | -4.5027 | 385.4569 | 59.2 | 63.3241 | -4.1241 | 0.98445 | 29-03-2026 12:20 | 352.404 | 362.482 | 1131.4 | 60.4137 | 64.2428 | -3.8292 | 385.4569 | 58.2 | 63.3241 | -5.1241 | 0.9722 | 29-03-2026 12:20 | 352.755 | 358.491 | 1138.6 | 59.7485 | 64.2428 | -4.4943 | 385.4569 | 58.3 | 63.3241 | -5.0241 | 0.984 | 29-03-2026 12:20 | 271.145 | 275.442 | 848.7 | 45.907 | 47.5873 | -1.6803 | 285.5236 | 44.7 | 46.9068 | -2.2068 | 0.9844 | 29-03-2026 12:20 | 267.3 | 272.519 | 845.8 | 45.4198 | 47.5873 | -2.1674 | 285.5236 | 44.1 | 46.9068 | -2.8068 | 0.98085 | 29-03-2026 12:20 | 267.824 | 273.691 | 846.2 | 45.6152 | 47.5873 | -1.9721 | 285.5236 | 44.3 | 46.9068 | -2.6068 | 0.97856 | 29-03-2026 12:20 | 269.504 | 277.427 | 853.7 | 46.2378 | 47.5873 | -1.3494 | 285.5236 | 44.7 | 46.9068 | -2.2068 | 0.97144 | 29-03-2026 12:20 | 254.166 | 258.194 | 806.5 | 43.0323 | 45.2734 | -2.2411 | 271.6404 | 42 | 44.626 | -2.626 | 0.9844 | 29-03-2026 12:20 | 465.8668 | 492.5938 | -26.7269 | 2955.5626 | 453 | 485.5497 | -32.5497 | -12.8668
29-03-2026 12:10 | 1071 | 51.37 | 352.899 | 358.416 | 1082.7 | 59.736 | 63.1461 | -3.4101 | 378.8765 | 59.4 | 62.2431 | -2.8431 | 0.98461 | 29-03-2026 12:10 | 352.882 | 358.398 | 1087 | 59.733 | 63.1461 | -3.4131 | 378.8765 | 58.5 | 62.2431 | -3.7431 | 0.98461 | 29-03-2026 12:10 | 352.679 | 362.565 | 1073.2 | 60.4275 | 63.1461 | -2.7186 | 378.8765 | 58.5 | 62.2431 | -3.7431 | 0.97273 | 29-03-2026 12:10 | 352.617 | 358.351 | 1080.3 | 59.7252 | 63.1461 | -3.4209 | 378.8765 | 58.5 | 62.2431 | -3.7431 | 0.984 | 29-03-2026 12:10 | 269.696 | 273.97 | 804 | 45.6617 | 46.7749 | -1.1132 | 280.6493 | 44.4 | 46.106 | -1.706 | 0.9844 | 29-03-2026 12:10 | 265.57 | 270.969 | 801.7 | 45.1615 | 46.7749 | -1.6134 | 280.6493 | 43.7 | 46.106 | -2.406 | 0.98008 | 29-03-2026 12:10 | 267.165 | 272.678 | 801.9 | 45.4463 | 46.7749 | -1.3285 | 280.6493 | 44.6 | 46.106 | -1.506 | 0.97978 | 29-03-2026 12:10 | 268.962 | 277.283 | 809 | 46.2138 | 46.7749 | -0.56105 | 280.6493 | 44.8 | 46.106 | -1.306 | 0.96999 | 29-03-2026 12:10 | 253.438 | 257.402 | 764.5 | 42.9003 | 44.5005 | -1.6002 | 267.003 | 42.4 | 43.8641 | -1.4641 | 0.9846 | 29-03-2026 12:10 | 465.0053 | 484.1844 | -19.1791 | 2905.1064 | 454.8 | 477.2606 | -22.4606 | -10.2053
29-03-2026 12:00 | 1061 | 52.23 | 352.812 | 358.331 | 1023.3 | 59.7218 | 62.3491 | -2.6272 | 374.0943 | 58.6 | 61.4575 | -2.8575 | 0.9846 | 29-03-2026 12:00 | 352.744 | 358.433 | 1028.5 | 59.7388 | 62.3491 | -2.6102 | 374.0943 | 60.7 | 61.4575 | -0.75746 | 0.98413 | 29-03-2026 12:00 | 352.836 | 362.676 | 1014.7 | 60.446 | 62.3491 | -1.9031 | 374.0943 | 58.5 | 61.4575 | -2.9575 | 0.97287 | 29-03-2026 12:00 | 352.784 | 358.557 | 1021.8 | 59.7595 | 62.3491 | -2.5896 | 374.0943 | 59.3 | 61.4575 | -2.1575 | 0.9839 | 29-03-2026 12:00 | 266.839 | 271.013 | 759.6 | 45.1688 | 46.1845 | -1.0156 | 277.1069 | 44.2 | 45.524 | -1.324 | 0.9846 | 29-03-2026 12:00 | 263.359 | 268.253 | 758 | 44.7088 | 46.1845 | -1.4756 | 277.1069 | 43.7 | 45.524 | -1.824 | 0.98176 | 29-03-2026 12:00 | 264.324 | 269.809 | 757.3 | 44.9682 | 46.1845 | -1.2163 | 277.1069 | 43.1 | 45.524 | -2.424 | 0.97967 | 29-03-2026 12:00 | 265.922 | 274.012 | 764.2 | 45.6687 | 46.1845 | -0.51582 | 277.1069 | 43.4 | 45.524 | -2.124 | 0.97048 | 29-03-2026 12:00 | 250.758 | 254.706 | 722.1 | 42.451 | 43.9388 | -1.4878 | 263.6329 | 41.8 | 43.3105 | -1.5105 | 0.9845 | 29-03-2026 12:00 | 462.6317 | 478.0729 | -15.4413 | 2868.4377 | 453.3 | 471.2365 | -17.9365 | -9.3317
29-03-2026 11:50 | 1046 | 52.52 | 352.725 | 358.606 | 964.7 | 59.7677 | 61.3986 | -1.631 | 368.3917 | 61.1 | 60.5206 | 0.57938 | 0.9836 | 29-03-2026 11:50 | 352.767 | 358.612 | 967.8 | 59.7687 | 61.3986 | -1.63 | 368.3917 | 56.6 | 60.5206 | -3.9206 | 0.9837 | 29-03-2026 11:50 | 350.137 | 360.291 | 956.2 | 60.0485 | 61.3986 | -1.3501 | 368.3917 | 58.5 | 60.5206 | -2.0206 | 0.97182 | 29-03-2026 11:50 | 352.093 | 358.219 | 962.5 | 59.7032 | 61.3986 | -1.6955 | 368.3917 | 58.1 | 60.5206 | -2.4206 | 0.9829 | 29-03-2026 11:50 | 262.943 | 267.083 | 715.4 | 44.5138 | 45.4805 | -0.96663 | 272.8828 | 43.9 | 44.8301 | -0.93009 | 0.9845 | 29-03-2026 11:50 | 259.82 | 264.757 | 714.3 | 44.1262 | 45.4805 | -1.3543 | 272.8828 | 43.3 | 44.8301 | -1.5301 | 0.98135 | 29-03-2026 11:50 | 260.121 | 265.272 | 714.2 | 44.212 | 45.4805 | -1.2685 | 272.8828 | 43.5 | 44.8301 | -1.3301 | 0.98058 | 29-03-2026 11:50 | 261.855 | 269.785 | 720.8 | 44.9642 | 45.4805 | -0.51629 | 272.8828 | 43.8 | 44.8301 | -1.0301 | 0.97061 | 29-03-2026 11:50 | 247.251 | 251.093 | 680.3 | 41.8488 | 43.269 | -1.4202 | 259.6142 | 40.9 | 42.6503 | -1.7503 | 0.9847 | 29-03-2026 11:50 | 458.953 | 470.7854 | -11.8324 | 2824.7122 | 449.7 | 464.0531 | -14.3531 | -9.253
29-03-2026 11:40 | 1041 | 52.81 | 352.503 | 358.563 | 903.6 | 59.7605 | 61.0365 | -1.276 | 366.219 | 56.1 | 60.1637 | -4.0637 | 0.9831 | 29-03-2026 11:40 | 352.673 | 358.517 | 911.2 | 59.7528 | 61.0365 | -1.2837 | 366.219 | 58.3 | 60.1637 | -1.8637 |  | 29-03-2026 11:40 | 349.332 | 359.384 | 897.7 | 59.8973 | 61.0365 | -1.1392 | 366.219 | 57.3 | 60.1637 | -2.8637 | 0.97203 | 29-03-2026 11:40 | 351.441 | 357.519 | 904.4 | 59.5865 | 61.0365 | -1.45 | 366.219 | 57.5 | 60.1637 | -2.6637 | 0.983 | 29-03-2026 11:40 | 262.876 | 266.933 | 671.5 | 44.4888 | 45.2122 | -0.72339 | 271.2733 | 43.8 | 44.5657 | -0.76569 | 0.9848 | 29-03-2026 11:40 | 259.491 | 264.312 | 671 | 44.052 | 45.2122 | -1.1602 | 271.2733 | 43.3 | 44.5657 | -1.2657 | 0.98176 | 29-03-2026 11:40 | 260.702 | 265.998 | 670.7 | 44.333 | 45.2122 | -0.87922 | 271.2733 | 43.3 | 44.5657 | -1.2657 | 0.98009 | 29-03-2026 11:40 | 262.623 | 270.491 | 677 | 45.0818 | 45.2122 | -0.13039 | 271.2733 | 43.6 | 44.5657 | -0.96569 | 0.97091 | 29-03-2026 11:40 | 247.374 | 251.194 | 639.4 | 41.8657 | 43.0138 | -1.1482 | 258.083 | 40.6 | 42.3987 | -1.7987 | 0.98479 | 29-03-2026 11:40 | 458.8185 | 468.0087 | -9.1902 | 2808.0522 | 443.8 | 461.3162 | -17.5162 | -15.0185
29-03-2026 11:30 | 853 | 53.38 | 336.794 | 282.438 | 847.5 | 47.073 | 49.903 | -2.83 | 299.4182 | 57.4 | 49.1894 | 8.2106 | 1.1925 | 29-03-2026 11:30 | 266.503 | 269.803 | 852.9 | 44.9672 | 49.903 | -4.9359 | 299.4182 | 60.6 | 49.1894 | 11.4106 | 0.98777 | 29-03-2026 11:30 | 301.348 | 307.382 | 840.4 | 51.2303 | 49.903 | 1.3273 | 299.4182 | 57.9 | 49.1894 | 8.7106 | 0.98037 | 29-03-2026 11:30 | 299.438 | 304.307 | 846.9 | 50.7178 | 49.903 | 0.81479 | 299.4182 | 58.8 | 49.1894 | 9.6106 | 0.984 | 29-03-2026 11:30 | 219.954 | 223.879 | 627.7 | 37.3132 | 36.9652 | 0.34795 | 221.7913 | 44.4 | 36.4366 | 7.9634 | 0.98247 | 29-03-2026 11:30 | 213.087 | 218.858 | 627.7 | 36.4763 | 36.9652 | -0.48888 | 221.7913 | 44 | 36.4366 | 7.5634 | 0.97363 | 29-03-2026 11:30 | 215.324 | 221.626 | 627.4 | 36.9377 | 36.9652 | -0.027548 | 221.7913 | 44.8 | 36.4366 | 8.3634 | 0.97156 | 29-03-2026 11:30 | 212.879 | 219.738 | 633.4 | 36.623 | 36.9652 | -0.34221 | 221.7913 | 44.5 | 36.4366 | 8.0634 | 0.96879 | 29-03-2026 11:30 | 204.478 | 208.328 | 598.8 | 34.7213 | 35.1678 | -0.44649 | 211.0069 | 42.1 | 34.6649 | 7.4351 | 0.98152 | 29-03-2026 11:30 | 376.0598 | 382.6408 | -6.581 | 2295.845 | 454.5 | 377.1691 | 77.3309 | 78.4402
29-03-2026 11:20 | 1076 | 51.66 | 352.792 | 357.874 | 790.1 | 59.6457 | 63.37 | -3.7243 | 380.2197 | 43 | 62.4638 | -19.4638 | 0.9858 | 29-03-2026 11:20 | 291.558 | 296.088 | 792.3 | 49.348 | 63.37 | -14.022 | 380.2197 | 40.2 | 62.4638 | -22.2638 | 0.9847 | 29-03-2026 11:20 | 352.288 | 361.739 | 782.5 | 60.2898 | 63.37 | -3.0801 | 380.2197 | 42.4 | 62.4638 | -20.0638 | 0.97387 | 29-03-2026 11:20 | 352.459 | 357.79 | 788.1 | 59.6317 | 63.37 | -3.7383 | 380.2197 | 41.7 | 62.4638 | -20.7638 | 0.9851 | 29-03-2026 11:20 | 270.615 | 274.811 | 583.3 | 45.8018 | 46.9407 | -1.1389 | 281.6442 | 31.2 | 46.2695 | -15.0695 | 0.98473 | 29-03-2026 11:20 | 261.198 | 268.191 | 583.7 | 44.6985 | 46.9407 | -2.2422 | 281.6442 | 30.9 | 46.2695 | -15.3695 | 0.97393 | 29-03-2026 11:20 | 250.397 | 254.159 | 582.6 | 42.3598 | 46.9407 | -4.5809 | 281.6442 | 30.4 | 46.2695 | -15.8695 | 0.9852 | 29-03-2026 11:20 | 267.972 | 276.634 | 588.9 | 46.1057 | 46.9407 | -0.83504 | 281.6442 | 31.3 | 46.2695 | -14.9695 | 0.96869 | 29-03-2026 11:20 | 248.644 | 254.621 | 556.7 | 42.4368 | 44.6583 | -2.2214 | 267.9496 | 29.4 | 44.0197 | -14.6197 | 0.97653 | 29-03-2026 11:20 | 450.3178 | 485.9009 | -35.5831 | 2915.4053 | 320.5 | 478.9525 | -158.4525 | -129.8178
29-03-2026 11:10 | 697 | 51.66 | 275.026 | 279.129 | 747.1 | 46.5215 | 41.0491 | 5.4724 | 246.2947 | 43.6 | 40.4621 | 3.1379 | 0.9853 | 29-03-2026 11:10 | 271.7 | 280.859 | 752.1 | 46.8098 | 41.0491 | 5.7607 | 246.2947 | 43.9 | 40.4621 | 3.4379 | 0.96739 | 29-03-2026 11:10 | 247.132 | 254.82 | 740.1 | 42.47 | 41.0491 | 1.4209 | 246.2947 | 43.7 | 40.4621 | 3.2379 | 0.96983 | 29-03-2026 11:10 | 256.924 | 264.873 | 746.4 | 44.1455 | 41.0491 | 3.0964 | 246.2947 | 44 | 40.4621 | 3.5379 | 0.96999 | 29-03-2026 11:10 | 169.062 | 177.042 | 552.1 | 29.507 | 30.4068 | -0.89976 | 182.4405 | 33.3 | 29.9719 | 3.3281 | 0.95493 | 29-03-2026 11:10 | 182.214 | 184.689 | 552.8 | 30.7815 | 30.4068 | 0.37474 | 182.4405 | 33 | 29.9719 | 3.0281 | 0.9866 | 29-03-2026 11:10 | 160.876 | 163.078 | 552.2 | 27.1797 | 30.4068 | -3.2271 | 182.4405 | 33 | 29.9719 | 3.0281 | 0.9865 | 29-03-2026 11:10 | 161.625 | 165.738 | 557.6 | 27.623 | 30.4068 | -2.7838 | 182.4405 | 33.1 | 29.9719 | 3.1281 | 0.97518 | 29-03-2026 11:10 | 157.996 | 160.158 | 527.3 | 26.693 | 28.9283 | -2.2353 | 173.5696 | 31.3 | 28.5146 | 2.7854 | 0.9865 | 29-03-2026 11:10 | 321.731 | 314.7518 | 6.9792 | 1888.5107 | 338.9 | 310.2508 | 28.6492 | 17.169
29-03-2026 11:00 | 624 | 52.52 | 232.58 | 235.906 | 703.5 | 39.3177 | 36.6279 | 2.6898 | 219.7672 | 42 | 36.1041 | 5.8959 | 0.9859 | 29-03-2026 11:00 | 229.176 | 232.501 | 708.2 | 38.7502 | 36.6279 | 2.1223 | 219.7672 | 41.7 | 36.1041 | 5.5959 | 0.9857 | 29-03-2026 11:00 | 232.718 | 238.736 | 696.4 | 39.7893 | 36.6279 | 3.1615 | 219.7672 | 40.5 | 36.1041 | 4.3959 | 0.97479 | 29-03-2026 11:00 | 218.744 | 221.805 | 702.4 | 36.9675 | 36.6279 | 0.33964 | 219.7672 | 40.8 | 36.1041 | 4.6959 | 0.9862 | 29-03-2026 11:00 | 164.487 | 167.344 | 518.8 | 27.8907 | 27.1317 | 0.75892 | 162.7905 | 29.9 | 26.7438 | 3.1562 | 0.98293 | 29-03-2026 11:00 | 162.836 | 164.997 | 519.8 | 27.4995 | 27.1317 | 0.36775 | 162.7905 | 29.7 | 26.7438 | 2.9562 | 0.9869 | 29-03-2026 11:00 | 167.585 | 170.831 | 519.2 | 28.4718 | 27.1317 | 1.3401 | 162.7905 | 29.6 | 26.7438 | 2.8562 | 0.981 | 29-03-2026 11:00 | 169.493 | 174.85 | 524.5 | 29.1417 | 27.1317 | 2.0099 | 162.7905 | 30.2 | 26.7438 | 3.4562 | 0.96936 | 29-03-2026 11:00 | 156.51 | 158.62 | 496 | 26.4367 | 25.8125 | 0.62417 | 154.875 | 28.6 | 25.4434 | 3.1566 | 0.9867 | 29-03-2026 11:00 | 294.265 | 280.8509 | 13.4141 | 1685.1055 | 313 | 276.8348 | 36.1652 | 18.735
29-03-2026 10:50 | 681 | 49.94 | 259.954 | 263.806 | 661.5 | 43.9677 | 40.3731 | 3.5946 | 242.2387 | 48.8 | 39.7958 | 9.0042 | 0.9854 | 29-03-2026 10:50 | 244.445 | 248.117 | 666.5 | 41.3528 | 40.3731 | 0.97972 | 242.2387 | 50.5 | 39.7958 | 10.7042 | 0.9852 | 29-03-2026 10:50 | 235.471 | 240.837 | 655.9 | 40.1395 | 40.3731 | -0.23361 | 242.2387 | 49 | 39.7958 | 9.2042 | 0.97772 | 29-03-2026 10:50 | 239.464 | 243.037 | 661.6 | 40.5062 | 40.3731 | 0.13306 | 242.2387 | 49.5 | 39.7958 | 9.7042 | 0.9853 | 29-03-2026 10:50 | 177.285 | 179.675 | 488.9 | 29.9458 | 29.906 | 0.039827 | 179.436 | 36.7 | 29.4784 | 7.2216 | 0.9867 | 29-03-2026 10:50 | 177.882 | 180.349 | 490.1 | 30.0582 | 29.906 | 0.15216 | 179.436 | 36.5 | 29.4784 | 7.0216 | 0.98632 | 29-03-2026 10:50 | 178.081 | 180.884 | 489.6 | 30.1473 | 29.906 | 0.24133 | 179.436 | 36.5 | 29.4784 | 7.0216 | 0.9845 | 29-03-2026 10:50 | 179.204 | 184.097 | 494.3 | 30.6828 | 29.906 | 0.77683 | 179.436 | 36.9 | 29.4784 | 7.4216 | 0.97342 | 29-03-2026 10:50 | 169.001 | 171.348 | 467.4 | 28.558 | 28.4519 | 0.10614 | 170.7112 | 34.9 | 28.045 | 6.855 | 0.9863 | 29-03-2026 10:50 | 315.3583 | 309.5683 | 5.79 | 1857.4099 | 379.3 | 305.1415 | 74.1585 | 63.9417
29-03-2026 10:40 | 961 | 50.51 | 334.936 | 340.451 | 612.7 | 56.7418 | 56.8484 | -0.10655 | 341.0903 | 54.6 | 56.0355 | -1.4355 | 0.9838 | 29-03-2026 10:40 | 337.212 | 342.835 | 616 | 57.1392 | 56.8484 | 0.29078 | 341.0903 | 53.5 | 56.0355 | -2.5355 | 0.9836 | 29-03-2026 10:40 | 330.44 | 338.759 | 606.9 | 56.4598 | 56.8484 | -0.38855 | 341.0903 | 54.3 | 56.0355 | -1.7355 | 0.97544 | 29-03-2026 10:40 | 333.785 | 339.35 | 612.1 | 56.5583 | 56.8484 | -0.29005 | 341.0903 | 54.5 | 56.0355 | -1.5355 | 0.9836 | 29-03-2026 10:40 | 248.723 | 252.434 | 452.2 | 42.0723 | 42.1099 | -0.037583 | 252.6595 | 40.8 | 41.5077 | -0.70774 | 0.9853 | 29-03-2026 10:40 | 246.801 | 250.804 | 453.6 | 41.8007 | 42.1099 | -0.30925 | 252.6595 | 40.4 | 41.5077 | -1.1077 | 0.98404 | 29-03-2026 10:40 | 248.145 | 251.774 | 453.1 | 41.9623 | 42.1099 | -0.14758 | 252.6595 | 40.5 | 41.5077 | -1.0077 | 0.98559 | 29-03-2026 10:40 | 249.733 | 256.822 | 457.4 | 42.8037 | 42.1099 | 0.69375 | 252.6595 | 40.2 | 41.5077 | -1.3077 | 0.9724 | 29-03-2026 10:40 | 235.952 | 239.472 | 432.5 | 39.912 | 40.0624 | -0.15037 | 240.3742 | 37.9 | 39.4895 | -1.5895 | 0.9853 | 29-03-2026 10:40 | 435.4502 | 435.8956 | -0.44542 | 2615.3735 | 416.7 | 429.6623 | -12.9623 | -18.7502
29-03-2026 10:30 | 886 | 50.51 | 312.382 | 310.75 | 558.1 | 51.7917 | 52.4117 | -0.62006 | 314.4704 | 51.6 | 51.6622 | -0.062241 | 1.0053 | 29-03-2026 10:30 | 311.175 | 316.235 | 562.5 | 52.7058 | 52.4117 | 0.2941 | 314.4704 | 52.5 | 51.6622 | 0.83776 | 0.984 | 29-03-2026 10:30 | 305.576 | 313.553 | 552.6 | 52.2588 | 52.4117 | -0.1529 | 314.4704 | 50.3 | 51.6622 | -1.3622 | 0.97456 | 29-03-2026 10:30 | 304.152 | 308.274 | 557.6 | 51.379 | 52.4117 | -1.0327 | 314.4704 | 50.7 | 51.6622 | -0.96224 | 0.98663 | 29-03-2026 10:30 | 229.356 | 232.66 | 411.4 | 38.7767 | 38.8235 | -0.046836 | 232.941 | 37.8 | 38.2683 | -0.46833 | 0.9858 | 29-03-2026 10:30 | 227.109 | 230.912 | 413.2 | 38.4853 | 38.8235 | -0.33817 | 232.941 | 37.6 | 38.2683 | -0.66833 | 0.98353 | 29-03-2026 10:30 | 227.549 | 231.423 | 412.6 | 38.5705 | 38.8235 | -0.253 | 232.941 | 37.6 | 38.2683 | -0.66833 | 0.98326 | 29-03-2026 10:30 | 228.622 | 235.104 | 417.2 | 39.184 | 38.8235 | 0.3605 | 232.941 | 37.9 | 38.2683 | -0.36833 | 0.97243 | 29-03-2026 10:30 | 216.292 | 219.385 | 394.6 | 36.5642 | 36.9358 | -0.37159 | 221.6145 | 35.8 | 36.4076 | -0.60757 | 0.9859 | 29-03-2026 10:30 | 399.716 | 401.8767 | -2.1607 | 2411.2601 | 391.8 | 396.1298 | -4.3298 | -7.916
29-03-2026 10:20 | 868 | 50.8 | 303.352 | 308.034 | 506.5 | 51.339 | 51.2897 | 0.049296 | 307.7382 | 44 | 50.5563 | -6.5563 | 0.9848 | 29-03-2026 10:20 | 304.554 | 308.9 | 510 | 51.4833 | 51.2897 | 0.19363 | 307.7382 | 44.3 | 50.5563 | -6.2563 | 0.98593 | 29-03-2026 10:20 | 305.724 | 313.636 | 502.3 | 52.2727 | 51.2897 | 0.98296 | 307.7382 | 44.3 | 50.5563 | -6.2563 | 0.97477 | 29-03-2026 10:20 | 305.852 | 310.667 | 506.9 | 51.7778 | 51.2897 | 0.48813 | 307.7382 | 44.5 | 50.5563 | -6.0563 | 0.9845 | 29-03-2026 10:20 | 230.715 | 234.062 | 373.6 | 39.0103 | 37.9924 | 1.018 | 227.9542 | 33.2 | 37.4491 | -4.2491 | 0.9857 | 29-03-2026 10:20 | 227.918 | 231.294 | 375.6 | 38.549 | 37.9924 | 0.55663 | 227.9542 | 33 | 37.4491 | -4.4491 | 0.9854 | 29-03-2026 10:20 | 229.833 | 233.536 | 375 | 38.9227 | 37.9924 | 0.93029 | 227.9542 | 33.1 | 37.4491 | -4.3491 | 0.98414 | 29-03-2026 10:20 | 231.476 | 238.094 | 379.3 | 39.6823 | 37.9924 | 1.69 | 227.9542 | 33.4 | 37.4491 | -4.0491 | 0.9722 | 29-03-2026 10:20 | 218.456 | 221.155 | 358.8 | 36.8592 | 36.145 | 0.71413 | 216.8702 | 31.6 | 35.6282 | -4.0282 | 0.9878 | 29-03-2026 10:20 | 399.8963 | 393.2733 | 6.623 | 2359.6401 | 341.4 | 387.6495 | -46.2495 | -58.4963
29-03-2026 10:10 | 653 | 50.23 | 230.758 | 234.616 | 462.5 | 39.1027 | 38.6701 | 0.43259 | 232.0205 | 40.8 | 38.1171 | 2.6829 | 0.98356 | 29-03-2026 10:10 | 227.612 | 230.844 | 465.7 | 38.474 | 38.6701 | -0.19608 | 232.0205 | 41.1 | 38.1171 | 2.9829 | 0.986 | 29-03-2026 10:10 | 230.174 | 235.053 | 458 | 39.1755 | 38.6701 | 0.50542 | 232.0205 | 40.3 | 38.1171 | 2.1829 | 0.97924 | 29-03-2026 10:10 | 228.744 | 231.992 | 462.4 | 38.6653 | 38.6701 | -0.0047428 | 232.0205 | 41.5 | 38.1171 | 3.3829 | 0.986 | 29-03-2026 10:10 | 169.814 | 172.016 | 340.4 | 28.6693 | 28.6445 | 0.024832 | 171.867 | 30.6 | 28.2349 | 2.3651 | 0.9872 | 29-03-2026 10:10 | 168.478 | 170.837 | 342.6 | 28.4728 | 28.6445 | -0.17167 | 171.867 | 30.6 | 28.2349 | 2.3651 | 0.98619 | 29-03-2026 10:10 | 168.611 | 170.832 | 341.9 | 28.472 | 28.6445 | -0.1725 | 171.867 | 30.5 | 28.2349 | 2.2651 | 0.987 | 29-03-2026 10:10 | 170.703 | 175.487 | 345.9 | 29.2478 | 28.6445 | 0.60333 | 171.867 | 30.8 | 28.2349 | 2.5651 | 0.97274 | 29-03-2026 10:10 | 160.799 | 162.933 | 327.2 | 27.1555 | 27.2517 | -0.096195 | 163.5102 | 29.1 | 26.862 | 2.238 | 0.9869 | 29-03-2026 10:10 | 297.435 | 296.51 | 0.925 | 1779.06 | 315.3 | 292.2699 | 23.0301 | 17.865
29-03-2026 10:00 | 805 | 50.8 | 287.737 | 292.089 | 421.7 | 48.6815 | 47.5671 | 1.1144 | 285.4024 | 50.1 | 46.8869 | 3.2131 | 0.9851 | 29-03-2026 10:00 | 286.086 | 290.502 | 424.6 | 48.417 | 47.5671 | 0.84994 | 285.4024 | 51 | 46.8869 | 4.1131 | 0.9848 | 29-03-2026 10:00 | 281.396 | 288.215 | 417.7 | 48.0358 | 47.5671 | 0.46877 | 285.4024 | 49.4 | 46.8869 | 2.5131 | 0.97634 | 29-03-2026 10:00 | 286.139 | 290.585 | 420.9 | 48.4308 | 47.5671 | 0.86377 | 285.4024 | 48.4 | 46.8869 | 1.5131 | 0.9847 | 29-03-2026 10:00 | 212.678 | 215.588 | 309.8 | 35.9313 | 35.2349 | 0.69647 | 211.4092 | 35.9 | 34.731 | 1.169 | 0.9865 | 29-03-2026 10:00 | 211.341 | 214.63 | 312 | 35.7717 | 35.2349 | 0.5368 | 211.4092 | 35.8 | 34.731 | 1.069 | 0.98468 | 29-03-2026 10:00 | 209.218 | 215.504 | 311.4 | 35.9173 | 35.2349 | 0.68247 | 211.4092 | 36.1 | 34.731 | 1.369 | 0.97083 | 29-03-2026 10:00 | 209.364 | 219.917 | 315.1 | 36.6528 | 35.2349 | 1.418 | 211.4092 | 36.4 | 34.731 | 1.669 | 0.95201 | 29-03-2026 10:00 | 201.923 | 204.494 | 298.1 | 34.0823 | 33.5216 | 0.56073 | 201.1296 | 34.5 | 33.0422 | 1.4578 | 0.98743 | 29-03-2026 10:00 | 371.9207 | 364.7293 | 7.1914 | 2188.3759 | 377.6 | 359.5137 | 18.0863 | 5.6793
29-03-2026 09:50 | 828 | 50.8 | 293.371 | 297.687 | 371.6 | 49.6145 | 48.9261 | 0.68838 | 293.5567 | 35.1 | 48.2265 | -13.1265 |  | 29-03-2026 09:50 | 290.306 | 294.607 | 373.6 | 49.1012 | 48.9261 | 0.17504 | 293.5567 | 34 | 48.2265 | -14.2265 |  | 29-03-2026 09:50 | 293.43 | 301.957 | 368.3 | 50.3262 | 48.9261 | 1.4 | 293.5567 | 34.3 | 48.2265 | -13.9265 |  | 29-03-2026 09:50 | 298.411 | 302.925 | 372.5 | 50.4875 | 48.9261 | 1.5614 | 293.5567 | 35.1 | 48.2265 | -13.1265 |  | 29-03-2026 09:50 | 221.679 | 224.742 | 273.9 | 37.457 | 36.2416 | 1.2154 | 217.4494 | 26.1 | 35.7233 | -9.6233 |  | 29-03-2026 09:50 | 221.895 | 225.112 | 276.2 | 37.5187 | 36.2416 | 1.2771 | 217.4494 | 26 | 35.7233 | -9.7233 |  | 29-03-2026 09:50 | 221.255 | 224.931 | 275.3 | 37.4885 | 36.2416 | 1.2469 | 217.4494 | 25.8 | 35.7233 | -9.9233 |  | 29-03-2026 09:50 | 222.763 | 229.541 | 278.7 | 38.2568 | 36.2416 | 2.0153 | 217.4494 | 26.2 | 35.7233 | -9.5233 |  | 29-03-2026 09:50 | 208.997 | 212.226 | 263.6 | 35.371 | 34.4794 | 0.89163 | 206.8762 | 24.7 | 33.9863 | -9.2863 |  | 29-03-2026 09:50 | 385.6213 | 375.1502 | 10.4712 | 2250.9009 | 267.3 | 369.7855 | -102.4855 | -118.3213
29-03-2026 09:40 | 466 | 50.8 | 134.973 | 138.437 | 336.5 | 23.0728 | 27.5357 | -4.4629 | 165.2143 | 33.5 | 27.142 | 6.358 |  | 29-03-2026 09:40 | 161.389 | 164.239 | 339.6 | 27.3732 | 27.5357 | -0.16255 | 165.2143 | 34.8 | 27.142 | 7.658 |  | 29-03-2026 09:40 | 162.671 | 168.797 | 334 | 28.1328 | 27.5357 | 0.59712 | 165.2143 | 33.6 | 27.142 | 6.458 |  | 29-03-2026 09:40 | 158.919 | 160.98 | 337.4 | 26.83 | 27.5357 | -0.70572 | 165.2143 | 33.9 | 27.142 | 6.758 |  | 29-03-2026 09:40 | 121.582 | 125.196 | 247.8 | 20.866 | 20.3968 | 0.46917 | 122.381 | 25.1 | 20.1052 | 4.9948 |  | 29-03-2026 09:40 | 116.565 | 118.926 | 250.2 | 19.821 | 20.3968 | -0.57583 | 122.381 | 25.1 | 20.1052 | 4.9948 |  | 29-03-2026 09:40 | 122.48 | 124.826 | 249.5 | 20.8043 | 20.3968 | 0.40751 | 122.381 | 25.6 | 20.1052 | 5.4948 |  | 29-03-2026 09:40 | 107.419 | 111.194 | 252.5 | 18.5323 | 20.3968 | -1.8645 | 122.381 | 25.6 | 20.1052 | 5.4948 |  | 29-03-2026 09:40 | 102.02 | 103.4 | 238.9 | 17.2333 | 19.4051 | -2.1717 | 116.4303 | 24.1 | 19.1276 | 4.9724 |  | 29-03-2026 09:40 | 202.6658 | 211.1352 | -8.4694 | 1266.8114 | 261.3 | 208.116 | 53.184 | 58.6342
29-03-2026 09:30 | 697 | 51.09 | 250.4 | 253.904 | 303 | 42.3173 | 41.1394 | 1.1779 | 246.8367 | 39 | 40.5511 | -1.5511 |  | 29-03-2026 09:30 | 252.576 | 256.188 | 304.8 | 42.698 | 41.1394 | 1.5586 | 246.8367 | 39.5 | 40.5511 | -1.0511 |  | 29-03-2026 09:30 | 246.469 | 251.796 | 300.4 | 41.966 | 41.1394 | 0.82656 | 246.8367 | 38.9 | 40.5511 | -1.6511 |  | 29-03-2026 09:30 | 249.38 | 252.972 | 303.5 | 42.162 | 41.1394 | 1.0226 | 246.8367 | 39.3 | 40.5511 | -1.2511 |  | 29-03-2026 09:30 | 184.045 | 186.45 | 222.7 | 31.075 | 30.4737 | 0.60134 | 182.842 | 29 | 30.0379 | -1.0379 |  | 29-03-2026 09:30 | 185.385 | 187.827 | 225.1 | 31.3045 | 30.4737 | 0.83084 | 182.842 | 29.1 | 30.0379 | -0.93789 |  | 29-03-2026 09:30 | 184.685 | 187.099 | 223.9 | 31.1832 | 30.4737 | 0.7095 | 182.842 | 28.5 | 30.0379 | -1.5379 |  | 29-03-2026 09:30 | 186.662 | 191.672 | 226.9 | 31.9453 | 30.4737 | 1.4717 | 182.842 | 28.9 | 30.0379 | -1.1379 |  | 29-03-2026 09:30 | 176.734 | 179.062 | 214.8 | 29.8437 | 28.9919 | 0.85175 | 173.9515 | 27.3 | 28.5773 | -1.2773 |  | 29-03-2026 09:30 | 324.495 | 315.4443 | 9.0507 | 1892.666 | 299.5 | 310.9335 | -11.4335 | -24.995
29-03-2026 09:20 | 648 | 50.8 | 233.264 | 236.903 | 264 | 39.4838 | 38.29 | 1.1938 | 229.7401 | 36.8 | 37.7425 | -0.94246 |  | 29-03-2026 09:20 | 231.915 | 236.455 | 265.3 | 39.4092 | 38.29 | 1.1192 | 229.7401 | 35.4 | 37.7425 | -2.3425 |  | 29-03-2026 09:20 | 230.602 | 235.601 | 261.5 | 39.2668 | 38.29 | 0.97682 | 229.7401 | 35.5 | 37.7425 | -2.2425 |  | 29-03-2026 09:20 | 232.443 | 235.648 | 264.2 | 39.2747 | 38.29 | 0.98466 | 229.7401 | 35.6 | 37.7425 | -2.1425 |  | 29-03-2026 09:20 | 171.671 | 173.879 | 193.7 | 28.9798 | 28.363 | 0.61686 | 170.1778 | 26.4 | 27.9574 | -1.5574 |  | 29-03-2026 09:20 | 172.415 | 174.615 | 196 | 29.1025 | 28.363 | 0.73953 | 170.1778 | 26.8 | 27.9574 | -1.1574 |  | 29-03-2026 09:20 | 171.96 | 174.277 | 195.4 | 29.0462 | 28.363 | 0.6832 | 170.1778 | 26.8 | 27.9574 | -1.1574 |  | 29-03-2026 09:20 | 173.726 | 178.281 | 198 | 29.7135 | 28.363 | 1.3505 | 170.1778 | 27 | 27.9574 | -0.95738 |  | 29-03-2026 09:20 | 164.51 | 166.626 | 187.5 | 27.771 | 26.9839 | 0.78715 | 161.9031 | 25.6 | 26.598 | -0.99798 |  | 29-03-2026 09:20 | 302.0475 | 293.5958 | 8.4517 | 1761.5746 | 275.9 | 289.3974 | -13.4974 | -26.1475
29-03-2026 09:10 | 537 | 50.51 | 210.661 | 194.828 | 227.2 | 32.4713 | 31.7665 | 0.70486 | 190.5989 | 34.2 | 31.3122 | 2.8878 |  | 29-03-2026 09:10 | 193.182 | 195.687 | 229.9 | 32.6145 | 31.7665 | 0.84802 | 190.5989 | 35.5 | 31.3122 | 4.1878 |  | 29-03-2026 09:10 | 189.182 | 192.676 | 226 | 32.1127 | 31.7665 | 0.34619 | 190.5989 | 33.8 | 31.3122 | 2.4878 |  | 29-03-2026 09:10 | 191.905 | 194.433 | 228.6 | 32.4055 | 31.7665 | 0.63902 | 190.5989 | 34.2 | 31.3122 | 2.8878 |  | 29-03-2026 09:10 | 140.538 | 142.259 | 167.3 | 23.7098 | 23.5307 | 0.17911 | 141.1843 | 25 | 23.1942 | 1.8058 |  | 29-03-2026 09:10 | 138.913 | 140.629 | 169.2 | 23.4382 | 23.5307 | -0.092557 | 141.1843 | 25.2 | 23.1942 | 2.0058 |  | 29-03-2026 09:10 | 140.11 | 141.953 | 168.6 | 23.6588 | 23.5307 | 0.12811 | 141.1843 | 24.8 | 23.1942 | 1.6058 |  | 29-03-2026 09:10 | 140.733 | 144.897 | 171 | 24.1495 | 23.5307 | 0.61878 | 141.1843 | 25.3 | 23.1942 | 2.1058 |  | 29-03-2026 09:10 | 132.659 | 134.311 | 161.9 | 22.3852 | 22.3866 | -0.0014023 | 134.3194 | 24 | 22.0664 | 1.9336 |  | 29-03-2026 09:10 | 246.9455 | 243.5754 | 3.3701 | 1461.4522 | 262 | 240.0922 | 21.9078 | 15.0545
29-03-2026 09:00 | 582 | 50.51 | 206.729 | 209.367 | 193 | 34.8945 | 34.4285 | 0.46603 | 206.5708 | 32.8 | 33.9361 | -1.1361 |  | 29-03-2026 09:00 | 207.365 | 210.03 | 194.4 | 35.005 | 34.4285 | 0.57653 | 206.5708 | 33.9 | 33.9361 | -0.036145 |  | 29-03-2026 09:00 | 206.01 | 210.259 | 192.2 | 35.0432 | 34.4285 | 0.61469 | 206.5708 | 32.5 | 33.9361 | -1.4361 |  | 29-03-2026 09:00 | 207.218 | 209.947 | 194.4 | 34.9912 | 34.4285 | 0.56269 | 206.5708 | 32.9 | 33.9361 | -1.0361 |  | 29-03-2026 09:00 | 153.146 | 155.037 | 142.3 | 25.8395 | 25.5026 | 0.33693 | 153.0154 | 24.2 | 25.1379 | -0.93789 |  | 29-03-2026 09:00 | 152.904 | 155.263 | 144 | 25.8772 | 25.5026 | 0.37459 | 153.0154 | 24.1 | 25.1379 | -1.0379 |  | 29-03-2026 09:00 | 153.77 | 155.669 | 143.8 | 25.9448 | 25.5026 | 0.44226 | 153.0154 | 24.3 | 25.1379 | -0.83789 |  | 29-03-2026 09:00 | 155.141 | 159.256 | 145.7 | 26.5427 | 25.5026 | 1.0401 | 153.0154 | 24.3 | 25.1379 | -0.83789 |  | 29-03-2026 09:00 | 146.547 | 148.342 | 137.9 | 24.7237 | 24.2625 | 0.46113 | 145.5752 | 23 | 23.9156 | -0.91558 |  | 29-03-2026 09:00 | 268.8617 | 263.9867 | 4.875 | 1583.9203 | 252 | 260.2117 | -8.2117 | -16.8617
29-03-2026 08:50 | 536 | 49.94 | 188.924 | 191.315 | 160.2 | 31.8858 | 31.7768 | 0.10905 | 190.6607 | 29.5 | 31.3224 | -1.8224 |  | 29-03-2026 08:50 | 189.821 | 192.263 | 160.5 | 32.0438 | 31.7768 | 0.26705 | 190.6607 | 28.5 | 31.3224 | -2.8224 |  | 29-03-2026 08:50 | 187.129 | 190.523 | 159.7 | 31.7538 | 31.7768 | -0.022946 | 190.6607 | 29.7 | 31.3224 | -1.6224 |  | 29-03-2026 08:50 | 189.055 | 191.448 | 161.5 | 31.908 | 31.7768 | 0.13122 | 190.6607 | 29.9 | 31.3224 | -1.4224 |  | 29-03-2026 08:50 | 138.714 | 140.399 | 118.1 | 23.3998 | 23.5384 | -0.13852 | 141.2301 | 22.3 | 23.2018 | -0.90176 |  | 29-03-2026 08:50 | 140.047 | 141.748 | 119.9 | 23.6247 | 23.5384 | 0.086312 | 141.2301 | 22.5 | 23.2018 | -0.70176 |  | 29-03-2026 08:50 | 139.366 | 141.059 | 119.5 | 23.5098 | 23.5384 | -0.028521 | 141.2301 | 22.4 | 23.2018 | -0.80176 |  | 29-03-2026 08:50 | 141.014 | 144.619 | 121.4 | 24.1032 | 23.5384 | 0.56481 | 141.2301 | 22.7 | 23.2018 | -0.50176 |  | 29-03-2026 08:50 | 133.719 | 135.329 | 114.9 | 22.5548 | 22.3938 | 0.161 | 134.363 | 21.6 | 22.0736 | -0.4736 |  | 29-03-2026 08:50 | 244.7838 | 243.6544 | 1.1295 | 1461.9262 | 229.1 | 240.1701 | -11.0701 | -15.6838
29-03-2026 08:40 | 497 | 48.22 | 173.012 | 175.131 | 130.7 | 29.1885 | 29.659 | -0.4705 | 177.954 | 26.1 | 29.2349 | -3.1349 |  | 29-03-2026 08:40 | 175.636 | 177.841 | 132 | 29.6402 | 29.659 | -0.018837 | 177.954 | 26.8 | 29.2349 | -2.4349 |  | 29-03-2026 08:40 | 172.31 | 175.312 | 130 | 29.2187 | 29.659 | -0.44034 | 177.954 | 26.1 | 29.2349 | -3.1349 |  | 29-03-2026 08:40 | 174.083 | 176.233 | 131.6 | 29.3722 | 29.659 | -0.28684 | 177.954 | 26.4 | 29.2349 | -2.8349 |  | 29-03-2026 08:40 | 127.63 | 129.167 | 95.8 | 21.5278 | 21.9696 | -0.4418 | 131.8178 | 19.1 | 21.6555 | -2.5555 |  | 29-03-2026 08:40 | 128.965 | 130.479 | 97.4 | 21.7465 | 21.9696 | -0.22313 | 131.8178 | 19.3 | 21.6555 | -2.3555 |  | 29-03-2026 08:40 | 128.525 | 130.047 | 97.1 | 21.6745 | 21.9696 | -0.29513 | 131.8178 | 19.2 | 21.6555 | -2.4555 |  | 29-03-2026 08:40 | 130.351 | 133.861 | 98.7 | 22.3102 | 21.9696 | 0.34053 | 131.8178 | 19.7 | 21.6555 | -1.9555 |  | 29-03-2026 08:40 | 123.281 | 124.753 | 93.3 | 20.7922 | 20.9014 | -0.10922 | 125.4083 | 18.6 | 20.6025 | -2.0025 |  | 29-03-2026 08:40 | 225.4707 | 227.4159 | -1.9453 | 1364.4956 | 201.3 | 224.1639 | -22.8639 | -24.1707
29-03-2026 08:30 | 365 | 46.49 | 127.964 | 129.453 | 104.6 | 21.5755 | 21.9253 | -0.34982 | 131.5519 | 24.3 | 21.6118 | 2.6882 |  | 29-03-2026 08:30 | 151.261 | 151.405 | 105.2 | 25.2342 | 21.9253 | 3.3088 | 131.5519 | 24.4 | 21.6118 | 2.7882 |  | 29-03-2026 08:30 | 120.22 | 121.668 | 103.9 | 20.278 | 21.9253 | -1.6473 | 131.5519 | 24 | 21.6118 | 2.3882 |  | 29-03-2026 08:30 | 126.586 | 128.098 | 105.2 | 21.3497 | 21.9253 | -0.57565 | 131.5519 | 24.3 | 21.6118 | 2.6882 |  | 29-03-2026 08:30 | 84.246 | 85.269 | 76.7 | 14.2115 | 16.241 | -2.0295 | 97.4459 | 17.8 | 16.0087 | 1.7913 |  | 29-03-2026 08:30 | 88.494 | 89.533 | 78.1 | 14.9222 | 16.241 | -1.3188 | 97.4459 | 18 | 16.0087 | 1.9913 |  | 29-03-2026 08:30 | 82.701 | 83.705 | 77.9 | 13.9508 | 16.241 | -2.2901 | 97.4459 | 18.2 | 16.0087 | 2.1913 |  | 29-03-2026 08:30 | 95.173 | 96.351 | 79 | 16.0585 | 16.241 | -0.18248 | 97.4459 | 18.2 | 16.0087 | 2.1913 |  | 29-03-2026 08:30 | 92.727 | 95.636 | 74.7 | 15.9393 | 15.4513 | 0.48806 | 92.7077 | 17.2 | 15.2303 | 1.9697 |  | 29-03-2026 08:30 | 163.5197 | 168.1165 | -4.5968 | 1008.6988 | 186.4 | 165.7124 | 20.6876 | 22.8803
29-03-2026 08:20 | 401 | 44.2 | 134.804 | 136.345 | 80.3 | 22.7242 | 24.2966 | -1.5724 | 145.7795 | 20.2 | 23.9491 | -3.7491 |  | 29-03-2026 08:20 | 137.92 | 140.407 | 80.8 | 23.4012 | 24.2966 | -0.89542 | 145.7795 | 21.7 | 23.9491 | -2.2491 |  | 29-03-2026 08:20 | 136.902 | 138.885 | 79.9 | 23.1475 | 24.2966 | -1.1491 | 145.7795 | 20.9 | 23.9491 | -3.0491 |  | 29-03-2026 08:20 | 137.779 | 139.396 | 80.9 | 23.2327 | 24.2966 | -1.0639 | 145.7795 | 21 | 23.9491 | -2.9491 |  | 29-03-2026 08:20 | 101.465 | 102.614 | 58.9 | 17.1023 | 17.9975 | -0.89513 | 107.9848 | 15.4 | 17.7401 | -2.3401 |  | 29-03-2026 08:20 | 102.63 | 103.771 | 60.1 | 17.2952 | 17.9975 | -0.7023 | 107.9848 | 15.7 | 17.7401 | -2.0401 |  | 29-03-2026 08:20 | 101.94 | 103.095 | 59.7 | 17.1825 | 17.9975 | -0.81497 | 107.9848 | 15.4 | 17.7401 | -2.3401 |  | 29-03-2026 08:20 | 103.398 | 106.027 | 60.8 | 17.6712 | 17.9975 | -0.3263 | 107.9848 | 15.6 | 17.7401 | -2.1401 |  | 29-03-2026 08:20 | 98.162 | 99.274 | 57.5 | 16.5457 | 17.1224 | -0.5767 | 102.7342 | 14.8 | 16.8775 | -2.0775 |  | 29-03-2026 08:20 | 178.3023 | 186.2986 | -7.9962 | 1117.7914 | 160.7 | 183.6345 | -22.9345 | -17.6023
29-03-2026 08:10 | 354 | 39.89 | 119.239 | 120.565 | 60.1 | 20.0942 | 21.7957 | -1.7016 | 130.7743 | 16.2 | 21.484 | -5.284 |  | 29-03-2026 08:10 | 119.012 | 120.372 | 59.1 | 20.062 | 21.7957 | -1.7337 | 130.7743 | 14.9 | 21.484 | -6.584 |  | 29-03-2026 08:10 | 118.098 | 119.81 | 59 | 19.9683 | 21.7957 | -1.8274 | 130.7743 | 15.5 | 21.484 | -5.984 |  | 29-03-2026 08:10 | 119.539 | 120.917 | 59.9 | 20.1528 | 21.7957 | -1.6429 | 130.7743 | 15.9 | 21.484 | -5.584 |  | 29-03-2026 08:10 | 87.183 | 88.188 | 43.5 | 14.698 | 16.145 | -1.447 | 96.8699 | 11.6 | 15.9141 | -4.3141 |  | 29-03-2026 08:10 | 88.877 | 89.908 | 44.4 | 14.9847 | 16.145 | -1.1603 | 96.8699 | 11.9 | 15.9141 | -4.0141 |  | 29-03-2026 08:10 | 88.513 | 89.527 | 44.3 | 14.9212 | 16.145 | -1.2238 | 96.8699 | 11.8 | 15.9141 | -4.1141 |  | 29-03-2026 08:10 | 89.925 | 92.251 | 45.2 | 15.3752 | 16.145 | -0.76981 | 96.8699 | 12.1 | 15.9141 | -3.8141 |  | 29-03-2026 08:10 | 85.33 | 86.313 | 42.7 | 14.3855 | 15.3599 | -0.97445 | 92.1597 | 11.5 | 15.1403 | -3.6403 |  | 29-03-2026 08:10 | 154.6418 | 167.1227 | -12.4809 | 1002.7363 | 121.4 | 164.7329 | -43.3329 | -33.2418
29-03-2026 08:00 | 292 | 38.75 | 95.085 | 96.123 | 43.9 | 16.0205 | 18.0541 | -2.0336 | 108.3244 | 13 | 17.7959 | -4.7959 |  | 29-03-2026 08:00 | 95.721 | 96.694 | 44.2 | 16.1157 | 18.0541 | -1.9384 | 108.3244 | 13.8 | 17.7959 | -3.9959 |  | 29-03-2026 08:00 | 95.262 | 96.399 | 43.5 | 16.0665 | 18.0541 | -1.9876 | 108.3244 | 13.2 | 17.7959 | -4.5959 |  | 29-03-2026 08:00 | 95.384 | 96.455 | 44 | 16.0758 | 18.0541 | -1.9782 | 108.3244 | 13.3 | 17.7959 | -4.4959 |  | 29-03-2026 08:00 | 69.775 | 70.622 | 31.9 | 11.7703 | 13.3734 | -1.603 | 80.2403 | 9.7 | 13.1821 | -3.4821 |  | 29-03-2026 08:00 | 71.169 | 72.012 | 32.5 | 12.002 | 13.3734 | -1.3714 | 80.2403 | 9.8 | 13.1821 | -3.3821 |  | 29-03-2026 08:00 | 71.19 | 71.937 | 32.5 | 11.9895 | 13.3734 | -1.3839 | 80.2403 | 9.8 | 13.1821 | -3.3821 |  | 29-03-2026 08:00 | 72.482 | 74.543 | 33.1 | 12.4238 | 13.3734 | -0.94955 | 80.2403 | 10 | 13.1821 | -3.1821 |  | 29-03-2026 08:00 | 68.648 | 69.496 | 31.2 | 11.5827 | 12.7231 | -1.1405 | 76.3387 | 9.5 | 12.5412 | -3.0412 |  | 29-03-2026 08:00 | 124.0468 | 138.4329 | -14.3861 | 830.5975 | 102.1 | 136.4533 | -34.3533 | -21.9468
29-03-2026 07:50 | 234 | 37.02 | 70.967 | 77.263 | 30.9 | 12.8772 | 14.56 | -1.6829 | 87.3601 | 11.4 | 14.3518 | -2.9518 |  | 29-03-2026 07:50 | 67.644 | 68.373 | 30.4 | 11.3955 | 14.56 | -3.1645 | 87.3601 | 10.7 | 14.3518 | -3.6518 |  | 29-03-2026 07:50 | 73.44 | 74.317 | 30.3 | 12.3862 | 14.56 | -2.1739 | 87.3601 | 10.9 | 14.3518 | -3.4518 |  | 29-03-2026 07:50 | 73.894 | 74.792 | 30.7 | 12.4653 | 14.56 | -2.0947 | 87.3601 | 11 | 14.3518 | -3.3518 |  | 29-03-2026 07:50 | 54.89 | 55.636 | 22.2 | 9.2727 | 10.7852 | -1.5125 | 64.7112 | 8.1 | 10.631 | -2.531 |  | 29-03-2026 07:50 | 55.837 | 56.567 | 22.7 | 9.4278 | 10.7852 | -1.3574 | 64.7112 | 8.4 | 10.631 | -2.231 |  | 29-03-2026 07:50 | 56.546 | 57.291 | 22.7 | 9.5485 | 10.7852 | -1.2367 | 64.7112 | 8.4 | 10.631 | -2.231 |  | 29-03-2026 07:50 | 57.582 | 59.247 | 23.1 | 9.8745 | 10.7852 | -0.9107 | 64.7112 | 8.5 | 10.631 | -2.131 |  | 29-03-2026 07:50 | 54.347 | 55.091 | 21.7 | 9.1818 | 10.2608 | -1.0789 | 61.5647 | 8 | 10.1141 | -2.1141 |  | 29-03-2026 07:50 | 96.4295 | 111.6416 | -15.2121 | 669.8499 | 85.4 | 110.0452 | -24.6452 | -11.0295
29-03-2026 07:40 | 197 | 34.44 | 58.803 | 59.559 | 19.5 | 9.9265 | 12.3733 | -2.4468 | 74.2401 | 6.9 | 12.1964 | -5.2964 |  | 29-03-2026 07:40 | 61.933 | 62.798 | 19.7 | 10.4663 | 12.3733 | -1.907 | 74.2401 | 7.2 | 12.1964 | -4.9964 |  | 29-03-2026 07:40 | 60.641 | 61.396 | 19.4 | 10.2327 | 12.3733 | -2.1407 | 74.2401 | 7 | 12.1964 | -5.1964 |  | 29-03-2026 07:40 | 61.884 | 62.661 | 19.7 | 10.4435 | 12.3733 | -1.9298 | 74.2401 | 7.2 | 12.1964 | -4.9964 |  | 29-03-2026 07:40 | 44.536 | 45.205 | 14.1 | 7.5342 | 9.1654 | -1.6313 | 54.9926 | 5.1 | 9.0344 | -3.9344 |  | 29-03-2026 07:40 | 45.809 | 46.469 | 14.3 | 7.7448 | 9.1654 | -1.4206 | 54.9926 | 5.2 | 9.0344 | -3.8344 |  | 29-03-2026 07:40 | 45.611 | 46.287 | 14.3 | 7.7145 | 9.1654 | -1.4509 | 54.9926 | 5.2 | 9.0344 | -3.8344 |  | 29-03-2026 07:40 | 46.555 | 47.781 | 14.6 | 7.9635 | 9.1654 | -1.2019 | 54.9926 | 5.3 | 9.0344 | -3.7344 |  | 29-03-2026 07:40 | 44.238 | 44.907 | 13.7 | 7.4845 | 8.7198 | -1.2353 | 52.3187 | 5 | 8.5951 | -3.5951 |  | 29-03-2026 07:40 | 79.5105 | 94.8749 | -15.3644 | 569.2494 | 54.1 | 93.5182 | -39.4182 | -25.4105
29-03-2026 07:30 | 112 | 32.43 | 34.533 | 35.596 | 12.6 | 5.9327 | 7.0858 | -1.1531 | 42.5146 | 3.9 | 6.9844 | -3.0844 |  | 29-03-2026 07:30 | 33.944 | 34.528 | 12.5 | 5.7547 | 7.0858 | -1.3311 | 42.5146 | 3.7 | 6.9844 | -3.2844 |  | 29-03-2026 07:30 | 33.899 | 34.478 | 12.4 | 5.7463 | 7.0858 | -1.3394 | 42.5146 | 3.8 | 6.9844 | -3.1844 |  | 29-03-2026 07:30 | 34.458 | 35.047 | 12.5 | 5.8412 | 7.0858 | -1.2446 | 42.5146 | 3.9 | 6.9844 | -3.0844 |  | 29-03-2026 07:30 | 24.972 | 25.487 | 9 | 4.2478 | 5.2487 | -1.0009 | 31.4923 | 2.8 | 5.1737 | -2.3737 |  | 29-03-2026 07:30 | 25.509 | 26.008 | 9.1 | 4.3347 | 5.2487 | -0.91405 | 31.4923 | 2.8 | 5.1737 | -2.3737 |  | 29-03-2026 07:30 | 25.501 | 26.013 | 9.1 | 4.3355 | 5.2487 | -0.91322 | 31.4923 | 2.8 | 5.1737 | -2.3737 |  | 29-03-2026 07:30 | 25.956 | 26.812 | 9.3 | 4.4687 | 5.2487 | -0.78005 | 31.4923 | 2.9 | 5.1737 | -2.2737 |  | 29-03-2026 07:30 | 24.522 | 25.02 | 8.7 | 4.17 | 4.9935 | -0.82351 | 29.961 | 2.8 | 4.9221 | -2.1221 |  | 29-03-2026 07:30 | 44.8315 | 54.3315 | -9.5 | 325.9887 | 29.4 | 53.5545 | -24.1545 | -15.4315
29-03-2026 07:20 | 49 | 31.86 | 16.459 | 16.965 | 8.7 | 2.8275 | 3.1064 | -0.27887 | 18.6382 | 2.7 | 3.062 | -0.36195 |  | 29-03-2026 07:20 | 16.704 | 17.408 | 8.8 | 2.9013 | 3.1064 | -0.20504 | 18.6382 | 2.8 | 3.062 | -0.26195 |  | 29-03-2026 07:20 | 16.397 | 16.833 | 8.6 | 2.8055 | 3.1064 | -0.30087 | 18.6382 | 2.7 | 3.062 | -0.36195 |  | 29-03-2026 07:20 | 16.504 | 17.124 | 8.6 | 2.854 | 3.1064 | -0.25237 | 18.6382 | 2.7 | 3.062 | -0.36195 |  | 29-03-2026 07:20 | 11.922 | 12.39 | 6.2 | 2.065 | 2.301 | -0.23602 | 13.8061 | 2 | 2.2681 | -0.26811 |  | 29-03-2026 07:20 | 12.056 | 12.448 | 6.3 | 2.0747 | 2.301 | -0.22635 | 13.8061 | 2 | 2.2681 | -0.26811 |  | 29-03-2026 07:20 | 12.014 | 12.412 | 6.3 | 2.0687 | 2.301 | -0.23235 | 13.8061 | 2 | 2.2681 | -0.26811 |  | 29-03-2026 07:20 | 12.227 | 12.885 | 6.4 | 2.1475 | 2.301 | -0.15352 | 13.8061 | 2 | 2.2681 | -0.26811 |  | 29-03-2026 07:20 | 11.481 | 11.873 | 5.9 | 1.9788 | 2.1891 | -0.2103 | 13.1348 | 1.8 | 2.1578 | -0.35783 |  | 29-03-2026 07:20 | 21.723 | 23.8187 | -2.0957 | 142.9122 | 20.7 | 23.4781 | -2.7781 | -1.023
29-03-2026 07:10 | 47 | 31.86 | 16.988 | 17.423 | 6 | 2.9038 | 2.9796 | -0.07575 | 17.8775 | 2.9 | 2.937 | -0.036975 |  | 29-03-2026 07:10 | 17.055 | 17.588 | 6 | 2.9313 | 2.9796 | -0.04825 | 17.8775 | 3 | 2.937 | 0.063025 |  | 29-03-2026 07:10 | 16.828 | 17.263 | 5.9 | 2.8772 | 2.9796 | -0.10242 | 17.8775 | 2.8 | 2.937 | -0.13698 |  | 29-03-2026 07:10 | 16.948 | 17.723 | 5.9 | 2.9538 | 2.9796 | -0.02575 | 17.8775 | 2.8 | 2.937 | -0.13698 |  | 29-03-2026 07:10 | 12.228 | 12.701 | 4.2 | 2.1168 | 2.2071 | -0.090265 | 13.2426 | 2 | 2.1755 | -0.17554 |  | 29-03-2026 07:10 | 12.393 | 12.788 | 4.3 | 2.1313 | 2.2071 | -0.075765 | 13.2426 | 2.1 | 2.1755 | -0.075537 |  | 29-03-2026 07:10 | 12.367 | 12.768 | 4.3 | 2.128 | 2.2071 | -0.079099 | 13.2426 | 2.1 | 2.1755 | -0.075537 |  | 29-03-2026 07:10 | 12.539 | 12.937 | 4.4 | 2.1562 | 2.2071 | -0.050932 | 13.2426 | 2.1 | 2.1755 | -0.075537 |  | 29-03-2026 07:10 | 11.754 | 12.149 | 4.1 | 2.0248 | 2.0998 | -0.074948 | 12.5987 | 2 | 2.0698 | -0.069754 |  | 29-03-2026 07:10 | 22.2233 | 22.8465 | -0.62317 | 137.079 | 21.8 | 22.5198 | -0.7198 | -0.42333
29-03-2026 07:00 | 43 | 31 | 16.031 | 16.449 | 3.1 | 2.7415 | 2.7344 | 0.0070913 | 16.4065 | 3.1 | 2.6953 | 0.40469 |  | 29-03-2026 07:00 | 15.711 | 16.585 | 3 | 2.7642 | 2.7344 | 0.029758 | 16.4065 | 3 | 2.6953 | 0.30469 |  | 29-03-2026 07:00 | 15.85 | 16.266 | 3.1 | 2.711 | 2.7344 | -0.023409 | 16.4065 | 3.1 | 2.6953 | 0.40469 |  | 29-03-2026 07:00 | 15.792 | 16.526 | 3.1 | 2.7543 | 2.7344 | 0.019925 | 16.4065 | 3.1 | 2.6953 | 0.40469 |  | 29-03-2026 07:00 | 11.509 | 12.189 | 2.2 | 2.0315 | 2.0255 | 0.0060121 | 12.1529 | 2.2 | 1.9965 | 0.20348 |  | 29-03-2026 07:00 | 11.694 | 12.082 | 2.2 | 2.0137 | 2.0255 | -0.011821 | 12.1529 | 2.2 | 1.9965 | 0.20348 |  | 29-03-2026 07:00 | 11.712 | 12.076 | 2.2 | 2.0127 | 2.0255 | -0.012821 | 12.1529 | 2.2 | 1.9965 | 0.20348 |  | 29-03-2026 07:00 | 11.909 | 12.54 | 2.3 | 2.09 | 2.0255 | 0.064512 | 12.1529 | 2.3 | 1.9965 | 0.30348 |  | 29-03-2026 07:00 | 11.015 | 11.39 | 2.1 | 1.8983 | 1.927 | -0.028668 | 11.562 | 2.1 | 1.8994 | 0.20056 |  | 29-03-2026 07:00 | 21.0172 | 20.9666 | 0.05058 | 125.7995 | 23.3 | 20.6668 | 2.6332 | 2.2828
[110 empty] | Total: - | 19074.169 | 19567.7725 | -493.6035 |  | 18842.7 | 19287.9533 | -445.2533 | -231.469
Sum:- | 43048 |  | 14727.863 |  | 96299.4 |  |  |  |  | 2455.8 | 2515.4855 | -59.6855 | 0.99148 |  | 14691.641 |  | 94268.3 |  |  |  |  | 2468 | 2515.4855 | -47.4855 | 0.98392 |  | 14604.412 |  | 95710.5 |  |  |  |  | 2442.1 | 2515.4855 | -73.3855 | 0.97334 |  | 14629.278 |  | 96096.4 |  |  |  |  | 2449.5 | 2515.4855 | -65.9855 | 0.98379 |  | 10959.612 |  | 72000.4 |  |  |  |  | 1839.1 | 1863.3226 | -24.2226 | 0.98387 |  | 10829.537 |  | 71422.8 |  |  |  |  | 1818.5 | 1863.3226 | -44.8226 | 0.98139 |  | 10845.22 |  | 71532.2 |  |  |  |  | 1822.5 | 1863.3226 | -40.8226 | 0.98219 |  | 10872.749 |  | 70199.1 |  |  |  |  | 1825.1 | 1863.3226 | -38.2226 | 0.97141 |  | 10265.097 |  | 64542.2 |  |  |  |  | 1722.1 | 1772.7207 | -50.6207 | 0.98468 | [8 empty] | -1.214%

## 30 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
30-03-2026 19:00 | 2 | 44.77 | 0 | 0 | 1964 | 0 | 0.12092 | -0.12092 | 0.72552 | 0 | 0.11919 | -0.11919 |  | 30-03-2026 19:00 | 0 | 0 | 1978.5 | 0 | 0.12092 | -0.12092 | 0.72552 | 0 | 0.11919 | -0.11919 |  | 30-03-2026 19:00 | 0 | 0 | 1947.6 | 0 | 0.12092 | -0.12092 | 0.72552 | 0 | 0.11919 | -0.11919 | [5 empty] | 0 | 0.12092 | -0.12092 | 0.72552 | 0 | 0.11919 | -0.11919 |  | 30-03-2026 19:00 | 0 | 0 | 1468.4 | 0 | 0.089571 | -0.089571 | 0.53743 | 0 | 0.08829 | -0.08829 | [5 empty] | 0 | 0.089571 | -0.089571 | 0.53743 | 0 | 0.08829 | -0.08829 |  | 30-03-2026 19:00 | 0 | 0 | 1456.9 | 0 | 0.089571 | -0.089571 | 0.53743 | 0 | 0.08829 | -0.08829 |  | 30-03-2026 19:00 | 0 | 0 | 1465.6 | 0 | 0.089571 | -0.089571 | 0.53743 | 0 | 0.08829 | -0.08829 |  | 30-03-2026 19:00 | 0 | 0 | 1387.5 | 0 | 0.085216 | -0.085216 | 0.51129 | 0 | 0.083997 | -0.083997 |  | 30-03-2026 19:00 | 0 | 0.92718 | -0.92718 | 5.5631 | 0 | 0.91392 | -0.91392 | 0 | 1 | 98.49%
30-03-2026 18:50 | 2 | 45.06 | 0 | 0 | 1964 | 0 | 0.12079 | -0.12079 | 0.72473 | 0 | 0.11906 | -0.11906 |  | 30-03-2026 18:50 | 0 | 0 | 1978.5 | 0 | 0.12079 | -0.12079 | 0.72473 | 0 | 0.11906 | -0.11906 |  | 30-03-2026 18:50 | 0 | 0 | 1947.6 | 0 | 0.12079 | -0.12079 | 0.72473 | 0 | 0.11906 | -0.11906 | [5 empty] | 0 | 0.12079 | -0.12079 | 0.72473 | 0 | 0.11906 | -0.11906 | [5 empty] | 0 | 0.089473 | -0.089473 | 0.53684 | 0 | 0.088194 | -0.088194 |  | 30-03-2026 18:50 | 0 | 0 | 1452.7 | 0 | 0.089473 | -0.089473 | 0.53684 | 0 | 0.088194 | -0.088194 |  | 30-03-2026 18:50 | 0 | 0 | 1456.9 | 0 | 0.089473 | -0.089473 | 0.53684 | 0 | 0.088194 | -0.088194 |  | 30-03-2026 18:50 | 0 | 0 | 1465.6 | 0 | 0.089473 | -0.089473 | 0.53684 | 0 | 0.088194 | -0.088194 |  | 30-03-2026 18:50 | 0 | 0 | 1387.5 | 0 | 0.085123 | -0.085123 | 0.51074 | 0 | 0.083905 | -0.083905 |  | 30-03-2026 18:50 | 0 | 0.92617 | -0.92617 | 5.557 | 0 | 0.91293 | -0.91293 | 0 | 2 | 97.27%
30-03-2026 18:40 | 6 | 44.77 | 0 | 0 | 1964 | 0 | 0.36276 | -0.36276 | 2.1766 | 0 | 0.35757 | -0.35757 |  | 30-03-2026 18:40 | 0 | 0 | 1978.5 | 0 | 0.36276 | -0.36276 | 2.1766 | 0 | 0.35757 | -0.35757 |  | 30-03-2026 18:40 | 0 | 0 | 1947.6 | 0 | 0.36276 | -0.36276 | 2.1766 | 0 | 0.35757 | -0.35757 | [5 empty] | 0 | 0.36276 | -0.36276 | 2.1766 | 0 | 0.35757 | -0.35757 | [5 empty] | 0 | 0.26871 | -0.26871 | 1.6123 | 0 | 0.26487 | -0.26487 |  | 30-03-2026 18:40 | 0 | 0 | 1452.7 | 0 | 0.26871 | -0.26871 | 1.6123 | 0 | 0.26487 | -0.26487 |  | 30-03-2026 18:40 | 0 | 0 | 1456.9 | 0 | 0.26871 | -0.26871 | 1.6123 | 0 | 0.26487 | -0.26487 |  | 30-03-2026 18:40 | 0 | 0 | 1465.6 | 0 | 0.26871 | -0.26871 | 1.6123 | 0 | 0.26487 | -0.26487 |  | 30-03-2026 18:40 | 0 | 0 | 1387.5 | 0 | 0.25565 | -0.25565 | 1.5339 | 0 | 0.25199 | -0.25199 |  | 30-03-2026 18:40 | 0 | 2.7815 | -2.7815 | 16.6893 | 0 | 2.7418 | -2.7418 | 0 | 3 | 97.34%
30-03-2026 18:30 | 13 | 45.06 | 0 | 0 | 1964 | 0 | 0.78513 | -0.78513 | 4.7108 | 1 | 0.7739 | 0.2261 |  | 30-03-2026 18:30 | 0 | 0 | 1978.5 | 0 | 0.78513 | -0.78513 | 4.7108 | 1.1 | 0.7739 | 0.3261 |  | 30-03-2026 18:30 | 0 | 0 | 1947.6 | 0 | 0.78513 | -0.78513 | 4.7108 | 1.1 | 0.7739 | 0.3261 |  | 30-03-2026 18:30 | 0 | 0 | 1961.9 | 0 | 0.78513 | -0.78513 | 4.7108 | 1 | 0.7739 | 0.2261 |  | 30-03-2026 18:30 | 0 | 0 | 1468.4 | 0 | 0.58158 | -0.58158 | 3.4895 | 0.7 | 0.57326 | 0.12674 |  | 30-03-2026 18:30 | 0 | 0 | 1452.7 | 0 | 0.58158 | -0.58158 | 3.4895 | 0.8 | 0.57326 | 0.22674 |  | 30-03-2026 18:30 | 0 | 0 | 1456.9 | 0 | 0.58158 | -0.58158 | 3.4895 | 0.7 | 0.57326 | 0.12674 |  | 30-03-2026 18:30 | 0 | 0 | 1465.6 | 0 | 0.58158 | -0.58158 | 3.4895 | 0.7 | 0.57326 | 0.12674 |  | 30-03-2026 18:30 | 0 | 0 | 1387.5 | 0 | 0.5533 | -0.5533 | 3.3198 | 0.7 | 0.54539 | 0.15461 |  | 30-03-2026 18:30 | 0 | 6.0201 | -6.0201 | 36.1207 | 7.8 | 5.934 | 1.866 | 7.8 | 4 | 98.33%
30-03-2026 18:20 | 24 | 45.35 | 8.849 | 9.213 | 1963 | 1.5355 | 1.4479 | 0.087615 | 8.6873 | 1.9 | 1.4272 | 0.47282 |  | 30-03-2026 18:20 | 9.23 | 9.605 | 1977.4 | 1.6008 | 1.4479 | 0.15295 | 8.6873 | 2 | 1.4272 | 0.57282 |  | 30-03-2026 18:20 | 8.816 | 9.177 | 1946.5 | 1.5295 | 1.4479 | 0.081615 | 8.6873 | 1.9 | 1.4272 | 0.47282 |  | 30-03-2026 18:20 | 8.961 | 9.431 | 1960.9 | 1.5718 | 1.4479 | 0.12395 | 8.6873 | 2 | 1.4272 | 0.57282 |  | 30-03-2026 18:20 | 6.388 | 6.716 | 1467.7 | 1.1193 | 1.0725 | 0.046826 | 6.435 | 1.4 | 1.0572 | 0.34283 |  | 30-03-2026 18:20 | 6.444 | 6.738 | 1451.9 | 1.123 | 1.0725 | 0.050493 | 6.435 | 1.4 | 1.0572 | 0.34283 |  | 30-03-2026 18:20 | 6.428 | 6.725 | 1456.2 | 1.1208 | 1.0725 | 0.048326 | 6.435 | 1.4 | 1.0572 | 0.34283 |  | 30-03-2026 18:20 | 6.506 | 7.022 | 1464.9 | 1.1703 | 1.0725 | 0.097826 | 6.435 | 1.5 | 1.0572 | 0.44283 |  | 30-03-2026 18:20 | 6.134 | 6.417 | 1386.8 | 1.0695 | 1.0204 | 0.049142 | 6.1221 | 1.3 | 1.0058 | 0.29423 |  | 30-03-2026 18:20 | 11.8407 | 11.1019 | 0.73874 | 66.6116 | 14.8 | 10.9432 | 3.8568 | 2.9593 | 5 | 98.43%
30-03-2026 18:10 | 41 | 45.92 | 14.766 | 15.212 | 1961.1 | 2.5353 | 2.4682 | 0.067176 | 14.8089 | 2.7 | 2.4329 | 0.26714 |  | 30-03-2026 18:10 | 15.193 | 15.654 | 1975.4 | 2.609 | 2.4682 | 0.14084 | 14.8089 | 2.6 | 2.4329 | 0.16714 |  | 30-03-2026 18:10 | 14.588 | 15.039 | 1944.6 | 2.5065 | 2.4682 | 0.038343 | 14.8089 | 2.5 | 2.4329 | 0.067138 |  | 30-03-2026 18:10 | 14.862 | 15.343 | 1958.9 | 2.5572 | 2.4682 | 0.08901 | 14.8089 | 2.6 | 2.4329 | 0.16714 |  | 30-03-2026 18:10 | 10.765 | 11.165 | 1466.3 | 1.8608 | 1.8283 | 0.032569 | 10.9696 | 1.9 | 1.8021 | 0.09788 |  | 30-03-2026 18:10 | 10.711 | 11.106 | 1450.5 | 1.851 | 1.8283 | 0.022736 | 10.9696 | 1.8 | 1.8021 | -0.0021203 |  | 30-03-2026 18:10 | 10.72 | 11.118 | 1454.8 | 1.853 | 1.8283 | 0.024736 | 10.9696 | 1.9 | 1.8021 | 0.09788 |  | 30-03-2026 18:10 | 10.836 | 11.301 | 1463.4 | 1.8835 | 1.8283 | 0.055236 | 10.9696 | 1.9 | 1.8021 | 0.09788 |  | 30-03-2026 18:10 | 10.206 | 10.588 | 1385.5 | 1.7647 | 1.7394 | 0.025299 | 10.4362 | 1.8 | 1.7145 | 0.085506 |  | 30-03-2026 18:10 | 19.421 | 18.9251 | 0.49595 | 113.5503 | 19.7 | 18.6544 | 1.0456 | 0.279 | 6 | 98.17%
30-03-2026 18:00 | 47 | 46.21 | 16.413 | 16.862 | 1958.4 | 2.8103 | 2.8263 | -0.015919 | 16.9575 | 3.2 | 2.7858 | 0.41416 |  | 30-03-2026 18:00 | 16.802 | 17.405 | 1972.8 | 2.9008 | 2.8263 | 0.074581 | 16.9575 | 3.3 | 2.7858 | 0.51416 |  | 30-03-2026 18:00 | 16.24 | 16.692 | 1942.1 | 2.782 | 2.8263 | -0.044252 | 16.9575 | 3.2 | 2.7858 | 0.41416 |  | 30-03-2026 18:00 | 16.516 | 16.974 | 1956.3 | 2.829 | 2.8263 | 0.002748 | 16.9575 | 3.2 | 2.7858 | 0.41416 |  | 30-03-2026 18:00 | 12.022 | 12.446 | 1464.4 | 2.0743 | 2.0935 | -0.019187 | 12.5611 | 2.4 | 2.0636 | 0.33642 |  | 30-03-2026 18:00 | 11.89 | 12.31 | 1448.7 | 2.0517 | 2.0935 | -0.041853 | 12.5611 | 2.4 | 2.0636 | 0.33642 |  | 30-03-2026 18:00 | 11.912 | 12.333 | 1452.9 | 2.0555 | 2.0935 | -0.03802 | 12.5611 | 2.3 | 2.0636 | 0.23642 |  | 30-03-2026 18:00 | 11.999 | 12.714 | 1461.5 | 2.119 | 2.0935 | 0.02548 | 12.5611 | 2.3 | 2.0636 | 0.23642 |  | 30-03-2026 18:00 | 11.338 | 11.746 | 1383.7 | 1.9577 | 1.9917 | -0.034058 | 11.9504 | 2.2 | 1.9632 | 0.23676 |  | 30-03-2026 18:00 | 21.5803 | 21.6708 | -0.09048 | 130.0249 | 24.5 | 21.3609 | 3.1391 | 2.9197 | 7 | 98.12%
30-03-2026 17:50 | 62 | 47.07 | 21.539 | 22.071 | 1955.2 | 3.6785 | 3.7161 | -0.037625 | 22.2968 | 3.3 | 3.663 | -0.36298 |  | 30-03-2026 17:50 | 21.748 | 22.418 | 1969.5 | 3.7363 | 3.7161 | 0.020208 | 22.2968 | 3.4 | 3.663 | -0.26298 |  | 30-03-2026 17:50 | 21.509 | 22.035 | 1938.9 | 3.6725 | 3.7161 | -0.043625 | 22.2968 | 3.4 | 3.663 | -0.26298 |  | 30-03-2026 17:50 | 21.664 | 22.201 | 1953.1 | 3.7002 | 3.7161 | -0.015959 | 22.2968 | 3.4 | 3.663 | -0.26298 |  | 30-03-2026 17:50 | 15.881 | 16.317 | 1462 | 2.7195 | 2.7527 | -0.033186 | 16.5161 | 2.5 | 2.7133 | -0.21332 |  | 30-03-2026 17:50 | 15.659 | 16.082 | 1446.3 | 2.6803 | 2.7527 | -0.072352 | 16.5161 | 2.4 | 2.7133 | -0.31332 |  | 30-03-2026 17:50 | 15.688 | 16.123 | 1450.6 | 2.6872 | 2.7527 | -0.065519 | 16.5161 | 2.5 | 2.7133 | -0.21332 |  | 30-03-2026 17:50 | 15.755 | 16.378 | 1459.2 | 2.7297 | 2.7527 | -0.023019 | 16.5161 | 2.5 | 2.7133 | -0.21332 |  | 30-03-2026 17:50 | 14.893 | 15.335 | 1381.5 | 2.5558 | 2.6188 | -0.063006 | 15.713 | 2.4 | 2.5814 | -0.18139 |  | 30-03-2026 17:50 | 28.16 | 28.4941 | -0.33408 | 170.9645 | 25.8 | 28.0866 | -2.2866 | -2.36 | 8 | 97.07%
30-03-2026 17:40 | 58 | 48.5 | 19.486 | 19.986 | 1951.9 | 3.331 | 3.4575 | -0.12652 | 20.7451 | 4.5 | 3.4081 | 1.0919 |  | 30-03-2026 17:40 | 19.892 | 20.423 | 1966.1 | 3.4038 | 3.4575 | -0.053686 | 20.7451 | 4.3 | 3.4081 | 0.89192 |  | 30-03-2026 17:40 | 19.364 | 19.867 | 1935.5 | 3.3112 | 3.4575 | -0.14635 | 20.7451 | 4.3 | 3.4081 | 0.89192 |  | 30-03-2026 17:40 | 19.644 | 20.154 | 1949.7 | 3.359 | 3.4575 | -0.09852 | 20.7451 | 4.3 | 3.4081 | 0.89192 |  | 30-03-2026 17:40 | 14.426 | 14.872 | 1459.5 | 2.4787 | 2.5611 | -0.082459 | 15.3668 | 3.2 | 2.5245 | 0.6755 |  | 30-03-2026 17:40 | 14.202 | 14.613 | 1443.9 | 2.4355 | 2.5611 | -0.12563 | 15.3668 | 3.2 | 2.5245 | 0.6755 |  | 30-03-2026 17:40 | 14.204 | 14.646 | 1448.1 | 2.441 | 2.5611 | -0.12013 | 15.3668 | 3.2 | 2.5245 | 0.6755 |  | 30-03-2026 17:40 | 14.286 | 14.981 | 1456.7 | 2.4968 | 2.5611 | -0.064292 | 15.3668 | 3.2 | 2.5245 | 0.6755 |  | 30-03-2026 17:40 | 13.487 | 13.927 | 1379.1 | 2.3212 | 2.4366 | -0.11543 | 14.6196 | 2.9 | 2.4018 | 0.49825 |  | 30-03-2026 17:40 | 25.5782 | 26.5112 | -0.93301 | 159.0671 | 33.1 | 26.1321 | 6.9679 | 7.5218 | 9 | 98.32%
30-03-2026 17:30 | 95 | 49.36 | 26.511 | 27.088 | 1947.4 | 4.5147 | 5.6446 | -1.1299 | 33.8676 | 6.6 | 5.5639 | 1.0361 |  | 30-03-2026 17:30 | 26.943 | 31.267 | 1961.8 | 5.2112 | 5.6446 | -0.43344 | 33.8676 | 7 | 5.5639 | 1.4361 |  | 30-03-2026 17:30 | 30.242 | 30.825 | 1931.2 | 5.1375 | 5.6446 | -0.5071 | 33.8676 | 7.1 | 5.5639 | 1.5361 |  | 30-03-2026 17:30 | 30.585 | 30.948 | 1945.4 | 5.158 | 5.6446 | -0.4866 | 33.8676 | 7.3 | 5.5639 | 1.7361 |  | 30-03-2026 17:30 | 22.67 | 23.216 | 1456.3 | 3.8693 | 4.1812 | -0.31186 | 25.0871 | 5.4 | 4.1214 | 1.2786 |  | 30-03-2026 17:30 | 22.012 | 22.537 | 1440.7 | 3.7562 | 4.1812 | -0.42502 | 25.0871 | 5.3 | 4.1214 | 1.1786 |  | 30-03-2026 17:30 | 20.998 | 21.517 | 1444.9 | 3.5862 | 4.1812 | -0.59502 | 25.0871 | 5.3 | 4.1214 | 1.1786 |  | 30-03-2026 17:30 | 21.05 | 21.892 | 1453.5 | 3.6487 | 4.1812 | -0.53252 | 25.0871 | 5.4 | 4.1214 | 1.2786 |  | 30-03-2026 17:30 | 19.936 | 20.441 | 1376.2 | 3.4068 | 3.9779 | -0.57105 | 23.8673 | 5.1 | 3.921 | 1.179 |  | 30-03-2026 17:30 | 38.2885 | 43.2811 | -4.9926 | 259.6863 | 54.5 | 42.6621 | 11.8379 | 16.2115
30-03-2026 17:20 | 308 | 48.79 | 105.255 | 106.49 | 1940.8 | 17.7483 | 18.3403 | -0.59198 | 110.0419 | 14.8 | 18.078 | -3.278 |  | 30-03-2026 17:20 | 105.134 | 106.62 | 1954.8 | 17.77 | 18.3403 | -0.57032 | 110.0419 | 14.9 | 18.078 | -3.178 |  | 30-03-2026 17:20 | 94.845 | 97.215 | 1924.1 | 16.2025 | 18.3403 | -2.1378 | 110.0419 | 14.8 | 18.078 | -3.278 |  | 30-03-2026 17:20 | 88.873 | 90.304 | 1938.1 | 15.0507 | 18.3403 | -3.2896 | 110.0419 | 14.6 | 18.078 | -3.478 |  | 30-03-2026 17:20 | 69.223 | 71.171 | 1450.9 | 11.8618 | 13.5854 | -1.7236 | 81.5125 | 11.2 | 13.3911 | -2.1911 |  | 30-03-2026 17:20 | 65.899 | 66.956 | 1435.4 | 11.1593 | 13.5854 | -2.4261 | 81.5125 | 10.8 | 13.3911 | -2.5911 |  | 30-03-2026 17:20 | 66.121 | 66.992 | 1439.6 | 11.1653 | 13.5854 | -2.4201 | 81.5125 | 10.9 | 13.3911 | -2.4911 |  | 30-03-2026 17:20 | 60.384 | 63.833 | 1448.1 | 10.6388 | 13.5854 | -2.9466 | 81.5125 | 10.9 | 13.3911 | -2.4911 |  | 30-03-2026 17:20 | 61.647 | 62.491 | 1371.1 | 10.4152 | 12.9248 | -2.5097 | 77.5491 | 10.5 | 12.74 | -2.24 |  | 30-03-2026 17:20 | 122.012 | 140.6278 | -18.6158 | 843.7667 | 113.4 | 138.6168 | -25.2168 | -8.612
30-03-2026 17:10 | 180 | 49.08 | 60.49 | 61.503 | 1926 | 10.2505 | 10.7065 | -0.456 | 64.239 | 19.6 | 10.5534 | 9.0466 |  | 30-03-2026 17:10 | 61.679 | 62.587 | 1939.9 | 10.4312 | 10.7065 | -0.27533 | 64.239 | 20.3 | 10.5534 | 9.7466 |  | 30-03-2026 17:10 | 63.407 | 64.486 | 1909.3 | 10.7477 | 10.7065 | 0.041168 | 64.239 | 19.7 | 10.5534 | 9.1466 |  | 30-03-2026 17:10 | 62.22 | 63.116 | 1923.5 | 10.5193 | 10.7065 | -0.18717 | 64.239 | 19.9 | 10.5534 | 9.3466 |  | 30-03-2026 17:10 | 54.4 | 55.35 | 1439.7 | 9.225 | 7.9307 | 1.2943 | 47.5844 | 14.8 | 7.8173 | 6.9827 |  | 30-03-2026 17:10 | 47.937 | 48.726 | 1424.6 | 8.121 | 7.9307 | 0.19026 | 47.5844 | 14.5 | 7.8173 | 6.6827 |  | 30-03-2026 17:10 | 59.529 | 60.405 | 1428.7 | 10.0675 | 7.9307 | 2.1368 | 47.5844 | 14.4 | 7.8173 | 6.5827 |  | 30-03-2026 17:10 | 61.053 | 63.687 | 1437.2 | 10.6145 | 7.9307 | 2.6838 | 47.5844 | 14.4 | 7.8173 | 6.5827 |  | 30-03-2026 17:10 | 45.873 | 46.647 | 1360.6 | 7.7745 | 7.5451 | 0.22938 | 45.2707 | 13.6 | 7.4372 | 6.1628 |  | 30-03-2026 17:10 | 87.7512 | 82.0941 | 5.6571 | 492.5644 | 151.2 | 80.9201 | 70.2799 | 63.4488
30-03-2026 17:00 | 463 | 48.5 | 156.086 | 156.901 | 1906.4 | 26.1502 | 27.6005 | -1.4504 | 165.6033 | 18.9 | 27.2059 | -8.3059 |  | 30-03-2026 17:00 | 160.444 | 162.508 | 1919.6 | 27.0847 | 27.6005 | -0.51588 | 165.6033 | 18.3 | 27.2059 | -8.9059 |  | 30-03-2026 17:00 | 155.463 | 160.577 | 1889.6 | 26.7628 | 27.6005 | -0.83771 | 165.6033 | 18.3 | 27.2059 | -8.9059 |  | 30-03-2026 17:00 | 150.381 | 152.331 | 1903.6 | 25.3885 | 27.6005 | -2.212 | 165.6033 | 18.4 | 27.2059 | -8.8059 |  | 30-03-2026 17:00 | 120.589 | 122.069 | 1424.9 | 20.3448 | 20.4448 | -0.10001 | 122.6691 | 13.7 | 20.1525 | -6.4525 |  | 30-03-2026 17:00 | 114.531 | 117.362 | 1410.1 | 19.5603 | 20.4448 | -0.88451 | 122.6691 | 13.6 | 20.1525 | -6.5525 |  | 30-03-2026 17:00 | 118.71 | 120.152 | 1414.3 | 20.0253 | 20.4448 | -0.41951 | 122.6691 | 13.6 | 20.1525 | -6.5525 |  | 30-03-2026 17:00 | 117.551 | 121.755 | 1422.8 | 20.2925 | 20.4448 | -0.15235 | 122.6691 | 13.6 | 20.1525 | -6.5525 |  | 30-03-2026 17:00 | 111.472 | 112.96 | 1347 | 18.8267 | 19.4507 | -0.62407 | 116.7044 | 13 | 19.1726 | -6.1726 |  | 30-03-2026 17:00 | 204.4358 | 211.6323 | -7.1965 | 1269.7939 | 141.4 | 208.606 | -67.206 | -63.0358
30-03-2026 16:50 | 243 | 48.5 | 84.025 | 85.132 | 1887.5 | 14.1887 | 14.4858 | -0.29715 | 86.9149 | 36.3 | 14.2787 | 22.0213 |  | 30-03-2026 16:50 | 85.917 | 85.884 | 1901.3 | 14.314 | 14.4858 | -0.17182 | 86.9149 | 14.8 | 14.2787 | 0.52133 |  | 30-03-2026 16:50 | 85.794 | 87.777 | 1871.3 | 14.6295 | 14.4858 | 0.14368 | 86.9149 | 14.7 | 14.2787 | 0.42133 |  | 30-03-2026 16:50 | 85.457 | 86.618 | 1885.2 | 14.4363 | 14.4858 | -0.049482 | 86.9149 | 14.7 | 14.2787 | 0.42133 |  | 30-03-2026 16:50 | 64.534 | 65.45 | 1411.2 | 10.9083 | 10.7302 | 0.1781 | 64.3814 | 11.2 | 10.5768 | 0.62321 |  | 30-03-2026 16:50 | 63.201 | 64.105 | 1396.5 | 10.6842 | 10.7302 | -0.046067 | 64.3814 | 10.8 | 10.5768 | 0.22321 |  | 30-03-2026 16:50 | 64.004 | 64.926 | 1400.7 | 10.821 | 10.7302 | 0.090767 | 64.3814 | 11 | 10.5768 | 0.42321 |  | 30-03-2026 16:50 | 63.715 | 65.955 | 1409.2 | 10.9925 | 10.7302 | 0.26227 | 64.3814 | 11.1 | 10.5768 | 0.52321 |  | 30-03-2026 16:50 | 60.36 | 61.242 | 1334 | 10.207 | 10.2085 | -0.0014882 | 61.2509 | 10.3 | 10.0625 | 0.23749 |  | 30-03-2026 16:50 | 111.1815 | 111.0727 | 0.10882 | 666.4361 | 134.9 | 109.4843 | 25.4157 | 23.7185
30-03-2026 16:40 | 154 | 49.08 | 51.873 | 52.743 | 1873.2 | 8.7905 | 9.16 | -0.3695 | 54.96 | 0 | 9.029 | -9.029 |  | 30-03-2026 16:40 | 52.483 | 53.391 | 1886.5 | 8.8985 | 9.16 | -0.2615 | 54.96 | 60.3 | 9.029 | 51.271 |  | 30-03-2026 16:40 | 52.878 | 53.782 | 1856.6 | 8.9637 | 9.16 | -0.19634 | 54.96 | 22.1 | 9.029 | 13.071 |  | 30-03-2026 16:40 | 53.509 | 54.429 | 1870.5 | 9.0715 | 9.16 | -0.088505 | 54.96 | 22.2 | 9.029 | 13.171 |  | 30-03-2026 16:40 | 39.52 | 40.265 | 1400 | 6.7108 | 6.7852 | -0.074355 | 40.7111 | 16.5 | 6.6882 | 9.8118 |  | 30-03-2026 16:40 | 39.147 | 39.885 | 1385.7 | 6.6475 | 6.7852 | -0.13769 | 40.7111 | 16.3 | 6.6882 | 9.6118 |  | 30-03-2026 16:40 | 38.843 | 39.624 | 1389.7 | 6.604 | 6.7852 | -0.18119 | 40.7111 | 16.2 | 6.6882 | 9.5118 |  | 30-03-2026 16:40 | 39.109 | 40.183 | 1398.1 | 6.6972 | 6.7852 | -0.088022 | 40.7111 | 16.2 | 6.6882 | 9.5118 |  | 30-03-2026 16:40 | 36.995 | 37.712 | 1323.7 | 6.2853 | 6.4553 | -0.16993 | 38.7316 | 15.5 | 6.363 | 9.137 |  | 30-03-2026 16:40 | 68.669 | 70.236 | -1.567 | 421.4162 | 185.3 | 69.2317 | 116.0683 | 116.631
30-03-2026 16:30 | 419 | 49.94 | 166.933 | 173.035 | 1851.2 | 28.8392 | 24.8404 | 3.9987 | 149.0426 | 37.5 | 24.4852 | 13.0148 | [5 empty] | 0 | 24.8404 | -24.8404 | 149.0426 | 0 | 24.4852 | -24.4852 |  | 30-03-2026 16:30 | 132.42 | 136.691 | 1834.5 | 22.7818 | 24.8404 | -2.0586 | 149.0426 | 36.8 | 24.4852 | 12.3148 |  | 30-03-2026 16:30 | 164.897 | 167.171 | 1848.3 | 27.8618 | 24.8404 | 3.0214 | 149.0426 | 37.4 | 24.4852 | 12.9148 |  | 30-03-2026 16:30 | 94.17 | 100.48 | 1383.5 | 16.7467 | 18.4003 | -1.6537 | 110.4019 | 27 | 18.1372 | 8.8628 |  | 30-03-2026 16:30 | 103 | 104.325 | 1369.4 | 17.3875 | 18.4003 | -1.0128 | 110.4019 | 27.2 | 18.1372 | 9.0628 |  | 30-03-2026 16:30 | 94.873 | 97.587 | 1373.5 | 16.2645 | 18.4003 | -2.1358 | 110.4019 | 26.5 | 18.1372 | 8.3628 |  | 30-03-2026 16:30 | 91.292 | 94.491 | 1381.9 | 15.7485 | 18.4003 | -2.6518 | 110.4019 | 27 | 18.1372 | 8.8628 |  | 30-03-2026 16:30 | 89.83 | 91.244 | 1308.2 | 15.2073 | 17.5056 | -2.2983 | 105.0337 | 26.6 | 17.2553 | 9.3447 |  | 30-03-2026 16:30 | 160.8373 | 190.4686 | -29.6313 | 1142.8117 | 246 | 187.7449 | 58.2551 | 85.1627
30-03-2026 16:20 | 812 | 49.65 | 272.992 | 288.424 | 1813.7 | 48.0707 | 48.193 | -0.12232 | 289.1579 | 28.3 | 47.5038 | -19.2038 |  | 30-03-2026 16:20 | 274.089 | 274.711 | 1826.2 | 45.7852 | 48.193 | -2.4078 | 289.1579 | 29.6 | 47.5038 | -17.9038 |  | 30-03-2026 16:20 | 281.8 | 289.154 | 1797.7 | 48.1923 | 48.193 | -0.00064978 | 289.1579 | 27.6 | 47.5038 | -19.9038 |  | 30-03-2026 16:20 | 281.943 | 286.207 | 1810.9 | 47.7012 | 48.193 | -0.49182 | 289.1579 | 27.8 | 47.5038 | -19.7038 |  | 30-03-2026 16:20 | 204.658 | 210.367 | 1356.5 | 35.0612 | 35.6985 | -0.63734 | 214.191 | 20.5 | 35.188 | -14.688 |  | 30-03-2026 16:20 | 203.131 | 208.877 | 1342.2 | 34.8128 | 35.6985 | -0.88567 | 214.191 | 20.3 | 35.188 | -14.888 |  | 30-03-2026 16:20 | 197.443 | 202.601 | 1347 | 33.7668 | 35.6985 | -1.9317 | 214.191 | 20.2 | 35.188 | -14.988 |  | 30-03-2026 16:20 | 185.191 | 187.687 | 1354.9 | 31.2812 | 35.6985 | -4.4173 | 214.191 | 20 | 35.188 | -15.188 |  | 30-03-2026 16:20 | 118.191 | 130.282 | 1281.6 | 21.7137 | 33.9627 | -12.249 | 203.7762 | 18.4 | 33.477 | -15.077 |  | 30-03-2026 16:20 | 346.385 | 369.5287 | -23.1437 | 2217.172 | 212.7 | 364.2444 | -151.5444 | -133.685
30-03-2026 16:10 | 383 | 49.65 | 137.363 | 137.333 | 1785.4 | 22.8888 | 22.7314 | 0.15741 | 136.3885 | 21.3 | 22.4064 | -1.1064 |  | 30-03-2026 16:10 | 136.827 | 138.643 | 1796.6 | 23.1072 | 22.7314 | 0.37575 | 136.3885 | 20.7 | 22.4064 | -1.7064 |  | 30-03-2026 16:10 | 138.863 | 141.691 | 1770.1 | 23.6152 | 22.7314 | 0.88375 | 136.3885 | 21.1 | 22.4064 | -1.3064 |  | 30-03-2026 16:10 | 139.721 | 141.59 | 1783.1 | 23.5983 | 22.7314 | 0.86691 | 136.3885 | 21.2 | 22.4064 | -1.2064 |  | 30-03-2026 16:10 | 103.821 | 105.156 | 1336 | 17.526 | 16.8381 | 0.68791 | 101.0285 | 15.8 | 16.5973 | -0.7973 |  | 30-03-2026 16:10 | 103.096 | 104.422 | 1321.9 | 17.4037 | 16.8381 | 0.56558 | 101.0285 | 15.6 | 16.5973 | -0.9973 |  | 30-03-2026 16:10 | 102.812 | 104.091 | 1326.8 | 17.3485 | 16.8381 | 0.51041 | 101.0285 | 15.6 | 16.5973 | -0.9973 |  | 30-03-2026 16:10 | 102.449 | 105.584 | 1334.9 | 17.5973 | 16.8381 | 0.75924 | 101.0285 | 15.5 | 16.5973 | -1.0973 |  | 30-03-2026 16:10 | 97.266 | 98.537 | 1263.2 | 16.4228 | 16.0194 | 0.40348 | 96.1161 | 14.6 | 15.7903 | -1.1903 |  | 30-03-2026 16:10 | 179.5078 | 174.2974 | 5.2104 | 1045.7843 | 161.4 | 171.8049 | -10.4049 | -18.1078
30-03-2026 16:00 | 194 | 49.65 | 72.346 | 73.849 | 1764.1 | 12.3082 | 11.5141 | 0.79408 | 69.0845 | 18.6 | 11.3494 | 7.2506 |  | 30-03-2026 16:00 | 68.543 | 72.333 | 1775.9 | 12.0555 | 11.5141 | 0.54141 | 69.0845 | 18.7 | 11.3494 | 7.3506 |  | 30-03-2026 16:00 | 71.822 | 73.171 | 1749 | 12.1952 | 11.5141 | 0.68108 | 69.0845 | 18.5 | 11.3494 | 7.1506 |  | 30-03-2026 16:00 | 72.086 | 73.079 | 1761.9 | 12.1798 | 11.5141 | 0.66575 | 69.0845 | 18.6 | 11.3494 | 7.2506 |  | 30-03-2026 16:00 | 53.77 | 54.618 | 1320.2 | 9.103 | 8.529 | 0.57405 | 51.1737 | 13.9 | 8.407 | 5.493 |  | 30-03-2026 16:00 | 53.077 | 53.956 | 1306.3 | 8.9927 | 8.529 | 0.46371 | 51.1737 | 13.8 | 8.407 | 5.393 |  | 30-03-2026 16:00 | 53.323 | 54.201 | 1311.2 | 9.0335 | 8.529 | 0.50455 | 51.1737 | 13.9 | 8.407 | 5.493 |  | 30-03-2026 16:00 | 53.483 | 55.431 | 1319.4 | 9.2385 | 8.529 | 0.70955 | 51.1737 | 13.9 | 8.407 | 5.493 |  | 30-03-2026 16:00 | 50.653 | 51.524 | 1248.6 | 8.5873 | 8.1142 | 0.47309 | 48.6855 | 13.2 | 7.9982 | 5.2018 |  | 30-03-2026 16:00 | 93.6937 | 88.2864 | 5.4073 | 529.7184 | 143.1 | 87.0239 | 56.0761 | 49.4063
30-03-2026 15:50 | 645 | 50.23 | 246.167 | 239.183 | 1745.5 | 39.8638 | 38.1963 | 1.6675 | 229.1779 | 42.9 | 37.6501 | 5.2499 |  | 30-03-2026 15:50 | 231.437 | 234.938 | 1757.2 | 39.1563 | 38.1963 | 0.96001 | 229.1779 | 43.3 | 37.6501 | 5.6499 |  | 30-03-2026 15:50 | 233.265 | 239.022 | 1730.5 | 39.837 | 38.1963 | 1.6407 | 229.1779 | 43.2 | 37.6501 | 5.5499 |  | 30-03-2026 15:50 | 238.715 | 243.685 | 1743.3 | 40.6142 | 38.1963 | 2.4178 | 229.1779 | 43.5 | 37.6501 | 5.8499 |  | 30-03-2026 15:50 | 175.162 | 177.595 | 1306.3 | 29.5992 | 28.2936 | 1.3056 | 169.7614 | 33.2 | 27.889 | 5.311 |  | 30-03-2026 15:50 | 174.923 | 177.371 | 1292.5 | 29.5618 | 28.2936 | 1.2683 | 169.7614 | 32.2 | 27.889 | 4.311 |  | 30-03-2026 15:50 | 173.613 | 176.042 | 1297.3 | 29.3403 | 28.2936 | 1.0468 | 169.7614 | 32.3 | 27.889 | 4.411 |  | 30-03-2026 15:50 | 174.851 | 179.567 | 1305.5 | 29.9278 | 28.2936 | 1.6343 | 169.7614 | 32.6 | 27.889 | 4.711 |  | 30-03-2026 15:50 | 164.414 | 166.698 | 1235.4 | 27.783 | 26.9178 | 0.86517 | 161.507 | 30.7 | 26.5329 | 4.1671 |  | 30-03-2026 15:50 | 305.6835 | 292.8774 | 12.8061 | 1757.2645 | 333.9 | 288.6893 | 45.2107 | 28.2165
30-03-2026 15:40 | 616 | 49.65 | 245.981 | 204.412 | 1702.6 | 34.0687 | 36.5602 | -2.4915 | 219.3612 | 32.7 | 36.0374 | -3.3374 |  | 30-03-2026 15:40 | 250.777 | 254.467 | 1713.9 | 42.4112 | 36.5602 | 5.851 | 219.3612 | 32.2 | 36.0374 | -3.8374 |  | 30-03-2026 15:40 | 246.171 | 249.742 | 1687.3 | 41.6237 | 36.5602 | 5.0635 | 219.3612 | 31.9 | 36.0374 | -4.1374 |  | 30-03-2026 15:40 | 249.867 | 253.543 | 1699.8 | 42.2572 | 36.5602 | 5.697 | 219.3612 | 31.9 | 36.0374 | -4.1374 |  | 30-03-2026 15:40 | 195.778 | 198.457 | 1273.1 | 33.0762 | 27.0816 | 5.9945 | 162.4898 | 23.6 | 26.6944 | -3.0944 |  | 30-03-2026 15:40 | 187.555 | 190.083 | 1260.3 | 31.6805 | 27.0816 | 4.5989 | 162.4898 | 23.7 | 26.6944 | -2.9944 |  | 30-03-2026 15:40 | 188.115 | 190.631 | 1265 | 31.7718 | 27.0816 | 4.6902 | 162.4898 | 24 | 26.6944 | -2.6944 |  | 30-03-2026 15:40 | 191.22 | 196.722 | 1272.9 | 32.787 | 27.0816 | 5.7054 | 162.4898 | 24.1 | 26.6944 | -2.5944 |  | 30-03-2026 15:40 | 177.408 | 179.799 | 1204.7 | 29.9665 | 25.7648 | 4.2017 | 154.5889 | 22.7 | 25.3964 | -2.6964 |  | 30-03-2026 15:40 | 319.6427 | 280.3321 | 39.3106 | 1681.9925 | 246.8 | 276.3233 | -29.5233 | -72.8427
30-03-2026 15:30 | 327 | 49.08 | 110.891 | 112.283 | 1669.9 | 18.7138 | 19.4501 | -0.73631 | 116.7008 | 15.1 | 19.172 | -4.072 |  | 30-03-2026 15:30 | 114.399 | 115.871 | 1681.7 | 19.3118 | 19.4501 | -0.13831 | 116.7008 | 15.5 | 19.172 | -3.672 |  | 30-03-2026 15:30 | 122.84 | 125.632 | 1655.4 | 20.9387 | 19.4501 | 1.4885 | 116.7008 | 15.5 | 19.172 | -3.672 |  | 30-03-2026 15:30 | 120.813 | 122.379 | 1667.9 | 20.3965 | 19.4501 | 0.94636 | 116.7008 | 15.6 | 19.172 | -3.572 |  | 30-03-2026 15:30 | 93.55 | 94.793 | 1249.5 | 15.7988 | 14.4075 | 1.3913 | 86.4451 | 11.7 | 14.2015 | -2.5015 |  | 30-03-2026 15:30 | 91.368 | 92.713 | 1236.6 | 15.4522 | 14.4075 | 1.0447 | 86.4451 | 11.5 | 14.2015 | -2.7015 |  | 30-03-2026 15:30 | 94.029 | 95.242 | 1241 | 15.8737 | 14.4075 | 1.4662 | 86.4451 | 11.6 | 14.2015 | -2.6015 |  | 30-03-2026 15:30 | 94.877 | 97.769 | 1248.8 | 16.2948 | 14.4075 | 1.8873 | 86.4451 | 11.7 | 14.2015 | -2.5015 |  | 30-03-2026 15:30 | 88.671 | 89.812 | 1182 | 14.9687 | 13.707 | 1.2617 | 82.2418 | 11.2 | 13.511 | -2.311 |  | 30-03-2026 15:30 | 157.749 | 149.1376 | 8.6114 | 894.8254 | 119.4 | 147.0049 | -27.6049 | -38.349
30-03-2026 15:20 | 199 | 48.79 | 73.817 | 78.249 | 1654.8 | 13.0415 | 11.8497 | 1.1918 | 71.0985 | 11.5 | 11.6803 | -0.1803 |  | 30-03-2026 15:20 | 77.718 | 78.798 | 1666.2 | 13.133 | 11.8497 | 1.2833 | 71.0985 | 11.7 | 11.6803 | 0.019702 |  | 30-03-2026 15:20 | 76.67 | 78.014 | 1639.9 | 13.0023 | 11.8497 | 1.1526 | 71.0985 | 11.4 | 11.6803 | -0.2803 |  | 30-03-2026 15:20 | 77.213 | 78.286 | 1652.3 | 13.0477 | 11.8497 | 1.1979 | 71.0985 | 11.5 | 11.6803 | -0.1803 |  | 30-03-2026 15:20 | 57.342 | 58.216 | 1237.8 | 9.7027 | 8.7776 | 0.92507 | 52.6656 | 8.5 | 8.6521 | -0.15207 |  | 30-03-2026 15:20 | 56.934 | 57.813 | 1225.1 | 9.6355 | 8.7776 | 0.85791 | 52.6656 | 8.5 | 8.6521 | -0.15207 |  | 30-03-2026 15:20 | 56.9 | 57.784 | 1229.4 | 9.6307 | 8.7776 | 0.85307 | 52.6656 | 8.5 | 8.6521 | -0.15207 |  | 30-03-2026 15:20 | 57.146 | 59.049 | 1237.1 | 9.8415 | 8.7776 | 1.0639 | 52.6656 | 8.5 | 8.6521 | -0.15207 |  | 30-03-2026 15:20 | 53.903 | 54.763 | 1170.8 | 9.1272 | 8.3508 | 0.77637 | 50.1048 | 8 | 8.2314 | -0.23138 |  | 30-03-2026 15:20 | 100.162 | 90.8602 | 9.3018 | 545.1609 | 88.1 | 89.5609 | -1.4609 | -12.062
30-03-2026 15:10 | 197 | 48.79 | 74.092 | 75.114 | 1643.3 | 12.519 | 11.7307 | 0.78834 | 70.3839 | 20.4 | 11.5629 | 8.8371 |  | 30-03-2026 15:10 | 75.486 | 76.558 | 1654.5 | 12.7597 | 11.7307 | 1.029 | 70.3839 | 20 | 11.5629 | 8.4371 |  | 30-03-2026 15:10 | 73.534 | 74.822 | 1628.5 | 12.4703 | 11.7307 | 0.73968 | 70.3839 | 19.7 | 11.5629 | 8.1371 |  | 30-03-2026 15:10 | 74.32 | 75.375 | 1640.8 | 12.5625 | 11.7307 | 0.83184 | 70.3839 | 20.5 | 11.5629 | 8.9371 |  | 30-03-2026 15:10 | 54.919 | 55.789 | 1229.3 | 9.2982 | 8.6894 | 0.60879 | 52.1363 | 14.8 | 8.5651 | 6.2349 |  | 30-03-2026 15:10 | 54.713 | 55.623 | 1216.6 | 9.2705 | 8.6894 | 0.58112 | 52.1363 | 14.7 | 8.5651 | 6.1349 |  | 30-03-2026 15:10 | 54.54 | 55.454 | 1220.9 | 9.2423 | 8.6894 | 0.55296 | 52.1363 | 14.6 | 8.5651 | 6.0349 |  | 30-03-2026 15:10 | 55.014 | 56.807 | 1228.6 | 9.4678 | 8.6894 | 0.77846 | 52.1363 | 14.8 | 8.5651 | 6.2349 |  | 30-03-2026 15:10 | 52.144 | 53.003 | 1162.8 | 8.8338 | 8.2669 | 0.56697 | 49.6012 | 14 | 8.1486 | 5.8514 |  | 30-03-2026 15:10 | 96.4242 | 89.947 | 6.4772 | 539.6819 | 153.5 | 88.6607 | 64.8393 | 57.0758
30-03-2026 15:00 | 581 | 48.79 | 214.386 | 216.085 | 1622.9 | 36.0142 | 34.5965 | 1.4177 | 207.579 | 16 | 34.1018 | -18.1018 | 0.99214 | 30-03-2026 15:00 | 152.783 | 217.722 | 1634.5 | 36.287 | 34.5965 | 1.6905 | 207.579 | 17.1 | 34.1018 | -17.0018 | 0.70173 | 30-03-2026 15:00 | 218.11 | 223.528 | 1608.8 | 37.2547 | 34.5965 | 2.6582 | 207.579 | 16.6 | 34.1018 | -17.5018 | 0.97576 | 30-03-2026 15:00 | 204.689 | 208.27 | 1620.3 | 34.7117 | 34.5965 | 0.11516 | 207.579 | 16 | 34.1018 | -18.1018 | 0.98281 | 30-03-2026 15:00 | 164.081 | 167.556 | 1214.5 | 27.926 | 25.627 | 2.299 | 153.7622 | 12.5 | 25.2606 | -12.7606 | 0.9859 | 30-03-2026 15:00 | 158.076 | 161.464 | 1201.9 | 26.9107 | 25.627 | 1.2836 | 153.7622 | 12.3 | 25.2606 | -12.9606 | 0.97902 | 30-03-2026 15:00 | 164.787 | 168.101 | 1206.3 | 28.0168 | 25.627 | 2.3898 | 153.7622 | 12.5 | 25.2606 | -12.7606 | 0.98029 | 30-03-2026 15:00 | 165.045 | 169.874 | 1213.8 | 28.3123 | 25.627 | 2.6853 | 153.7622 | 12.6 | 25.2606 | -12.6606 | 0.97157 | 30-03-2026 15:00 | 153.202 | 155.22 | 1148.8 | 25.87 | 24.381 | 1.489 | 146.2857 | 11.9 | 24.0323 | -12.1323 | 0.987 | 30-03-2026 15:00 | 281.3033 | 265.2751 | 16.0282 | 1591.6508 | 127.5 | 261.4817 | -133.9817 | -153.8033
30-03-2026 14:50 | 196 | 48.79 | 74.091 | 75.151 | 1606.9 | 12.5252 | 11.6711 | 0.85406 | 70.0267 | 15.5 | 11.5042 | 3.9958 | 0.9859 | 30-03-2026 14:50 | 71.58 | 72.648 | 1617.4 | 12.108 | 11.6711 | 0.43689 | 70.0267 | 14.7 | 11.5042 | 3.1958 | 0.9853 | 30-03-2026 14:50 | 73.855 | 75.341 | 1592.2 | 12.5568 | 11.6711 | 0.88572 | 70.0267 | 14.7 | 11.5042 | 3.1958 | 0.98028 | 30-03-2026 14:50 | 74.26 | 75.36 | 1604.3 | 12.56 | 11.6711 | 0.88889 | 70.0267 | 15.7 | 11.5042 | 4.1958 | 0.9854 | 30-03-2026 14:50 | 55.458 | 56.332 | 1202 | 9.3887 | 8.6453 | 0.7434 | 51.8716 | 11.2 | 8.5216 | 2.6784 | 0.9845 | 30-03-2026 14:50 | 54.87 | 55.779 | 1189.6 | 9.2965 | 8.6453 | 0.65123 | 51.8716 | 11.4 | 8.5216 | 2.8784 | 0.9837 | 30-03-2026 14:50 | 55.22 | 56.129 | 1193.8 | 9.3548 | 8.6453 | 0.70957 | 51.8716 | 11 | 8.5216 | 2.4784 | 0.98381 | 30-03-2026 14:50 | 55.25 | 56.91 | 1201.2 | 9.485 | 8.6453 | 0.83973 | 51.8716 | 10.9 | 8.5216 | 2.3784 | 0.97083 | 30-03-2026 14:50 | 52.118 | 53.009 | 1136.9 | 8.8348 | 8.2249 | 0.60993 | 49.3494 | 10.5 | 8.1073 | 2.3927 | 0.98319 | 30-03-2026 14:50 | 96.1098 | 89.4904 | 6.6194 | 536.9424 | 115.6 | 88.2107 | 27.3893 | 19.4902
30-03-2026 14:40 | 703 | 49.65 | 243.799 | 247.612 | 1591.4 | 41.2687 | 41.7237 | -0.45506 | 250.3424 | 50 | 41.1271 | 8.8729 | 0.9846 | 30-03-2026 14:40 | 235.542 | 239.177 | 1602.7 | 39.8628 | 41.7237 | -1.8609 | 250.3424 | 51.1 | 41.1271 | 9.9729 | 0.9848 | 30-03-2026 14:40 | 238.856 | 244.325 | 1577.5 | 40.7208 | 41.7237 | -1.0029 | 250.3424 | 50.2 | 41.1271 | 9.0729 | 0.97762 | 30-03-2026 14:40 | 241.054 | 244.874 | 1588.6 | 40.8123 | 41.7237 | -0.91139 | 250.3424 | 50.9 | 41.1271 | 9.7729 | 0.9844 | 30-03-2026 14:40 | 174.152 | 176.643 | 1190.8 | 29.4405 | 30.9065 | -1.466 | 185.4388 | 38.2 | 30.4645 | 7.7355 | 0.98477 | 30-03-2026 14:40 | 174.272 | 177.375 | 1178.2 | 29.5625 | 30.9065 | -1.344 | 185.4388 | 37.6 | 30.4645 | 7.1355 | 0.98251 | 30-03-2026 14:40 | 164.583 | 169.322 | 1182.8 | 28.2203 | 30.9065 | -2.6861 | 185.4388 | 37.7 | 30.4645 | 7.2355 | 0.97201 | 30-03-2026 14:40 | 164.428 | 167.452 | 1190.3 | 27.9087 | 30.9065 | -2.9978 | 185.4388 | 38 | 30.4645 | 7.5355 | 0.98194 | 30-03-2026 14:40 | 164.061 | 166.441 | 1126.4 | 27.7402 | 29.4037 | -1.6635 | 176.422 | 35.9 | 28.9832 | 6.9168 | 0.9857 | 30-03-2026 14:40 | 305.5368 | 319.9244 | -14.3876 | 1919.5467 | 389.6 | 315.3495 | 74.2505 | 84.0632
30-03-2026 14:30 | 973 | 49.65 | 326.021 | 331.558 | 1541.4 | 55.2597 | 57.7485 | -2.4888 | 346.4909 | 53.2 | 56.9227 | -3.7227 | 0.9833 | 30-03-2026 14:30 | 330.029 | 335.771 | 1551.6 | 55.9618 | 57.7485 | -1.7867 | 346.4909 | 54.7 | 56.9227 | -2.2227 | 0.9829 | 30-03-2026 14:30 | 322.274 | 331.382 | 1527.3 | 55.2303 | 57.7485 | -2.5182 | 346.4909 | 52.8 | 56.9227 | -4.1227 | 0.97252 | 30-03-2026 14:30 | 327.773 | 333.475 | 1537.7 | 55.5792 | 57.7485 | -2.1693 | 346.4909 | 52.5 | 56.9227 | -4.4227 | 0.9829 | 30-03-2026 14:30 | 244.083 | 247.926 | 1152.6 | 41.321 | 42.7767 | -1.4557 | 256.6599 | 39.3 | 42.165 | -2.865 | 0.9849 | 30-03-2026 14:30 | 241.28 | 246.158 | 1140.6 | 41.0263 | 42.7767 | -1.7503 | 256.6599 | 39.4 | 42.165 | -2.765 | 0.98018 | 30-03-2026 14:30 | 240.796 | 245.418 | 1145.1 | 40.903 | 42.7767 | -1.8737 | 256.6599 | 39.4 | 42.165 | -2.765 | 0.98117 | 30-03-2026 14:30 | 241.849 | 249.103 | 1152.3 | 41.5172 | 42.7767 | -1.2595 | 256.6599 | 39.6 | 42.165 | -2.565 | 0.97088 | 30-03-2026 14:30 | 229.688 | 233.281 | 1090.5 | 38.8802 | 40.6967 | -1.8165 | 244.1802 | 37.5 | 40.1147 | -2.6147 | 0.9846 | 30-03-2026 14:30 | 425.6787 | 442.7973 | -17.1186 | 2656.7837 | 408.4 | 436.4653 | -28.0653 | -17.2787
30-03-2026 14:20 | 1038 | 49.65 | 347.14 | 353 | 1488.2 | 58.8333 | 61.6063 | -2.773 | 369.6378 | 45.2 | 60.7253 | -15.5253 | 0.9834 | 30-03-2026 14:20 | 324.523 | 330.001 | 1496.9 | 55.0002 | 61.6063 | -6.6061 | 369.6378 | 46.3 | 60.7253 | -14.4253 | 0.9834 | 30-03-2026 14:20 | 349.804 | 359.529 | 1474.5 | 59.9215 | 61.6063 | -1.6848 | 369.6378 | 45.2 | 60.7253 | -15.5253 | 0.97295 | 30-03-2026 14:20 | 352.321 | 358.268 | 1485.2 | 59.7113 | 61.6063 | -1.895 | 369.6378 | 46.3 | 60.7253 | -14.4253 | 0.9834 | 30-03-2026 14:20 | 263.926 | 268.008 | 1113.3 | 44.668 | 45.6343 | -0.9663 | 273.8058 | 34.9 | 44.9817 | -10.0817 | 0.9864 | 30-03-2026 14:20 | 258.701 | 263.833 | 1101.2 | 43.9722 | 45.6343 | -1.6621 | 273.8058 | 33.8 | 44.9817 | -11.1817 | 0.98055 | 30-03-2026 14:20 | 261.005 | 266.431 | 1105.7 | 44.4052 | 45.6343 | -1.2291 | 273.8058 | 34.1 | 44.9817 | -10.8817 | 0.97963 | 30-03-2026 14:20 | 261.681 | 269.948 | 1112.7 | 44.9913 | 45.6343 | -0.64296 | 273.8058 | 34.2 | 44.9817 | -10.7817 | 0.96938 | 30-03-2026 14:20 | 247.838 | 251.689 | 1053 | 41.9482 | 43.4154 | -1.4672 | 260.4923 | 32.4 | 42.7945 | -10.3945 | 0.9847 | 30-03-2026 14:20 | 453.4512 | 472.3778 | -18.9266 | 2834.2666 | 352.4 | 465.6228 | -113.2228 | -101.0512
30-03-2026 14:10 | 968 | 49.08 | 328.206 | 333.577 | 1443 | 55.5962 | 57.5772 | -1.981 | 345.463 | 40.4 | 56.7538 | -16.3538 | 0.9839 | 30-03-2026 14:10 | 330.155 | 335.66 | 1450.6 | 55.9433 | 57.5772 | -1.6338 | 345.463 | 39.4 | 56.7538 | -17.3538 | 0.9836 | 30-03-2026 14:10 | 333.633 | 343.082 | 1429.3 | 57.1803 | 57.5772 | -0.39684 | 345.463 | 40.6 | 56.7538 | -16.1538 | 0.97246 | 30-03-2026 14:10 | 327.413 | 333.008 | 1438.9 | 55.5013 | 57.5772 | -2.0758 | 345.463 | 39.8 | 56.7538 | -16.9538 | 0.9832 | 30-03-2026 14:10 | 250.945 | 254.792 | 1078.4 | 42.4653 | 42.6498 | -0.18442 | 255.8985 | 30.3 | 42.0399 | -11.7399 | 0.9855 | 30-03-2026 14:10 | 245.166 | 250.049 | 1067.4 | 41.6748 | 42.6498 | -0.97492 | 255.8985 | 30.2 | 42.0399 | -11.8399 | 0.98047 | 30-03-2026 14:10 | 249.795 | 254.646 | 1071.6 | 42.441 | 42.6498 | -0.20876 | 255.8985 | 30.6 | 42.0399 | -11.4399 | 0.98095 | 30-03-2026 14:10 | 250.511 | 258.773 | 1078.5 | 43.1288 | 42.6498 | 0.47908 | 255.8985 | 30.9 | 42.0399 | -11.1399 | 0.96807 | 30-03-2026 14:10 | 235.335 | 238.939 | 1020.6 | 39.8232 | 40.576 | -0.75279 | 243.4558 | 29.1 | 39.9957 | -10.8957 | 0.98492 | 30-03-2026 14:10 | 433.7543 | 441.4837 | -7.7293 | 2648.9021 | 311.3 | 435.1705 | -123.8705 | -122.4543
30-03-2026 14:00 | 604 | 49.08 | 220.55 | 224.233 | 1402.6 | 37.3722 | 35.9263 | 1.4459 | 215.5575 | 35.8 | 35.4125 | 0.38749 | 0.98358 | 30-03-2026 14:00 | 211.648 | 218.669 | 1411.2 | 36.4448 | 35.9263 | 0.51858 | 215.5575 | 38.7 | 35.4125 | 3.2875 | 0.96789 | 30-03-2026 14:00 | 228.908 | 235.371 | 1388.7 | 39.2285 | 35.9263 | 3.3022 | 215.5575 | 36.6 | 35.4125 | 1.1875 | 0.97254 | 30-03-2026 14:00 | 218.282 | 222.352 | 1399.1 | 37.0587 | 35.9263 | 1.1324 | 215.5575 | 36.8 | 35.4125 | 1.3875 | 0.9817 | 30-03-2026 14:00 | 174.462 | 176.867 | 1048.1 | 29.4778 | 26.612 | 2.8658 | 159.6722 | 27.8 | 26.2315 | 1.5685 | 0.986 | 30-03-2026 14:00 | 142.897 | 147.8 | 1037.2 | 24.6333 | 26.612 | -1.9787 | 159.6722 | 26.9 | 26.2315 | 0.66851 | 0.96683 | 30-03-2026 14:00 | 169.198 | 171.792 | 1041 | 28.632 | 26.612 | 2.02 | 159.6722 | 27 | 26.2315 | 0.76851 | 0.9849 | 30-03-2026 14:00 | 170.601 | 175.469 | 1047.6 | 29.2448 | 26.612 | 2.6328 | 159.6722 | 27.2 | 26.2315 | 0.96851 | 0.97226 | 30-03-2026 14:00 | 150.227 | 154.155 | 991.5 | 25.6925 | 25.3181 | 0.37444 | 151.9084 | 25.6 | 24.956 | 0.64399 | 0.97452 | 30-03-2026 14:00 | 287.7847 | 275.4712 | 12.3134 | 1652.8273 | 282.4 | 271.532 | 10.868 | -5.3847
30-03-2026 13:50 | 800 | 49.08 | 267.579 | 271.764 | 1366.8 | 45.294 | 47.5844 | -2.2904 | 285.5066 | 46.1 | 46.904 | -0.80398 | 0.9846 | 30-03-2026 13:50 | 276.924 | 281.398 | 1372.5 | 46.8997 | 47.5844 | -0.68477 | 285.5066 | 95.1 | 46.904 | 48.196 | 0.9841 | 30-03-2026 13:50 | 270.448 | 278.046 | 1352.1 | 46.341 | 47.5844 | -1.2434 | 285.5066 | 44.9 | 46.904 | -2.004 | 0.97267 | 30-03-2026 13:50 | 264.933 | 269.186 | 1362.3 | 44.8643 | 47.5844 | -2.7201 | 285.5066 | 45.3 | 46.904 | -1.604 | 0.9842 | 30-03-2026 13:50 | 204.083 | 207.086 | 1020.3 | 34.5143 | 35.2477 | -0.7334 | 211.4864 | 33.9 | 34.7437 | -0.84369 | 0.98732 | 30-03-2026 13:50 | 199.144 | 203.327 | 1010.3 | 33.8878 | 35.2477 | -1.3599 | 211.4864 | 33.5 | 34.7437 | -1.2437 | 0.97943 | 30-03-2026 13:50 | 199.472 | 202.345 | 1014 | 33.7242 | 35.2477 | -1.5236 | 211.4864 | 33.6 | 34.7437 | -1.1437 | 0.9858 | 30-03-2026 13:50 | 200.223 | 205.502 | 1020.4 | 34.2503 | 35.2477 | -0.9974 | 211.4864 | 33.8 | 34.7437 | -0.94369 | 0.97431 | 30-03-2026 13:50 | 190.51 | 193.333 | 965.9 | 32.2222 | 33.5339 | -1.3117 | 201.2031 | 32 | 33.0543 | -1.0543 | 0.9854 | 30-03-2026 13:50 | 351.9978 | 364.8625 | -12.8647 | 2189.1753 | 398.2 | 359.645 | 38.555 | 46.2022
30-03-2026 13:40 | 792 | 49.36 | 254.295 | 257.819 | 1320.7 | 42.9698 | 47.0582 | -4.0883 | 282.3491 | 49.2 | 46.3852 | 2.8148 | 0.98633 |  |  |  |  | 0 | 47.0582 | -47.0582 | 282.3491 | 0 | 46.3852 | -46.3852 |  | 30-03-2026 13:40 | 232.979 | 247.159 | 1307.2 | 41.1932 | 47.0582 | -5.865 | 282.3491 | 48.3 | 46.3852 | 1.9148 | 0.94263 | 30-03-2026 13:40 | 235.515 | 239.199 | 1317 | 39.8665 | 47.0582 | -7.1917 | 282.3491 | 48.7 | 46.3852 | 2.3148 | 0.9846 | 30-03-2026 13:40 | 165.499 | 167.849 | 986.4 | 27.9748 | 34.8579 | -6.8831 | 209.1475 | 36.5 | 34.3594 | 2.1406 | 0.9849 | 30-03-2026 13:40 | 167.73 | 172.672 | 976.8 | 28.7787 | 34.8579 | -6.0792 | 209.1475 | 36 | 34.3594 | 1.6406 | 0.97138 | 30-03-2026 13:40 | 162.492 | 168.539 | 980.4 | 28.0898 | 34.8579 | -6.7681 | 209.1475 | 36.1 | 34.3594 | 1.7406 | 0.96412 | 30-03-2026 13:40 | 175.56 | 179.605 | 986.6 | 29.9342 | 34.8579 | -4.9237 | 209.1475 | 36.3 | 34.3594 | 1.9406 | 0.97748 | 30-03-2026 13:40 | 163.93 | 172.942 | 933.9 | 28.8237 | 33.163 | -4.3393 | 198.9779 | 34.8 | 32.6888 | 2.1112 | 0.94789 | 30-03-2026 13:40 | 267.6307 | 360.8273 | -93.1967 | 2164.9641 | 325.9 | 355.6675 | -29.7675 | 58.2693
30-03-2026 13:30 | 846 | 49.65 | 296.884 | 301.742 | 1271.5 | 50.2903 | 50.2109 | 0.079417 | 301.2655 | 48.1 | 49.4929 | -1.3929 | 0.9839 | 30-03-2026 13:30 | 287.589 | 292.325 | 1277.4 | 48.7208 | 50.2109 | -1.4901 | 301.2655 | 48.7 | 49.4929 | -0.7929 | 0.9838 | 30-03-2026 13:30 | 287.903 | 295.565 | 1258.9 | 49.2608 | 50.2109 | -0.95008 | 301.2655 | 47.6 | 49.4929 | -1.8929 | 0.97408 | 30-03-2026 13:30 | 290.835 | 295.684 | 1268.3 | 49.2807 | 50.2109 | -0.93025 | 301.2655 | 48.2 | 49.4929 | -1.2929 | 0.9836 | 30-03-2026 13:30 | 220.595 | 223.429 | 949.9 | 37.2382 | 37.1933 | 0.044896 | 223.1596 | 36.5 | 36.6614 | -0.16141 | 0.9853 | 30-03-2026 13:30 | 214.953 | 218.926 | 940.8 | 36.4877 | 37.1933 | -0.7056 | 223.1596 | 36 | 36.6614 | -0.66141 | 0.98185 | 30-03-2026 13:30 | 219.529 | 223.981 | 944.3 | 37.3302 | 37.1933 | 0.1369 | 223.1596 | 36.1 | 36.6614 | -0.56141 | 0.98012 | 30-03-2026 13:30 | 219.291 | 225.903 | 950.3 | 37.6505 | 37.1933 | 0.45723 | 223.1596 | 36.3 | 36.6614 | -0.36141 | 0.97073 | 30-03-2026 13:30 | 206.764 | 209.849 | 899.1 | 34.9748 | 35.3848 | -0.40996 | 212.3087 | 34 | 34.8788 | -0.87879 | 0.9853 | 30-03-2026 13:30 | 381.234 | 385.0015 | -3.7675 | 2310.0092 | 371.5 | 379.496 | -7.996 | -9.734
30-03-2026 13:20 | 887 | 49.36 | 304.819 | 309.807 | 1223.4 | 51.6345 | 52.7028 | -1.0683 | 316.2167 | 45.1 | 51.9491 | -6.8491 | 0.9839 | 30-03-2026 13:20 | 308.131 | 313.859 | 1228.7 | 52.3098 | 52.7028 | -0.39295 | 316.2167 | 43.6 | 51.9491 | -8.3491 | 0.98175 | 30-03-2026 13:20 | 299.165 | 308.215 | 1211.3 | 51.3692 | 52.7028 | -1.3336 | 316.2167 | 45.5 | 51.9491 | -6.4491 | 0.97064 | 30-03-2026 13:20 | 301.684 | 306.776 | 1220.1 | 51.1293 | 52.7028 | -1.5735 | 316.2167 | 45.8 | 51.9491 | -6.1491 | 0.9834 | 30-03-2026 13:20 | 227.122 | 230.604 | 913.4 | 38.434 | 39.0391 | -0.6051 | 234.2346 | 34 | 38.4808 | -4.4808 | 0.9848 | 30-03-2026 13:20 | 225.006 | 228.719 | 904.8 | 38.1198 | 39.0391 | -0.91927 | 234.2346 | 33.5 | 38.4808 | -4.9808 | 0.98377 | 30-03-2026 13:20 | 225.767 | 230.264 | 908.2 | 38.3773 | 39.0391 | -0.66177 | 234.2346 | 33.7 | 38.4808 | -4.7808 | 0.98047 | 30-03-2026 13:20 | 227.14 | 234.297 | 914 | 39.0495 | 39.0391 | 0.0104 | 234.2346 | 33.8 | 38.4808 | -4.6808 | 0.96945 | 30-03-2026 13:20 | 213.969 | 217.486 | 865.1 | 36.2477 | 37.1409 | -0.8932 | 222.8452 | 31.9 | 36.6098 | -4.7098 | 0.98383 | 30-03-2026 13:20 | 396.6712 | 404.1084 | -7.4372 | 2424.6504 | 346.9 | 398.3297 | -51.4297 | -49.7712
30-03-2026 13:10 | 708 | 49.36 | 283.409 | 287.988 | 1178.3 | 47.998 | 42.0672 | 5.9308 | 252.403 | 49.9 | 41.4656 | 8.4344 | 0.9841 | 30-03-2026 13:10 | 271.448 | 278.928 | 1185.1 | 46.488 | 42.0672 | 4.4208 | 252.403 | 50.9 | 41.4656 | 9.4344 | 0.97318 | 30-03-2026 13:10 | 272.489 | 276.863 | 1165.8 | 46.1438 | 42.0672 | 4.0767 | 252.403 | 48.8 | 41.4656 | 7.3344 | 0.9842 | 30-03-2026 13:10 | 280.224 | 289.893 | 1174.3 | 48.3155 | 42.0672 | 6.2483 | 252.403 | 49.2 | 41.4656 | 7.7344 | 0.96665 | 30-03-2026 13:10 | 209.285 | 212.407 | 879.4 | 35.4012 | 31.1609 | 4.2403 | 186.9652 | 37.1 | 30.7153 | 6.3847 | 0.9841 | 30-03-2026 13:10 | 217.72 | 220.968 | 871.3 | 36.828 | 31.1609 | 5.6671 | 186.9652 | 36.5 | 30.7153 | 5.7847 | 0.9853 | 30-03-2026 13:10 | 197.734 | 200.643 | 874.5 | 33.4405 | 31.1609 | 2.2796 | 186.9652 | 36.8 | 30.7153 | 6.0847 | 0.9855 | 30-03-2026 13:10 | 208.965 | 212.061 | 880.2 | 35.3435 | 31.1609 | 4.1826 | 186.9652 | 36.9 | 30.7153 | 6.1847 | 0.9854 | 30-03-2026 13:10 | 199.596 | 204.898 | 833.2 | 34.1497 | 29.6457 | 4.504 | 177.8742 | 35 | 29.2218 | 5.7782 | 0.97412 | 30-03-2026 13:10 | 364.1082 | 322.5578 | 41.5504 | 1935.3467 | 381.1 | 317.9452 | 63.1548 | 16.9918
30-03-2026 13:00 | 871 | 50.23 | 313.877 | 319.11 | 1128.4 | 53.185 | 51.5798 | 1.6052 | 309.479 | 50.7 | 50.8422 | -0.14225 | 0.9836 | 30-03-2026 13:00 | 313.934 | 322.351 | 1134.2 | 53.7252 | 51.5798 | 2.1453 | 309.479 | 49.9 | 50.8422 | -0.94225 | 0.97389 | 30-03-2026 13:00 | 297.72 | 304.801 | 1117 | 50.8002 | 51.5798 | -0.77967 | 309.479 | 48.9 | 50.8422 | -1.9422 | 0.97677 | 30-03-2026 13:00 | 304.51 | 309.682 | 1125.1 | 51.6137 | 51.5798 | 0.033825 | 309.479 | 49.4 | 50.8422 | -1.4422 | 0.9833 | 30-03-2026 13:00 | 225.509 | 228.99 | 842.3 | 38.165 | 38.2073 | -0.04229 | 229.2437 | 37.2 | 37.6609 | -0.46093 | 0.9841 | 30-03-2026 13:00 | 221.538 | 224.912 | 834.8 | 37.4853 | 38.2073 | -0.72196 | 229.2437 | 36.6 | 37.6609 | -1.0609 | 0.985 | 30-03-2026 13:00 | 218.939 | 222.228 | 837.7 | 37.038 | 38.2073 | -1.1693 | 229.2437 | 36.9 | 37.6609 | -0.76093 | 0.9852 | 30-03-2026 13:00 | 219.552 | 226.052 | 843.3 | 37.6753 | 38.2073 | -0.53196 | 229.2437 | 37.7 | 37.6609 | 0.039074 | 0.97125 | 30-03-2026 13:00 | 219.514 | 222.857 | 798.2 | 37.1428 | 36.3495 | 0.79333 | 218.097 | 35.6 | 35.8297 | -0.22971 | 0.985 | 30-03-2026 13:00 | 396.8305 | 395.498 | 1.3325 | 2372.9882 | 382.9 | 389.8424 | -6.9424 | -13.9305
30-03-2026 12:50 | 1047 | 53.09 | 344.79 | 350.967 | 1077.7 | 58.4945 | 61.3216 | -2.8271 | 367.9299 | 54.9 | 60.4447 | -5.5447 | 0.9824 | 30-03-2026 12:50 | 314.252 | 319.719 | 1084.3 | 53.2865 | 61.3216 | -8.0351 | 367.9299 | 56.9 | 60.4447 | -3.5447 | 0.9829 | 30-03-2026 12:50 | 346.825 | 355.882 | 1068.1 | 59.3137 | 61.3216 | -2.008 | 367.9299 | 54.5 | 60.4447 | -5.9447 | 0.97455 | 30-03-2026 12:50 | 341.735 | 347.327 | 1075.7 | 57.8878 | 61.3216 | -3.4338 | 367.9299 | 54.9 | 60.4447 | -5.5447 | 0.9839 | 30-03-2026 12:50 | 263.22 | 267.473 | 805.1 | 44.5788 | 45.4234 | -0.84461 | 272.5406 | 41.2 | 44.7739 | -3.5739 | 0.9842 | 30-03-2026 12:50 | 259.901 | 264.828 | 798.2 | 44.138 | 45.4234 | -1.2854 | 272.5406 | 40.7 | 44.7739 | -4.0739 | 0.9814 | 30-03-2026 12:50 | 259.535 | 264.237 | 800.8 | 44.0395 | 45.4234 | -1.3839 | 272.5406 | 41.3 | 44.7739 | -3.4739 | 0.98221 | 30-03-2026 12:50 | 265.423 | 273.258 | 805.6 | 45.543 | 45.4234 | 0.11956 | 272.5406 | 41.1 | 44.7739 | -3.6739 | 0.97133 | 30-03-2026 12:50 | 251.037 | 255.067 | 762.6 | 42.5112 | 43.2148 | -0.70361 | 259.2887 | 38.9 | 42.5968 | -3.6968 | 0.9842 | 30-03-2026 12:50 | 449.793 | 470.1951 | -20.4021 | 2821.1707 | 424.4 | 463.4713 | -39.0713 | -25.393
30-03-2026 12:40 | 1016 | 52.52 | 335.787 | 341.629 | 1022.8 | 56.9382 | 59.6377 | -2.6995 | 357.826 | 54.8 | 58.7848 | -3.9848 | 0.9829 | 30-03-2026 12:40 | 342.99 | 348.603 | 1027.4 | 58.1005 | 59.6377 | -1.5372 | 357.826 | 56 | 58.7848 | -2.7848 | 0.9839 | 30-03-2026 12:40 | 340.78 | 349.781 | 1013.6 | 58.2968 | 59.6377 | -1.3408 | 357.826 | 57.5 | 58.7848 | -1.2848 | 0.97427 | 30-03-2026 12:40 | 340.544 | 346.297 | 1020.8 | 57.7162 | 59.6377 | -1.9215 | 357.826 | 56.8 | 58.7848 | -1.9848 | 0.98339 | 30-03-2026 12:40 | 258.906 | 263.089 | 763.9 | 43.8482 | 44.1761 | -0.32788 | 265.0563 | 44.1 | 43.5443 | 0.55567 | 0.9846 | 30-03-2026 12:40 | 253.782 | 258.509 | 757.5 | 43.0848 | 44.1761 | -1.0912 | 265.0563 | 43.5 | 43.5443 | -0.044333 | 0.98171 | 30-03-2026 12:40 | 258.777 | 263.265 | 759.5 | 43.8775 | 44.1761 | -0.29855 | 265.0563 | 43.3 | 43.5443 | -0.24433 | 0.98295 | 30-03-2026 12:40 | 260.433 | 267.57 | 764.5 | 44.595 | 44.1761 | 0.41895 | 265.0563 | 43.6 | 43.5443 | 0.055667 | 0.97333 | 30-03-2026 12:40 | 245.861 | 249.833 | 723.7 | 41.6388 | 42.028 | -0.38921 | 252.1682 | 41.1 | 41.427 | -0.32704 | 0.9841 | 30-03-2026 12:40 | 448.096 | 457.2829 | -9.1869 | 2743.6975 | 440.7 | 450.7438 | -10.0438 | -7.396
30-03-2026 12:30 | 983 | 52.52 | 326.959 | 332.546 | 968 | 55.4243 | 57.7006 | -2.2763 | 346.2037 | 57.1 | 56.8755 | 0.2245 | 0.9832 | 30-03-2026 12:30 | 336.216 | 342.205 | 971.4 | 57.0342 | 57.7006 | -0.66645 | 346.2037 | 55.2 | 56.8755 | -1.6755 | 0.9825 | 30-03-2026 12:30 | 328.294 | 337.899 | 956.1 | 56.3165 | 57.7006 | -1.3841 | 346.2037 | 55.7 | 56.8755 | -1.1755 | 0.97157 | 30-03-2026 12:30 | 333.747 | 339.657 | 964 | 56.6095 | 57.7006 | -1.0911 | 346.2037 | 55.6 | 56.8755 | -1.2755 | 0.9826 | 30-03-2026 12:30 | 247.177 | 251.145 | 719.8 | 41.8575 | 42.7412 | -0.8837 | 256.4472 | 42.3 | 42.13 | 0.17 | 0.9843 | 30-03-2026 12:30 | 244.848 | 249.611 | 714 | 41.6018 | 42.7412 | -1.1394 | 256.4472 | 41.6 | 42.13 | -0.53 | 0.98092 | 30-03-2026 12:30 | 245.976 | 251.24 | 716.2 | 41.8733 | 42.7412 | -0.86786 | 256.4472 | 42 | 42.13 | -0.13 | 0.97905 | 30-03-2026 12:30 | 247.86 | 255.209 | 720.9 | 42.5348 | 42.7412 | -0.20636 | 256.4472 | 43.4 | 42.13 | 1.27 | 0.9712 | 30-03-2026 12:30 | 234.494 | 238.21 | 682.6 | 39.7017 | 40.663 | -0.96129 | 243.9777 | 40.6 | 40.0815 | 0.51852 | 0.9844 | 30-03-2026 12:30 | 432.9537 | 442.4302 | -9.4766 | 2654.5813 | 433.5 | 436.1035 | -2.6035 | 0.54633
30-03-2026 12:20 | 955 | 52.23 | 318.983 | 324.4 | 910.9 | 54.0667 | 56.12 | -2.0534 | 336.7201 | 57.5 | 55.3175 | 2.1825 | 0.9833 | 30-03-2026 12:20 | 322.164 | 327.702 | 916.2 | 54.617 | 56.12 | -1.503 | 336.7201 | 58.3 | 55.3175 | 2.9825 | 0.9831 | 30-03-2026 12:20 | 314.18 | 322.912 | 900.4 | 53.8187 | 56.12 | -2.3014 | 336.7201 | 57.1 | 55.3175 | 1.7825 | 0.97296 | 30-03-2026 12:20 | 318.236 | 323.773 | 908.4 | 53.9622 | 56.12 | -2.1579 | 336.7201 | 56.8 | 55.3175 | 1.4825 | 0.9829 | 30-03-2026 12:20 | 236.73 | 240.433 | 677.5 | 40.0722 | 41.5704 | -1.4982 | 249.4223 | 43.9 | 40.9759 | 2.9241 | 0.9846 | 30-03-2026 12:20 | 234.281 | 238.721 | 672.4 | 39.7868 | 41.5704 | -1.7836 | 249.4223 | 43.3 | 40.9759 | 2.3241 | 0.9814 | 30-03-2026 12:20 | 238.633 | 239.5 | 674.2 | 39.9167 | 41.5704 | -1.6537 | 249.4223 | 43.5 | 40.9759 | 2.5241 | 0.99638 | 30-03-2026 12:20 | 239.382 | 246.736 | 677.5 | 41.1227 | 41.5704 | -0.44772 | 249.4223 | 42.6 | 40.9759 | 1.6241 | 0.97019 | 30-03-2026 12:20 | 225.995 | 229.483 | 642 | 38.2472 | 39.5491 | -1.3019 | 237.2944 | 40.7 | 38.9835 | 1.7165 | 0.9848 | 30-03-2026 12:20 | 415.61 | 430.3107 | -14.7007 | 2581.8643 | 443.7 | 424.1573 | 19.5427 | 28.09
30-03-2026 12:10 | 1046 | 52.52 | 351.4 | 356.263 | 853.4 | 59.3772 | 61.3986 | -2.0215 | 368.3917 | 57.7 | 60.5206 | -2.8206 | 0.98635 | 30-03-2026 12:10 | 350.688 | 356.608 | 857.9 | 59.4347 | 61.3986 | -1.964 | 368.3917 | 57.1 | 60.5206 | -3.4206 | 0.9834 | 30-03-2026 12:10 | 346.908 | 356.463 | 843.3 | 59.4105 | 61.3986 | -1.9881 | 368.3917 | 57 | 60.5206 | -3.5206 | 0.97319 | 30-03-2026 12:10 | 339.414 | 344.898 | 851.6 | 57.483 | 61.3986 | -3.9156 | 368.3917 | 58.3 | 60.5206 | -2.2206 | 0.9841 | 30-03-2026 12:10 | 262.834 | 267.026 | 633.6 | 44.5043 | 45.4805 | -0.97613 | 272.8828 | 43.2 | 44.8301 | -1.6301 | 0.9848 | 30-03-2026 12:10 | 259.709 | 264.728 | 629.1 | 44.1213 | 45.4805 | -1.3591 | 272.8828 | 42.7 | 44.8301 | -2.1301 | 0.98104 | 30-03-2026 12:10 | 260.775 | 265.936 | 630.7 | 44.3227 | 45.4805 | -1.1578 | 272.8828 | 43.4 | 44.8301 | -1.4301 | 0.98059 | 30-03-2026 12:10 | 262.215 | 270.072 | 634.9 | 45.012 | 45.4805 | -0.46846 | 272.8828 | 43.1 | 44.8301 | -1.7301 | 0.97091 | 30-03-2026 12:10 | 248.315 | 252.276 | 601.3 | 42.046 | 43.269 | -1.223 | 259.6142 | 40.8 | 42.6503 | -1.8503 | 0.9843 | 30-03-2026 12:10 | 455.7117 | 470.7854 | -15.0737 | 2824.7122 | 443.3 | 464.0531 | -20.7531 | -12.4117
30-03-2026 12:00 | 1035 | 52.23 | 349.372 | 355.342 | 795.7 | 59.2237 | 60.8212 | -1.5975 | 364.9271 | 54.8 | 59.9514 | -5.1514 | 0.9832 | 30-03-2026 12:00 | 352.47 | 358.475 | 800.8 | 59.7458 | 60.8212 | -1.0753 | 364.9271 | 56.8 | 59.9514 | -3.1514 | 0.98325 | 30-03-2026 12:00 | 346.472 | 356.231 | 786.3 | 59.3718 | 60.8212 | -1.4493 | 364.9271 | 53.7 | 59.9514 | -6.2514 | 0.9726 | 30-03-2026 12:00 | 349.897 | 356.021 | 793.3 | 59.3368 | 60.8212 | -1.4843 | 364.9271 | 53.3 | 59.9514 | -6.6514 | 0.9828 | 30-03-2026 12:00 | 261.458 | 265.547 | 590.4 | 44.2578 | 45.0527 | -0.79489 | 270.3163 | 39.8 | 44.4085 | -4.6085 | 0.9849 | 30-03-2026 12:00 | 258.815 | 263.482 | 586.4 | 43.9137 | 45.0527 | -1.1391 | 270.3163 | 39.4 | 44.4085 | -5.0085 | 0.98229 | 30-03-2026 12:00 | 259.512 | 264.189 | 587.3 | 44.0315 | 45.0527 | -1.0212 | 270.3163 | 39 | 44.4085 | -5.4085 | 0.9823 | 30-03-2026 12:00 | 261.237 | 268.957 | 591.8 | 44.8262 | 45.0527 | -0.22656 | 270.3163 | 39.8 | 44.4085 | -4.6085 | 0.9713 | 30-03-2026 12:00 | 247.157 | 251.048 | 560.5 | 41.8413 | 42.8621 | -1.0208 | 257.1725 | 37.6 | 42.2492 | -4.6492 | 0.9845 | 30-03-2026 12:00 | 456.5487 | 466.3577 | -9.809 | 2798.1461 | 414.2 | 459.6888 | -45.4888 | -42.3487
30-03-2026 11:50 | 959 | 51.95 | 323.737 | 330.286 | 740.9 | 55.0477 | 56.4161 | -1.3685 | 338.4968 | 53.1 | 55.6094 | -2.5094 | 0.98017 | 30-03-2026 11:50 | 326.943 | 332.563 | 744 | 55.4272 | 56.4161 | -0.98896 | 338.4968 | 50.8 | 55.6094 | -4.8094 | 0.9831 | 30-03-2026 11:50 | 321.198 | 330.17 | 732.6 | 55.0283 | 56.4161 | -1.3878 | 338.4968 | 51.9 | 55.6094 | -3.7094 | 0.97283 | 30-03-2026 11:50 | 325.71 | 331.309 | 740 | 55.2182 | 56.4161 | -1.198 | 338.4968 | 52.4 | 55.6094 | -3.2094 | 0.9831 | 30-03-2026 11:50 | 243.233 | 246.987 | 550.6 | 41.1645 | 41.7897 | -0.62522 | 250.7383 | 39.2 | 41.1921 | -1.9921 | 0.9848 | 30-03-2026 11:50 | 240.818 | 245.004 | 547 | 40.834 | 41.7897 | -0.95572 | 250.7383 | 39.4 | 41.1921 | -1.7921 | 0.98291 | 30-03-2026 11:50 | 241.502 | 246.01 | 548.3 | 41.0017 | 41.7897 | -0.78806 | 250.7383 | 39.5 | 41.1921 | -1.6921 | 0.98168 | 30-03-2026 11:50 | 243.181 | 250.147 | 552 | 41.6912 | 41.7897 | -0.098556 | 250.7383 | 39.8 | 41.1921 | -1.3921 | 0.97215 | 30-03-2026 11:50 | 230.187 | 233.74 | 522.9 | 38.9567 | 39.7577 | -0.80108 | 238.5465 | 37.7 | 39.1892 | -1.4892 | 0.9848 | 30-03-2026 11:50 | 424.3693 | 432.5811 | -8.2118 | 2595.4868 | 403.8 | 426.3952 | -22.5952 | -20.5693
30-03-2026 11:40 | 922 | 52.81 | 321.205 | 326.527 | 687.8 | 54.4212 | 54.0592 | 0.36194 | 324.3553 | 53.5 | 53.2862 | 0.21382 | 0.9837 | 30-03-2026 11:40 | 317.184 | 322.473 | 693.2 | 53.7455 | 54.0592 | -0.31372 | 324.3553 | 56.3 | 53.2862 | 3.0138 | 0.9836 | 30-03-2026 11:40 | 311.311 | 320.058 | 680.7 | 53.343 | 54.0592 | -0.71622 | 324.3553 | 54.3 | 53.2862 | 1.0138 | 0.97267 | 30-03-2026 11:40 | 315.036 | 320.354 | 687.6 | 53.3923 | 54.0592 | -0.66689 | 324.3553 | 55.1 | 53.2862 | 1.8138 | 0.9834 | 30-03-2026 11:40 | 233.505 | 237.085 | 511.4 | 39.5142 | 40.0439 | -0.5297 | 240.2632 | 41.1 | 39.4712 | 1.6288 | 0.985 | 30-03-2026 11:40 | 231.663 | 236.03 | 507.6 | 39.3383 | 40.0439 | -0.70554 | 240.2632 | 40.1 | 39.4712 | 0.62876 | 0.9815 | 30-03-2026 11:40 | 232.499 | 237.006 | 508.8 | 39.501 | 40.0439 | -0.54287 | 240.2632 | 40.2 | 39.4712 | 0.72876 | 0.98098 | 30-03-2026 11:40 | 234.748 | 241.431 | 512.2 | 40.2385 | 40.0439 | 0.19463 | 240.2632 | 40.5 | 39.4712 | 1.0288 | 0.97232 | 30-03-2026 11:40 | 222.03 | 225.388 | 485.2 | 37.5647 | 38.0968 | -0.53211 | 228.5807 | 38.9 | 37.552 | 1.348 | 0.9851 | 30-03-2026 11:40 | 411.0587 | 414.5091 | -3.4505 | 2487.0549 | 420 | 408.5817 | 11.4183 | 8.9413
30-03-2026 11:30 | 941 | 53.09 | 318.641 | 324.572 | 634.3 | 54.0953 | 55.1133 | -1.018 | 330.68 | 55.2 | 54.3252 | 0.87478 | 0.98173 | 30-03-2026 11:30 | 330.264 | 335.873 | 636.9 | 55.9788 | 55.1133 | 0.86549 | 330.68 | 54.8 | 54.3252 | 0.47478 | 0.9833 | 30-03-2026 11:30 | 323.069 | 332.856 | 626.4 | 55.476 | 55.1133 | 0.36266 | 330.68 | 53.9 | 54.3252 | -0.42522 | 0.9706 | 30-03-2026 11:30 | 321.423 | 326.915 | 632.5 | 54.4858 | 55.1133 | -0.62751 | 330.68 | 54.4 | 54.3252 | 0.074779 | 0.9832 | 30-03-2026 11:30 | 247.925 | 251.752 | 470.3 | 41.9587 | 40.8247 | 1.134 | 244.9482 | 40.7 | 40.2409 | 0.4591 | 0.9853 | 30-03-2026 11:30 | 243.065 | 248.051 | 467.5 | 41.3418 | 40.8247 | 0.51714 | 244.9482 | 40.3 | 40.2409 | 0.059096 | 0.9799 | 30-03-2026 11:30 | 247.887 | 252.796 | 468.6 | 42.1327 | 40.8247 | 1.308 | 244.9482 | 40.9 | 40.2409 | 0.6591 | 0.98058 | 30-03-2026 11:30 | 244.736 | 257.759 | 471.7 | 42.9598 | 40.8247 | 2.1351 | 244.9482 | 41.2 | 40.2409 | 0.9591 | 0.94948 | 30-03-2026 11:30 | 229.738 | 233.26 | 446.3 | 38.8767 | 38.8396 | 0.037023 | 233.0379 | 38.4 | 38.2842 | 0.11576 | 0.9849 | 30-03-2026 11:30 | 427.3057 | 422.5918 | 4.7139 | 2535.5508 | 419.8 | 416.5487 | 3.2513 | -7.5057
30-03-2026 11:20 | 966 | 52.81 | 329.767 | 336.282 | 579.1 | 56.047 | 56.6391 | -0.59206 | 339.8343 | 52.3 | 55.8291 | -3.5291 | 0.98063 | 30-03-2026 11:20 | 333.306 | 338.967 | 582.1 | 56.4945 | 56.6391 | -0.14456 | 339.8343 | 52.8 | 55.8291 | -3.0291 | 0.9833 | 30-03-2026 11:20 | 326.979 | 335.805 | 572.5 | 55.9675 | 56.6391 | -0.67156 | 339.8343 | 52.4 | 55.8291 | -3.4291 | 0.97372 | 30-03-2026 11:20 | 331.175 | 337.019 | 578.1 | 56.1698 | 56.6391 | -0.46922 | 339.8343 | 53.1 | 55.8291 | -2.7291 | 0.98266 | 30-03-2026 11:20 | 247.783 | 251.556 | 429.6 | 41.926 | 41.9549 | -0.028856 | 251.7291 | 39.6 | 41.3549 | -1.7549 | 0.985 | 30-03-2026 11:20 | 245.303 | 249.927 | 427.2 | 41.6545 | 41.9549 | -0.30036 | 251.7291 | 39.4 | 41.3549 | -1.9549 | 0.9815 | 30-03-2026 11:20 | 246.925 | 251.569 | 427.7 | 41.9282 | 41.9549 | -0.026689 | 251.7291 | 39 | 41.3549 | -2.3549 | 0.98154 | 30-03-2026 11:20 | 248.341 | 255.928 | 430.5 | 42.6547 | 41.9549 | 0.69981 | 251.7291 | 39.2 | 41.3549 | -2.1549 | 0.97035 | 30-03-2026 11:20 | 234.98 | 238.583 | 407.9 | 39.7638 | 39.9148 | -0.15102 | 239.4891 | 37.8 | 39.3441 | -1.5441 | 0.9849 | 30-03-2026 11:20 | 432.606 | 434.2905 | -1.6845 | 2605.743 | 405.6 | 428.0801 | -22.4801 | -27.006
30-03-2026 11:10 | 865 | 51.37 | 306.542 | 304.474 | 526.8 | 50.7457 | 51.0003 | -0.25468 | 306.0021 | 50.3 | 50.271 | 0.028961 | 1.0068 | 30-03-2026 11:10 | 309.114 | 314.268 | 529.3 | 52.378 | 51.0003 | 1.3777 | 306.0021 | 53.8 | 50.271 | 3.529 | 0.9836 | 30-03-2026 11:10 | 298.05 | 305.553 | 520.1 | 50.9255 | 51.0003 | -0.074844 | 306.0021 | 50.6 | 50.271 | 0.32896 | 0.97544 | 30-03-2026 11:10 | 299.319 | 305.155 | 525 | 50.8592 | 51.0003 | -0.14118 | 306.0021 | 51.1 | 50.271 | 0.82896 | 0.98088 | 30-03-2026 11:10 | 225.308 | 228.669 | 390 | 38.1115 | 37.778 | 0.33347 | 226.6682 | 38.1 | 37.2378 | 0.86219 | 0.9853 | 30-03-2026 11:10 | 222.938 | 226.753 | 387.8 | 37.7922 | 37.778 | 0.014134 | 226.6682 | 37.9 | 37.2378 | 0.66219 | 0.98318 | 30-03-2026 11:10 | 224.504 | 227.807 | 388.7 | 37.9678 | 37.778 | 0.1898 | 226.6682 | 37.9 | 37.2378 | 0.66219 | 0.9855 | 30-03-2026 11:10 | 226.046 | 232.279 | 391.3 | 38.7132 | 37.778 | 0.93513 | 226.6682 | 38.3 | 37.2378 | 1.0622 | 0.97317 | 30-03-2026 11:10 | 215.219 | 218.43 | 370.1 | 36.405 | 35.9411 | 0.46388 | 215.6467 | 35.6 | 35.4272 | 0.17284 | 0.9853 | 30-03-2026 11:10 | 393.898 | 391.0546 | 2.8434 | 2346.3278 | 393.6 | 385.4625 | 8.1375 | -0.298
30-03-2026 11:00 | 956 | 50.8 | 328.868 | 334.317 | 476.5 | 55.7195 | 56.4896 | -0.77008 | 338.9375 | 54.1 | 55.6818 | -1.5818 | 0.9837 | 30-03-2026 11:00 | 328.418 | 333.962 | 475.5 | 55.6603 | 56.4896 | -0.82925 | 338.9375 | 50.9 | 55.6818 | -4.7818 | 0.9834 | 30-03-2026 11:00 | 323.962 | 332.931 | 469.5 | 55.4885 | 56.4896 | -1.0011 | 338.9375 | 52.1 | 55.6818 | -3.5818 | 0.97306 | 30-03-2026 11:00 | 327.365 | 332.783 | 473.9 | 55.4638 | 56.4896 | -1.0257 | 338.9375 | 52.6 | 55.6818 | -3.0818 | 0.98372 | 30-03-2026 11:00 | 244.665 | 248.391 | 351.9 | 41.3985 | 41.8441 | -0.44563 | 251.0648 | 39.3 | 41.2458 | -1.9458 | 0.97105 | 30-03-2026 11:00 | 243.41 | 247.883 | 349.9 | 41.3138 | 41.8441 | -0.5303 | 251.0648 | 39.5 | 41.2458 | -1.7458 | 0.98196 | 30-03-2026 11:00 | 243.378 | 248.091 | 350.8 | 41.3485 | 41.8441 | -0.49563 | 251.0648 | 39.8 | 41.2458 | -1.4458 | 0.981 | 30-03-2026 11:00 | 244.962 | 252.38 | 353 | 42.0633 | 41.8441 | 0.2192 | 251.0648 | 40 | 41.2458 | -1.2458 | 0.97061 | 30-03-2026 11:00 | 232.745 | 236.289 | 334.5 | 39.3815 | 39.8095 | -0.42801 | 238.8571 | 37.9 | 39.2402 | -1.3402 | 0.985 | 30-03-2026 11:00 | 427.8378 | 433.1444 | -5.3065 | 2598.8663 | 406.2 | 426.9504 | -20.7504 | -21.6378
30-03-2026 10:50 | 917 | 52.81 | 318.188 | 323.362 | 422.4 | 53.8937 | 53.7661 | 0.12761 | 322.5964 | 53.5 | 52.9972 | 0.50279 | 0.984 | 30-03-2026 10:50 | 320.841 | 324.992 | 424.6 | 54.1653 | 53.7661 | 0.39927 | 322.5964 | 53.2 | 52.9972 | 0.20279 | 0.98723 | 30-03-2026 10:50 | 313.737 | 321.846 | 417.4 | 53.641 | 53.7661 | -0.12506 | 322.5964 | 51.3 | 52.9972 | -1.6972 | 0.9748 | 30-03-2026 10:50 | 317.759 | 323.057 | 421.3 | 53.8428 | 53.7661 | 0.076773 | 322.5964 | 52.2 | 52.9972 | -0.79721 | 0.9836 | 30-03-2026 10:50 | 237.686 | 241.232 | 312.6 | 40.2053 | 39.8267 | 0.37862 | 238.9603 | 38.6 | 39.2572 | -0.65719 | 0.98534 | 30-03-2026 10:50 | 236.247 | 240.191 | 310.4 | 40.0318 | 39.8267 | 0.20512 | 238.9603 | 38 | 39.2572 | -1.2572 | 0.98358 | 30-03-2026 10:50 | 236.757 | 241.039 | 311 | 40.1732 | 39.8267 | 0.34646 | 238.9603 | 38 | 39.2572 | -1.2572 | 0.98224 | 30-03-2026 10:50 | 238.654 | 245.743 | 313 | 40.9572 | 39.8267 | 1.1305 | 238.9603 | 38.3 | 39.2572 | -0.95719 | 0.97115 | 30-03-2026 10:50 | 225.979 | 229.416 | 296.6 | 38.236 | 37.8902 | 0.34582 | 227.3411 | 36.5 | 37.3484 | -0.84835 | 0.98502 | 30-03-2026 10:50 | 415.1463 | 412.2613 | 2.8851 | 2473.5676 | 399.6 | 406.3659 | -6.7659 | -15.5463
30-03-2026 10:40 | 810 | 53.38 | 325.228 | 330.583 | 368.9 | 55.0972 | 47.3874 | 7.7098 | 284.3245 | 48.6 | 46.7098 | 1.8902 | 0.9838 | 30-03-2026 10:40 | 327.392 | 336.548 | 371.4 | 56.0913 | 47.3874 | 8.7039 | 284.3245 | 53.1 | 46.7098 | 6.3902 | 0.97279 | 30-03-2026 10:40 | 242.902 | 249.035 | 366.1 | 41.5058 | 47.3874 | -5.8816 | 284.3245 | 50.5 | 46.7098 | 3.7902 | 0.97537 | 30-03-2026 10:40 | 263.097 | 267.212 | 369.1 | 44.5353 | 47.3874 | -2.8521 | 284.3245 | 51.2 | 46.7098 | 4.4902 | 0.9846 | 30-03-2026 10:40 | 169.79 | 174.852 | 274 | 29.142 | 35.1018 | -5.9598 | 210.6107 | 37.7 | 34.5998 | 3.1002 | 0.9861 | 30-03-2026 10:40 | 197.1 | 199.838 | 272.4 | 33.3063 | 35.1018 | -1.7955 | 210.6107 | 37.8 | 34.5998 | 3.2002 | 0.9863 | 30-03-2026 10:40 | 156.97 | 159.917 | 273 | 26.6528 | 35.1018 | -8.449 | 210.6107 | 37.2 | 34.5998 | 2.6002 | 0.98157 | 30-03-2026 10:40 | 146.879 | 153.979 | 274.7 | 25.6632 | 35.1018 | -9.4386 | 210.6107 | 37.4 | 34.5998 | 2.8002 | 0.95389 | 30-03-2026 10:40 | 154.656 | 156.757 | 260.1 | 26.1262 | 33.395 | -7.2688 | 200.37 | 35.7 | 32.9175 | 2.7825 | 0.9866 | 30-03-2026 10:40 | 338.1202 | 363.3518 | -25.2316 | 2180.1108 | 389.2 | 358.1559 | 31.0441 | 51.0798
30-03-2026 10:30 | 885 | 53.96 | 309.743 | 314.684 | 320.3 | 52.4473 | 51.6584 | 0.78889 | 309.9506 | 50.9 | 50.9197 | -0.019725 | 0.9843 | 30-03-2026 10:30 | 311.81 | 316.88 | 318.3 | 52.8133 | 51.6584 | 1.1549 | 309.9506 | 49.2 | 50.9197 | -1.7197 | 0.984 | 30-03-2026 10:30 | 305.239 | 313.393 | 315.6 | 52.2322 | 51.6584 | 0.57373 | 309.9506 | 49.7 | 50.9197 | -1.2197 | 0.97398 | 30-03-2026 10:30 | 309.445 | 314.509 | 317.9 | 52.4182 | 51.6584 | 0.75973 | 309.9506 | 50.2 | 50.9197 | -0.71972 | 0.9839 | 30-03-2026 10:30 | 229.555 | 232.971 | 236.3 | 38.8285 | 38.2655 | 0.56299 | 229.5931 | 37.4 | 37.7183 | -0.31831 | 0.9861 | 30-03-2026 10:30 | 229.168 | 232.97 | 234.6 | 38.8283 | 38.2655 | 0.56282 | 229.5931 | 37.2 | 37.7183 | -0.51831 | 0.98368 | 30-03-2026 10:30 | 228.896 | 232.699 | 235.8 | 38.7832 | 38.2655 | 0.51766 | 229.5931 | 37.3 | 37.7183 | -0.41831 | 0.98366 | 30-03-2026 10:30 | 230.625 | 237.437 | 237.3 | 39.5728 | 38.2655 | 1.3073 | 229.5931 | 37.6 | 37.7183 | -0.11831 | 0.97131 | 30-03-2026 10:30 | 218.849 | 222.024 | 224.4 | 37.004 | 36.4049 | 0.59911 | 218.4294 | 36.1 | 35.8843 | 0.2157 | 0.9857 | 30-03-2026 10:30 | 402.9278 | 396.1007 | 6.8271 | 2376.6042 | 385.6 | 390.4365 | -4.8365 | -17.3278
30-03-2026 10:20 | 820 | 53.09 | 289.372 | 293.809 | 269.4 | 48.9682 | 48.0265 | 0.94166 | 288.159 | 46.6 | 47.3397 | -0.73972 | 0.9849 | 30-03-2026 10:20 | 286.48 | 290.961 | 269.1 | 48.4935 | 48.0265 | 0.467 | 288.159 | 46.8 | 47.3397 | -0.53972 | 0.9846 | 30-03-2026 10:20 | 285.306 | 291.976 | 265.9 | 48.6627 | 48.0265 | 0.63616 | 288.159 | 46.4 | 47.3397 | -0.93972 | 0.97716 | 30-03-2026 10:20 | 288.671 | 292.777 | 267.7 | 48.7962 | 48.0265 | 0.76966 | 288.159 | 47.2 | 47.3397 | -0.13972 | 0.98598 | 30-03-2026 10:20 | 212.948 | 215.95 | 198.9 | 35.9917 | 35.5752 | 0.41648 | 213.4511 | 34.7 | 35.0665 | -0.36646 | 0.97982 | 30-03-2026 10:20 | 213.664 | 216.698 | 197.4 | 36.1163 | 35.5752 | 0.54115 | 213.4511 | 34.9 | 35.0665 | -0.16646 | 0.986 | 30-03-2026 10:20 | 211.68 | 214.664 | 198.5 | 35.7773 | 35.5752 | 0.20215 | 213.4511 | 34.6 | 35.0665 | -0.46646 | 0.9861 | 30-03-2026 10:20 | 212.682 | 218.226 | 199.7 | 36.371 | 35.5752 | 0.79581 | 213.4511 | 34.9 | 35.0665 | -0.16646 | 0.9746 | 30-03-2026 10:20 | 204.743 | 207.629 | 188.3 | 34.6048 | 33.8454 | 0.75945 | 203.0723 | 32.8 | 33.3614 | -0.5614 | 0.9861 | 30-03-2026 10:20 | 373.7817 | 368.2522 | 5.5295 | 2209.5129 | 358.9 | 362.9861 | -4.0861 | -14.8817
30-03-2026 10:10 | 869 | 52.81 | 308.16 | 312.885 | 222.8 | 52.1475 | 50.9517 | 1.1958 | 305.7102 | 51 | 50.2231 | 0.77691 | 0.9849 | 30-03-2026 10:10 | 308.466 | 313.291 | 222.3 | 52.2152 | 50.9517 | 1.2635 | 305.7102 | 48.9 | 50.2231 | -1.3231 | 0.9846 | 30-03-2026 10:10 | 303.153 | 310.85 | 219.5 | 51.8083 | 50.9517 | 0.85664 | 305.7102 | 47.8 | 50.2231 | -2.4231 | 0.97524 | 30-03-2026 10:10 | 306.407 | 311.199 | 220.5 | 51.8665 | 50.9517 | 0.9148 | 305.7102 | 48.3 | 50.2231 | -1.9231 | 0.9846 | 30-03-2026 10:10 | 228.044 | 231.259 | 164.2 | 38.5432 | 37.742 | 0.80117 | 226.452 | 35.9 | 37.2023 | -1.3023 | 0.98449 | 30-03-2026 10:10 | 227.757 | 231.087 | 162.5 | 38.5145 | 37.742 | 0.7725 | 226.452 | 35.8 | 37.2023 | -1.4023 | 0.98559 | 30-03-2026 10:10 | 226.47 | 229.948 | 163.9 | 38.3247 | 37.742 | 0.58267 | 226.452 | 35.9 | 37.2023 | -1.3023 | 0.98487 | 30-03-2026 10:10 | 228.481 | 234.853 | 164.8 | 39.1422 | 37.742 | 1.4002 | 226.452 | 36.2 | 37.2023 | -1.0023 | 0.97287 | 30-03-2026 10:10 | 216.537 | 219.589 | 155.5 | 36.5982 | 35.9068 | 0.69133 | 215.441 | 34.3 | 35.3934 | -1.0934 | 0.9861 | 30-03-2026 10:10 | 399.1602 | 390.6816 | 8.4786 | 2344.0897 | 374.1 | 385.0949 | -10.9949 | -25.0602
30-03-2026 10:00 | 480 | 40.18 | 234.632 | 237.626 | 171.8 | 39.6043 | 29.5219 | 10.0825 | 177.1312 | 21.9 | 29.0997 | -7.1997 | 0.9874 | 30-03-2026 10:00 | 166.169 | 168.963 | 173.4 | 28.1605 | 29.5219 | -1.3614 | 177.1312 | 23.6 | 29.0997 | -5.4997 | 0.98346 | 30-03-2026 10:00 | 162.574 | 166.364 | 171.7 | 27.7273 | 29.5219 | -1.7945 | 177.1312 | 23.6 | 29.0997 | -5.4997 | 0.97722 | 30-03-2026 10:00 | 164.851 | 166.103 | 172.2 | 27.6838 | 29.5219 | -1.838 | 177.1312 | 23.7 | 29.0997 | -5.3997 | 0.99246 | 30-03-2026 10:00 | 127.627 | 130.256 | 128.3 | 21.7093 | 21.8681 | -0.15872 | 131.2083 | 18 | 21.5553 | -3.5553 | 0.9784 | 30-03-2026 10:00 | 120.473 | 121.924 | 126.7 | 20.3207 | 21.8681 | -1.5474 | 131.2083 | 17.8 | 21.5553 | -3.7553 | 0.9881 | 30-03-2026 10:00 | 133.326 | 138.998 | 128 | 23.1663 | 21.8681 | 1.2983 | 131.2083 | 18.1 | 21.5553 | -3.4553 | 0.95919 | 30-03-2026 10:00 | 133.088 | 138.699 | 128.6 | 23.1165 | 21.8681 | 1.2484 | 131.2083 | 18.2 | 21.5553 | -3.3553 | 0.95955 | 30-03-2026 10:00 | 135.303 | 136.905 | 121.2 | 22.8175 | 20.8047 | 2.0128 | 124.8285 | 17.3 | 20.5072 | -3.2072 | 0.9883 | 30-03-2026 10:00 | 234.3063 | 226.3644 | 7.9419 | 1358.1866 | 182.2 | 223.1274 | -40.9274 | -52.1063
30-03-2026 09:50 | 148 | 33.58 | 58.642 | 59.356 | 149.9 | 9.8927 | 9.3246 | 0.56802 | 55.9479 | 7.4 | 9.1913 | -1.7913 |  | 30-03-2026 09:50 | 59.674 | 60.503 | 149.8 | 10.0838 | 9.3246 | 0.75919 | 55.9479 | 7.5 | 9.1913 | -1.6913 |  | 30-03-2026 09:50 | 59.118 | 59.945 | 148.1 | 9.9908 | 9.3246 | 0.66619 | 55.9479 | 7.4 | 9.1913 | -1.7913 |  | 30-03-2026 09:50 | 59.227 | 60.056 | 148.5 | 10.0093 | 9.3246 | 0.68469 | 55.9479 | 7.5 | 9.1913 | -1.6913 |  | 30-03-2026 09:50 | 43.933 | 44.625 | 110.3 | 7.4375 | 6.9071 | 0.53036 | 41.4429 | 5.6 | 6.8084 | -1.2084 |  | 30-03-2026 09:50 | 43.592 | 44.278 | 108.9 | 7.3797 | 6.9071 | 0.47252 | 41.4429 | 5.5 | 6.8084 | -1.3084 |  | 30-03-2026 09:50 | 43.665 | 44.352 | 109.9 | 7.392 | 6.9071 | 0.48486 | 41.4429 | 5.5 | 6.8084 | -1.3084 |  | 30-03-2026 09:50 | 43.679 | 45.024 | 110.4 | 7.504 | 6.9071 | 0.59686 | 41.4429 | 5.6 | 6.8084 | -1.2084 |  | 30-03-2026 09:50 | 41.02 | 41.691 | 103.9 | 6.9485 | 6.5713 | 0.37721 | 39.4278 | 5.2 | 6.4773 | -1.2773 |  | 30-03-2026 09:50 | 76.6383 | 71.4984 | 5.1399 | 428.9907 | 57.2 | 70.476 | -13.276 | -19.4383
30-03-2026 09:40 | 81 | 41.61 | 34.269 | 34.886 | 142.5 | 5.8143 | 4.9555 | 0.85885 | 29.7329 | 7.2 | 4.8846 | 2.3154 |  | 30-03-2026 09:40 | 34.297 | 34.934 | 142.3 | 5.8223 | 4.9555 | 0.86685 | 29.7329 | 7.9 | 4.8846 | 3.0154 |  | 30-03-2026 09:40 | 33.932 | 34.55 | 140.7 | 5.7583 | 4.9555 | 0.80285 | 29.7329 | 7 | 4.8846 | 2.1154 |  | 30-03-2026 09:40 | 34.056 | 34.684 | 141 | 5.7807 | 4.9555 | 0.82518 | 29.7329 | 7 | 4.8846 | 2.1154 |  | 30-03-2026 09:40 | 24.963 | 25.514 | 104.7 | 4.2523 | 3.6707 | 0.58161 | 22.0244 | 5.2 | 3.6182 | 1.5818 |  | 30-03-2026 09:40 | 24.929 | 25.461 | 103.4 | 4.2435 | 3.6707 | 0.57277 | 22.0244 | 5.2 | 3.6182 | 1.5818 |  | 30-03-2026 09:40 | 24.804 | 25.346 | 104.4 | 4.2243 | 3.6707 | 0.55361 | 22.0244 | 5.2 | 3.6182 | 1.5818 |  | 30-03-2026 09:40 | 24.957 | 26.036 | 104.8 | 4.3393 | 3.6707 | 0.66861 | 22.0244 | 5.2 | 3.6182 | 1.5818 |  | 30-03-2026 09:40 | 23.627 | 24.154 | 98.7 | 4.0257 | 3.4922 | 0.53342 | 20.9535 | 4.9 | 3.4423 | 1.4577 |  | 30-03-2026 09:40 | 44.2608 | 37.9971 | 6.2637 | 227.9825 | 54.8 | 37.4537 | 17.3463 | 10.5392
30-03-2026 09:30 | 194 | 49.08 | 82.622 | 77.721 | 135.3 | 12.9535 | 11.5392 | 1.4143 | 69.2354 | 17.2 | 11.3742 | 5.8258 |  | 30-03-2026 09:30 | 83.367 | 84.448 | 134.4 | 14.0747 | 11.5392 | 2.5354 | 69.2354 | 18.1 | 11.3742 | 6.7258 |  | 30-03-2026 09:30 | 73.951 | 74.955 | 133.7 | 12.4925 | 11.5392 | 0.95327 | 69.2354 | 16.1 | 11.3742 | 4.7258 |  | 30-03-2026 09:30 | 75.48 | 76.497 | 134 | 12.7495 | 11.5392 | 1.2103 | 69.2354 | 16.5 | 11.3742 | 5.1258 |  | 30-03-2026 09:30 | 55.93 | 56.916 | 99.5 | 9.486 | 8.5476 | 0.93842 | 51.2855 | 11.9 | 8.4253 | 3.4747 |  | 30-03-2026 09:30 | 56.585 | 57.429 | 98.2 | 9.5715 | 8.5476 | 1.0239 | 51.2855 | 12.3 | 8.4253 | 3.8747 |  | 30-03-2026 09:30 | 55.717 | 56.525 | 99.2 | 9.4208 | 8.5476 | 0.87326 | 51.2855 | 12.2 | 8.4253 | 3.7747 |  | 30-03-2026 09:30 | 56.178 | 57.852 | 99.6 | 9.642 | 8.5476 | 1.0944 | 51.2855 | 12.8 | 8.4253 | 4.3747 |  | 30-03-2026 09:30 | 53.703 | 54.532 | 93.8 | 9.0887 | 8.132 | 0.95671 | 48.7918 | 11.8 | 8.0157 | 3.7843 |  | 30-03-2026 09:30 | 99.4792 | 88.4792 | 11 | 530.875 | 128.9 | 87.2139 | 41.6861 | 29.4208
30-03-2026 09:20 | 694 | 49.94 | 273.084 | 276.877 | 118.1 | 46.1462 | 41.1438 | 5.0024 | 246.8629 | 21 | 40.5555 | -19.5555 |  | 30-03-2026 09:20 | 273.414 | 142.231 | 116.3 | 23.7052 | 41.1438 | -17.4386 | 246.8629 | 19.8 | 40.5555 | -20.7555 |  | 30-03-2026 09:20 | 244.596 | 247.868 | 117.6 | 41.3113 | 41.1438 | 0.16752 | 246.8629 | 22.1 | 40.5555 | -18.4555 |  | 30-03-2026 09:20 | 262.316 | 265.96 | 117.5 | 44.3267 | 41.1438 | 3.1829 | 246.8629 | 21.8 | 40.5555 | -18.7555 |  | 30-03-2026 09:20 | 180.453 | 182.682 | 87.6 | 30.447 | 30.4769 | -0.0299 | 182.8614 | 16.8 | 30.0411 | -13.2411 |  | 30-03-2026 09:20 | 196.269 | 198.774 | 85.9 | 33.129 | 30.4769 | 2.6521 | 182.8614 | 16.4 | 30.0411 | -13.6411 |  | 30-03-2026 09:20 | 195.966 | 198.487 | 87 | 33.0812 | 30.4769 | 2.6043 | 182.8614 | 16.9 | 30.0411 | -13.1411 |  | 30-03-2026 09:20 | 201.572 | 207.264 | 86.8 | 34.544 | 30.4769 | 4.0671 | 182.8614 | 16.5 | 30.0411 | -13.5411 |  | 30-03-2026 09:20 | 191.075 | 193.494 | 82 | 32.249 | 28.995 | 3.254 | 173.97 | 15.7 | 28.5804 | -12.8804 |  | 30-03-2026 09:20 | 318.9395 | 315.4779 | 3.4616 | 1892.8671 | 167 | 310.9665 | -143.9665 | -151.9395
30-03-2026 09:10 | 275 | 50.23 | 99.708 | 100.95 | 97.1 | 16.825 | 16.2853 | 0.53975 | 97.7115 | 26.5 | 16.0524 | 10.4476 |  | 30-03-2026 09:10 | 100.237 | 101.516 | 96.5 | 16.9193 | 16.2853 | 0.63408 | 97.7115 | 26.1 | 16.0524 | 10.0476 |  | 30-03-2026 09:10 | 98.7 | 100.118 | 95.5 | 16.6863 | 16.2853 | 0.40108 | 97.7115 | 26.4 | 16.0524 | 10.3476 |  | 30-03-2026 09:10 | 99.335 | 100.592 | 95.7 | 16.7653 | 16.2853 | 0.48008 | 97.7115 | 26.5 | 16.0524 | 10.4476 |  | 30-03-2026 09:10 | 73.739 | 74.703 | 70.8 | 12.4505 | 12.0632 | 0.38735 | 72.3789 | 19.4 | 11.8906 | 7.5094 |  | 30-03-2026 09:10 | 73.806 | 74.843 | 69.5 | 12.4738 | 12.0632 | 0.41068 | 72.3789 | 19.2 | 11.8906 | 7.3094 |  | 30-03-2026 09:10 | 73.939 | 74.92 | 70.1 | 12.4867 | 12.0632 | 0.42352 | 72.3789 | 19 | 11.8906 | 7.1094 |  | 30-03-2026 09:10 | 74.353 | 76.66 | 70.3 | 12.7767 | 12.0632 | 0.71352 | 72.3789 | 18.9 | 11.8906 | 7.0094 |  | 30-03-2026 09:10 | 70.447 | 71.411 | 66.3 | 11.9018 | 11.4766 | 0.42524 | 68.8596 | 18.1 | 11.3125 | 6.7875 |  | 30-03-2026 09:10 | 129.2855 | 124.8702 | 4.4153 | 749.2213 | 200.1 | 123.0846 | 77.0154 | 70.8145
30-03-2026 09:00 | 525 | 50.8 | 145.627 | 150.313 | 70.6 | 25.0522 | 31.022 | -5.9698 | 186.132 | 27.4 | 30.5784 | -3.1784 |  | 30-03-2026 09:00 | 190.271 | 192.719 | 70.4 | 32.1198 | 31.022 | 1.0978 | 186.132 | 26.9 | 30.5784 | -3.6784 |  | 30-03-2026 09:00 | 209.907 | 213.618 | 69.1 | 35.603 | 31.022 | 4.581 | 186.132 | 26.3 | 30.5784 | -4.2784 |  | 30-03-2026 09:00 | 177.204 | 188.122 | 69.2 | 31.3537 | 31.022 | 0.33167 | 186.132 | 26.2 | 30.5784 | -4.3784 |  | 30-03-2026 09:00 | 160.779 | 162.748 | 51.4 | 27.1247 | 22.9793 | 4.1454 | 137.8755 | 19.7 | 22.6507 | -2.9507 |  | 30-03-2026 09:00 | 148.94 | 153.283 | 50.3 | 25.5472 | 22.9793 | 2.5679 | 137.8755 | 19.4 | 22.6507 | -3.2507 |  | 30-03-2026 09:00 | 161.06 | 163.033 | 51.1 | 27.1722 | 22.9793 | 4.1929 | 137.8755 | 19.6 | 22.6507 | -3.0507 |  | 30-03-2026 09:00 | 156.921 | 163.168 | 51.4 | 27.1947 | 22.9793 | 4.2154 | 137.8755 | 19.7 | 22.6507 | -2.9507 |  | 30-03-2026 09:00 | 150.277 | 152.118 | 48.2 | 25.353 | 21.8619 | 3.4911 | 131.1715 | 18.5 | 21.5493 | -3.0493 |  | 30-03-2026 09:00 | 256.5203 | 237.8669 | 18.6534 | 1427.2017 | 203.7 | 234.4654 | -30.7654 | -52.8203
30-03-2026 08:50 | 318 | 47.93 | 83.07 | 84.147 | 43.2 | 14.0245 | 18.998 | -4.9735 | 113.9877 | 14.9 | 18.7263 | -3.8263 |  | 30-03-2026 08:50 | 122.439 | 123.926 | 43.5 | 20.6543 | 18.998 | 1.6564 | 113.9877 | 15 | 18.7263 | -3.7263 |  | 30-03-2026 08:50 | 109.971 | 111.329 | 42.8 | 18.5548 | 18.998 | -0.44312 | 113.9877 | 14.7 | 18.7263 | -4.0263 |  | 30-03-2026 08:50 | 117.581 | 119.021 | 43 | 19.8368 | 18.998 | 0.83888 | 113.9877 | 14.6 | 18.7263 | -4.1263 |  | 30-03-2026 08:50 | 78.332 | 79.332 | 31.7 | 13.222 | 14.0726 | -0.85056 | 84.4354 | 11 | 13.8713 | -2.8713 |  | 30-03-2026 08:50 | 80.517 | 81.536 | 30.9 | 13.5893 | 14.0726 | -0.48323 | 84.4354 | 11 | 13.8713 | -2.8713 |  | 30-03-2026 08:50 | 73.504 | 76.317 | 31.5 | 12.7195 | 14.0726 | -1.3531 | 84.4354 | 11 | 13.8713 | -2.8713 |  | 30-03-2026 08:50 | 70.124 | 72.275 | 31.7 | 12.0458 | 14.0726 | -2.0267 | 84.4354 | 11.1 | 13.8713 | -2.7713 |  | 30-03-2026 08:50 | 67.787 | 68.81 | 29.7 | 11.4683 | 13.3883 | -1.92 | 80.3298 | 10.2 | 13.1968 | -2.9968 |  | 30-03-2026 08:50 | 136.1155 | 145.6703 | -9.5548 | 874.0221 | 113.5 | 143.5873 | -30.0873 | -22.6155
30-03-2026 08:40 | 278 | 44.77 | 0 | 0 | 28.3 | 0 | 16.808 | -16.808 | 100.8479 | 0 | 16.5676 | -16.5676 |  | 30-03-2026 08:40 | 0 | 0 | 28.5 | 0 | 16.808 | -16.808 | 100.8479 | 0 | 16.5676 | -16.5676 |  | 30-03-2026 08:40 | 0 | 0 | 28.1 | 0 | 16.808 | -16.808 | 100.8479 | 0 | 16.5676 | -16.5676 |  | 30-03-2026 08:40 | 0 | 0 | 28.4 | 0 | 16.808 | -16.808 | 100.8479 | 0 | 16.5676 | -16.5676 |  | 30-03-2026 08:40 | 0 | 0 | 20.7 | 0 | 12.4504 | -12.4504 | 74.7022 | 0 | 12.2723 | -12.2723 |  | 30-03-2026 08:40 | 0 | 0 | 19.9 | 0 | 12.4504 | -12.4504 | 74.7022 | 0 | 12.2723 | -12.2723 |  | 30-03-2026 08:40 | 0 | 0 | 20.5 | 0 | 12.4504 | -12.4504 | 74.7022 | 0 | 12.2723 | -12.2723 |  | 30-03-2026 08:40 | 0 | 0 | 20.6 | 0 | 12.4504 | -12.4504 | 74.7022 | 0 | 12.2723 | -12.2723 |  | 30-03-2026 08:40 | 0 | 0 | 19.5 | 0 | 11.845 | -11.845 | 71.0699 | 0 | 11.6756 | -11.6756 |  | 30-03-2026 08:40 | 0 | 128.8784 | -128.8784 | 773.2703 | 0 | 127.0354 | -127.0354 | 0
30-03-2026 08:30 | 153 | 41.04 | 0 | 0 | 28.3 | 0 | 9.3802 | -9.3802 | 56.2811 | 4.1 | 9.246 | -5.146 |  | 30-03-2026 08:30 | 0 | 0 | 28.5 | 0 | 9.3802 | -9.3802 | 56.2811 | 4 | 9.246 | -5.246 |  | 30-03-2026 08:30 | 0 | 0 | 28.1 | 0 | 9.3802 | -9.3802 | 56.2811 | 3.9 | 9.246 | -5.346 |  | 30-03-2026 08:30 | 0 | 0 | 28.4 | 0 | 9.3802 | -9.3802 | 56.2811 | 3.9 | 9.246 | -5.346 |  | 30-03-2026 08:30 | 0 | 0 | 20.7 | 0 | 6.9483 | -6.9483 | 41.6897 | 2.9 | 6.8489 | -3.9489 |  | 30-03-2026 08:30 | 0 | 0 | 19.9 | 0 | 6.9483 | -6.9483 | 41.6897 | 2.9 | 6.8489 | -3.9489 |  | 30-03-2026 08:30 | 0 | 0 | 20.5 | 0 | 6.9483 | -6.9483 | 41.6897 | 2.8 | 6.8489 | -4.0489 |  | 30-03-2026 08:30 | 0 | 0 | 20.6 | 0 | 6.9483 | -6.9483 | 41.6897 | 2.8 | 6.8489 | -4.0489 |  | 30-03-2026 08:30 | 0 | 0 | 19.5 | 0 | 6.6104 | -6.6104 | 39.6626 | 2.7 | 6.5159 | -3.8159 |  | 30-03-2026 08:30 | 0 | 71.9243 | -71.9243 | 431.5458 | 30 | 70.8958 | -40.8958 | 30
30-03-2026 08:20 | 143 | 39.32 | 50.644 | 51.397 | 24.2 | 8.5662 | 8.823 | -0.25685 | 52.9381 | 6.8 | 8.6968 | -1.8968 |  | 30-03-2026 08:20 | 49.486 | 50.275 | 24.5 | 8.3792 | 8.823 | -0.44385 | 52.9381 | 6.8 | 8.6968 | -1.8968 |  | 30-03-2026 08:20 | 51.112 | 51.911 | 24.2 | 8.6518 | 8.823 | -0.17118 | 52.9381 | 6.8 | 8.6968 | -1.8968 |  | 30-03-2026 08:20 | 51.552 | 52.358 | 24.5 | 8.7263 | 8.823 | -0.096682 | 52.9381 | 6.9 | 8.6968 | -1.7968 |  | 30-03-2026 08:20 | 38.011 | 38.676 | 17.8 | 6.446 | 6.5356 | -0.089567 | 39.2134 | 5.1 | 6.4421 | -1.3421 |  | 30-03-2026 08:20 | 38.025 | 38.683 | 17 | 6.4472 | 6.5356 | -0.088401 | 39.2134 | 5 | 6.4421 | -1.4421 |  | 30-03-2026 08:20 | 37.955 | 38.611 | 17.7 | 6.4352 | 6.5356 | -0.1004 | 39.2134 | 5.1 | 6.4421 | -1.3421 |  | 30-03-2026 08:20 | 37.588 | 38.697 | 17.8 | 6.4495 | 6.5356 | -0.086067 | 39.2134 | 5.1 | 6.4421 | -1.3421 |  | 30-03-2026 08:20 | 36.078 | 36.706 | 16.8 | 6.1177 | 6.2178 | -0.10012 | 37.3067 | 4.8 | 6.1289 | -1.3289 |  | 30-03-2026 08:20 | 66.219 | 67.6521 | -1.4331 | 405.9127 | 52.4 | 66.6847 | -14.2847 | -13.819
30-03-2026 08:10 | 95 | 38.17 | 34.836 | 35.46 | 17.4 | 5.91 | 5.8863 | 0.023719 | 35.3177 | 5.5 | 5.8021 | -0.30211 |  | 30-03-2026 08:10 | 35.101 | 35.748 | 17.7 | 5.958 | 5.8863 | 0.071719 | 35.3177 | 5.5 | 5.8021 | -0.30211 |  | 30-03-2026 08:10 | 34.651 | 35.283 | 17.4 | 5.8805 | 5.8863 | -0.0057812 | 35.3177 | 5.5 | 5.8021 | -0.30211 |  | 30-03-2026 08:10 | 34.992 | 35.623 | 17.6 | 5.9372 | 5.8863 | 0.050885 | 35.3177 | 5.5 | 5.8021 | -0.30211 |  | 30-03-2026 08:10 | 25.683 | 26.226 | 12.7 | 4.371 | 4.3602 | 0.010792 | 26.1612 | 4 | 4.2979 | -0.29786 |  | 30-03-2026 08:10 | 24.436 | 24.973 | 12 | 4.1622 | 4.3602 | -0.19804 | 26.1612 | 3.9 | 4.2979 | -0.39786 |  | 30-03-2026 08:10 | 25.614 | 26.161 | 12.6 | 4.3602 | 4.3602 | -4.1609e-05 | 26.1612 | 4 | 4.2979 | -0.29786 |  | 30-03-2026 08:10 | 25.545 | 26.469 | 12.7 | 4.4115 | 4.3602 | 0.051292 | 26.1612 | 4 | 4.2979 | -0.29786 |  | 30-03-2026 08:10 | 24.136 | 24.671 | 12 | 4.1118 | 4.1482 | -0.036365 | 24.8892 | 3.9 | 4.0889 | -0.18888 |  | 30-03-2026 08:10 | 45.1023 | 45.1342 | -0.031823 | 270.8049 | 41.8 | 44.4887 | -2.6887 | -3.3023
30-03-2026 08:00 | 86 | 37.31 | 31.125 | 31.685 | 11.9 | 5.2808 | 5.3454 | -0.064614 | 32.0727 | 4.1 | 5.269 | -1.169 |  | 30-03-2026 08:00 | 31.257 | 32.026 | 12.2 | 5.3377 | 5.3454 | -0.0077811 | 32.0727 | 4.1 | 5.269 | -1.169 |  | 30-03-2026 08:00 | 31.17 | 31.758 | 11.9 | 5.293 | 5.3454 | -0.052448 | 32.0727 | 4 | 5.269 | -1.269 |  | 30-03-2026 08:00 | 31.283 | 31.866 | 12.1 | 5.311 | 5.3454 | -0.034448 | 32.0727 | 4.1 | 5.269 | -1.169 |  | 30-03-2026 08:00 | 23.064 | 23.735 | 8.7 | 3.9558 | 3.9596 | -0.0037576 | 23.7575 | 3 | 3.903 | -0.90297 |  | 30-03-2026 08:00 | 21.797 | 22.306 | 8.1 | 3.7177 | 3.9596 | -0.24192 | 23.7575 | 2.7 | 3.903 | -1.203 |  | 30-03-2026 08:00 | 22.986 | 23.51 | 8.6 | 3.9183 | 3.9596 | -0.041258 | 23.7575 | 3 | 3.903 | -0.90297 |  | 30-03-2026 08:00 | 22.942 | 23.957 | 8.7 | 3.9928 | 3.9596 | 0.033242 | 23.7575 | 3 | 3.903 | -0.90297 |  | 30-03-2026 08:00 | 21.569 | 22.075 | 8.1 | 3.6792 | 3.7671 | -0.087894 | 22.6024 | 2.8 | 3.7132 | -0.91319 |  | 30-03-2026 08:00 | 40.4863 | 40.9872 | -0.50088 | 245.9233 | 30.8 | 40.4011 | -9.6011 | -9.6863
30-03-2026 07:50 | 51 | 36.45 | 18.123 | 18.584 | 7.8 | 3.0973 | 3.1799 | -0.082613 | 19.0797 | 3.1 | 3.1345 | -0.034473 |  | 30-03-2026 07:50 | 18.307 | 18.858 | 8.1 | 3.143 | 3.1799 | -0.036946 | 19.0797 | 3.3 | 3.1345 | 0.16553 |  | 30-03-2026 07:50 | 18.053 | 18.525 | 7.9 | 3.0875 | 3.1799 | -0.092446 | 19.0797 | 3.3 | 3.1345 | 0.16553 |  | 30-03-2026 07:50 | 18.203 | 18.672 | 8 | 3.112 | 3.1799 | -0.067946 | 19.0797 | 3.3 | 3.1345 | 0.16553 |  | 30-03-2026 07:50 | 13.253 | 13.746 | 5.7 | 2.291 | 2.3555 | -0.064516 | 14.1331 | 2.4 | 2.3218 | 0.078168 |  | 30-03-2026 07:50 | 12.571 | 12.983 | 5.4 | 2.1638 | 2.3555 | -0.19168 | 14.1331 | 2.3 | 2.3218 | -0.021832 |  | 30-03-2026 07:50 | 13.171 | 13.595 | 5.6 | 2.2658 | 2.3555 | -0.089682 | 14.1331 | 2.3 | 2.3218 | -0.021832 |  | 30-03-2026 07:50 | 13.315 | 13.99 | 5.7 | 2.3317 | 2.3555 | -0.023849 | 14.1331 | 2.4 | 2.3218 | 0.078168 |  | 30-03-2026 07:50 | 12.55 | 12.962 | 5.3 | 2.1603 | 2.241 | -0.080648 | 13.4459 | 2.2 | 2.2089 | -0.0089353 |  | 30-03-2026 07:50 | 23.6525 | 24.3828 | -0.73033 | 146.297 | 24.6 | 24.0342 | 0.56585 | 0.9475
30-03-2026 07:40 | 54 | 35.59 | 19.419 | 19.892 | 4.7 | 3.3153 | 3.3776 | -0.062226 | 20.2654 | 2.3 | 3.3293 | -1.0293 |  | 30-03-2026 07:40 | 19.371 | 20.004 | 4.8 | 3.334 | 3.3776 | -0.043559 | 20.2654 | 2.3 | 3.3293 | -1.0293 |  | 30-03-2026 07:40 | 19.239 | 19.722 | 4.6 | 3.287 | 3.3776 | -0.090559 | 20.2654 | 2.2 | 3.3293 | -1.1293 |  | 30-03-2026 07:40 | 19.553 | 20.267 | 4.7 | 3.3778 | 3.3776 | 0.00027386 | 20.2654 | 2.3 | 3.3293 | -1.0293 |  | 30-03-2026 07:40 | 14.078 | 14.638 | 3.3 | 2.4397 | 2.5019 | -0.062229 | 15.0114 | 1.7 | 2.4661 | -0.76612 |  | 30-03-2026 07:40 | 13.491 | 13.907 | 3.1 | 2.3178 | 2.5019 | -0.18406 | 15.0114 | 1.6 | 2.4661 | -0.86612 |  | 30-03-2026 07:40 | 14.06 | 14.487 | 3.3 | 2.4145 | 2.5019 | -0.087396 | 15.0114 | 1.7 | 2.4661 | -0.76612 |  | 30-03-2026 07:40 | 14.151 | 14.86 | 3.3 | 2.4767 | 2.5019 | -0.025229 | 15.0114 | 1.6 | 2.4661 | -0.86612 |  | 30-03-2026 07:40 | 13.498 | 13.918 | 3.1 | 2.3197 | 2.3802 | -0.060577 | 14.2815 | 1.6 | 2.3462 | -0.74621 |  | 30-03-2026 07:40 | 25.2825 | 25.8981 | -0.61557 | 155.3884 | 17.3 | 25.5277 | -8.2277 | -7.9825
30-03-2026 07:30 | 25 | 34.44 | 8.291 | 8.636 | 2.4 | 1.4393 | 1.5702 | -0.13089 | 9.4213 | 1.1 | 1.5478 | -0.44777 |  | 30-03-2026 07:30 | 8.091 | 8.765 | 2.5 | 1.4608 | 1.5702 | -0.10939 | 9.4213 | 1.1 | 1.5478 | -0.44777 |  | 30-03-2026 07:30 | 8.372 | 8.718 | 2.4 | 1.453 | 1.5702 | -0.11722 | 9.4213 | 1 | 1.5478 | -0.54777 |  | 30-03-2026 07:30 | 8.459 | 9.106 | 2.4 | 1.5177 | 1.5702 | -0.052554 | 9.4213 | 1 | 1.5478 | -0.54777 |  | 30-03-2026 07:30 | 6.094 | 6.579 | 1.6 | 1.0965 | 1.1631 | -0.066627 | 6.9788 | 0.7 | 1.1465 | -0.44649 |  | 30-03-2026 07:30 | 5.733 | 5.991 | 1.5 | 0.9985 | 1.1631 | -0.16463 | 6.9788 | 0.7 | 1.1465 | -0.44649 |  | 30-03-2026 07:30 | 6.07 | 6.345 | 1.6 | 1.0575 | 1.1631 | -0.10563 | 6.9788 | 0.7 | 1.1465 | -0.44649 |  | 30-03-2026 07:30 | 6.112 | 6.659 | 1.7 | 1.1098 | 1.1631 | -0.053293 | 6.9788 | 0.8 | 1.1465 | -0.34649 |  | 30-03-2026 07:30 | 5.68 | 5.943 | 1.5 | 0.9905 | 1.1066 | -0.11607 | 6.6394 | 0.7 | 1.0907 | -0.39075 |  | 30-03-2026 07:30 | 11.1237 | 12.04 | -0.9163 | 72.2398 | 7.8 | 11.8678 | -4.0678 | -3.3237
30-03-2026 07:20 | 14 | 33.29 | 5.369 | 5.621 | 1.3 | 0.93683 | 0.88298 | 0.053849 | 5.2979 | 0.6 | 0.87036 | -0.27036 |  | 30-03-2026 07:20 | 5.508 | 6.211 | 1.4 | 1.0352 | 0.88298 | 0.15218 | 5.2979 | 0.6 | 0.87036 | -0.27036 |  | 30-03-2026 07:20 | 5.3 | 5.547 | 1.4 | 0.9245 | 0.88298 | 0.041516 | 5.2979 | 0.7 | 0.87036 | -0.17036 |  | 30-03-2026 07:20 | 5.448 | 6.05 | 1.4 | 1.0083 | 0.88298 | 0.12535 | 5.2979 | 0.7 | 0.87036 | -0.17036 |  | 30-03-2026 07:20 | 3.777 | 4.255 | 0.9 | 0.70917 | 0.65406 | 0.055104 | 3.9244 | 0.4 | 0.64471 | -0.24471 |  | 30-03-2026 07:20 | 3.601 | 3.782 | 0.8 | 0.63033 | 0.65406 | -0.023729 | 3.9244 | 0.4 | 0.64471 | -0.24471 |  | 30-03-2026 07:20 | 3.788 | 3.958 | 0.9 | 0.65967 | 0.65406 | 0.0056045 | 3.9244 | 0.5 | 0.64471 | -0.14471 |  | 30-03-2026 07:20 | 3.826 | 4.111 | 0.9 | 0.68517 | 0.65406 | 0.031104 | 3.9244 | 0.4 | 0.64471 | -0.24471 |  | 30-03-2026 07:20 | 3.601 | 3.779 | 0.8 | 0.62983 | 0.62226 | 0.0075741 | 3.7336 | 0.4 | 0.61336 | -0.21336 |  | 30-03-2026 07:20 | 7.219 | 6.7704 | 0.44856 | 40.6227 | 4.7 | 6.6736 | -1.9736 | -2.519
30-03-2026 07:10 | 7 | 35.01 | 2.235 | 2.35 | 0.7 | 0.39167 | 0.43875 | -0.047088 | 2.6325 | 0.3 | 0.43248 | -0.13248 |  | 30-03-2026 07:10 | 2.265 | 2.834 | 0.8 | 0.47233 | 0.43875 | 0.033579 | 2.6325 | 0.4 | 0.43248 | -0.032481 |  | 30-03-2026 07:10 | 2.239 | 2.354 | 0.7 | 0.39233 | 0.43875 | -0.046421 | 2.6325 | 0.3 | 0.43248 | -0.13248 |  | 30-03-2026 07:10 | 2.232 | 3.036 | 0.7 | 0.506 | 0.43875 | 0.067245 | 2.6325 | 0.3 | 0.43248 | -0.13248 |  | 30-03-2026 07:10 | 1.496 | 1.984 | 0.5 | 0.33067 | 0.325 | 0.0056631 | 1.95 | 0.3 | 0.32036 | -0.020356 |  | 30-03-2026 07:10 | 1.399 | 1.453 | 0.4 | 0.24217 | 0.325 | -0.082837 | 1.95 | 0.2 | 0.32036 | -0.12036 |  | 30-03-2026 07:10 | 1.462 | 1.537 | 0.4 | 0.25617 | 0.325 | -0.068837 | 1.95 | 0.2 | 0.32036 | -0.12036 |  | 30-03-2026 07:10 | 1.576 | 2.011 | 0.5 | 0.33517 | 0.325 | 0.010163 | 1.95 | 0.3 | 0.32036 | -0.020356 |  | 30-03-2026 07:10 | 1.391 | 1.463 | 0.4 | 0.24383 | 0.3092 | -0.065367 | 1.8552 | 0.2 | 0.30478 | -0.10478 |  | 30-03-2026 07:10 | 3.1703 | 3.3642 | -0.1939 | 20.1854 | 2.5 | 3.3161 | -0.81613 | -0.67033
30-03-2026 07:00 | 8 | 35.01 | 2.495 | 2.618 | 0.4 | 0.43633 | 0.50143 | -0.065101 | 3.0086 | 0.4 | 0.49426 | -0.094264 |  | 30-03-2026 07:00 | 2.742 | 3.253 | 0.4 | 0.54217 | 0.50143 | 0.040733 | 3.0086 | 0.4 | 0.49426 | -0.094264 |  | 30-03-2026 07:00 | 2.482 | 2.61 | 0.4 | 0.435 | 0.50143 | -0.066434 | 3.0086 | 0.4 | 0.49426 | -0.094264 |  | 30-03-2026 07:00 | 2.572 | 3.261 | 0.4 | 0.5435 | 0.50143 | 0.042066 | 3.0086 | 0.4 | 0.49426 | -0.094264 |  | 30-03-2026 07:00 | 1.691 | 2.116 | 0.2 | 0.35267 | 0.37143 | -0.018766 | 2.2286 | 0.2 | 0.36612 | -0.16612 |  | 30-03-2026 07:00 | 1.6 | 1.682 | 0.2 | 0.28033 | 0.37143 | -0.091099 | 2.2286 | 0.2 | 0.36612 | -0.16612 |  | 30-03-2026 07:00 | 1.68 | 1.766 | 0.2 | 0.29433 | 0.37143 | -0.077099 | 2.2286 | 0.2 | 0.36612 | -0.16612 |  | 30-03-2026 07:00 | 1.772 | 2.109 | 0.2 | 0.3515 | 0.37143 | -0.019933 | 2.2286 | 0.2 | 0.36612 | -0.16612 |  | 30-03-2026 07:00 | 1.598 | 1.68 | 0.2 | 0.28 | 0.35337 | -0.073372 | 2.1202 | 0.2 | 0.34832 | -0.14832 |  | 30-03-2026 07:00 | 3.5158 | 3.8448 | -0.32901 | 23.069 | 2.6 | 3.7899 | -1.1899 | -0.91583
[110 empty] | Total: - | 15567.3362 | 15916.995 | -349.6589 |  | 15083.1 | 15689.382 | -606.282 | -484.2362
Sum:- | 35078 |  | 12131.864 |  | 74876.5 |  |  |  |  | 1964 | 2046.1691 | -82.1691 | 0.98486 |  | 11640.021 |  | 72154.8 |  |  |  |  | 1978.5 | 2046.1691 | -67.6691 | 0.97275 |  | 11910.407 |  | 74184 |  |  |  |  | 1947.6 | 2046.1691 | -98.5691 | 0.97343 |  | 11989.064 |  | 68853.7 |  |  |  |  | 1961.9 | 2046.1691 | -84.2691 | 0.98327 |  | 8966.458 |  | 52980.5 |  |  |  |  | 1468.4 | 1515.6808 | -47.2808 | 0.98428 |  | 8871.016 |  | 53902.2 |  |  |  |  | 1452.7 | 1515.6808 | -62.9808 | 0.98171 |  | 8881.565 |  | 55542.5 |  |  |  |  | 1456.9 | 1515.6808 | -58.7808 | 0.98117 |  | 8911.447 |  | 55883.9 |  |  |  |  | 1465.6 | 1515.6808 | -50.0808 | 0.97075 |  | 8403.435 |  | 52895.1 |  |  |  |  | 1387.5 | 1441.9826 | -54.4826 | 0.98323 | [8 empty] | -3.111%

## 31 march 2026
|  |  | Inverter 01 | [10 empty] | Inverter 02 | [11 empty] | Inverter 03 | [11 empty] | Inverter 04 | [11 empty] | Inverter 05 | [11 empty] | Inverter 06 | [11 empty] | Inverter 07 | [11 empty] | Inverter 08 | [11 empty] | Inverter 09 | [15 empty] | Sum of datas of all Inverters
Time | POA(W/m^2) | Module Temp.(degree C) | Output Active Power | Total DC I/P power actual | Daily Energy actual | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Output Active Power | Total DC I/P power TrackSo(Inv.) | Daily Energy(Inv.) | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Efficiency | Time | Actual Inv. I/P DC Energy at MPPT | Expected Inv. I/P DC energy | Diiference between expected Inv. I/P DC energy & actual Inv. I/P DC energy at MPPT = DC loss | Expected O/P Power Generated | Actual Inv. O/P AC Energy | Expected Inv. O/P AC energy | Diiference between expected inv. O/P AC energy & Actual Inv. O/P AC Energy = Inv. Loss | Inv. i/p - inv. o/p, actual Inv. Loss | Inverter No. | Efficiency
31-03-2026 19:00 | 3 | 41.61 | 0 | 0 | 2158.6 | 0 | 0.18354 | -0.18354 | 1.1012 | 0 | 0.18091 | -0.18091 |  | 31-03-2026 19:00 | 0 | 0 | 2172.4 | 0 | 0.18354 | -0.18354 | 1.1012 | 0 | 0.18091 | -0.18091 |  | 31-03-2026 19:00 | 0 | 0 | 2141.4 | 0 | 0.18354 | -0.18354 | 1.1012 | 0 | 0.18091 | -0.18091 |  | 31-03-2026 19:00 | 0 | 0 | 2151.9 | 0 | 0.18354 | -0.18354 | 1.1012 | 0 | 0.18091 | -0.18091 |  | 31-03-2026 19:00 | 0 | 0 | 1610.5 | 0 | 0.13595 | -0.13595 | 0.81572 | 0 | 0.13401 | -0.13401 |  | 31-03-2026 19:00 | 0 | 0 | 1596.2 | 0 | 0.13595 | -0.13595 | 0.81572 | 0 | 0.13401 | -0.13401 |  | 31-03-2026 19:00 | 0 | 0 | 1598.8 | 0 | 0.13595 | -0.13595 | 0.81572 | 0 | 0.13401 | -0.13401 |  | 31-03-2026 19:00 | 0 | 0 | 1612.4 | 0 | 0.13595 | -0.13595 | 0.81572 | 0 | 0.13401 | -0.13401 |  | 31-03-2026 19:00 | 0 | 0 | 1528.3 | 0 | 0.12934 | -0.12934 | 0.77605 | 0 | 0.12749 | -0.12749 |  | 31-03-2026 19:00 | 0 | 1.4073 | -1.4073 | 8.4438 | 0 | 1.3872 | -1.3872 | 0 | 1 | 99.53%
31-03-2026 18:50 | 3 | 42.19 | 0 | 0 | 2158.6 | 0 | 0.18314 | -0.18314 | 1.0988 | 0 | 0.18052 | -0.18052 |  | 31-03-2026 18:50 | 0 | 0 | 2172.4 | 0 | 0.18314 | -0.18314 | 1.0988 | 0 | 0.18052 | -0.18052 |  | 31-03-2026 18:50 | 0 | 0 | 2141.4 | 0 | 0.18314 | -0.18314 | 1.0988 | 0 | 0.18052 | -0.18052 |  | 31-03-2026 18:50 | 0 | 0 | 2151.9 | 0 | 0.18314 | -0.18314 | 1.0988 | 0 | 0.18052 | -0.18052 |  | 31-03-2026 18:50 | 0 | 0 | 1610.5 | 0 | 0.13566 | -0.13566 | 0.81396 | 0 | 0.13372 | -0.13372 |  | 31-03-2026 18:50 | 0 | 0 | 1596.2 | 0 | 0.13566 | -0.13566 | 0.81396 | 0 | 0.13372 | -0.13372 |  | 31-03-2026 18:50 | 0 | 0 | 1598.8 | 0 | 0.13566 | -0.13566 | 0.81396 | 0 | 0.13372 | -0.13372 |  | 31-03-2026 18:50 | 0 | 0 | 1612.4 | 0 | 0.13566 | -0.13566 | 0.81396 | 0 | 0.13372 | -0.13372 |  | 31-03-2026 18:50 | 0 | 0 | 1528.3 | 0 | 0.12906 | -0.12906 | 0.77438 | 0 | 0.12722 | -0.12722 |  | 31-03-2026 18:50 | 0 | 1.4043 | -1.4043 | 8.4256 | 0 | 1.3842 | -1.3842 | 0 | 2 | 98.42%
31-03-2026 18:40 | 10 | 43.34 | 0 | 0 | 2158.6 | 0 | 0.60785 | -0.60785 | 3.6471 | 0.1 | 0.59916 | -0.49916 |  | 31-03-2026 18:40 | 0 | 0 | 2172.4 | 0 | 0.60785 | -0.60785 | 3.6471 | 0.1 | 0.59916 | -0.49916 |  | 31-03-2026 18:40 | 0 | 0 | 2141.4 | 0 | 0.60785 | -0.60785 | 3.6471 | 0.1 | 0.59916 | -0.49916 |  | 31-03-2026 18:40 | 0 | 0 | 2151.9 | 0 | 0.60785 | -0.60785 | 3.6471 | 0.1 | 0.59916 | -0.49916 |  | 31-03-2026 18:40 | 0 | 0 | 1610.5 | 0 | 0.45026 | -0.45026 | 2.7016 | 0.1 | 0.44382 | -0.34382 |  | 31-03-2026 18:40 | 0 | 0 | 1596.2 | 0 | 0.45026 | -0.45026 | 2.7016 | 0.1 | 0.44382 | -0.34382 |  | 31-03-2026 18:40 | 0 | 0 | 1598.8 | 0 | 0.45026 | -0.45026 | 2.7016 | 0.1 | 0.44382 | -0.34382 |  | 31-03-2026 18:40 | 0 | 0 | 1612.4 | 0 | 0.45026 | -0.45026 | 2.7016 | 0 | 0.44382 | -0.44382 |  | 31-03-2026 18:40 | 0 | 0 | 1528.3 | 0 | 0.42837 | -0.42837 | 2.5702 | 0.1 | 0.42224 | -0.32224 |  | 31-03-2026 18:40 | 0 | 4.6608 | -4.6608 | 27.965 | 0.8 | 4.5942 | -3.7942 | 0.8 | 3 | 97.39%
31-03-2026 18:30 | 21 | 44.2 | 7.787 | 8.123 | 2158.5 | 1.3538 | 1.2724 | 0.081444 | 7.6343 | 2 | 1.2542 | 0.74581 |  | 31-03-2026 18:30 | 8.191 | 8.712 | 2172.3 | 1.452 | 1.2724 | 0.17961 | 7.6343 | 2 | 1.2542 | 0.74581 |  | 31-03-2026 18:30 | 7.82 | 8.158 | 2141.3 | 1.3597 | 1.2724 | 0.087277 | 7.6343 | 2 | 1.2542 | 0.74581 |  | 31-03-2026 18:30 | 7.966 | 8.463 | 2151.8 | 1.4105 | 1.2724 | 0.13811 | 7.6343 | 2 | 1.2542 | 0.74581 |  | 31-03-2026 18:30 | 5.666 | 5.945 | 1610.4 | 0.99083 | 0.94251 | 0.048323 | 5.6551 | 1.4 | 0.92903 | 0.47097 |  | 31-03-2026 18:30 | 5.607 | 5.868 | 1596.1 | 0.978 | 0.94251 | 0.035489 | 5.6551 | 1.4 | 0.92903 | 0.47097 |  | 31-03-2026 18:30 | 5.601 | 5.874 | 1598.7 | 0.979 | 0.94251 | 0.036489 | 5.6551 | 1.4 | 0.92903 | 0.47097 |  | 31-03-2026 18:30 | 5.688 | 6.143 | 1612.4 | 1.0238 | 0.94251 | 0.081323 | 5.6551 | 1.5 | 0.92903 | 0.57097 |  | 31-03-2026 18:30 | 5.319 | 5.572 | 1528.2 | 0.92867 | 0.89668 | 0.031984 | 5.3801 | 1.3 | 0.88386 | 0.41614 |  | 31-03-2026 18:30 | 10.4763 | 9.7563 | 0.72005 | 58.5377 | 15 | 9.6168 | 5.3832 | 4.5237 | 4 | 98.38%
31-03-2026 18:20 | 40 | 45.06 | 15.078 | 15.506 | 2156.5 | 2.5843 | 2.4158 | 0.16855 | 14.4947 | 2.6 | 2.3812 | 0.21877 |  | 31-03-2026 18:20 | 15.479 | 15.999 | 2170.3 | 2.6665 | 2.4158 | 0.25072 | 14.4947 | 2.7 | 2.3812 | 0.31877 |  | 31-03-2026 18:20 | 15.002 | 15.428 | 2139.3 | 2.5713 | 2.4158 | 0.15555 | 14.4947 | 2.6 | 2.3812 | 0.21877 |  | 31-03-2026 18:20 | 15.142 | 15.57 | 2149.8 | 2.595 | 2.4158 | 0.17922 | 14.4947 | 2.6 | 2.3812 | 0.21877 |  | 31-03-2026 18:20 | 11.069 | 11.604 | 1609 | 1.934 | 1.7895 | 0.14453 | 10.7368 | 1.9 | 1.7639 | 0.13612 |  | 31-03-2026 18:20 | 10.897 | 11.297 | 1594.7 | 1.8828 | 1.7895 | 0.093368 | 10.7368 | 1.9 | 1.7639 | 0.13612 |  | 31-03-2026 18:20 | 10.937 | 11.342 | 1597.3 | 1.8903 | 1.7895 | 0.10087 | 10.7368 | 1.9 | 1.7639 | 0.13612 |  | 31-03-2026 18:20 | 11.026 | 11.652 | 1610.9 | 1.942 | 1.7895 | 0.15253 | 10.7368 | 1.9 | 1.7639 | 0.13612 |  | 31-03-2026 18:20 | 10.387 | 10.775 | 1526.9 | 1.7958 | 1.7025 | 0.093378 | 10.2147 | 1.8 | 1.6781 | 0.12189 |  | 31-03-2026 18:20 | 19.8622 | 18.5234 | 1.3387 | 111.1406 | 19.9 | 18.2585 | 1.6415 | 0.037833 | 5 | 98.5%
31-03-2026 18:10 | 43 | 46.21 | 15.72 | 16.16 | 2153.9 | 2.6933 | 2.5857 | 0.10761 | 15.5143 | 3.3 | 2.5487 | 0.75126 |  | 31-03-2026 18:10 | 15.957 | 16.413 | 2167.6 | 2.7355 | 2.5857 | 0.14978 | 15.5143 | 3.3 | 2.5487 | 0.75126 |  | 31-03-2026 18:10 | 15.452 | 15.889 | 2136.7 | 2.6482 | 2.5857 | 0.062447 | 15.5143 | 3.3 | 2.5487 | 0.75126 |  | 31-03-2026 18:10 | 15.64 | 16.082 | 2147.2 | 2.6803 | 2.5857 | 0.094613 | 15.5143 | 3.3 | 2.5487 | 0.75126 |  | 31-03-2026 18:10 | 11.4 | 11.811 | 1607.1 | 1.9685 | 1.9153 | 0.053152 | 11.4921 | 2.4 | 1.888 | 0.51204 |  | 31-03-2026 18:10 | 11.151 | 11.552 | 1592.8 | 1.9253 | 1.9153 | 0.0099852 | 11.4921 | 2.3 | 1.888 | 0.41204 |  | 31-03-2026 18:10 | 11.206 | 11.616 | 1595.4 | 1.936 | 1.9153 | 0.020652 | 11.4921 | 2.4 | 1.888 | 0.51204 |  | 31-03-2026 18:10 | 11.322 | 11.916 | 1609 | 1.986 | 1.9153 | 0.070652 | 11.4921 | 2.4 | 1.888 | 0.51204 |  | 31-03-2026 18:10 | 10.675 | 11.076 | 1525.1 | 1.846 | 1.8222 | 0.023783 | 10.9333 | 2.3 | 1.7962 | 0.50384 |  | 31-03-2026 18:10 | 20.4192 | 19.8265 | 0.59268 | 118.9589 | 25 | 19.543 | 5.457 | 4.5808 | 6 | 98.12%
31-03-2026 18:00 | 72 | 47.93 | 26.684 | 27.265 | 2150.6 | 4.5442 | 4.3014 | 0.24274 | 25.8085 | 6.2 | 4.2399 | 1.9601 |  | 31-03-2026 18:00 | 28.438 | 29.039 | 2164.3 | 4.8398 | 4.3014 | 0.53841 | 25.8085 | 12.6 | 4.2399 | 8.3601 |  | 31-03-2026 18:00 | 26.377 | 26.97 | 2133.4 | 4.495 | 4.3014 | 0.19358 | 25.8085 | 5.9 | 4.2399 | 1.6601 |  | 31-03-2026 18:00 | 26.533 | 27.122 | 2143.9 | 4.5203 | 4.3014 | 0.21891 | 25.8085 | 5.9 | 4.2399 | 1.6601 |  | 31-03-2026 18:00 | 19.498 | 19.994 | 1604.7 | 3.3323 | 3.1862 | 0.14609 | 19.1174 | 4.4 | 3.1407 | 1.2593 |  | 31-03-2026 18:00 | 19.267 | 19.763 | 1590.5 | 3.2938 | 3.1862 | 0.10759 | 19.1174 | 4.3 | 3.1407 | 1.1593 |  | 31-03-2026 18:00 | 19.35 | 19.848 | 1593 | 3.308 | 3.1862 | 0.12176 | 19.1174 | 4.3 | 3.1407 | 1.1593 |  | 31-03-2026 18:00 | 19.503 | 20.363 | 1606.6 | 3.3938 | 3.1862 | 0.20759 | 19.1174 | 4.3 | 3.1407 | 1.1593 |  | 31-03-2026 18:00 | 18.484 | 18.962 | 1522.8 | 3.1603 | 3.0313 | 0.12902 | 18.1879 | 4.1 | 2.988 | 1.112 |  | 31-03-2026 18:00 | 34.8877 | 32.982 | 1.9057 | 197.8918 | 52 | 32.5103 | 19.4897 | 17.1123 | 7 | 98.15%
31-03-2026 17:50 | 108 | 48.22 | 40.307 | 41.012 | 2144.4 | 6.8353 | 6.445 | 0.39032 | 38.6701 | 6.2 | 6.3529 | -0.15285 | [5 empty] | 0 | 6.445 | -6.445 | 38.6701 | 0 | 6.3529 | -6.3529 |  | 31-03-2026 17:50 | 40.204 | 40.928 | 2127.5 | 6.8213 | 6.445 | 0.37632 | 38.6701 | 6.3 | 6.3529 | -0.052851 |  | 31-03-2026 17:50 | 40.486 | 41.216 | 2138 | 6.8693 | 6.445 | 0.42432 | 38.6701 | 6.4 | 6.3529 | 0.047149 |  | 31-03-2026 17:50 | 29.824 | 30.43 | 1600.3 | 5.0717 | 4.7741 | 0.29758 | 28.6445 | 4.7 | 4.7058 | -0.0058157 |  | 31-03-2026 17:50 | 29.528 | 30.115 | 1586.2 | 5.0192 | 4.7741 | 0.24508 | 28.6445 | 4.7 | 4.7058 | -0.0058157 |  | 31-03-2026 17:50 | 29.436 | 30.028 | 1588.7 | 5.0047 | 4.7741 | 0.23058 | 28.6445 | 4.6 | 4.7058 | -0.10582 |  | 31-03-2026 17:50 | 29.633 | 30.428 | 1602.3 | 5.0713 | 4.7741 | 0.29725 | 28.6445 | 4.7 | 4.7058 | -0.0058157 |  | 31-03-2026 17:50 | 28.025 | 28.61 | 1518.7 | 4.7683 | 4.542 | 0.22638 | 27.2517 | 4.4 | 4.477 | -0.077001 |  | 31-03-2026 17:50 | 45.4612 | 49.4184 | -3.9572 | 296.5101 | 42 | 48.7117 | -6.7117 | -3.4612 | 8 | 97.43%
31-03-2026 17:40 | 101 | 48.5 | 37.659 | 38.341 | 2138.2 | 6.3902 | 6.0209 | 0.36931 | 36.1251 | 5.8 | 5.9348 | -0.13476 |  | 31-03-2026 17:40 | 38.074 | 38.772 | 2151.7 | 6.462 | 6.0209 | 0.44115 | 36.1251 | 5.8 | 5.9348 | -0.13476 |  | 31-03-2026 17:40 | 37.621 | 38.307 | 2121.2 | 6.3845 | 6.0209 | 0.36365 | 36.1251 | 5.9 | 5.9348 | -0.034755 |  | 31-03-2026 17:40 | 37.749 | 38.453 | 2131.6 | 6.4088 | 6.0209 | 0.38798 | 36.1251 | 5.9 | 5.9348 | -0.034755 |  | 31-03-2026 17:40 | 28.053 | 28.631 | 1595.6 | 4.7718 | 4.4599 | 0.31194 | 26.7593 | 4.4 | 4.3961 | 0.0038852 |  | 31-03-2026 17:40 | 27.564 | 28.141 | 1581.5 | 4.6902 | 4.4599 | 0.23028 | 26.7593 | 4.3 | 4.3961 | -0.096115 |  | 31-03-2026 17:40 | 27.469 | 28.052 | 1584.1 | 4.6753 | 4.4599 | 0.21544 | 26.7593 | 4.4 | 4.3961 | 0.0038852 |  | 31-03-2026 17:40 | 27.769 | 28.727 | 1597.6 | 4.7878 | 4.4599 | 0.32794 | 26.7593 | 4.4 | 4.3961 | 0.0038852 |  | 31-03-2026 17:40 | 26.234 | 26.81 | 1514.3 | 4.4683 | 4.243 | 0.2253 | 25.4582 | 4.1 | 4.1824 | -0.082359 |  | 31-03-2026 17:40 | 49.039 | 46.166 | 2.873 | 276.9961 | 45 | 45.5058 | -0.50584 | -4.039 | 9 | 98.51%
31-03-2026 17:30 | 91 | 49.65 | 34.856 | 35.517 | 2132.4 | 5.9195 | 5.4009 | 0.51856 | 32.4056 | 6.4 | 5.3237 | 1.0763 |  | 31-03-2026 17:30 | 35.16 | 35.83 | 2145.9 | 5.9717 | 5.4009 | 0.57073 | 32.4056 | 6.5 | 5.3237 | 1.1763 |  | 31-03-2026 17:30 | 34.61 | 35.273 | 2115.3 | 5.8788 | 5.4009 | 0.4779 | 32.4056 | 6.3 | 5.3237 | 0.9763 |  | 31-03-2026 17:30 | 34.755 | 35.417 | 2125.7 | 5.9028 | 5.4009 | 0.5019 | 32.4056 | 6.5 | 5.3237 | 1.1763 |  | 31-03-2026 17:30 | 25.704 | 26.274 | 1591.2 | 4.379 | 4.0007 | 0.37831 | 24.0042 | 4.7 | 3.9435 | 0.75652 |  | 31-03-2026 17:30 | 25.408 | 25.974 | 1577.2 | 4.329 | 4.0007 | 0.32831 | 24.0042 | 4.7 | 3.9435 | 0.75652 |  | 31-03-2026 17:30 | 25.319 | 25.883 | 1579.7 | 4.3138 | 4.0007 | 0.31314 | 24.0042 | 4.6 | 3.9435 | 0.65652 |  | 31-03-2026 17:30 | 25.569 | 26.523 | 1593.2 | 4.4205 | 4.0007 | 0.41981 | 24.0042 | 4.6 | 3.9435 | 0.65652 |  | 31-03-2026 17:30 | 24.141 | 24.697 | 1510.2 | 4.1162 | 3.8062 | 0.31 | 22.837 | 4.5 | 3.7517 | 0.74826 |  | 31-03-2026 17:30 | 45.2313 | 41.4127 | 3.8186 | 248.4762 | 48.8 | 40.8205 | 7.9795 | 3.5687
31-03-2026 17:20 | 118 | 50.23 | 44.653 | 45.416 | 2126 | 7.5693 | 6.9879 | 0.58148 | 41.9271 | 9.3 | 6.8879 | 2.4121 |  | 31-03-2026 17:20 | 45.925 | 45.76 | 2139.4 | 7.6267 | 6.9879 | 0.63881 | 41.9271 | 9 | 6.8879 | 2.1121 |  | 31-03-2026 17:20 | 44.306 | 44.739 | 2109 | 7.4565 | 6.9879 | 0.46865 | 41.9271 | 9 | 6.8879 | 2.1121 |  | 31-03-2026 17:20 | 44.496 | 45.279 | 2119.2 | 7.5465 | 6.9879 | 0.55865 | 41.9271 | 9 | 6.8879 | 2.1121 |  | 31-03-2026 17:20 | 32.848 | 33.467 | 1586.5 | 5.5778 | 5.1762 | 0.40164 | 31.0571 | 6.7 | 5.1022 | 1.5978 |  | 31-03-2026 17:20 | 32.506 | 33.125 | 1572.5 | 5.5208 | 5.1762 | 0.34464 | 31.0571 | 6.6 | 5.1022 | 1.4978 |  | 31-03-2026 17:20 | 32.336 | 32.952 | 1575.1 | 5.492 | 5.1762 | 0.31581 | 31.0571 | 6.5 | 5.1022 | 1.3978 |  | 31-03-2026 17:20 | 32.576 | 33.41 | 1588.6 | 5.5683 | 5.1762 | 0.39214 | 31.0571 | 6.7 | 5.1022 | 1.5978 |  | 31-03-2026 17:20 | 30.83 | 31.424 | 1505.7 | 5.2373 | 4.9245 | 0.31283 | 29.547 | 6.3 | 4.8541 | 1.4459 |  | 31-03-2026 17:20 | 57.5953 | 53.5807 | 4.0147 | 321.484 | 69.1 | 52.8145 | 16.2855 | 11.5047
31-03-2026 17:10 | 171 | 51.09 | 64.967 | 65.883 | 2116.7 | 10.9805 | 10.093 | 0.88747 | 60.5582 | 12.3 | 9.9487 | 2.3513 |  | 31-03-2026 17:10 | 65.104 | 66.035 | 2130.4 | 11.0058 | 10.093 | 0.9128 | 60.5582 | 12.5 | 9.9487 | 2.5513 |  | 31-03-2026 17:10 | 63.747 | 64.665 | 2100 | 10.7775 | 10.093 | 0.68447 | 60.5582 | 12.3 | 9.9487 | 2.3513 |  | 31-03-2026 17:10 | 64.062 | 65.012 | 2110.2 | 10.8353 | 10.093 | 0.7423 | 60.5582 | 12.3 | 9.9487 | 2.3513 |  | 31-03-2026 17:10 | 47.416 | 48.211 | 1579.8 | 8.0352 | 7.4763 | 0.55885 | 44.8579 | 9.1 | 7.3694 | 1.7306 |  | 31-03-2026 17:10 | 46.911 | 47.688 | 1565.9 | 7.948 | 7.4763 | 0.47168 | 44.8579 | 9 | 7.3694 | 1.6306 |  | 31-03-2026 17:10 | 46.917 | 47.52 | 1568.6 | 7.92 | 7.4763 | 0.44368 | 44.8579 | 9 | 7.3694 | 1.6306 |  | 31-03-2026 17:10 | 47.146 | 48.816 | 1581.9 | 8.136 | 7.4763 | 0.65968 | 44.8579 | 9 | 7.3694 | 1.6306 |  | 31-03-2026 17:10 | 44.8 | 45.575 | 1499.4 | 7.5958 | 7.1128 | 0.48304 | 42.6768 | 8.7 | 7.0111 | 1.6889 |  | 31-03-2026 17:10 | 83.2342 | 77.3902 | 5.8439 | 464.3413 | 94.2 | 76.2835 | 17.9165 | 10.9658
31-03-2026 17:00 | 235 | 51.09 | 87.274 | 88.388 | 2104.4 | 14.7313 | 13.8705 | 0.86079 | 83.2233 | 16 | 13.6722 | 2.3278 |  | 31-03-2026 17:00 | 87.789 | 88.954 | 2117.9 | 14.8257 | 13.8705 | 0.95512 | 83.2233 | 16 | 13.6722 | 2.3278 |  | 31-03-2026 17:00 | 86.57 | 87.895 | 2087.7 | 14.6492 | 13.8705 | 0.77862 | 83.2233 | 15.8 | 13.6722 | 2.1278 |  | 31-03-2026 17:00 | 87.098 | 88.236 | 2097.9 | 14.706 | 13.8705 | 0.83546 | 83.2233 | 15.8 | 13.6722 | 2.1278 |  | 31-03-2026 17:00 | 64.251 | 65.143 | 1570.7 | 10.8572 | 10.2745 | 0.58269 | 61.6469 | 11.7 | 10.1276 | 1.5724 |  | 31-03-2026 17:00 | 63.584 | 64.48 | 1556.9 | 10.7467 | 10.2745 | 0.47219 | 61.6469 | 11.8 | 10.1276 | 1.6724 |  | 31-03-2026 17:00 | 63.425 | 64.319 | 1559.6 | 10.7198 | 10.2745 | 0.44536 | 61.6469 | 11.8 | 10.1276 | 1.6724 |  | 31-03-2026 17:00 | 63.958 | 65.589 | 1572.9 | 10.9315 | 10.2745 | 0.65702 | 61.6469 | 11.8 | 10.1276 | 1.6724 |  | 31-03-2026 17:00 | 60.721 | 61.603 | 1490.7 | 10.2672 | 9.7749 | 0.49227 | 58.6494 | 11 | 9.6351 | 1.3649 |  | 31-03-2026 17:00 | 112.4345 | 106.355 | 6.0795 | 638.1299 | 121.7 | 104.8341 | 16.8659 | 9.2655
31-03-2026 16:50 | 243 | 51.09 | 90.857 | 91.988 | 2088.4 | 15.3313 | 14.3427 | 0.9886 | 86.0564 | 27.3 | 14.1376 | 13.1624 |  | 31-03-2026 16:50 | 92.132 | 93.308 | 2101.9 | 15.5513 | 14.3427 | 1.2086 | 86.0564 | 13.6 | 14.1376 | -0.53763 |  | 31-03-2026 16:50 | 91.134 | 92.786 | 2071.9 | 15.4643 | 14.3427 | 1.1216 | 86.0564 | 13.2 | 14.1376 | -0.93763 |  | 31-03-2026 16:50 | 90.898 | 92.058 | 2082.1 | 15.343 | 14.3427 | 1.0003 | 86.0564 | 13.3 | 14.1376 | -0.83763 |  | 31-03-2026 16:50 | 67.52 | 68.961 | 1559 | 11.4935 | 10.6242 | 0.86925 | 63.7455 | 9.9 | 10.4723 | -0.57232 |  | 31-03-2026 16:50 | 66.559 | 67.484 | 1545.1 | 11.2473 | 10.6242 | 0.62309 | 63.7455 | 9.5 | 10.4723 | -0.97232 |  | 31-03-2026 16:50 | 66.531 | 67.448 | 1547.8 | 11.2413 | 10.6242 | 0.61709 | 63.7455 | 9.5 | 10.4723 | -0.97232 |  | 31-03-2026 16:50 | 66.919 | 68.9 | 1561.1 | 11.4833 | 10.6242 | 0.85909 | 63.7455 | 9.7 | 10.4723 | -0.77232 |  | 31-03-2026 16:50 | 63.448 | 64.342 | 1479.7 | 10.7237 | 10.1077 | 0.61601 | 60.6459 | 9.2 | 9.9631 | -0.76312 |  | 31-03-2026 16:50 | 117.8792 | 109.9756 | 7.9036 | 659.8534 | 115.2 | 108.4029 | 6.7971 | -2.6792
31-03-2026 16:40 | 201 | 51.09 | 75.782 | 76.811 | 2075.3 | 12.8018 | 11.8637 | 0.93809 | 71.1825 | 0 | 11.6941 | -11.6941 |  | 31-03-2026 16:40 | 76.152 | 77.21 | 2088.3 | 12.8683 | 11.8637 | 1.0046 | 71.1825 | 13.9 | 11.6941 | 2.2059 |  | 31-03-2026 16:40 | 75.215 | 76.62 | 2058.7 | 12.77 | 11.8637 | 0.90626 | 71.1825 | 13.9 | 11.6941 | 2.2059 |  | 31-03-2026 16:40 | 75.321 | 76.361 | 2068.8 | 12.7268 | 11.8637 | 0.86309 | 71.1825 | 13.9 | 11.6941 | 2.2059 |  | 31-03-2026 16:40 | 55.917 | 56.78 | 1549.1 | 9.4633 | 8.788 | 0.67538 | 52.7277 | 10.2 | 8.6623 | 1.5377 |  | 31-03-2026 16:40 | 55.356 | 56.216 | 1535.6 | 9.3693 | 8.788 | 0.58138 | 52.7277 | 10.6 | 8.6623 | 1.9377 |  | 31-03-2026 16:40 | 55.266 | 56.125 | 1538.3 | 9.3542 | 8.788 | 0.56621 | 52.7277 | 10.4 | 8.6623 | 1.7377 |  | 31-03-2026 16:40 | 55.636 | 57.132 | 1551.4 | 9.522 | 8.788 | 0.73404 | 52.7277 | 10.3 | 8.6623 | 1.6377 |  | 31-03-2026 16:40 | 52.751 | 53.603 | 1470.5 | 8.9338 | 8.3607 | 0.57318 | 50.1639 | 9.8 | 8.2411 | 1.5589 |  | 31-03-2026 16:40 | 97.8097 | 90.9674 | 6.8422 | 545.8047 | 93 | 89.6666 | 3.3334 | -4.8097
31-03-2026 16:30 | 251 | 50.8 | 94.136 | 94.548 | 2061.1 | 15.758 | 14.8315 | 0.92653 | 88.9888 | 18.1 | 14.6194 | 3.4806 |  | 31-03-2026 16:30 | 97.005 | 94.894 | 2074.4 | 15.8157 | 14.8315 | 0.9842 | 88.9888 | 18.1 | 14.6194 | 3.4806 |  | 31-03-2026 16:30 | 92.403 | 94.014 | 2044.8 | 15.669 | 14.8315 | 0.83753 | 88.9888 | 18.2 | 14.6194 | 3.5806 |  | 31-03-2026 16:30 | 92.854 | 94.058 | 2054.9 | 15.6763 | 14.8315 | 0.84486 | 88.9888 | 18.2 | 14.6194 | 3.5806 |  | 31-03-2026 16:30 | 67.944 | 68.881 | 1538.9 | 11.4802 | 10.9863 | 0.49389 | 65.9176 | 13.5 | 10.8292 | 2.6708 |  | 31-03-2026 16:30 | 68.797 | 69.746 | 1525 | 11.6243 | 10.9863 | 0.63806 | 65.9176 | 13 | 10.8292 | 2.1708 |  | 31-03-2026 16:30 | 67.842 | 68.798 | 1527.9 | 11.4663 | 10.9863 | 0.48006 | 65.9176 | 13.2 | 10.8292 | 2.3708 |  | 31-03-2026 16:30 | 68.198 | 69.948 | 1541.1 | 11.658 | 10.9863 | 0.67173 | 65.9176 | 13.3 | 10.8292 | 2.4708 |  | 31-03-2026 16:30 | 64.79 | 65.703 | 1460.7 | 10.9505 | 10.4521 | 0.49842 | 62.7125 | 12.6 | 10.3026 | 2.2974 |  | 31-03-2026 16:30 | 120.0983 | 113.7231 | 6.3753 | 682.3383 | 138.2 | 112.0968 | 26.1032 | 18.1017
31-03-2026 16:20 | 301 | 51.09 | 109.796 | 111.004 | 2043 | 18.5007 | 17.7661 | 0.73457 | 106.5966 | 16.7 | 17.512 | -0.81205 |  | 31-03-2026 16:20 | 110.3 | 114.749 | 2056.3 | 19.1248 | 17.7661 | 1.3587 | 106.5966 | 18.2 | 17.512 | 0.68795 |  | 31-03-2026 16:20 | 111.022 | 113.231 | 2026.6 | 18.8718 | 17.7661 | 1.1057 | 106.5966 | 16.5 | 17.512 | -1.012 |  | 31-03-2026 16:20 | 111.025 | 112.465 | 2036.7 | 18.7442 | 17.7661 | 0.97807 | 106.5966 | 16.6 | 17.512 | -0.91205 |  | 31-03-2026 16:20 | 82.98 | 84.073 | 1525.4 | 14.0122 | 13.1601 | 0.85209 | 78.9604 | 12.4 | 12.9719 | -0.57189 |  | 31-03-2026 16:20 | 81.902 | 82.981 | 1512 | 13.8302 | 13.1601 | 0.67009 | 78.9604 | 12.2 | 12.9719 | -0.77189 |  | 31-03-2026 16:20 | 82.212 | 83.203 | 1514.7 | 13.8672 | 13.1601 | 0.70709 | 78.9604 | 12.3 | 12.9719 | -0.67189 |  | 31-03-2026 16:20 | 82.709 | 84.981 | 1527.8 | 14.1635 | 13.1601 | 1.0034 | 78.9604 | 12.4 | 12.9719 | -0.57189 |  | 31-03-2026 16:20 | 78.202 | 79.256 | 1448.1 | 13.2093 | 12.5202 | 0.68915 | 75.1211 | 11.8 | 12.3411 | -0.54114 |  | 31-03-2026 16:20 | 144.3238 | 136.2249 | 8.0989 | 817.3493 | 129.1 | 134.2769 | -5.1769 | -15.2238
31-03-2026 16:10 | 311 | 51.37 | 114.284 | 115.754 | 2026.3 | 19.2923 | 18.3365 | 0.95579 | 110.0192 | 23.5 | 18.0743 | 5.4257 |  | 31-03-2026 16:10 | 127.03 | 128.729 | 2038.1 | 21.4548 | 18.3365 | 3.1183 | 110.0192 | 22.6 | 18.0743 | 4.5257 |  | 31-03-2026 16:10 | 113.021 | 114.7 | 2010.1 | 19.1167 | 18.3365 | 0.78013 | 110.0192 | 23.2 | 18.0743 | 5.1257 |  | 31-03-2026 16:10 | 113.742 | 115.252 | 2020.1 | 19.2087 | 18.3365 | 0.87213 | 110.0192 | 23.5 | 18.0743 | 5.4257 |  | 31-03-2026 16:10 | 83.665 | 84.784 | 1513 | 14.1307 | 13.5826 | 0.54804 | 81.4957 | 17.4 | 13.3884 | 4.0116 |  | 31-03-2026 16:10 | 83.248 | 84.37 | 1499.8 | 14.0617 | 13.5826 | 0.47904 | 81.4957 | 17.3 | 13.3884 | 3.9116 |  | 31-03-2026 16:10 | 84.14 | 85.248 | 1502.4 | 14.208 | 13.5826 | 0.62538 | 81.4957 | 17.1 | 13.3884 | 3.7116 |  | 31-03-2026 16:10 | 84.518 | 86.449 | 1515.4 | 14.4082 | 13.5826 | 0.82554 | 81.4957 | 17.2 | 13.3884 | 3.8116 |  | 31-03-2026 16:10 | 80.329 | 81.428 | 1436.3 | 13.5713 | 12.9222 | 0.64915 | 77.5331 | 16.2 | 12.7374 | 3.4626 |  | 31-03-2026 16:10 | 149.4523 | 140.5988 | 8.8535 | 843.593 | 178 | 138.5883 | 39.4117 | 28.5477
31-03-2026 16:00 | 354 | 51.09 | 123.157 | 124.741 | 2002.8 | 20.7902 | 20.8944 | -0.10418 | 125.3661 | 23.5 | 20.5956 | 2.9044 |  | 31-03-2026 16:00 | 127.929 | 129.627 | 2015.5 | 21.6045 | 20.8944 | 0.71015 | 125.3661 | 23.6 | 20.5956 | 3.0044 |  | 31-03-2026 16:00 | 132.23 | 134.881 | 1986.9 | 22.4802 | 20.8944 | 1.5858 | 125.3661 | 23.6 | 20.5956 | 3.0044 |  | 31-03-2026 16:00 | 126.522 | 128.201 | 1996.6 | 21.3668 | 20.8944 | 0.47248 | 125.3661 | 23.3 | 20.5956 | 2.7044 |  | 31-03-2026 16:00 | 95.332 | 96.87 | 1495.6 | 16.145 | 15.4773 | 0.6677 | 92.8638 | 17.4 | 15.256 | 2.144 |  | 31-03-2026 16:00 | 93.932 | 94.897 | 1482.5 | 15.8162 | 15.4773 | 0.33887 | 92.8638 | 17.2 | 15.256 | 1.944 |  | 31-03-2026 16:00 | 95.351 | 96.649 | 1485.3 | 16.1082 | 15.4773 | 0.63087 | 92.8638 | 17.7 | 15.256 | 2.444 |  | 31-03-2026 16:00 | 96.349 | 99.11 | 1498.2 | 16.5183 | 15.4773 | 1.041 | 92.8638 | 17.6 | 15.256 | 2.344 |  | 31-03-2026 16:00 | 90.585 | 91.76 | 1420.1 | 15.2933 | 14.7247 | 0.5686 | 88.3484 | 16.7 | 14.5142 | 2.1858 |  | 31-03-2026 16:00 | 166.1227 | 160.2113 | 5.9113 | 961.268 | 180.6 | 157.9203 | 22.6797 | 14.4773
31-03-2026 15:50 | 488 | 51.95 | 195.68 | 183.567 | 1979.3 | 30.5945 | 28.7081 | 1.8864 | 172.2486 | 27.7 | 28.2976 | -0.59758 |  | 31-03-2026 15:50 | 174.171 | 175.795 | 1991.9 | 29.2992 | 28.7081 | 0.59107 | 172.2486 | 28.2 | 28.2976 | -0.097576 |  | 31-03-2026 15:50 | 175.207 | 179.392 | 1963.3 | 29.8987 | 28.7081 | 1.1906 | 172.2486 | 27.7 | 28.2976 | -0.59758 |  | 31-03-2026 15:50 | 173.386 | 175.088 | 1973.3 | 29.1813 | 28.7081 | 0.47323 | 172.2486 | 28 | 28.2976 | -0.29758 |  | 31-03-2026 15:50 | 133.708 | 135.455 | 1478.2 | 22.5758 | 21.2653 | 1.3106 | 127.5916 | 21.4 | 20.9612 | 0.43883 |  | 31-03-2026 15:50 | 129.822 | 132.038 | 1465.3 | 22.0063 | 21.2653 | 0.74107 | 127.5916 | 21 | 20.9612 | 0.038833 |  | 31-03-2026 15:50 | 127.215 | 128.878 | 1467.6 | 21.4797 | 21.2653 | 0.21441 | 127.5916 | 20.8 | 20.9612 | -0.16117 |  | 31-03-2026 15:50 | 126.189 | 130.85 | 1480.6 | 21.8083 | 21.2653 | 0.54307 | 127.5916 | 21.2 | 20.9612 | 0.23883 |  | 31-03-2026 15:50 | 118.763 | 120.352 | 1403.4 | 20.0587 | 20.2313 | -0.17259 | 121.3876 | 19.9 | 19.942 | -0.041955 |  | 31-03-2026 15:50 | 226.9025 | 220.1247 | 6.7778 | 1320.7483 | 215.9 | 216.9769 | -1.0769 | -11.0025
31-03-2026 15:40 | 593 | 51.95 | 211.302 | 215.63 | 1951.6 | 35.9383 | 34.885 | 1.0533 | 209.3103 | 32.5 | 34.3862 | -1.8862 |  | 31-03-2026 15:40 | 204.705 | 208.182 | 1963.7 | 34.697 | 34.885 | -0.18805 | 209.3103 | 34.5 | 34.3862 | 0.11381 |  | 31-03-2026 15:40 | 208.511 | 212.822 | 1935.6 | 35.4703 | 34.885 | 0.58528 | 209.3103 | 32.4 | 34.3862 | -1.9862 |  | 31-03-2026 15:40 | 211.895 | 214.925 | 1945.3 | 35.8208 | 34.885 | 0.93578 | 209.3103 | 32.5 | 34.3862 | -1.8862 |  | 31-03-2026 15:40 | 164.314 | 166.546 | 1456.8 | 27.7577 | 25.8408 | 1.9169 | 155.0447 | 23.9 | 25.4713 | -1.5713 |  | 31-03-2026 15:40 | 161.973 | 164.156 | 1444.3 | 27.3593 | 25.8408 | 1.5186 | 155.0447 | 23.5 | 25.4713 | -1.9713 |  | 31-03-2026 15:40 | 162.167 | 164.353 | 1446.8 | 27.3922 | 25.8408 | 1.5514 | 155.0447 | 23.9 | 25.4713 | -1.5713 |  | 31-03-2026 15:40 | 163.121 | 167.734 | 1459.4 | 27.9557 | 25.8408 | 2.1149 | 155.0447 | 24.1 | 25.4713 | -1.3713 |  | 31-03-2026 15:40 | 154.419 | 156.516 | 1383.5 | 26.086 | 24.5843 | 1.5017 | 147.5058 | 22.7 | 24.2327 | -1.5327 |  | 31-03-2026 15:40 | 278.4773 | 267.4876 | 10.9897 | 1604.9257 | 250 | 263.6625 | -13.6625 | -28.4773
31-03-2026 15:30 | 499 | 51.95 | 177.554 | 179.947 | 1919.1 | 29.9912 | 29.3552 | 0.63596 | 176.1313 | 36 | 28.9354 | 7.0646 |  | 31-03-2026 15:30 | 179.253 | 182.236 | 1929.2 | 30.3727 | 29.3552 | 1.0175 | 176.1313 | 35 | 28.9354 | 6.0646 |  | 31-03-2026 15:30 | 177.374 | 181.777 | 1903.2 | 30.2962 | 29.3552 | 0.94096 | 176.1313 | 35.8 | 28.9354 | 6.8646 |  | 31-03-2026 15:30 | 177.525 | 180.009 | 1912.8 | 30.0015 | 29.3552 | 0.64629 | 176.1313 | 35.9 | 28.9354 | 6.9646 |  | 31-03-2026 15:30 | 133.566 | 135.339 | 1432.9 | 22.5565 | 21.7446 | 0.8119 | 130.4676 | 27 | 21.4337 | 5.5663 |  | 31-03-2026 15:30 | 128.135 | 130.017 | 1420.8 | 21.6695 | 21.7446 | -0.0751 | 130.4676 | 26.8 | 21.4337 | 5.3663 |  | 31-03-2026 15:30 | 128.998 | 131.077 | 1422.9 | 21.8462 | 21.7446 | 0.10157 | 130.4676 | 26.4 | 21.4337 | 4.9663 |  | 31-03-2026 15:30 | 130.076 | 133.933 | 1435.3 | 22.3222 | 21.7446 | 0.57757 | 130.4676 | 26.5 | 21.4337 | 5.0663 |  | 31-03-2026 15:30 | 123.068 | 124.727 | 1360.8 | 20.7878 | 20.6873 | 0.10054 | 124.1238 | 25.2 | 20.3915 | 4.8085 |  | 31-03-2026 15:30 | 229.8437 | 225.0865 | 4.7571 | 1350.5192 | 274.6 | 221.8678 | 52.7322 | 44.7563
31-03-2026 15:20 | 426 | 51.37 | 156.849 | 158.899 | 1883.1 | 26.4832 | 25.1169 | 1.3662 | 150.7016 | 24.3 | 24.7578 | -0.45776 |  | 31-03-2026 15:20 | 161.279 | 163.486 | 1894.2 | 27.2477 | 25.1169 | 2.1307 | 150.7016 | 23.5 | 24.7578 | -1.2578 |  | 31-03-2026 15:20 | 156.512 | 159.882 | 1867.4 | 26.647 | 25.1169 | 1.5301 | 150.7016 | 23.5 | 24.7578 | -1.2578 |  | 31-03-2026 15:20 | 156.634 | 158.778 | 1876.9 | 26.463 | 25.1169 | 1.3461 | 150.7016 | 23.5 | 24.7578 | -1.2578 |  | 31-03-2026 15:20 | 116.135 | 117.641 | 1405.9 | 19.6068 | 18.6051 | 1.0017 | 111.6308 | 17.6 | 18.3391 | -0.73908 |  | 31-03-2026 15:20 | 114.538 | 116.011 | 1394 | 19.3352 | 18.6051 | 0.73003 | 111.6308 | 17.3 | 18.3391 | -1.0391 |  | 31-03-2026 15:20 | 115.368 | 116.864 | 1396.5 | 19.4773 | 18.6051 | 0.8722 | 111.6308 | 17.3 | 18.3391 | -1.0391 |  | 31-03-2026 15:20 | 116.239 | 119.575 | 1408.8 | 19.9292 | 18.6051 | 1.324 | 111.6308 | 17.5 | 18.3391 | -0.83908 |  | 31-03-2026 15:20 | 109.993 | 111.442 | 1335.6 | 18.5737 | 17.7005 | 0.87318 | 106.2029 | 16.6 | 17.4474 | -0.84736 |  | 31-03-2026 15:20 | 203.763 | 192.5888 | 11.1742 | 1155.5325 | 181.1 | 189.8347 | -8.7347 | -22.663
31-03-2026 15:10 | 382 | 51.95 | 134.437 | 136.222 | 1858.8 | 22.7037 | 22.4723 | 0.23134 | 134.834 | 27.2 | 22.151 | 5.049 |  | 31-03-2026 15:10 | 139.276 | 141.153 | 1870.7 | 23.5255 | 22.4723 | 1.0532 | 134.834 | 27.6 | 22.151 | 5.449 |  | 31-03-2026 15:10 | 137.988 | 140.874 | 1843.9 | 23.479 | 22.4723 | 1.0067 | 134.834 | 27.3 | 22.151 | 5.149 |  | 31-03-2026 15:10 | 137.957 | 139.831 | 1853.4 | 23.3052 | 22.4723 | 0.83284 | 134.834 | 27.3 | 22.151 | 5.149 |  | 31-03-2026 15:10 | 100.901 | 102.22 | 1388.3 | 17.0367 | 16.6462 | 0.3905 | 99.877 | 20.1 | 16.4081 | 3.6919 |  | 31-03-2026 15:10 | 99.807 | 101.122 | 1376.7 | 16.8537 | 16.6462 | 0.2075 | 99.877 | 19.8 | 16.4081 | 3.3919 |  | 31-03-2026 15:10 | 99.903 | 101.237 | 1379.2 | 16.8728 | 16.6462 | 0.22667 | 99.877 | 19.9 | 16.4081 | 3.4919 |  | 31-03-2026 15:10 | 100.344 | 103.317 | 1391.3 | 17.2195 | 16.6462 | 0.57333 | 99.877 | 19.9 | 16.4081 | 3.4919 |  | 31-03-2026 15:10 | 95.271 | 96.536 | 1319 | 16.0893 | 15.8368 | 0.25257 | 95.0206 | 19.1 | 15.6103 | 3.4897 |  | 31-03-2026 15:10 | 177.0853 | 172.3107 | 4.7746 | 1033.8644 | 208.2 | 169.8467 | 38.3533 | 31.1147
31-03-2026 15:00 | 463 | 52.23 | 195.822 | 165.084 | 1831.6 | 27.514 | 27.2079 | 0.30607 | 163.2476 | 40.1 | 26.8189 | 13.2811 | 1.1862 | 31-03-2026 15:00 | 183.481 | 186.105 | 1843.1 | 31.0175 | 27.2079 | 3.8096 | 163.2476 | 39.3 | 26.8189 | 12.4811 | 0.9859 | 31-03-2026 15:00 | 213.938 | 216.932 | 1816.6 | 36.1553 | 27.2079 | 8.9474 | 163.2476 | 38.8 | 26.8189 | 11.9811 | 0.9862 | 31-03-2026 15:00 | 186.013 | 190.34 | 1826.1 | 31.7233 | 27.2079 | 4.5154 | 163.2476 | 38.9 | 26.8189 | 12.0811 | 0.97727 | 31-03-2026 15:00 | 163.974 | 166.201 | 1368.2 | 27.7002 | 20.154 | 7.5461 | 120.9241 | 29 | 19.8658 | 9.1342 | 0.9866 | 31-03-2026 15:00 | 135.316 | 146.054 | 1356.9 | 24.3423 | 20.154 | 4.1883 | 120.9241 | 29 | 19.8658 | 9.1342 | 0.92648 | 31-03-2026 15:00 | 159.662 | 161.798 | 1359.3 | 26.9663 | 20.154 | 6.8123 | 120.9241 | 28.9 | 19.8658 | 9.0342 | 0.9868 | 31-03-2026 15:00 | 159.423 | 163.694 | 1371.4 | 27.2823 | 20.154 | 7.1283 | 120.9241 | 29.1 | 19.8658 | 9.2342 | 0.97391 | 31-03-2026 15:00 | 118.814 | 120.391 | 1299.9 | 20.0652 | 19.1741 | 0.89111 | 115.0443 | 27.3 | 18.8999 | 8.4001 | 0.9869 | 31-03-2026 15:00 | 252.7665 | 208.6218 | 44.1447 | 1251.7311 | 300.4 | 205.6385 | 94.7615 | 47.6335
31-03-2026 14:50 | 566 | 51.95 | 287.765 | 292.147 | 1791.5 | 48.6912 | 33.2967 | 15.3945 | 199.7801 | 27.7 | 32.8205 | -5.1205 | 0.985 | 31-03-2026 14:50 | 268.969 | 271.852 | 1803.8 | 45.3087 | 33.2967 | 12.012 | 199.7801 | 29.6 | 32.8205 | -3.2205 | 0.98939 | 31-03-2026 14:50 | 199.686 | 205.2 | 1777.8 | 34.2 | 33.2967 | 0.90331 | 199.7801 | 29 | 32.8205 | -3.8205 | 0.97313 | 31-03-2026 14:50 | 200.338 | 203.224 | 1787.2 | 33.8707 | 33.2967 | 0.57398 | 199.7801 | 29.1 | 32.8205 | -3.7205 | 0.9858 | 31-03-2026 14:50 | 157.68 | 159.805 | 1339.2 | 26.6342 | 24.6642 | 1.97 | 147.9853 | 21.7 | 24.3115 | -2.6115 | 0.9867 | 31-03-2026 14:50 | 162.433 | 164.606 | 1327.9 | 27.4343 | 24.6642 | 2.7701 | 147.9853 | 21 | 24.3115 | -3.3115 | 0.9868 | 31-03-2026 14:50 | 150.832 | 152.85 | 1330.4 | 25.475 | 24.6642 | 0.81078 | 147.9853 | 21.1 | 24.3115 | -3.2115 | 0.9868 | 31-03-2026 14:50 | 150.965 | 154.523 | 1342.3 | 25.7538 | 24.6642 | 1.0896 | 147.9853 | 21.2 | 24.3115 | -3.1115 | 0.97697 | 31-03-2026 14:50 | 143.985 | 145.955 | 1272.6 | 24.3258 | 23.4649 | 0.86089 | 140.7897 | 20.1 | 23.1294 | -3.0294 | 0.9865 | 31-03-2026 14:50 | 291.6937 | 255.3086 | 36.3851 | 1531.8515 | 220.5 | 251.6577 | -31.1577 | -71.1937
31-03-2026 14:40 | 561 | 52.52 | 198.708 | 201.57 | 1763.8 | 33.595 | 32.9299 | 0.66515 | 197.5791 | 40.1 | 32.459 | 7.641 | 0.9858 | 31-03-2026 14:40 | 200.239 | 203.165 | 1774.2 | 33.8608 | 32.9299 | 0.93098 | 197.5791 | 40.1 | 32.459 | 7.641 | 0.9856 | 31-03-2026 14:40 | 195.743 | 200.389 | 1748.8 | 33.3982 | 32.9299 | 0.46831 | 197.5791 | 39.8 | 32.459 | 7.341 | 0.97682 | 31-03-2026 14:40 | 196.832 | 199.708 | 1758.1 | 33.2847 | 32.9299 | 0.35481 | 197.5791 | 40 | 32.459 | 7.541 | 0.9856 | 31-03-2026 14:40 | 144.794 | 147.203 | 1317.5 | 24.5338 | 24.3925 | 0.14135 | 146.3549 | 29.8 | 24.0437 | 5.7563 | 0.98363 | 31-03-2026 14:40 | 143.869 | 145.838 | 1306.9 | 24.3063 | 24.3925 | -0.086151 | 146.3549 | 29.4 | 24.0437 | 5.3563 | 0.9865 | 31-03-2026 14:40 | 141.965 | 144.207 | 1309.3 | 24.0345 | 24.3925 | -0.35798 | 146.3549 | 29.3 | 24.0437 | 5.2563 | 0.98445 | 31-03-2026 14:40 | 142.754 | 146.853 | 1321.1 | 24.4755 | 24.3925 | 0.083016 | 146.3549 | 29.5 | 24.0437 | 5.4563 | 0.97209 | 31-03-2026 14:40 | 138.51 | 140.434 | 1252.5 | 23.4057 | 23.2064 | 0.19924 | 139.2386 | 28 | 22.8746 | 5.1254 | 0.9863 | 31-03-2026 14:40 | 254.8945 | 252.4958 | 2.3987 | 1514.9747 | 306 | 248.8851 | 57.1149 | 51.1055
31-03-2026 14:30 | 468 | 52.52 | 158.98 | 162.821 | 1723.7 | 27.1368 | 27.4709 | -0.33406 | 164.8254 | 33.6 | 27.0781 | 6.5219 | 0.97641 | 31-03-2026 14:30 | 170.85 | 174.285 | 1734.1 | 29.0475 | 27.4709 | 1.5766 | 164.8254 | 35.6 | 27.0781 | 8.5219 | 0.98029 | 31-03-2026 14:30 | 157.217 | 160.974 | 1709 | 26.829 | 27.4709 | -0.64189 | 164.8254 | 31.3 | 27.0781 | 4.2219 | 0.97666 | 31-03-2026 14:30 | 160.122 | 162.363 | 1718.1 | 27.0605 | 27.4709 | -0.41039 | 164.8254 | 32 | 27.0781 | 4.9219 | 0.9862 | 31-03-2026 14:30 | 117.163 | 118.754 | 1287.7 | 19.7923 | 20.3488 | -0.55648 | 122.0929 | 24.3 | 20.0578 | 4.2422 | 0.9866 | 31-03-2026 14:30 | 116.607 | 118.191 | 1277.5 | 19.6985 | 20.3488 | -0.65031 | 122.0929 | 23.5 | 20.0578 | 3.4422 | 0.9866 | 31-03-2026 14:30 | 115.755 | 117.315 | 1280 | 19.5525 | 20.3488 | -0.79631 | 122.0929 | 23.4 | 20.0578 | 3.3422 | 0.9867 | 31-03-2026 14:30 | 116.848 | 120.136 | 1291.6 | 20.0227 | 20.3488 | -0.32614 | 122.0929 | 23.6 | 20.0578 | 3.5422 | 0.97263 | 31-03-2026 14:30 | 111.168 | 112.689 | 1224.5 | 18.7815 | 19.3594 | -0.57787 | 116.1562 | 22.3 | 19.0825 | 3.2175 | 0.9865 | 31-03-2026 14:30 | 207.9213 | 210.6382 | -2.7169 | 1263.8292 | 249.6 | 207.6261 | 41.9739 | 41.6787
31-03-2026 14:20 | 878 | 53.09 | 300.506 | 305.579 | 1690.1 | 50.9298 | 51.4235 | -0.49367 | 308.541 | 54.2 | 50.6881 | 3.5119 | 0.9834 | 31-03-2026 14:20 | 316.287 | 308.41 | 1698.5 | 51.4017 | 51.4235 | -0.021834 | 308.541 | 54.6 | 50.6881 | 3.9119 | 1.0255 | 31-03-2026 14:20 | 293.628 | 303.375 | 1677.7 | 50.5625 | 51.4235 | -0.861 | 308.541 | 54.8 | 50.6881 | 4.1119 | 0.96787 | 31-03-2026 14:20 | 295.704 | 300.726 | 1686.1 | 50.121 | 51.4235 | -1.3025 | 308.541 | 54.2 | 50.6881 | 3.5119 | 0.9833 | 31-03-2026 14:20 | 218.535 | 222.186 | 1263.4 | 37.031 | 38.0915 | -1.0605 | 228.5489 | 41.4 | 37.5468 | 3.8532 | 0.98357 | 31-03-2026 14:20 | 217.194 | 221.646 | 1254 | 36.941 | 38.0915 | -1.1505 | 228.5489 | 41.3 | 37.5468 | 3.7532 | 0.97991 | 31-03-2026 14:20 | 219.066 | 222.737 | 1256.6 | 37.1228 | 38.0915 | -0.96865 | 228.5489 | 41.4 | 37.5468 | 3.8532 | 0.98352 | 31-03-2026 14:20 | 222.451 | 228.233 | 1268 | 38.0388 | 38.0915 | -0.052648 | 228.5489 | 42.2 | 37.5468 | 4.6532 | 0.97467 | 31-03-2026 14:20 | 209.167 | 212.309 | 1202.2 | 35.3848 | 36.2393 | -0.85449 | 217.436 | 39.9 | 35.7211 | 4.1789 | 0.9852 | 31-03-2026 14:20 | 387.5335 | 394.2993 | -6.7658 | 2365.7955 | 424 | 388.6608 | 35.3392 | 36.4665
31-03-2026 14:10 | 897 | 52.52 | 293.601 | 298.375 | 1635.9 | 49.7292 | 52.6525 | -2.9234 | 315.9153 | 44.4 | 51.8996 | -7.4996 | 0.984 | 31-03-2026 14:10 | 251.004 | 254.982 | 1643.9 | 42.497 | 52.6525 | -10.1555 | 315.9153 | 43.5 | 51.8996 | -8.3996 | 0.9844 | 31-03-2026 14:10 | 304.047 | 312.619 | 1622.9 | 52.1032 | 52.6525 | -0.54938 | 315.9153 | 45.3 | 51.8996 | -6.5996 | 0.97258 | 31-03-2026 14:10 | 300.117 | 305.121 | 1631.9 | 50.8535 | 52.6525 | -1.799 | 315.9153 | 45.6 | 51.8996 | -6.2996 | 0.9836 | 31-03-2026 14:10 | 224.58 | 227.907 | 1222 | 37.9845 | 39.0019 | -1.0174 | 234.0113 | 33.9 | 38.4442 | -4.5442 | 0.9854 | 31-03-2026 14:10 | 221.817 | 225.825 | 1212.7 | 37.6375 | 39.0019 | -1.3644 | 234.0113 | 33.5 | 38.4442 | -4.9442 | 0.98225 | 31-03-2026 14:10 | 214.986 | 223.693 | 1215.2 | 37.2822 | 39.0019 | -1.7197 | 234.0113 | 33.5 | 38.4442 | -4.9442 | 0.96108 | 31-03-2026 14:10 | 213.91 | 220.746 | 1225.8 | 36.791 | 39.0019 | -2.2109 | 234.0113 | 33.1 | 38.4442 | -5.3442 | 0.96903 | 31-03-2026 14:10 | 203.915 | 206.915 | 1162.3 | 34.4858 | 37.1055 | -2.6196 | 222.6328 | 31.5 | 36.5749 | -5.0749 | 0.9855 | 31-03-2026 14:10 | 379.3638 | 403.7232 | -24.3594 | 2422.3392 | 344.3 | 397.95 | -53.65 | -35.0638
31-03-2026 14:00 | 956 | 53.09 | 319.011 | 324.462 | 1591.5 | 54.077 | 55.9919 | -1.9149 | 335.9512 | 53.3 | 55.1912 | -1.8912 | 0.9832 | 31-03-2026 14:00 | 325.172 | 330.897 | 1600.4 | 55.1495 | 55.9919 | -0.84237 | 335.9512 | 53 | 55.1912 | -2.1912 | 0.9827 | 31-03-2026 14:00 | 319.641 | 328.884 | 1577.6 | 54.814 | 55.9919 | -1.1779 | 335.9512 | 52.9 | 55.1912 | -2.2912 | 0.9719 | 31-03-2026 14:00 | 321.546 | 327.207 | 1586.3 | 54.5345 | 55.9919 | -1.4574 | 335.9512 | 52.8 | 55.1912 | -2.3912 | 0.9827 | 31-03-2026 14:00 | 241.661 | 245.516 | 1188.1 | 40.9193 | 41.4755 | -0.55613 | 248.8528 | 40.1 | 40.8824 | -0.78236 | 0.9843 | 31-03-2026 14:00 | 237.951 | 242.607 | 1179.2 | 40.4345 | 41.4755 | -1.041 | 248.8528 | 39.5 | 40.8824 | -1.3824 | 0.98081 | 31-03-2026 14:00 | 239.234 | 244.095 | 1181.7 | 40.6825 | 41.4755 | -0.79296 | 248.8528 | 39.5 | 40.8824 | -1.3824 | 0.98009 | 31-03-2026 14:00 | 241.28 | 248.435 | 1192.7 | 41.4058 | 41.4755 | -0.06963 | 248.8528 | 39.9 | 40.8824 | -0.98236 | 0.9712 | 31-03-2026 14:00 | 228.342 | 231.961 | 1130.8 | 38.6602 | 39.4588 | -0.7986 | 236.7526 | 37.7 | 38.8945 | -1.1945 | 0.9844 | 31-03-2026 14:00 | 420.6773 | 429.3281 | -8.6508 | 2575.9687 | 408.7 | 423.1887 | -14.4887 | -11.9773
AVG of 13:40 & 14:00 | 1031 | 53.09 | 352.812 | 351.519 | 1538.2 | 58.5865 | 60.3845 | -1.798 | 362.3073 | 60.4 | 59.521 | 0.87896 | 1.0037 | 31-03-2026 13:50 | 332.633 | 337.801 | 1547.4 | 56.3002 | 60.3845 | -4.0844 | 362.3073 | 56.1 | 59.521 | -3.421 | 0.9847 | 31-03-2026 13:50 | 343.461 | 353.993 | 1524.7 | 58.9988 | 60.3845 | -1.3857 | 362.3073 | 56.6 | 59.521 | -2.921 | 0.97025 | 31-03-2026 13:50 | 329.381 | 334.533 | 1533.5 | 55.7555 | 60.3845 | -4.629 | 362.3073 | 56 | 59.521 | -3.521 | 0.9846 | 31-03-2026 13:50 | 266.427 | 270.842 | 1148 | 45.1403 | 44.7293 | 0.41104 | 268.3757 | 43.9 | 44.0897 | -0.18966 | 0.9837 | 31-03-2026 13:50 | 262.341 | 267.507 | 1139.7 | 44.5845 | 44.7293 | -0.14479 | 268.3757 | 43.2 | 44.0897 | -0.88966 | 0.98069 | 31-03-2026 13:50 | 263.298 | 269.016 | 1142.2 | 44.836 | 44.7293 | 0.10671 | 268.3757 | 43.4 | 44.0897 | -0.68966 | 0.97874 | 31-03-2026 13:50 | 264.496 | 272.828 | 1152.8 | 45.4713 | 44.7293 | 0.74204 | 268.3757 | 44.3 | 44.0897 | 0.21034 | 0.96946 | 31-03-2026 13:50 | 250.138 | 254.231 | 1093.1 | 42.3718 | 42.5544 | -0.18255 | 255.3263 | 41.9 | 41.9459 | -0.045853 | 0.9839 | AVG of 13:40 & 14:00 | 452.045 | 463.0097 | -10.9647 | 2778.0583 | 445.8 | 456.3887 | -10.5887 | -6.245
31-03-2026 13:40 | 1106 | 53.09 | 352.78 | 358.553 | 1477.8 | 59.7588 | 64.7772 | -5.0184 | 388.6633 | 49.2 | 63.8509 | -14.6509 | 0.9839 | 31-03-2026 13:40 | 339.491 | 344.696 | 1491.3 | 57.4493 | 64.7772 | -7.3279 | 388.6633 | 51.2 | 63.8509 | -12.6509 | 0.9849 | 31-03-2026 13:40 | 343.594 | 353.436 | 1468.1 | 58.906 | 64.7772 | -5.8712 | 388.6633 | 49.3 | 63.8509 | -14.5509 | 0.97215 | 31-03-2026 13:40 | 341.413 | 346.718 | 1477.5 | 57.7863 | 64.7772 | -6.9909 | 388.6633 | 49.4 | 63.8509 | -14.4509 | 0.9847 | 31-03-2026 13:40 | 273.852 | 278.333 | 1104.1 | 46.3888 | 47.9831 | -1.5943 | 287.8987 | 37.7 | 47.297 | -9.597 | 0.9839 | 31-03-2026 13:40 | 270.161 | 275.281 | 1096.5 | 45.8802 | 47.9831 | -2.103 | 287.8987 | 37.3 | 47.297 | -9.997 | 0.9814 | 31-03-2026 13:40 | 270.405 | 276.207 | 1098.8 | 46.0345 | 47.9831 | -1.9486 | 287.8987 | 37.3 | 47.297 | -9.997 | 0.97899 | 31-03-2026 13:40 | 272.701 | 280.701 | 1108.5 | 46.7835 | 47.9831 | -1.1996 | 287.8987 | 37 | 47.297 | -10.297 | 0.9715 | 31-03-2026 13:40 | 257.715 | 261.837 | 1051.2 | 43.6395 | 45.65 | -2.0105 | 273.9 | 35 | 44.9972 | -9.9972 | 0.98426 | 31-03-2026 13:40 | 462.627 | 496.6913 | -34.0643 | 2980.1479 | 383.4 | 489.5886 | -106.1886 | -79.227
31-03-2026 13:30 | 900 | 53.09 | 293.793 | 271.331 | 1428.6 | 45.2218 | 52.712 | -7.4902 | 316.2721 | 47.5 | 51.9582 | -4.4582 | 1.0828 | 31-03-2026 13:30 | 292.23 | 297.516 | 1440.1 | 49.586 | 52.712 | -3.126 | 316.2721 | 47.5 | 51.9582 | -4.4582 | 0.98223 | 31-03-2026 13:30 | 304.181 | 311.662 | 1418.8 | 51.9437 | 52.712 | -0.76835 | 316.2721 | 48.4 | 51.9582 | -3.5582 | 0.976 | 31-03-2026 13:30 | 296.589 | 301.565 | 1428.1 | 50.2608 | 52.712 | -2.4512 | 316.2721 | 48.4 | 51.9582 | -3.5582 | 0.9835 | 31-03-2026 13:30 | 226.286 | 229.802 | 1066.4 | 38.3003 | 39.0459 | -0.7456 | 234.2756 | 36.6 | 38.4876 | -1.8876 | 0.9847 | 31-03-2026 13:30 | 221.708 | 226.561 | 1059.2 | 37.7602 | 39.0459 | -1.2858 | 234.2756 | 36.2 | 38.4876 | -2.2876 | 0.97858 | 31-03-2026 13:30 | 225.151 | 229.368 | 1061.5 | 38.228 | 39.0459 | -0.81794 | 234.2756 | 36.3 | 38.4876 | -2.1876 | 0.98161 | 31-03-2026 13:30 | 227.037 | 233.518 | 1071.5 | 38.9197 | 39.0459 | -0.12627 | 234.2756 | 36.6 | 38.4876 | -1.8876 | 0.97225 | 31-03-2026 13:30 | 214.096 | 217.334 | 1016.2 | 36.2223 | 37.1474 | -0.92504 | 222.8842 | 35.1 | 36.6162 | -1.5162 | 0.9851 | 31-03-2026 13:30 | 386.4428 | 404.1792 | -17.7364 | 2425.0751 | 372.6 | 398.3994 | -25.7994 | -13.8428
31-03-2026 13:20 | 1042 | 53.96 | 343.355 | 349.471 | 1381.1 | 58.2452 | 60.8227 | -2.5775 | 364.9362 | 54.4 | 59.9529 | -5.5529 | 0.9825 | 31-03-2026 13:20 | 340.896 | 346.545 | 1392.6 | 57.7575 | 60.8227 | -3.0652 | 364.9362 | 55.6 | 59.9529 | -4.3529 | 0.9837 | 31-03-2026 13:20 | 342.245 | 354.027 | 1370.4 | 59.0045 | 60.8227 | -1.8182 | 364.9362 | 54.6 | 59.9529 | -5.3529 | 0.96672 | 31-03-2026 13:20 | 333.835 | 339.125 | 1379.7 | 56.5208 | 60.8227 | -4.3019 | 364.9362 | 54.4 | 59.9529 | -5.5529 | 0.9844 | 31-03-2026 13:20 | 262.18 | 266.619 | 1029.8 | 44.4365 | 45.0539 | -0.61736 | 270.3231 | 41.9 | 44.4096 | -2.5096 | 0.98335 | 31-03-2026 13:20 | 258.332 | 263.475 | 1023 | 43.9125 | 45.0539 | -1.1414 | 270.3231 | 41.1 | 44.4096 | -3.3096 | 0.98048 | 31-03-2026 13:20 | 262.577 | 268.521 | 1025.2 | 44.7535 | 45.0539 | -0.30036 | 270.3231 | 41.5 | 44.4096 | -2.9096 | 0.97786 | 31-03-2026 13:20 | 265.068 | 273.344 | 1034.9 | 45.5573 | 45.0539 | 0.50348 | 270.3231 | 41.7 | 44.4096 | -2.7096 | 0.96972 | 31-03-2026 13:20 | 243.064 | 246.365 | 981.1 | 41.0608 | 42.8632 | -1.8023 | 257.179 | 39.3 | 42.2502 | -2.9502 | 0.9866 | 31-03-2026 13:20 | 451.2487 | 466.3694 | -15.1207 | 2798.2165 | 424.5 | 459.7003 | -35.2003 | -26.7487
31-03-2026 13:10 | 890 | 52.52 | 304.363 | 309.375 | 1326.7 | 51.5625 | 52.2417 | -0.67916 | 313.4499 | 50 | 51.4946 | -1.4946 | 0.9838 | 31-03-2026 13:10 | 319.464 | 324.923 | 1337 | 54.1538 | 52.2417 | 1.9122 | 313.4499 | 47.9 | 51.4946 | -3.5946 | 0.9832 | 31-03-2026 13:10 | 301.537 | 308.244 | 1315.8 | 51.374 | 52.2417 | -0.86766 | 313.4499 | 48.6 | 51.4946 | -2.8946 | 0.97824 | 31-03-2026 13:10 | 305.529 | 310.655 | 1325.3 | 51.7758 | 52.2417 | -0.46582 | 313.4499 | 48.2 | 51.4946 | -3.2946 | 0.9835 | 31-03-2026 13:10 | 222.155 | 225.492 | 987.9 | 37.582 | 38.6975 | -1.1155 | 232.1851 | 36.1 | 38.1441 | -2.0441 | 0.9852 | 31-03-2026 13:10 | 222.265 | 225.627 | 981.9 | 37.6045 | 38.6975 | -1.093 | 232.1851 | 35.7 | 38.1441 | -2.4441 | 0.9851 | 31-03-2026 13:10 | 217.915 | 221.722 | 983.7 | 36.9537 | 38.6975 | -1.7439 | 232.1851 | 35.7 | 38.1441 | -2.4441 | 0.98283 | 31-03-2026 13:10 | 234.23 | 226.063 | 993.2 | 37.6772 | 38.6975 | -1.0204 | 232.1851 | 36.5 | 38.1441 | -1.6441 | 1.0361 | 31-03-2026 13:10 | 221.291 | 224.638 | 941.8 | 37.4397 | 36.8159 | 0.62377 | 220.8954 | 33.9 | 36.2894 | -2.3894 | 0.9851 | 31-03-2026 13:10 | 396.1232 | 400.5726 | -4.4495 | 2403.4358 | 372.6 | 394.8444 | -22.2444 | -23.5232
31-03-2026 13:00 | 792 | 52.23 | 254.499 | 245.836 | 1276.7 | 40.9727 | 46.5414 | -5.5688 | 279.2485 | 50 | 45.8759 | 4.1241 | 1.0352 | 31-03-2026 13:00 | 263.94 | 268.259 | 1289.1 | 44.7098 | 46.5414 | -1.8316 | 279.2485 | 52.2 | 45.8759 | 6.3241 | 0.9839 | 31-03-2026 13:00 | 273.76 | 282.348 | 1267.2 | 47.058 | 46.5414 | 0.51658 | 279.2485 | 51.6 | 45.8759 | 5.7241 | 0.96958 | 31-03-2026 13:00 | 265.545 | 269.89 | 1277.1 | 44.9817 | 46.5414 | -1.5598 | 279.2485 | 52.5 | 45.8759 | 6.6241 | 0.9839 | 31-03-2026 13:00 | 199.594 | 202.572 | 951.8 | 33.762 | 34.4751 | -0.71313 | 206.8508 | 39.9 | 33.9821 | 5.9179 | 0.9853 | 31-03-2026 13:00 | 195.588 | 199.893 | 946.2 | 33.3155 | 34.4751 | -1.1596 | 206.8508 | 39.3 | 33.9821 | 5.3179 | 0.97846 | 31-03-2026 13:00 | 199.207 | 202.68 | 948 | 33.78 | 34.4751 | -0.69513 | 206.8508 | 39.5 | 33.9821 | 5.5179 | 0.98286 | 31-03-2026 13:00 | 206.01 | 209.959 | 956.7 | 34.9932 | 34.4751 | 0.51804 | 206.8508 | 39.4 | 33.9821 | 5.4179 | 0.98119 | 31-03-2026 13:00 | 194.818 | 197.725 | 907.9 | 32.9542 | 32.7988 | 0.15535 | 196.7929 | 37.2 | 32.3298 | 4.8702 | 0.9853 | 31-03-2026 13:00 | 346.527 | 356.865 | -10.338 | 2141.1901 | 401.6 | 351.7618 | 49.8382 | 55.073
31-03-2026 12:50 | 855 | 52.52 | 287.527 | 292.232 | 1226.7 | 48.7053 | 50.1872 | -1.4819 | 301.1233 | 48.6 | 49.4695 | -0.86953 | 0.9839 | 31-03-2026 12:50 | 290.932 | 296.381 | 1236.9 | 49.3968 | 50.1872 | -0.79038 | 301.1233 | 49.9 | 49.4695 | 0.43047 | 0.98161 | 31-03-2026 12:50 | 289.195 | 296.073 | 1215.6 | 49.3455 | 50.1872 | -0.84171 | 301.1233 | 47.7 | 49.4695 | -1.7695 | 0.97677 | 31-03-2026 12:50 | 292.595 | 297.474 | 1224.6 | 49.579 | 50.1872 | -0.60821 | 301.1233 | 48.5 | 49.4695 | -0.96953 | 0.9836 | 31-03-2026 12:50 | 215.544 | 218.826 | 911.9 | 36.471 | 37.1757 | -0.70471 | 223.0543 | 35.9 | 36.6441 | -0.7441 | 0.985 | 31-03-2026 12:50 | 214.358 | 217.6 | 906.9 | 36.2667 | 37.1757 | -0.90904 | 223.0543 | 35.4 | 36.6441 | -1.2441 | 0.9851 | 31-03-2026 12:50 | 213.536 | 217.37 | 908.5 | 36.2283 | 37.1757 | -0.94738 | 223.0543 | 35.9 | 36.6441 | -0.7441 | 0.98236 | 31-03-2026 12:50 | 216.442 | 222.437 | 917.3 | 37.0728 | 37.1757 | -0.10288 | 223.0543 | 36.2 | 36.6441 | -0.4441 | 0.97305 | 31-03-2026 12:50 | 203.581 | 206.711 | 870.7 | 34.4518 | 35.3681 | -0.91625 | 212.2085 | 34.3 | 34.8623 | -0.56232 | 0.98486 | 31-03-2026 12:50 | 377.5173 | 384.8198 | -7.3024 | 2308.9186 | 372.4 | 379.3169 | -6.9169 | -5.1173
31-03-2026 12:40 | 746 | 51.95 | 252.799 | 256.805 | 1178.1 | 42.8008 | 43.8857 | -1.0849 | 263.3145 | 45.6 | 43.2582 | 2.3418 | 0.9844 | 31-03-2026 12:40 | 263.504 | 264.383 | 1187 | 44.0638 | 43.8857 | 0.17809 | 263.3145 | 44.8 | 43.2582 | 1.5418 | 0.99668 | 31-03-2026 12:40 | 251.18 | 257.429 | 1167.9 | 42.9048 | 43.8857 | -0.98091 | 263.3145 | 43.7 | 43.2582 | 0.44182 | 0.97573 | 31-03-2026 12:40 | 257.932 | 262.126 | 1176.1 | 43.6877 | 43.8857 | -0.19808 | 263.3145 | 43.1 | 43.2582 | -0.15818 | 0.984 | 31-03-2026 12:40 | 189.294 | 192.118 | 876 | 32.0197 | 32.508 | -0.48829 | 195.0478 | 32.8 | 32.0431 | 0.7569 | 0.9853 | 31-03-2026 12:40 | 188.661 | 190.421 | 871.5 | 31.7368 | 32.508 | -0.77113 | 195.0478 | 32.3 | 32.0431 | 0.2569 | 0.99076 | 31-03-2026 12:40 | 188.542 | 192.201 | 872.6 | 32.0335 | 32.508 | -0.47446 | 195.0478 | 32.2 | 32.0431 | 0.1569 | 0.98096 | 31-03-2026 12:40 | 190.012 | 195.344 | 881.1 | 32.5573 | 32.508 | 0.049374 | 195.0478 | 32.4 | 32.0431 | 0.3569 | 0.9727 | 31-03-2026 12:40 | 179.654 | 182.631 | 836.4 | 30.4385 | 30.9273 | -0.4888 | 185.5638 | 30.9 | 30.485 | 0.41496 | 0.9837 | 31-03-2026 12:40 | 332.243 | 336.5021 | -4.2591 | 2019.0127 | 337.8 | 331.6901 | 6.1099 | 5.557
31-03-2026 12:30 | 719 | 52.23 | 242.87 | 246.819 | 1132.5 | 41.1365 | 42.2516 | -1.1151 | 253.5097 | 54.1 | 41.6474 | 12.4526 | 0.984 | 31-03-2026 12:30 | 250.505 | 254.63 | 1142.2 | 42.4383 | 42.2516 | 0.18671 | 253.5097 | 54.3 | 41.6474 | 12.6526 | 0.9838 | 31-03-2026 12:30 | 237.164 | 244.039 | 1124.2 | 40.6732 | 42.2516 | -1.5785 | 253.5097 | 54 | 41.6474 | 12.3526 | 0.97183 | 31-03-2026 12:30 | 239.004 | 242.866 | 1133 | 40.4777 | 42.2516 | -1.774 | 253.5097 | 54.3 | 41.6474 | 12.6526 | 0.9841 | 31-03-2026 12:30 | 178.359 | 181.057 | 843.2 | 30.1762 | 31.2975 | -1.1213 | 187.785 | 41 | 30.8499 | 10.1501 | 0.9851 | 31-03-2026 12:30 | 175.646 | 178.597 | 839.2 | 29.7662 | 31.2975 | -1.5313 | 187.785 | 40.7 | 30.8499 | 9.8501 | 0.98348 | 31-03-2026 12:30 | 176.42 | 179.813 | 840.4 | 29.9688 | 31.2975 | -1.3287 | 187.785 | 41 | 30.8499 | 10.1501 | 0.98113 | 31-03-2026 12:30 | 178.103 | 183.572 | 848.7 | 30.5953 | 31.2975 | -0.70216 | 187.785 | 41.4 | 30.8499 | 10.5501 | 0.97021 | 31-03-2026 12:30 | 166.382 | 169.03 | 805.5 | 28.1717 | 29.7757 | -1.604 | 178.6541 | 38.9 | 29.3499 | 9.5501 | 0.98433 | 31-03-2026 12:30 | 313.4038 | 323.9721 | -10.5683 | 1943.8329 | 419.7 | 319.3393 | 100.3607 | 106.2962
31-03-2026 12:20 | 949 | 52.52 | 319.662 | 325.223 | 1078.4 | 54.2038 | 55.7049 | -1.501 | 334.2292 | 55.9 | 54.9083 | 0.99171 | 0.9829 | 31-03-2026 12:20 | 317.264 | 322.882 | 1087.9 | 53.8137 | 55.7049 | -1.8912 | 334.2292 | 56.5 | 54.9083 | 1.5917 | 0.9826 | 31-03-2026 12:20 | 312.801 | 322.921 | 1070.2 | 53.8202 | 55.7049 | -1.8847 | 334.2292 | 55.9 | 54.9083 | 0.99171 | 0.96866 | 31-03-2026 12:20 | 310.378 | 315.842 | 1078.7 | 52.6403 | 55.7049 | -3.0645 | 334.2292 | 56 | 54.9083 | 1.0917 | 0.9827 | 31-03-2026 12:20 | 240.946 | 244.016 | 802.2 | 40.6693 | 41.2629 | -0.59353 | 247.5772 | 42.4 | 40.6728 | 1.7272 | 0.98742 | 31-03-2026 12:20 | 226.579 | 230.146 | 798.5 | 38.3577 | 41.2629 | -2.9052 | 247.5772 | 42 | 40.6728 | 1.3272 | 0.9845 | 31-03-2026 12:20 | 226.125 | 231.832 | 799.4 | 38.6387 | 41.2629 | -2.6242 | 247.5772 | 41.5 | 40.6728 | 0.82719 | 0.97538 | 31-03-2026 12:20 | 229.57 | 237.714 | 807.3 | 39.619 | 41.2629 | -1.6439 | 247.5772 | 41.9 | 40.6728 | 1.2272 | 0.96574 | 31-03-2026 12:20 | 216.41 | 219.911 | 766.6 | 36.6518 | 39.2565 | -2.6047 | 235.539 | 40.2 | 38.6951 | 1.5049 | 0.98408 | 31-03-2026 12:20 | 408.4145 | 427.1274 | -18.7129 | 2562.7647 | 432.3 | 421.0195 | 11.2805 | 23.8855
31-03-2026 12:10 | 1119 | 53.09 | 352.698 | 358.287 | 1022.5 | 59.7145 | 65.5386 | -5.8241 | 393.2316 | 52.2 | 64.6014 | -12.4014 | 0.9844 | 31-03-2026 12:10 | 352.688 | 358.447 | 1031.4 | 59.7412 | 65.5386 | -5.7974 | 393.2316 | 52.7 | 64.6014 | -11.9014 | 0.98393 | 31-03-2026 12:10 | 352.482 | 362.44 | 1014.3 | 60.4067 | 65.5386 | -5.1319 | 393.2316 | 54.1 | 64.6014 | -10.5014 | 0.97253 | 31-03-2026 12:10 | 343.636 | 349.011 | 1022.7 | 58.1685 | 65.5386 | -7.3701 | 393.2316 | 53.1 | 64.6014 | -11.5014 | 0.9846 | 31-03-2026 12:10 | 275.068 | 279.626 | 759.8 | 46.6043 | 48.5471 | -1.9428 | 291.2827 | 41.6 | 47.8529 | -6.2529 | 0.9837 | 31-03-2026 12:10 | 272.42 | 277.52 | 756.5 | 46.2533 | 48.5471 | -2.2938 | 291.2827 | 40.8 | 47.8529 | -7.0529 | 0.98162 | 31-03-2026 12:10 | 272.01 | 278.039 | 757.9 | 46.3398 | 48.5471 | -2.2073 | 291.2827 | 41.1 | 47.8529 | -6.7529 | 0.97832 | 31-03-2026 12:10 | 274.469 | 282.819 | 765.4 | 47.1365 | 48.5471 | -1.4106 | 291.2827 | 41.4 | 47.8529 | -6.4529 | 0.97048 | 31-03-2026 12:10 | 261.021 | 265.292 | 726.4 | 44.2153 | 46.1866 | -1.9712 | 277.1194 | 38.5 | 45.5261 | -7.0261 | 0.9839 | 31-03-2026 12:10 | 468.5802 | 502.5295 | -33.9493 | 3015.1768 | 415.5 | 495.3433 | -79.8433 | -53.0802
31-03-2026 12:00 | 1076 | 55.1 | 344.309 | 350.477 | 970.3 | 58.4128 | 62.5285 | -4.1156 | 375.1707 | 59.2 | 61.6343 | -2.4343 | 0.9824 | 31-03-2026 12:00 | 352.792 | 358.93 | 978.7 | 59.8217 | 62.5285 | -2.7068 | 375.1707 | 57.2 | 61.6343 | -4.4343 | 0.9829 | 31-03-2026 12:00 | 352.662 | 362.695 | 960.2 | 60.4492 | 62.5285 | -2.0793 | 375.1707 | 56 | 61.6343 | -5.6343 | 0.97234 | 31-03-2026 12:00 | 352.307 | 358.181 | 969.6 | 59.6968 | 62.5285 | -2.8316 | 375.1707 | 57.6 | 61.6343 | -4.0343 | 0.9836 | 31-03-2026 12:00 | 269.112 | 273.488 | 718.2 | 45.5813 | 46.3174 | -0.73604 | 277.9043 | 43.5 | 45.655 | -2.155 | 0.984 | 31-03-2026 12:00 | 265.998 | 271.382 | 715.7 | 45.2303 | 46.3174 | -1.087 | 277.9043 | 42.8 | 45.655 | -2.855 | 0.98016 | 31-03-2026 12:00 | 265.631 | 271.251 | 716.8 | 45.2085 | 46.3174 | -1.1089 | 277.9043 | 43.1 | 45.655 | -2.555 | 0.97928 | 31-03-2026 12:00 | 267.354 | 275.325 | 724 | 45.8875 | 46.3174 | -0.42988 | 277.9043 | 43.3 | 45.655 | -2.355 | 0.97105 | 31-03-2026 12:00 | 253.821 | 257.907 | 687.9 | 42.9845 | 44.0652 | -1.0807 | 264.3915 | 41 | 43.4351 | -2.4351 | 0.98416 | 31-03-2026 12:00 | 463.2727 | 479.4486 | -16.1759 | 2876.6914 | 443.7 | 472.5925 | -28.8925 | -19.5727
31-03-2026 11:50 | 977 | 54.82 | 339.741 | 345.687 | 911.1 | 57.6145 | 56.8376 | 0.77693 | 341.0254 | 51.8 | 56.0248 | -4.2248 | 0.9828 | 31-03-2026 11:50 | 339.468 | 345.515 | 921.5 | 57.5858 | 56.8376 | 0.74827 | 341.0254 | 55.3 | 56.0248 | -0.72479 | 0.9825 | 31-03-2026 11:50 | 322.761 | 332.078 | 904.2 | 55.3463 | 56.8376 | -1.4912 | 341.0254 | 54.1 | 56.0248 | -1.9248 | 0.97194 | 31-03-2026 11:50 | 317.312 | 322.865 | 912 | 53.8108 | 56.8376 | -3.0267 | 341.0254 | 53.8 | 56.0248 | -2.2248 | 0.9828 | 31-03-2026 11:50 | 242.186 | 246.049 | 674.7 | 41.0082 | 42.1019 | -1.0937 | 252.6114 | 40.1 | 41.4998 | -1.3998 | 0.9843 | 31-03-2026 11:50 | 239.061 | 244.167 | 672.9 | 40.6945 | 42.1019 | -1.4074 | 252.6114 | 39.8 | 41.4998 | -1.6998 | 0.97909 | 31-03-2026 11:50 | 242.09 | 246.787 | 673.7 | 41.1312 | 42.1019 | -0.97073 | 252.6114 | 39.9 | 41.4998 | -1.5998 | 0.98097 | 31-03-2026 11:50 | 244.566 | 251.641 | 680.7 | 41.9402 | 42.1019 | -0.16173 | 252.6114 | 40.3 | 41.4998 | -1.1998 | 0.97188 | 31-03-2026 11:50 | 231.375 | 235.018 | 646.9 | 39.1697 | 40.0547 | -0.88508 | 240.3285 | 38.1 | 39.482 | -1.382 | 0.9845 | 31-03-2026 11:50 | 428.3012 | 435.8126 | -7.5114 | 2614.8757 | 413.2 | 429.5805 | -16.3805 | -15.1012
31-03-2026 11:40 | 1072 | 52.52 | 352.045 | 358.352 | 859.3 | 59.7253 | 62.9248 | -3.1995 | 377.5487 | 53.9 | 62.025 | -8.125 | 0.9824 | 31-03-2026 11:40 | 0 | 0 | 866.2 | 0 | 62.9248 | -62.9248 | 377.5487 | 54.5 | 62.025 | -7.525 |  | 31-03-2026 11:40 | 348.359 | 358.624 | 850.1 | 59.7707 | 62.9248 | -3.1541 | 377.5487 | 52.7 | 62.025 | -9.325 | 0.97138 | 31-03-2026 11:40 | 352.352 | 358.519 | 858.2 | 59.7532 | 62.9248 | -3.1716 | 377.5487 | 53.3 | 62.025 | -8.725 | 0.9828 | 31-03-2026 11:40 | 262.35 | 266.67 | 634.6 | 44.445 | 46.611 | -2.166 | 279.6657 | 39.6 | 45.9444 | -6.3444 | 0.9838 | 31-03-2026 11:40 | 259.422 | 264.693 | 633.1 | 44.1155 | 46.611 | -2.4955 | 279.6657 | 39.4 | 45.9444 | -6.5444 | 0.98009 | 31-03-2026 11:40 | 259.621 | 264.87 | 633.8 | 44.145 | 46.611 | -2.466 | 279.6657 | 39.4 | 45.9444 | -6.5444 | 0.98018 | 31-03-2026 11:40 | 261.795 | 269.708 | 640.4 | 44.9513 | 46.611 | -1.6596 | 279.6657 | 39.8 | 45.9444 | -6.1444 | 0.97066 | 31-03-2026 11:40 | 247.579 | 251.605 | 608.8 | 41.9342 | 44.3445 | -2.4104 | 266.0673 | 38.2 | 43.7104 | -5.5104 | 0.984 | 31-03-2026 11:40 | 398.8402 | 482.4875 | -83.6473 | 2894.9249 | 410.8 | 475.5879 | -64.7879 | 11.9598
31-03-2026 11:30 | 816 | 51.95 | 272.545 | 276.977 | 805.4 | 46.1628 | 48.0037 | -1.8409 | 288.0223 | 52.7 | 47.3173 | 5.3827 | 0.984 | 31-03-2026 11:30 | 270.211 | 274.661 | 811.7 | 45.7768 | 48.0037 | -2.2269 | 288.0223 | 54.4 | 47.3173 | 7.0827 | 0.9838 | 31-03-2026 11:30 | 273.693 | 281.108 | 797.4 | 46.8513 | 48.0037 | -1.1524 | 288.0223 | 53 | 47.3173 | 5.6827 | 0.97362 | 31-03-2026 11:30 | 274.506 | 279.111 | 804.9 | 46.5185 | 48.0037 | -1.4852 | 288.0223 | 53.1 | 47.3173 | 5.7827 | 0.9835 | 31-03-2026 11:30 | 206.693 | 209.862 | 595 | 34.977 | 35.5583 | -0.5813 | 213.3498 | 39.8 | 35.0498 | 4.7502 | 0.9849 | 31-03-2026 11:30 | 205.134 | 208.907 | 593.7 | 34.8178 | 35.5583 | -0.74047 | 213.3498 | 39.5 | 35.0498 | 4.4502 | 0.98194 | 31-03-2026 11:30 | 206.861 | 211.317 | 594.4 | 35.2195 | 35.5583 | -0.3388 | 213.3498 | 39.5 | 35.0498 | 4.4502 | 0.97891 | 31-03-2026 11:30 | 204.909 | 211.808 | 600.6 | 35.3013 | 35.5583 | -0.25697 | 213.3498 | 39.8 | 35.0498 | 4.7502 | 0.96743 | 31-03-2026 11:30 | 194.023 | 196.938 | 570.6 | 32.823 | 33.8293 | -1.0063 | 202.9759 | 37.4 | 33.3456 | 4.0544 | 0.9852 | 31-03-2026 11:30 | 358.4482 | 368.0774 | -9.6292 | 2208.4643 | 409.2 | 362.8139 | 46.3861 | 50.7518
31-03-2026 11:20 | 853 | 51.66 | 288.118 | 294.806 | 752.7 | 49.1343 | 50.2366 | -1.1023 | 301.4195 | 41.9 | 49.5182 | -7.6182 | 0.97731 | 31-03-2026 11:20 | 341.502 | 335.352 | 757.3 | 55.892 | 50.2366 | 5.6554 | 301.4195 | 39.6 | 49.5182 | -9.9182 | 1.0183 | 31-03-2026 11:20 | 293.362 | 301.802 | 744.4 | 50.3003 | 50.2366 | 0.063746 | 301.4195 | 40.3 | 49.5182 | -9.2182 | 0.97203 | 31-03-2026 11:20 | 288.288 | 293.035 | 751.8 | 48.8392 | 50.2366 | -1.3974 | 301.4195 | 40.5 | 49.5182 | -9.0182 | 0.9838 | 31-03-2026 11:20 | 221.711 | 224.973 | 555.2 | 37.4955 | 37.2123 | 0.28321 | 223.2737 | 30.2 | 36.6802 | -6.4802 | 0.9855 | 31-03-2026 11:20 | 220.943 | 224.907 | 554.2 | 37.4845 | 37.2123 | 0.27221 | 223.2737 | 29.9 | 36.6802 | -6.7802 | 0.98237 | 31-03-2026 11:20 | 218.598 | 221.837 | 554.9 | 36.9728 | 37.2123 | -0.23945 | 223.2737 | 29.9 | 36.6802 | -6.7802 | 0.9854 | 31-03-2026 11:20 | 222.103 | 227.001 | 560.8 | 37.8335 | 37.2123 | 0.62121 | 223.2737 | 30.6 | 36.6802 | -6.0802 | 0.97842 | 31-03-2026 11:20 | 209.532 | 212.637 | 533.2 | 35.4395 | 35.4029 | 0.036618 | 212.4173 | 28.9 | 34.8966 | -5.9966 | 0.9854 | 31-03-2026 11:20 | 389.3917 | 385.1984 | 4.1933 | 2311.1903 | 311.8 | 379.69 | -67.89 | -77.5917
31-03-2026 11:10 | 796 | 51.66 | 266.678 | 270.987 | 710.8 | 45.1645 | 46.8796 | -1.7151 | 281.2778 | 46.8 | 46.2093 | 0.59075 | 0.9841 | 31-03-2026 11:10 | 252.382 | 278.82 | 717.7 | 46.47 | 46.8796 | -0.40963 | 281.2778 | 47.8 | 46.2093 | 1.5907 | 0.90518 | 31-03-2026 11:10 | 268.151 | 276.037 | 704.1 | 46.0062 | 46.8796 | -0.87346 | 281.2778 | 46.9 | 46.2093 | 0.69075 | 0.97143 | 31-03-2026 11:10 | 268.585 | 272.238 | 711.3 | 45.373 | 46.8796 | -1.5066 | 281.2778 | 47.2 | 46.2093 | 0.99075 | 0.98658 | 31-03-2026 11:10 | 201.66 | 204.669 | 525 | 34.1115 | 34.7257 | -0.61415 | 208.3539 | 35.1 | 34.2291 | 0.87093 | 0.9853 | 31-03-2026 11:10 | 199.377 | 202.746 | 524.3 | 33.791 | 34.7257 | -0.93465 | 208.3539 | 35.5 | 34.2291 | 1.2709 | 0.98338 | 31-03-2026 11:10 | 199.366 | 202.661 | 525 | 33.7768 | 34.7257 | -0.94882 | 208.3539 | 35.5 | 34.2291 | 1.2709 | 0.98374 | 31-03-2026 11:10 | 198.674 | 204.439 | 530.2 | 34.0732 | 34.7257 | -0.65248 | 208.3539 | 35.3 | 34.2291 | 1.0709 | 0.9718 | 31-03-2026 11:10 | 187.462 | 190.259 | 504.3 | 31.7098 | 33.0372 | -1.3273 | 198.2229 | 33.5 | 32.5647 | 0.93528 | 0.9853 | 31-03-2026 11:10 | 350.476 | 359.4583 | -8.9823 | 2156.7497 | 363.6 | 354.318 | 9.282 | 13.124
31-03-2026 11:00 | 893 | 51.66 | 297.752 | 302.717 | 664 | 50.4528 | 52.5923 | -2.1395 | 315.5541 | 47.1 | 51.8403 | -4.7403 | 0.9836 | 31-03-2026 11:00 | 302.872 | 308.016 | 669.9 | 51.336 | 52.5923 | -1.2563 | 315.5541 | 47.7 | 51.8403 | -4.1403 | 0.9833 | 31-03-2026 11:00 | 297.546 | 306.034 | 657.2 | 51.0057 | 52.5923 | -1.5867 | 315.5541 | 46.1 | 51.8403 | -5.7403 | 0.97226 | 31-03-2026 11:00 | 299.245 | 304.327 | 664.1 | 50.7212 | 52.5923 | -1.8712 | 315.5541 | 46.5 | 51.8403 | -5.3403 | 0.9833 | 31-03-2026 11:00 | 225.748 | 229.256 | 489.9 | 38.2093 | 38.9573 | -0.74796 | 233.7438 | 34.7 | 38.4002 | -3.7002 | 0.9847 | 31-03-2026 11:00 | 226.361 | 230.629 | 488.8 | 38.4382 | 38.9573 | -0.51913 | 233.7438 | 33.8 | 38.4002 | -4.6002 | 0.98149 | 31-03-2026 11:00 | 228.005 | 231.524 | 489.5 | 38.5873 | 38.9573 | -0.36996 | 233.7438 | 33.8 | 38.4002 | -4.6002 | 0.9848 | 31-03-2026 11:00 | 229.321 | 235.459 | 494.9 | 39.2432 | 38.9573 | 0.28587 | 233.7438 | 34.5 | 38.4002 | -3.9002 | 0.97393 | 31-03-2026 11:00 | 217.876 | 221.171 | 470.8 | 36.8618 | 37.063 | -0.20121 | 222.3782 | 32.7 | 36.533 | -3.833 | 0.9851 | 31-03-2026 11:00 | 394.8555 | 403.2616 | -8.4061 | 2419.5697 | 356.9 | 397.495 | -40.595 | -37.9555
31-03-2026 10:50 | 979 | 51.95 | 333.329 | 339.094 | 616.9 | 56.5157 | 57.5927 | -1.077 | 345.5561 | 50.1 | 56.7691 | -6.6691 | 0.983 | 31-03-2026 10:50 | 333.63 | 339.469 | 622.2 | 56.5782 | 57.5927 | -1.0145 | 345.5561 | 49.9 | 56.7691 | -6.8691 | 0.9828 | 31-03-2026 10:50 | 325.889 | 335.184 | 611.1 | 55.864 | 57.5927 | -1.7287 | 345.5561 | 49.6 | 56.7691 | -7.1691 | 0.97227 | 31-03-2026 10:50 | 328.727 | 334.48 | 617.6 | 55.7467 | 57.5927 | -1.846 | 345.5561 | 51.4 | 56.7691 | -5.3691 | 0.9828 | 31-03-2026 10:50 | 245.867 | 249.738 | 455.2 | 41.623 | 42.6612 | -1.0382 | 255.9675 | 37.1 | 42.0512 | -4.9512 | 0.9845 | 31-03-2026 10:50 | 244.215 | 248.931 | 455 | 41.4885 | 42.6612 | -1.1727 | 255.9675 | 37 | 42.0512 | -5.0512 | 0.98105 | 31-03-2026 10:50 | 244.549 | 248.527 | 455.7 | 41.4212 | 42.6612 | -1.2401 | 255.9675 | 36.9 | 42.0512 | -5.1512 | 0.98399 | 31-03-2026 10:50 | 246.76 | 254.072 | 460.4 | 42.3453 | 42.6612 | -0.31592 | 255.9675 | 37.2 | 42.0512 | -4.8512 | 0.97122 | 31-03-2026 10:50 | 234.12 | 237.806 | 438.1 | 39.6343 | 40.5869 | -0.95256 | 243.5214 | 35.5 | 40.0065 | -4.5065 | 0.9845 | 31-03-2026 10:50 | 431.2168 | 441.6026 | -10.3858 | 2649.6159 | 384.7 | 435.2877 | -50.5877 | -46.5168
31-03-2026 10:40 | 862 | 52.23 | 291.883 | 299.357 | 566.8 | 49.8928 | 50.6549 | -0.7621 | 303.9296 | 42.7 | 49.9306 | -7.2306 | 0.97503 | 31-03-2026 10:40 | 296.115 | 301.916 | 572.3 | 50.3193 | 50.6549 | -0.3356 | 303.9296 | 44.4 | 49.9306 | -5.5306 | 0.98079 | 31-03-2026 10:40 | 291.332 | 299.112 | 561.5 | 49.852 | 50.6549 | -0.80293 | 303.9296 | 43 | 49.9306 | -6.9306 | 0.97399 | 31-03-2026 10:40 | 291.873 | 296.679 | 566.2 | 49.4465 | 50.6549 | -1.2084 | 303.9296 | 42.6 | 49.9306 | -7.3306 | 0.9838 | 31-03-2026 10:40 | 217.277 | 220.519 | 418.1 | 36.7532 | 37.5222 | -0.769 | 225.133 | 32.6 | 36.9856 | -4.3856 | 0.9853 | 31-03-2026 10:40 | 216.254 | 219.773 | 418 | 36.6288 | 37.5222 | -0.89334 | 225.133 | 32.5 | 36.9856 | -4.4856 | 0.98399 | 31-03-2026 10:40 | 214.126 | 218.499 | 418.8 | 36.4165 | 37.5222 | -1.1057 | 225.133 | 32.5 | 36.9856 | -4.4856 | 0.97999 | 31-03-2026 10:40 | 215.889 | 222.423 | 423.2 | 37.0705 | 37.5222 | -0.45167 | 225.133 | 32.4 | 36.9856 | -4.5856 | 0.97062 | 31-03-2026 10:40 | 205.827 | 208.947 | 402.6 | 34.8245 | 35.6977 | -0.8732 | 214.1862 | 30.8 | 35.1872 | -4.3872 | 0.98507 | 31-03-2026 10:40 | 381.2042 | 388.4061 | -7.2019 | 2330.4366 | 333.5 | 382.8519 | -49.3519 | -47.7042
31-03-2026 10:30 | 672 | 51.66 | 231.352 | 234.827 | 524.1 | 39.1378 | 39.5768 | -0.43894 | 237.4606 | 41.8 | 39.0108 | 2.7892 | 0.9852 | 31-03-2026 10:30 | 241.278 | 244.277 | 527.9 | 40.7128 | 39.5768 | 1.1361 | 237.4606 | 41.6 | 39.0108 | 2.5892 | 0.98772 | 31-03-2026 10:30 | 226.539 | 231.666 | 518.5 | 38.611 | 39.5768 | -0.96577 | 237.4606 | 41.3 | 39.0108 | 2.2892 | 0.97787 | 31-03-2026 10:30 | 238.862 | 242.573 | 523.6 | 40.4288 | 39.5768 | 0.85206 | 237.4606 | 42.5 | 39.0108 | 3.4892 | 0.9847 | 31-03-2026 10:30 | 174.211 | 176.703 | 385.5 | 29.4505 | 29.3161 | 0.13437 | 175.8968 | 30.6 | 28.8969 | 1.7031 | 0.9859 | 31-03-2026 10:30 | 175.338 | 177.846 | 385.5 | 29.641 | 29.3161 | 0.32487 | 175.8968 | 30.5 | 28.8969 | 1.6031 | 0.9859 | 31-03-2026 10:30 | 171.527 | 174.041 | 386.3 | 29.0068 | 29.3161 | -0.30929 | 175.8968 | 30.4 | 28.8969 | 1.5031 | 0.98556 | 31-03-2026 10:30 | 173.058 | 177.507 | 390.8 | 29.5845 | 29.3161 | 0.26837 | 175.8968 | 30.7 | 28.8969 | 1.8031 | 0.97494 | 31-03-2026 10:30 | 164.936 | 167.295 | 371.8 | 27.8825 | 27.8907 | -0.0081645 | 167.344 | 29.1 | 27.4918 | 1.6082 | 0.9859 | 31-03-2026 10:30 | 304.4558 | 303.4623 | 0.99357 | 1820.7736 | 318.5 | 299.1228 | 19.3772 | 14.0442
31-03-2026 10:20 | 870 | 55.39 | 300.87 | 305.762 | 482.3 | 50.9603 | 50.5 | 0.4603 | 303.0002 | 38.7 | 49.7779 | -11.0779 | 0.984 | 31-03-2026 10:20 | 303.914 | 308.919 | 486.3 | 51.4865 | 50.5 | 0.98646 | 303.0002 | 39.1 | 49.7779 | -10.6779 | 0.9838 | 31-03-2026 10:20 | 298.432 | 305.896 | 477.2 | 50.9827 | 50.5 | 0.48263 | 303.0002 | 38.4 | 49.7779 | -11.3779 | 0.9756 | 31-03-2026 10:20 | 300.99 | 305.946 | 481.1 | 50.991 | 50.5 | 0.49096 | 303.0002 | 37.3 | 49.7779 | -12.4779 | 0.9838 | 31-03-2026 10:20 | 223.643 | 226.911 | 354.9 | 37.8185 | 37.4074 | 0.41107 | 224.4446 | 28.7 | 36.8725 | -8.1725 | 0.9856 | 31-03-2026 10:20 | 223.323 | 226.632 | 355 | 37.772 | 37.4074 | 0.36457 | 224.4446 | 29.1 | 36.8725 | -7.7725 | 0.9854 | 31-03-2026 10:20 | 221.92 | 225.446 | 355.9 | 37.5743 | 37.4074 | 0.1669 | 224.4446 | 29 | 36.8725 | -7.8725 | 0.98436 | 31-03-2026 10:20 | 224.242 | 230.501 | 360.1 | 38.4168 | 37.4074 | 1.0094 | 224.4446 | 29.2 | 36.8725 | -7.6725 | 0.97285 | 31-03-2026 10:20 | 213.011 | 216.167 | 342.7 | 36.0278 | 35.5885 | 0.43929 | 213.5312 | 27.8 | 35.0796 | -7.2796 | 0.9854 | 31-03-2026 10:20 | 392.03 | 387.2184 | 4.8116 | 2323.3106 | 297.3 | 381.6812 | -84.3812 | -94.73
31-03-2026 10:10 | 657 | 54.82 | 229.842 | 231.945 | 443.6 | 38.6575 | 38.2214 | 0.43613 | 229.3282 | 41.2 | 37.6748 | 3.5252 | 0.99093 | 31-03-2026 10:10 | 230.634 | 234.17 | 447.2 | 39.0283 | 38.2214 | 0.80696 | 229.3282 | 43.4 | 37.6748 | 5.7252 | 0.9849 | 31-03-2026 10:10 | 223.526 | 226.861 | 438.8 | 37.8102 | 38.2214 | -0.41121 | 229.3282 | 40.8 | 37.6748 | 3.1252 | 0.9853 | 31-03-2026 10:10 | 226.315 | 229.761 | 443.8 | 38.2935 | 38.2214 | 0.072128 | 229.3282 | 41.2 | 37.6748 | 3.5252 | 0.985 | 31-03-2026 10:10 | 162.223 | 164.543 | 326.2 | 27.4238 | 28.3121 | -0.88829 | 169.8728 | 30.5 | 27.9073 | 2.5927 | 0.9859 | 31-03-2026 10:10 | 167.457 | 169.835 | 325.9 | 28.3058 | 28.3121 | -0.0062942 | 169.8728 | 30 | 27.9073 | 2.0927 | 0.986 | 31-03-2026 10:10 | 166.406 | 169.193 | 326.9 | 28.1988 | 28.3121 | -0.11329 | 169.8728 | 30 | 27.9073 | 2.0927 | 0.98353 | 31-03-2026 10:10 | 166.982 | 171.963 | 330.9 | 28.6605 | 28.3121 | 0.34837 | 169.8728 | 30.2 | 27.9073 | 2.2927 | 0.97103 | 31-03-2026 10:10 | 158.843 | 161.115 | 314.9 | 26.8525 | 26.9355 | -0.082983 | 161.6129 | 29.1 | 26.5503 | 2.5497 | 0.9859 | 31-03-2026 10:10 | 293.231 | 293.0695 | 0.16152 | 1758.4169 | 316.4 | 288.8786 | 27.5214 | 23.169
31-03-2026 10:00 | 714 | 53.38 | 249.353 | 253.202 | 402.4 | 42.2003 | 41.7711 | 0.42921 | 250.6268 | 42.5 | 41.1738 | 1.3262 | 0.9848 | 31-03-2026 10:00 | 255.283 | 259.276 | 403.8 | 43.2127 | 41.7711 | 1.4415 | 250.6268 | 41 | 41.1738 | -0.1738 | 0.9846 | 31-03-2026 10:00 | 246.059 | 251.675 | 398 | 41.9458 | 41.7711 | 0.17471 | 250.6268 | 41.4 | 41.1738 | 0.2262 | 0.97769 | 31-03-2026 10:00 | 250.289 | 254.178 | 402.6 | 42.363 | 41.7711 | 0.59187 | 250.6268 | 41.8 | 41.1738 | 0.6262 | 0.9847 | 31-03-2026 10:00 | 183.995 | 186.608 | 295.7 | 31.1013 | 30.9416 | 0.15976 | 185.6494 | 31 | 30.4991 | 0.50089 | 0.986 | 31-03-2026 10:00 | 184.69 | 187.331 | 295.9 | 31.2218 | 30.9416 | 0.28026 | 185.6494 | 30.9 | 30.4991 | 0.40089 | 0.9859 | 31-03-2026 10:00 | 182.82 | 185.435 | 296.9 | 30.9058 | 30.9416 | -0.035741 | 185.6494 | 30.8 | 30.4991 | 0.30089 | 0.9859 | 31-03-2026 10:00 | 184.577 | 189.573 | 300.7 | 31.5955 | 30.9416 | 0.65393 | 185.6494 | 31.5 | 30.4991 | 1.0009 | 0.97365 | 31-03-2026 10:00 | 178.453 | 180.87 | 285.8 | 30.145 | 29.4371 | 0.70792 | 176.6225 | 29.5 | 29.0161 | 0.48387 | 0.98664 | 31-03-2026 10:00 | 324.6913 | 320.2879 | 4.4035 | 1921.7273 | 320.4 | 315.7078 | 4.6922 | -4.2913
31-03-2026 09:50 | 722 | 53.09 | 252.081 | 255.933 | 359.9 | 42.6555 | 42.2868 | 0.36875 | 253.7205 | 39.9 | 41.6821 | -1.7821 |  | 31-03-2026 09:50 | 254.38 | 258.306 | 362.8 | 43.051 | 42.2868 | 0.76425 | 253.7205 | 40.3 | 41.6821 | -1.3821 |  | 31-03-2026 09:50 | 249.102 | 255.12 | 356.6 | 42.52 | 42.2868 | 0.23325 | 253.7205 | 40 | 41.6821 | -1.6821 |  | 31-03-2026 09:50 | 250.731 | 254.627 | 360.8 | 42.4378 | 42.2868 | 0.15108 | 253.7205 | 40.4 | 41.6821 | -1.2821 |  | 31-03-2026 09:50 | 185.595 | 188.23 | 264.7 | 31.3717 | 31.3235 | 0.048148 | 187.9411 | 29.8 | 30.8756 | -1.0756 |  | 31-03-2026 09:50 | 185.257 | 188.162 | 265 | 31.3603 | 31.3235 | 0.036814 | 187.9411 | 29.8 | 30.8756 | -1.0756 |  | 31-03-2026 09:50 | 185.57 | 188.801 | 266.1 | 31.4668 | 31.3235 | 0.14331 | 187.9411 | 29.8 | 30.8756 | -1.0756 |  | 31-03-2026 09:50 | 186.103 | 191.706 | 269.2 | 31.951 | 31.3235 | 0.62748 | 187.9411 | 29.7 | 30.8756 | -1.1756 |  | 31-03-2026 09:50 | 177.089 | 179.585 | 256.3 | 29.9308 | 29.8004 | 0.13038 | 178.8027 | 28.8 | 29.3743 | -0.5743 |  | 31-03-2026 09:50 | 326.745 | 324.2415 | 2.5035 | 1945.4492 | 308.5 | 319.6049 | -11.1049 | -18.245
31-03-2026 09:40 | 674 | 54.24 | 235.637 | 239.104 | 320 | 39.8507 | 39.2992 | 0.55144 | 235.7954 | 38 | 38.7373 | -0.73725 |  | 31-03-2026 09:40 | 237.344 | 240.909 | 322.5 | 40.1515 | 39.2992 | 0.85227 | 235.7954 | 38.2 | 38.7373 | -0.53725 |  | 31-03-2026 09:40 | 232.252 | 237.637 | 316.6 | 39.6062 | 39.2992 | 0.30694 | 235.7954 | 37.5 | 38.7373 | -1.2373 |  | 31-03-2026 09:40 | 235.142 | 238.674 | 320.4 | 39.779 | 39.2992 | 0.47977 | 235.7954 | 37.8 | 38.7373 | -0.93725 |  | 31-03-2026 09:40 | 173.108 | 175.495 | 234.9 | 29.2492 | 29.1105 | 0.13863 | 174.6632 | 27.9 | 28.6943 | -0.79426 |  | 31-03-2026 09:40 | 173.74 | 176.254 | 235.2 | 29.3757 | 29.1105 | 0.26513 | 174.6632 | 28 | 28.6943 | -0.69426 |  | 31-03-2026 09:40 | 172.792 | 175.21 | 236.3 | 29.2017 | 29.1105 | 0.091126 | 174.6632 | 28.4 | 28.6943 | -0.29426 |  | 31-03-2026 09:40 | 174.364 | 179.313 | 239.5 | 29.8855 | 29.1105 | 0.77496 | 174.6632 | 28.6 | 28.6943 | -0.09426 |  | 31-03-2026 09:40 | 166.555 | 168.894 | 227.5 | 28.149 | 27.6951 | 0.45393 | 166.1704 | 26.8 | 27.299 | -0.49903 |  | 31-03-2026 09:40 | 305.2483 | 301.3342 | 3.9142 | 1808.0049 | 291.2 | 297.0251 | -5.8251 | -14.0483
31-03-2026 09:30 | 628 | 54.53 | 220.943 | 224.103 | 282 | 37.3505 | 36.5757 | 0.77482 | 219.4541 | 36.2 | 36.0527 | 0.14735 |  | 31-03-2026 09:30 | 221.652 | 224.868 | 284.3 | 37.478 | 36.5757 | 0.90232 | 219.4541 | 37.1 | 36.0527 | 1.0473 |  | 31-03-2026 09:30 | 218.058 | 223.135 | 279.1 | 37.1892 | 36.5757 | 0.61348 | 219.4541 | 35.8 | 36.0527 | -0.25265 |  | 31-03-2026 09:30 | 220.5 | 223.676 | 282.6 | 37.2793 | 36.5757 | 0.70365 | 219.4541 | 36.3 | 36.0527 | 0.24735 |  | 31-03-2026 09:30 | 162.492 | 164.682 | 207 | 27.447 | 27.0931 | 0.3539 | 162.5586 | 26.8 | 26.7057 | 0.094333 |  | 31-03-2026 09:30 | 162.668 | 164.938 | 207.2 | 27.4897 | 27.0931 | 0.39657 | 162.5586 | 26.8 | 26.7057 | 0.094333 |  | 31-03-2026 09:30 | 162.106 | 164.393 | 207.9 | 27.3988 | 27.0931 | 0.30573 | 162.5586 | 26.2 | 26.7057 | -0.50567 |  | 31-03-2026 09:30 | 163.789 | 168.376 | 210.9 | 28.0627 | 27.0931 | 0.96957 | 162.5586 | 26.6 | 26.7057 | -0.10567 |  | 31-03-2026 09:30 | 155.951 | 158.065 | 200.7 | 26.3442 | 25.7757 | 0.56844 | 154.6544 | 25.2 | 25.4071 | -0.20713 |  | 31-03-2026 09:30 | 286.0393 | 280.4509 | 5.5885 | 1682.7051 | 277 | 276.4404 | 0.55959 | -9.0393
31-03-2026 09:20 | 598 | 54.24 | 211.273 | 214.229 | 245.8 | 35.7048 | 34.8679 | 0.83697 | 209.2072 | 33.2 | 34.3693 | -1.1693 |  | 31-03-2026 09:20 | 211.78 | 214.787 | 247.2 | 35.7978 | 34.8679 | 0.92997 | 209.2072 | 33.7 | 34.3693 | -0.66925 |  | 31-03-2026 09:20 | 208.484 | 213.142 | 243.3 | 35.5237 | 34.8679 | 0.6558 | 209.2072 | 32.7 | 34.3693 | -1.6693 |  | 31-03-2026 09:20 | 210.566 | 213.556 | 246.3 | 35.5927 | 34.8679 | 0.7248 | 209.2072 | 33 | 34.3693 | -1.3693 |  | 31-03-2026 09:20 | 155.002 | 157.059 | 180.2 | 26.1765 | 25.828 | 0.34845 | 154.9683 | 24.3 | 25.4587 | -1.1587 |  | 31-03-2026 09:20 | 155.85 | 157.935 | 180.4 | 26.3225 | 25.828 | 0.49445 | 154.9683 | 24.5 | 25.4587 | -0.95871 |  | 31-03-2026 09:20 | 155.213 | 157.357 | 181.7 | 26.2262 | 25.828 | 0.39812 | 154.9683 | 24.8 | 25.4587 | -0.65871 |  | 31-03-2026 09:20 | 157.002 | 161.234 | 184.3 | 26.8723 | 25.828 | 1.0443 | 154.9683 | 25 | 25.4587 | -0.45871 |  | 31-03-2026 09:20 | 149.395 | 151.393 | 175.5 | 25.2322 | 24.5722 | 0.65998 | 147.4331 | 24.5 | 24.2208 | 0.27919 |  | 31-03-2026 09:20 | 273.4487 | 267.3558 | 6.0928 | 1604.135 | 255.7 | 263.5326 | -7.8326 | -17.7487
31-03-2026 09:10 | 562 | 53.96 | 198.677 | 201.375 | 212.6 | 33.5625 | 32.8046 | 0.75793 | 196.8274 | 31.3 | 32.3355 | -1.0355 |  | 31-03-2026 09:10 | 200.095 | 202.884 | 213.5 | 33.814 | 32.8046 | 1.0094 | 196.8274 | 30.2 | 32.3355 | -2.1355 |  | 31-03-2026 09:10 | 195.039 | 198.984 | 210.6 | 33.164 | 32.8046 | 0.35943 | 196.8274 | 30.9 | 32.3355 | -1.4355 |  | 31-03-2026 09:10 | 197.654 | 200.399 | 213.3 | 33.3998 | 32.8046 | 0.59526 | 196.8274 | 31.3 | 32.3355 | -1.0355 |  | 31-03-2026 09:10 | 145.194 | 147.077 | 155.9 | 24.5128 | 24.2997 | 0.21315 | 145.7981 | 23 | 23.9522 | -0.9522 |  | 31-03-2026 09:10 | 146.341 | 148.253 | 155.9 | 24.7088 | 24.2997 | 0.40915 | 145.7981 | 23.2 | 23.9522 | -0.7522 |  | 31-03-2026 09:10 | 145.779 | 147.699 | 156.9 | 24.6165 | 24.2997 | 0.31682 | 145.7981 | 22.7 | 23.9522 | -1.2522 |  | 31-03-2026 09:10 | 147.489 | 151.613 | 159.3 | 25.2688 | 24.2997 | 0.96915 | 145.7981 | 23 | 23.9522 | -0.9522 |  | 31-03-2026 09:10 | 141.072 | 142.93 | 151 | 23.8217 | 23.1181 | 0.70353 | 138.7088 | 21.2 | 22.7875 | -1.5875 |  | 31-03-2026 09:10 | 256.869 | 251.5351 | 5.3339 | 1509.2108 | 236.8 | 247.9382 | -11.1382 | -20.069
31-03-2026 09:00 | 528 | 53.67 | 184.181 | 188.105 | 181.3 | 31.3508 | 30.8548 | 0.49607 | 185.1286 | 30.4 | 30.4135 | -0.013538 |  | 31-03-2026 09:00 | 186.773 | 189.31 | 183.3 | 31.5517 | 30.8548 | 0.69691 | 185.1286 | 30.1 | 30.4135 | -0.31354 |  | 31-03-2026 09:00 | 183.264 | 187.018 | 179.7 | 31.1697 | 30.8548 | 0.31491 | 185.1286 | 28.8 | 30.4135 | -1.6135 |  | 31-03-2026 09:00 | 185.092 | 187.625 | 182 | 31.2708 | 30.8548 | 0.41607 | 185.1286 | 29.1 | 30.4135 | -1.3135 |  | 31-03-2026 09:00 | 136.427 | 138.168 | 132.9 | 23.028 | 22.8554 | 0.17262 | 137.1323 | 21.4 | 22.5285 | -1.1285 |  | 31-03-2026 09:00 | 137.51 | 139.265 | 132.7 | 23.2108 | 22.8554 | 0.35545 | 137.1323 | 21.6 | 22.5285 | -0.92855 |  | 31-03-2026 09:00 | 136.923 | 138.684 | 134.2 | 23.114 | 22.8554 | 0.25862 | 137.1323 | 21.5 | 22.5285 | -1.0285 |  | 31-03-2026 09:00 | 138.725 | 142.398 | 136.3 | 23.733 | 22.8554 | 0.87762 | 137.1323 | 21.8 | 22.5285 | -0.72855 |  | 31-03-2026 09:00 | 131.816 | 133.764 | 129.8 | 22.294 | 21.7441 | 0.54994 | 130.4644 | 21 | 21.4331 | -0.43312 |  | 31-03-2026 09:00 | 240.7228 | 236.5846 | 4.1382 | 1419.5077 | 225.7 | 233.2015 | -7.5015 | -15.0228
31-03-2026 08:50 | 485 | 52.81 | 171.281 | 173.502 | 150.9 | 28.917 | 28.4368 | 0.48021 | 170.6208 | 25.7 | 28.0301 | -2.3301 |  | 31-03-2026 08:50 | 171.993 | 174.294 | 153.2 | 29.049 | 28.4368 | 0.61221 | 170.6208 | 27.5 | 28.0301 | -0.53015 |  | 31-03-2026 08:50 | 168.642 | 171.84 | 150.9 | 28.64 | 28.4368 | 0.20321 | 170.6208 | 26.6 | 28.0301 | -1.4301 |  | 31-03-2026 08:50 | 169.984 | 172.194 | 152.9 | 28.699 | 28.4368 | 0.26221 | 170.6208 | 27.3 | 28.0301 | -0.73015 |  | 31-03-2026 08:50 | 125.356 | 126.871 | 111.5 | 21.1452 | 21.0643 | 0.080876 | 126.3857 | 20.1 | 20.7631 | -0.66307 |  | 31-03-2026 08:50 | 125.973 | 127.555 | 111.1 | 21.2592 | 21.0643 | 0.19488 | 126.3857 | 20.2 | 20.7631 | -0.56307 |  | 31-03-2026 08:50 | 125.925 | 127.519 | 112.7 | 21.2532 | 21.0643 | 0.18888 | 126.3857 | 20.2 | 20.7631 | -0.56307 |  | 31-03-2026 08:50 | 127.551 | 130.965 | 114.5 | 21.8275 | 21.0643 | 0.76321 | 126.3857 | 20.4 | 20.7631 | -0.36307 |  | 31-03-2026 08:50 | 120.84 | 122.382 | 108.8 | 20.397 | 20.0401 | 0.35694 | 120.2404 | 19.2 | 19.7535 | -0.55349 |  | 31-03-2026 08:50 | 221.187 | 218.0444 | 3.1426 | 1308.2664 | 207.2 | 214.9264 | -7.7264 | -13.987
31-03-2026 08:40 | 464 | 51.95 | 162.313 | 164.384 | 125.2 | 27.3973 | 27.2962 | 0.10111 | 163.7774 | 25.4 | 26.9059 | -1.5059 |  | 31-03-2026 08:40 | 161.76 | 166.26 | 125.7 | 27.71 | 27.2962 | 0.41377 | 163.7774 | 24.6 | 26.9059 | -2.3059 |  | 31-03-2026 08:40 | 160.222 | 163.432 | 124.3 | 27.2387 | 27.2962 | -0.057561 | 163.7774 | 24.9 | 26.9059 | -2.0059 |  | 31-03-2026 08:40 | 162.349 | 164.437 | 125.6 | 27.4062 | 27.2962 | 0.10994 | 163.7774 | 24.8 | 26.9059 | -2.1059 |  | 31-03-2026 08:40 | 118.674 | 120.152 | 91.4 | 20.0253 | 20.2194 | -0.19409 | 121.3166 | 18.1 | 19.9303 | -1.8303 |  | 31-03-2026 08:40 | 119.869 | 121.337 | 90.9 | 20.2228 | 20.2194 | 0.0034054 | 121.3166 | 18.6 | 19.9303 | -1.3303 |  | 31-03-2026 08:40 | 119.268 | 120.765 | 92.5 | 20.1275 | 20.2194 | -0.091928 | 121.3166 | 18.5 | 19.9303 | -1.4303 |  | 31-03-2026 08:40 | 120.776 | 124.151 | 94.1 | 20.6918 | 20.2194 | 0.47241 | 121.3166 | 18.8 | 19.9303 | -1.1303 |  | 31-03-2026 08:40 | 115.377 | 116.814 | 89.6 | 19.469 | 19.2363 | 0.23272 | 115.4177 | 17.9 | 18.9612 | -1.0612 |  | 31-03-2026 08:40 | 210.2887 | 209.2989 | 0.98976 | 1255.7934 | 191.6 | 206.3059 | -14.7059 | -18.6887
31-03-2026 08:30 | 411 | 51.09 | 142.589 | 144.335 | 99.8 | 24.0558 | 24.2587 | -0.20286 | 145.5522 | 22.9 | 23.9118 | -1.0118 |  | 31-03-2026 08:30 | 144.574 | 146.404 | 101.1 | 24.4007 | 24.2587 | 0.14197 | 145.5522 | 24 | 23.9118 | 0.088203 |  | 31-03-2026 08:30 | 141.847 | 144.234 | 99.4 | 24.039 | 24.2587 | -0.2197 | 145.5522 | 23.2 | 23.9118 | -0.7118 |  | 31-03-2026 08:30 | 143.542 | 145.344 | 100.8 | 24.224 | 24.2587 | -0.034696 | 145.5522 | 23.4 | 23.9118 | -0.5118 |  | 31-03-2026 08:30 | 105.104 | 106.381 | 73.3 | 17.7302 | 17.9694 | -0.23924 | 107.8164 | 17.1 | 17.7124 | -0.61244 |  | 31-03-2026 08:30 | 106.503 | 107.835 | 72.3 | 17.9725 | 17.9694 | 0.0030955 | 107.8164 | 17.2 | 17.7124 | -0.51244 |  | 31-03-2026 08:30 | 105.926 | 107.213 | 74 | 17.8688 | 17.9694 | -0.10057 | 107.8164 | 17 | 17.7124 | -0.71244 |  | 31-03-2026 08:30 | 107.578 | 110.588 | 75.3 | 18.4313 | 17.9694 | 0.46193 | 107.8164 | 17.6 | 17.7124 | -0.11244 |  | 31-03-2026 08:30 | 102.436 | 103.68 | 71.7 | 17.28 | 17.0957 | 0.18434 | 102.574 | 16.8 | 16.8512 | -0.051195 |  | 31-03-2026 08:30 | 186.0023 | 186.0081 | -0.0057319 | 1116.0484 | 179.2 | 183.3481 | -4.1481 | -6.8023
31-03-2026 08:20 | 389 | 48.22 | 134.793 | 136.403 | 76.9 | 22.7338 | 23.214 | -0.48016 | 139.2839 | 18.8 | 22.882 | -4.082 |  | 31-03-2026 08:20 | 137.656 | 139.328 | 77.1 | 23.2213 | 23.214 | 0.0073444 | 139.2839 | 18.6 | 22.882 | -4.282 |  | 31-03-2026 08:20 | 134.6 | 136.67 | 76.2 | 22.7783 | 23.214 | -0.43566 | 139.2839 | 18.8 | 22.882 | -4.082 |  | 31-03-2026 08:20 | 136.517 | 138.166 | 77.4 | 23.0277 | 23.214 | -0.18632 | 139.2839 | 19 | 22.882 | -3.882 |  | 31-03-2026 08:20 | 99.653 | 100.823 | 56.2 | 16.8038 | 17.1955 | -0.39171 | 103.1733 | 14 | 16.9497 | -2.9497 |  | 31-03-2026 08:20 | 101.147 | 102.324 | 55.1 | 17.054 | 17.1955 | -0.14155 | 103.1733 | 13.7 | 16.9497 | -3.2497 |  | 31-03-2026 08:20 | 100.651 | 101.832 | 57 | 16.972 | 17.1955 | -0.22355 | 103.1733 | 14.1 | 16.9497 | -2.8497 |  | 31-03-2026 08:20 | 102.111 | 104.87 | 57.7 | 17.4783 | 17.1955 | 0.28279 | 103.1733 | 14 | 16.9497 | -2.9497 |  | 31-03-2026 08:20 | 97.306 | 98.448 | 54.9 | 16.408 | 16.3594 | 0.048566 | 98.1566 | 13.4 | 16.1255 | -2.7255 |  | 31-03-2026 08:20 | 176.4773 | 177.9976 | -1.5202 | 1067.9855 | 144.4 | 175.4522 | -31.0522 | -32.0773
31-03-2026 08:10 | 118 | 42.48 | 40.477 | 41.077 | 58.1 | 6.8462 | 7.1958 | -0.34959 | 43.1746 | 8.8 | 7.0929 | 1.7071 |  | 31-03-2026 08:10 | 40.92 | 41.573 | 58.5 | 6.9288 | 7.1958 | -0.26693 | 43.1746 | 8.4 | 7.0929 | 1.3071 |  | 31-03-2026 08:10 | 40.681 | 41.401 | 57.4 | 6.9002 | 7.1958 | -0.29559 | 43.1746 | 8.2 | 7.0929 | 1.1071 |  | 31-03-2026 08:10 | 40.508 | 41.23 | 58.4 | 6.8717 | 7.1958 | -0.32409 | 43.1746 | 8.6 | 7.0929 | 1.5071 |  | 31-03-2026 08:10 | 30.083 | 30.653 | 42.2 | 5.1088 | 5.3302 | -0.22136 | 31.9812 | 6.2 | 5.254 | 0.94603 |  | 31-03-2026 08:10 | 28.421 | 28.937 | 41.4 | 4.8228 | 5.3302 | -0.50736 | 31.9812 | 6 | 5.254 | 0.74603 |  | 31-03-2026 08:10 | 30.072 | 30.636 | 42.9 | 5.106 | 5.3302 | -0.22419 | 31.9812 | 6.3 | 5.254 | 1.046 |  | 31-03-2026 08:10 | 30.283 | 31.209 | 43.7 | 5.2015 | 5.3302 | -0.12869 | 31.9812 | 6.4 | 5.254 | 1.146 |  | 31-03-2026 08:10 | 28.121 | 28.689 | 41.5 | 4.7815 | 5.071 | -0.28952 | 30.4261 | 6 | 4.9985 | 1.0015 |  | 31-03-2026 08:10 | 52.5675 | 55.1748 | -2.6073 | 331.0489 | 64.9 | 54.3858 | 10.5142 | 12.3325
31-03-2026 08:00 | 262 | 43.62 | 87.488 | 88.497 | 49.3 | 14.7495 | 15.9091 | -1.1596 | 95.4547 | 13.1 | 15.6816 | -2.5816 |  | 31-03-2026 08:00 | 87.703 | 88.275 | 50.1 | 14.7125 | 15.9091 | -1.1966 | 95.4547 | 13.6 | 15.6816 | -2.0816 |  | 31-03-2026 08:00 | 86.151 | 87.37 | 49.2 | 14.5617 | 15.9091 | -1.3475 | 95.4547 | 13.3 | 15.6816 | -2.3816 |  | 31-03-2026 08:00 | 87.922 | 88.963 | 49.8 | 14.8272 | 15.9091 | -1.082 | 95.4547 | 13.5 | 15.6816 | -2.1816 |  | 31-03-2026 08:00 | 63.294 | 64.095 | 36 | 10.6825 | 11.7845 | -1.102 | 70.7072 | 9.8 | 11.616 | -1.816 |  | 31-03-2026 08:00 | 61.844 | 62.645 | 35.4 | 10.4408 | 11.7845 | -1.3437 | 70.7072 | 9.6 | 11.616 | -2.016 |  | 31-03-2026 08:00 | 64.22 | 65.046 | 36.6 | 10.841 | 11.7845 | -0.94353 | 70.7072 | 9.9 | 11.616 | -1.716 |  | 31-03-2026 08:00 | 65.657 | 67.438 | 37.3 | 11.2397 | 11.7845 | -0.54487 | 70.7072 | 10.2 | 11.616 | -1.416 |  | 31-03-2026 08:00 | 62.854 | 63.669 | 35.5 | 10.6115 | 11.2115 | -0.60003 | 67.2692 | 9.7 | 11.0512 | -1.3512 |  | 31-03-2026 08:00 | 112.6663 | 121.9862 | -9.3198 | 731.9169 | 102.7 | 120.2417 | -17.5417 | -9.9663
31-03-2026 07:50 | 223 | 43.34 | 73.007 | 73.886 | 36.2 | 12.3143 | 13.5552 | -1.2408 | 81.331 | 11 | 13.3613 | -2.3613 |  | 31-03-2026 07:50 | 72.83 | 73.752 | 36.5 | 12.292 | 13.5552 | -1.2632 | 81.331 | 11.3 | 13.3613 | -2.0613 |  | 31-03-2026 07:50 | 72.338 | 73.231 | 35.9 | 12.2052 | 13.5552 | -1.35 | 81.331 | 11 | 13.3613 | -2.3613 |  | 31-03-2026 07:50 | 73.268 | 74.18 | 36.3 | 12.3633 | 13.5552 | -1.1918 | 81.331 | 11.1 | 13.3613 | -2.2613 |  | 31-03-2026 07:50 | 53.309 | 54.071 | 26.2 | 9.0118 | 10.0409 | -1.029 | 60.2452 | 8 | 9.8973 | -1.8973 |  | 31-03-2026 07:50 | 51.77 | 52.5 | 25.8 | 8.75 | 10.0409 | -1.2909 | 60.2452 | 7.8 | 9.8973 | -2.0973 |  | 31-03-2026 07:50 | 54.34 | 55.106 | 26.7 | 9.1843 | 10.0409 | -0.85653 | 60.2452 | 8.3 | 9.8973 | -1.5973 |  | 31-03-2026 07:50 | 55.433 | 56.991 | 27.1 | 9.4985 | 10.0409 | -0.54236 | 60.2452 | 8.5 | 9.8973 | -1.3973 |  | 31-03-2026 07:50 | 52.722 | 53.476 | 25.8 | 8.9127 | 9.5526 | -0.63997 | 57.3158 | 8.1 | 9.416 | -1.316 |  | 31-03-2026 07:50 | 94.5322 | 103.9368 | -9.4046 | 623.6205 | 85.1 | 102.4505 | -17.3505 | -9.4322
31-03-2026 07:40 | 190 | 37.31 | 61.309 | 62.079 | 25.2 | 10.3465 | 11.8097 | -1.4632 | 70.8583 | 10 | 11.6408 | -1.6408 |  | 31-03-2026 07:40 | 60.153 | 60.933 | 25.2 | 10.1555 | 11.8097 | -1.6542 | 70.8583 | 9.7 | 11.6408 | -1.9408 |  | 31-03-2026 07:40 | 60.408 | 61.173 | 24.9 | 10.1955 | 11.8097 | -1.6142 | 70.8583 | 9.7 | 11.6408 | -1.9408 |  | 31-03-2026 07:40 | 61.308 | 62.103 | 25.2 | 10.3505 | 11.8097 | -1.4592 | 70.8583 | 9.8 | 11.6408 | -1.8408 |  | 31-03-2026 07:40 | 44.492 | 45.165 | 18.2 | 7.5275 | 8.7479 | -1.2204 | 52.4876 | 7.1 | 8.6228 | -1.5228 |  | 31-03-2026 07:40 | 43.294 | 43.958 | 18 | 7.3263 | 8.7479 | -1.4216 | 52.4876 | 6.9 | 8.6228 | -1.7228 |  | 31-03-2026 07:40 | 45.407 | 46.089 | 18.4 | 7.6815 | 8.7479 | -1.0664 | 52.4876 | 7.3 | 8.6228 | -1.3228 |  | 31-03-2026 07:40 | 46.11 | 47.355 | 18.6 | 7.8925 | 8.7479 | -0.85543 | 52.4876 | 7.3 | 8.6228 | -1.3228 |  | 31-03-2026 07:40 | 43.866 | 44.543 | 17.7 | 7.4238 | 8.3226 | -0.89874 | 49.9355 | 7 | 8.2036 | -1.2036 |  | 31-03-2026 07:40 | 78.8997 | 90.5531 | -11.6535 | 543.3189 | 74.8 | 89.2582 | -14.4582 | -4.0997
31-03-2026 07:30 | 185 | 33.29 | 62.001 | 62.773 | 15.2 | 10.4622 | 11.668 | -1.2058 | 70.008 | 7.3 | 11.5012 | -4.2012 |  | 31-03-2026 07:30 | 61.975 | 63.295 | 15.5 | 10.5492 | 11.668 | -1.1188 | 70.008 | 7.4 | 11.5012 | -4.1012 |  | 31-03-2026 07:30 | 61.246 | 62.034 | 15.2 | 10.339 | 11.668 | -1.329 | 70.008 | 7.2 | 11.5012 | -4.3012 |  | 31-03-2026 07:30 | 62.186 | 62.986 | 15.4 | 10.4977 | 11.668 | -1.1703 | 70.008 | 7.4 | 11.5012 | -4.1012 |  | 31-03-2026 07:30 | 44.951 | 45.64 | 11.1 | 7.6067 | 8.643 | -1.0363 | 51.8578 | 5.3 | 8.5194 | -3.2194 |  | 31-03-2026 07:30 | 43.713 | 44.379 | 11.1 | 7.3965 | 8.643 | -1.2465 | 51.8578 | 5.2 | 8.5194 | -3.3194 |  | 31-03-2026 07:30 | 45.438 | 46.115 | 11.1 | 7.6858 | 8.643 | -0.95713 | 51.8578 | 5.3 | 8.5194 | -3.2194 |  | 31-03-2026 07:30 | 46.076 | 47.336 | 11.3 | 7.8893 | 8.643 | -0.75363 | 51.8578 | 5.3 | 8.5194 | -3.2194 |  | 31-03-2026 07:30 | 44.083 | 44.763 | 10.7 | 7.4605 | 8.2227 | -0.76221 | 49.3363 | 5.1 | 8.1051 | -3.0051 |  | 31-03-2026 07:30 | 79.8868 | 89.4666 | -9.5797 | 536.7995 | 55.5 | 88.1872 | -32.6872 | -24.3868
31-03-2026 07:20 | 84 | 30.14 | 26.393 | 26.932 | 7.9 | 4.4887 | 5.3581 | -0.86939 | 32.1484 | 3.9 | 5.2814 | -1.3814 |  | 31-03-2026 07:20 | 27.201 | 27.75 | 8.1 | 4.625 | 5.3581 | -0.73306 | 32.1484 | 4 | 5.2814 | -1.2814 |  | 31-03-2026 07:20 | 26.773 | 27.319 | 8 | 4.5532 | 5.3581 | -0.80489 | 32.1484 | 4.1 | 5.2814 | -1.1814 |  | 31-03-2026 07:20 | 26.943 | 27.493 | 8 | 4.5822 | 5.3581 | -0.77589 | 32.1484 | 4 | 5.2814 | -1.2814 |  | 31-03-2026 07:20 | 19.402 | 19.895 | 5.8 | 3.3158 | 3.9689 | -0.6531 | 23.8136 | 3 | 3.9122 | -0.91218 |  | 31-03-2026 07:20 | 19.888 | 20.262 | 5.9 | 3.377 | 3.9689 | -0.59193 | 23.8136 | 3.1 | 3.9122 | -0.81218 |  | 31-03-2026 07:20 | 19.644 | 20.111 | 5.8 | 3.3518 | 3.9689 | -0.6171 | 23.8136 | 3 | 3.9122 | -0.91218 |  | 31-03-2026 07:20 | 19.747 | 20.504 | 6 | 3.4173 | 3.9689 | -0.5516 | 23.8136 | 3.1 | 3.9122 | -0.81218 |  | 31-03-2026 07:20 | 18.925 | 19.382 | 5.6 | 3.2303 | 3.7759 | -0.54561 | 22.6557 | 2.9 | 3.722 | -0.82195 |  | 31-03-2026 07:20 | 34.9413 | 41.0839 | -6.1426 | 246.5035 | 31.1 | 40.4964 | -9.3964 | -3.8413
31-03-2026 07:10 | 59 | 27.55 | 22.469 | 22.963 | 4 | 3.8272 | 3.7981 | 0.029028 | 22.7888 | 2.7 | 3.7438 | -1.0438 |  | 31-03-2026 07:10 | 22.633 | 23.135 | 4.1 | 3.8558 | 3.7981 | 0.057695 | 22.7888 | 2.8 | 3.7438 | -0.94383 |  | 31-03-2026 07:10 | 22.582 | 23.081 | 3.9 | 3.8468 | 3.7981 | 0.048695 | 22.7888 | 2.6 | 3.7438 | -1.1438 |  | 31-03-2026 07:10 | 22.612 | 23.285 | 4 | 3.8808 | 3.7981 | 0.082695 | 22.7888 | 2.7 | 3.7438 | -1.0438 |  | 31-03-2026 07:10 | 16.438 | 17.102 | 2.8 | 2.8503 | 2.8134 | 0.036897 | 16.8806 | 1.9 | 2.7732 | -0.8732 |  | 31-03-2026 07:10 | 16.818 | 17.237 | 2.8 | 2.8728 | 2.8134 | 0.059397 | 16.8806 | 1.9 | 2.7732 | -0.8732 |  | 31-03-2026 07:10 | 16.776 | 17.192 | 2.8 | 2.8653 | 2.8134 | 0.051897 | 16.8806 | 1.9 | 2.7732 | -0.8732 |  | 31-03-2026 07:10 | 17.125 | 17.904 | 2.9 | 2.984 | 2.8134 | 0.17056 | 16.8806 | 2 | 2.7732 | -0.7732 |  | 31-03-2026 07:10 | 16.102 | 16.51 | 2.7 | 2.7517 | 2.6766 | 0.075031 | 16.0598 | 1.9 | 2.6384 | -0.73836 |  | 31-03-2026 07:10 | 29.7348 | 29.1229 | 0.6119 | 174.7376 | 20.4 | 28.7065 | -8.3065 | -9.3348
31-03-2026 07:00 | 27 | 26.12 | 9.197 | 9.553 | 1.3 | 1.5922 | 1.7469 | -0.15474 | 10.4815 | 1.3 | 1.7219 | -0.42193 |  | 31-03-2026 07:00 | 9.37 | 9.946 | 1.3 | 1.6577 | 1.7469 | -0.089242 | 10.4815 | 1.3 | 1.7219 | -0.42193 |  | 31-03-2026 07:00 | 9.12 | 9.479 | 1.3 | 1.5798 | 1.7469 | -0.16708 | 10.4815 | 1.3 | 1.7219 | -0.42193 |  | 31-03-2026 07:00 | 9.225 | 9.98 | 1.3 | 1.6633 | 1.7469 | -0.083576 | 10.4815 | 1.3 | 1.7219 | -0.42193 |  | 31-03-2026 07:00 | 6.538 | 7.139 | 0.9 | 1.1898 | 1.294 | -0.10417 | 7.764 | 0.9 | 1.2755 | -0.3755 |  | 31-03-2026 07:00 | 6.66 | 6.939 | 0.9 | 1.1565 | 1.294 | -0.13751 | 7.764 | 0.9 | 1.2755 | -0.3755 |  | 31-03-2026 07:00 | 6.548 | 6.833 | 0.9 | 1.1388 | 1.294 | -0.15517 | 7.764 | 0.9 | 1.2755 | -0.3755 |  | 31-03-2026 07:00 | 6.727 | 7.274 | 0.9 | 1.2123 | 1.294 | -0.081673 | 7.764 | 0.9 | 1.2755 | -0.3755 |  | 31-03-2026 07:00 | 6.334 | 6.614 | 0.8 | 1.1023 | 1.2311 | -0.12875 | 7.3865 | 0.8 | 1.2135 | -0.41348 |  | 31-03-2026 07:00 | 12.2928 | 13.3947 | -1.1019 | 80.3685 | 9.6 | 13.2032 | -3.6032 | -2.6928
[110 empty] | Total: - | 16869.3863 | 17054.5974 | -185.2111 |  | 16570.5 | 16810.7166 | -240.2166 | -298.8863
Sum:- | 37849 |  | 13064.296 |  | 86802.9 |  |  |  |  | 2158.6 | 2192.4107 | -33.8107 | 0.99533 |  | 12739.771 |  | 85234.8 |  |  |  |  | 2172.4 | 2192.4107 | -20.0107 | 0.98419 |  | 12916.946 |  | 86090.8 |  |  |  |  | 2141.4 | 2192.4107 | -51.0107 | 0.97391 |  | 12903.895 |  | 86609.3 |  |  |  |  | 2151.9 | 2192.4107 | -40.5107 | 0.98385 |  | 9717.591 |  | 64676.5 |  |  |  |  | 1610.5 | 1624.0079 | -13.5079 | 0.98501 |  | 9614.577 |  | 64203.3 |  |  |  |  | 1596.2 | 1624.0079 | -27.8079 | 0.98117 |  | 9627.793 |  | 64329.8 |  |  |  |  | 1598.8 | 1624.0079 | -25.2079 | 0.98152 |  | 9723.133 |  | 64919.9 |  |  |  |  | 1612.4 | 1624.0079 | -11.6079 | 0.97427 |  | 9181.008 |  | 61570.8 |  |  |  |  | 1528.3 | 1545.0424 | -16.7424 | 0.98514 | [8 empty] | -1.772%