## Y24-Y25
Month | Irradiance (kWh/m²) | Energy (MWh), Expected Main Meter( PVSyst) | Energy (MWh), Actual main meter | % Generation (Actual / Expected) | Loss vs PVsyst (MWh) | PR (%) | Specific Yield (kWh/kWp) | CUF (%) | Plant+Grid Availability (%) | Energy (MWh) INV Actual | Energy (MWh) INV PVsyst | % of Energy available at main meter Actual | % of Energy available at main meter PVsyst
YOY-2024-2025
2024-10-01 |  | 472.7 | 136.78 | 28.9359 | -335.92 |  | 1.3967 | 5.784% |  | 135.94 | 488.71 | 100.6179 | 96.72%
2024-11-01 |  | 416 | 369.621 | 88.8512 | -46.379 |  | 3.9001 | 15.65% | 90.78% | 367.819 | 430.54 | 100.4899 | 96.62%
2024-12-01 |  | 424.4 | 387.44 | 91.2912 | -36.96 |  | 3.9562 | 14.68% |  | 345.058 | 438.92 | 112.2826 | 96.69%
2025-01-01 | 167.71 | 436.4 | 398.409 | 91.2945 | -37.991 | 75.2% | 4.0682 | 16.74% | 94.08% | 393.382 | 450.85 | 101.2779 | 96.79%
2025-02-01 | 163.05 | 395.4 | 435.424 | 110.1224 | 40.024 | 84.53% | 4.9226 | 18.58% | 96.42% | 436.662 | 456.47 | 99.7165 | 86.62%
2025-03-01 | 218.94 | 466.1 | 564.659 | 121.1455 | 98.559 | 81.64% | 5.7658 | 24.13% | 95.52% | 567.172 | 540.17 | 99.5569 | 86.29%
2025-04-01 | 219.4 | 512.4 | 562.384 | 109.7549 | 49.984 | 81.14% | 5.934 | 23.94% | 97.78% | 562.671 | 530.61 | 99.949 | 96.57%
2025-05-01 | 191.26 | 519.4 | 529.973 | 102.0356 | 10.573 | 87.71% | 5.4116 | 22.56% | 95.56% | 530.192 | 537.01 | 99.9587 | 96.72%
2025-06-01 | 175.8 | 454.7 | 452.394 | 99.4929 | -2.306 | 81.46% | 4.7734 | 20.02% | 97.44% | 470.45 | 469.48 | 96.162 | 96.85%
2025-07-01 | 116.1 | 341.3 | 343.351 | 100.6009 | 2.051 | 93.61% | 3.506 | 14.58% | 96.38% | 342.57 | 403.92 | 100.228 | 84.5%
2025-08-01 | 157.54 | 373.4 | 394.45 | 105.6374 | 21.05 | 79.26% | 4.0278 | 16.74% | 89.26% | 393.469 | 386.27 | 100.2493 | 96.67%
2025-09-01 | 173.95 | 438.1 | 434.15 | 99.0984 | -3.95 | 79% | 4.5809 | 18.52% | 95.82% | 435.2 | 452.92 | 99.7587 | 96.73%
2025-10-01 | 171 | 472.7 | 433.3 | 91.6649 | -39.4 | 80.21% | 4.4245 | 18.64% | 96.94% | 438.06 | 488.71 | 98.9134 | 96.72%
2025-11-01 | 163.81 | 416 | 419.548 | 100.8529 | 3.548 | 81.07% | 4.2841 | 18.1% | 93.24% | 425.5 | 419.5005 | 98.6012 | 99.17%
2025-12-01 | 166.4 | 424.4 | 425.015 | 100.1449 | 0.615 | 80.85% | 4.3399 | 18.35% | 94.05% | 431.286 | 425.2049 | 98.546 | 99.81%
TOTAL-24 |  | 1313.1 | 893.841 | 68.0711 | -419.259 |  | 3.0755 | 12.1689 |  | 848.817 | 1358.17
TOTAL-25 | 2084.96 | 5250.3 | 5393.057 | 102.719 | 142.757 | 81.8793 | 4.6771 | 19.6093 |  | 5426.614 | 5561.1153
TOTAL_24-25 |  | 6563.4 | 6286.898 | 95.7872 | -276.502 |  | 5.4523 | 22.6765 |  | 6275.431 | 6919.2853

## Y26
Month | Irradiance (kWh/m²) | Energy (MWh), Expected Main Meter( PVSyst) | Energy (MWh), Actual main meter | % Generation (Actual / Expected) | Loss vs PVsyst (MWh) | PR (%) | Specific Yield (kWh/kWp) | CUF (%) | Plant+Grid Availability (%) | Energy (MWh) INV Actual | Energy (MWh) INV PVsyst | % of Energy available at main meter Actual | % of Energy available at main meter PVsyst
YOY-2026
2026-01-01 | 169.98 | 436.4 | 449.674 | 103.0417 | 13.274 | 83.7407 | 4591.8369 | 19.4219 | 94.16% | 456.472 | 450.8521 | 98.5108 | 96.7945
2026-02-01 | 177.17 | 395.4 | 436.69 | 110.4426 | 41.29 | 78.0225 | 4459.2511 | 20.8876 | 95.22% | 443.4129 | 456.4717 | 98.4838 | 86.6209
2026-03-01 | 184.9945 | 466.1 | 524.9252 | 112.6207 | 58.8252 | 89.8204 | 5360.2627 | 25.119 | 96.48% | 533.2373 | 540.1746 | 98.4412 | 86.2869
2026-04-01 |  |  |  |  | 0
2026-05-01 |  |  |  |  | 0
2026-06-01 |  |  |  |  | 0
2026-07-01 |  |  |  |  | 0
2026-08-01 |  |  |  |  | 0
2026-09-01 |  |  |  |  | 0
2026-10-01 |  |  |  |  | 0
2026-11-01 |  |  |  |  | 0
2026-12-01 |  |  |  |  | 0
TOTAL-26 | 532.1445 | 1297.9 | 1411.2892 | 108.7364 | 113.3892 | 83.9505 | 1.2239 | 5.1786 |  | 1433.1222 | 1447.4984 | 98.4765 | 89.665