## March_2026
Date | Generation(kWh) at Inv. I/P, actual | Generation(kWh) at Inv. O/P, DGR | MFM reading(kWh), DGR | Main meter reading(kWh), DGR | Inv. Loss(kWh), %age | AC Loss(Inv. to MFM) %age | TL Line loss %age ( MFM to Main meter) | Energy Loss(kWh), IG vs MFM | Energy Loss(kWh), MFM-Main meter | Energy loss(kwh), (IG O/P to main meter) | % Losses (IG O/P-MM) | Remarks
1st March_2026 | 17279 | 17274.4 | 17189 | 17013 | 0.02662% | 0.4944% | 1.024% | 85.4 | 176 | 261.4 | 1.513%
2nd March_2026 | 17506.4953 | 17319 | 17240 | 17053 | 1.071% | 0.4561% | 1.085% | 79 | 187 | 266 | 1.536%
3rd March_2026 | 17502.3047 | 17226.4 | 17150 | 16957 | 1.576% | 0.4435% | 1.125% | 76.4 | 193 | 269.4 | 1.564%
4th March_2026 | 18276.2203 | 18060.9 | 17941 | 17778 | 1.178% | 0.6639% | 0.9085% | 119.9 | 163 | 282.9 | 1.566%
5th March_2026 | 19561.0233 | 19310.7 | 19212 | 19000 | 1.28% | 0.5111% | 1.103% | 98.7 | 212 | 310.7 | 1.609%
6th March_2026 | 19168.5005 | 19068.7 | 18975 | 18766 | 0.5206% | 0.4914% | 1.101% | 93.7 | 209 | 302.7 | 1.587%
7th March_2026 | 19792.8807 | 19538.6 | 19423 | 19221 | 1.285% | 0.5916% | 1.04% | 115.6 | 202 | 317.6 | 1.626%
8th March_2026 | 19258 | 19145.8 | 19048 | 18842 | 0.5826% | 0.5108% | 1.081% | 97.8 | 206 | 303.8 | 1.587%
9th March_2026 | 16352.1303 | 16158.7 | 16068 | 15883 | 1.183% | 0.5613% | 1.151% | 90.7 | 185 | 275.7 | 1.706%
10th March_2026 | 18847.2098 | 18624.1 | 18544 | 18333 | 1.184% | 0.4301% | 1.138% | 80.1 | 211 | 291.1 | 1.563%
11th March_2026 | 18732.5947 | 18592.8 | 18516 | 18308 | 0.7463% | 0.4131% | 1.123% | 76.8 | 208 | 284.8 | 1.532%
12th March_2026 | 19274.5385 | 18915.7 | 18840 | 18627 | 1.862% | 0.4002% | 1.131% | 75.7 | 213 | 288.7 | 1.526%
13th March_2026 | 18806.9373 | 18357.7 | 18289 | 18077 | 2.389% | 0.3742% | 1.159% | 68.7 | 212 | 280.7 | 1.529%
14th March_2026 | 16704.3087 | 16557.2 | 16489 | 16309 | 0.8807% | 0.4119% | 1.092% | 68.2 | 180 | 248.2 | 1.499%
15th March_2026 | 14916.1557 | 15176.9 | 15110 | 14941 | -1.748% | 0.4408% | 1.118% | 66.9 | 169 | 235.9 | 1.554% | Generation(kWh) at Inv. I/P, actual - DATA MISSING
16th March_2026 | 18941.4833 | 18823.1 | 18744 | 18519 | 0.625% | 0.4202% | 1.2% | 79.1 | 225 | 304.1 | 1.616%
17th March_2026 | 13202.0803 | 15550.6 | 15493 | 15319 | -17.79% | 0.3704% | 1.123% | 57.6 | 174 | 231.6 | 1.489% | Generation(kWh) at Inv. Input- DATA MISSING due to trackSo Work
18th March_2026 | 14972.1255 | 14909.4 | 14849 | 14698 | 0.4189% | 0.4051% | 1.017% | 60.4 | 151 | 211.4 | 1.418% |  | _
19th March_2026 | 14459.4623 | 14210.5 | 14127 | 13976 | 1.722% | 0.5876% | 1.069% | 83.5 | 151 | 234.5 | 1.65%
20th March_2026 | 19601.6347 | 19259.1 | 19144 | 18940 | 1.747% | 0.5976% | 1.066% | 115.1 | 204 | 319.1 | 1.657%
21st March_2026 | 16134.5913 | 16138.1 | 16078 | 15895 | -0.02175% | 0.3724% | 1.138% | 60.1 | 183 | 243.1 | 1.506% | Generation(kWh) at Inv. I/P, actual - DATA MISSING
22nd March_2026 | 14589.0357 | 14483.1 | 14417 | 14249 | 0.7261% | 0.4564% | 1.165% | 66.1 | 168 | 234.1 | 1.616%
23rd March_2026 | 14044.5985 | 13669 | 13590 | 13434 | 2.674% | 0.578% | 1.148% | 79 | 156 | 235 | 1.719% | Generation(kWh) at Inv. I/P, actual - DATA MISSING
24th March_2026 | 16949 | 16231.6 | 16163 | 15989 | 4.233% | 0.4226% | 1.077% | 68.6 | 174 | 242.6 | 1.495% | Inv. Loss is showing high because 3,4, datas of inv. data are missed due to this inv. input ke gen. add nhi huye hai jo miss huye hai but output me already add ho jaate hai. kyuki output me daily energy section from trackSo wale data use karte hai analysis ke liye jisme ki energy har 10 min. ka add hote rehta hai esa input ke case me nahi hai
25th March_2026 | 16222 | 15691.8 | 15637 | 15487 | 3.268% | 0.3492% | 0.9593% | 54.8 | 150 | 204.8 | 1.305%
26th March_2026 | 17966 | 17939.4 | 17852 | 17666 | 0.1481% | 0.4872% | 1.042% | 87.4 | 186 | 273.4 | 1.524%
27th March_2026 | 18659 | 18374.1 | 18304 | 18092 | 1.527% | 0.3815% | 1.158% | 70.1 | 212 | 282.1 | 1.535%
28th March_2026 | 17307 | 18134 | 18021 | 17843 | -4.778% | 0.6231% | 0.9877% | 113 | 178 | 291 | 1.605% | Inv. 3, 5 & 7 was offline on trackSo from 14:40 to 19:00, that's why Inv. input energy data is very less here
29th March_2026 | 19074 | 18842.8 | 18742 | 18534 | 1.212% | 0.535% | 1.11% | 100.8 | 208 | 308.8 | 1.639%
30th March_2026 | 15567 | 15083.1 | 15012 | 14846 | 3.108% | 0.4714% | 1.106% | 71.1 | 166 | 237.1 | 1.572%
31st March_2026 | 16869 | 16570 | 17110 | 16330.1635 | 1.772% | -3.259% | 4.558% | -540 | 779.8365 | 239.8365 | 1.447%
Total | 536536.3115 | 533237.3 | 531317 | 524925.1635 | 0.6149% | 0.3601% | 1.203% | 1920.3 | 6391.8365 | 8312.1365 | 1.5588
Expected |  | -6937.31 |  | 58825.1635