## March_26 Gen. & Loss Analysis
2026-03-01 | Actual Irradiance (kWh/m²) | Actual Irradiance (kWh/m²), during downtime period | PVsyst Irradiance (kWh/m²) | Expected energy gen. at module(kWh) | Expected Inv. I/P DC energy at MPPT | Actual Inv. I/P DC Energy at MPPT | Diff. b/w expec. & actual energy gen. at MPPT %age | DC Loss %age | Expected Inv. O/P AC energy | Actual Inv. O/P AC Energy | Diff. b/w expec. & actual inv. O/P AC energy %age | Inv. Loss %age | Expected Energy (kWh), MFM | Actual Energy(MFM) (kWh | Diff. b/w expec. & actual MFM meter energy %age | Plant AC Loss %age | Expected Energy (kWh), Main meter | Actual main meter energy (TrackSo), kWh | Diff. b/w expec. & actual main meter energy %age | TL Line Loss %age | PVsyst PR (%) | Day PR %, at main meter | Sum of diff. b/w exp. & actual energy Gen. | Overall Loss %age (Module-Main meter) | Gain/Loss of Actual vs Expected(kWh), Main meter | Downtime Periods | Total plant Down Time(Minutes), ( time considering from 07:00 to 19:00) | Total Grid Down Time(Minutes), ( time considering from 07:00 to 19:00) | Day time Plant availability, %age | Day Time Grid Availability( % ) | Expected Downtime losses(kWh), Inv. I/P, MPPT | Expected Downtime losses(kWh), Inv. O/P | Expected Downtime losses(kWh), MFM | Expected Downtime losses(kWh), Main Meter | Ambient Temp.(°C) (Average) | Wind Speed [Km/hr] (Average) | Module Temp.(°C) (Average) | Wheather | Remarks
1st March | 6.5812 | 0 | 6.4452 | 20790.5636 | 18096 | 17279 | -4.515% | -16.89% | 17838 | 17274 | -3.162% | -0.02894% | 17451.4551 | 17189 | -1.504% | -0.4921% | 17261.2343 | 17000 | -1.513% | -1.1% | 73.9% | 87.6% | -10.69% | -18.51% | -261.2343 | ------ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 28.8449 | 1.7048 | 44.0159 | 1st Half: Sunny, 2nd Half: Sunny
2nd March | WMS Not working | 0 | 6.4452 | WMS Not working | WMS Not working | 17506.4953 | WMS Not working | WMS Not working | WMS Not working | 17318.9 | WMS Not working | -1.072% | WMS Not working | 17226 | WMS Not working | -0.5364% | WMS Not working | 17053 | WMS Not working | -1.004% | 73.9% | WMS Not working | WMS Not working | WMS Not working | WMS Not working | ------ | 0 | 0 | 100% | 100% | WMS Not working | WMS Not working | WMS Not working | WMS Not working | WMS Not working | WMS Not working | WMS Not working | 1st Half: Sunny, 2nd Half: Sunny
3rd March |  | 0 | 6.4452 |  |  | 17502.3047 |  |  |  | 17226.4 |  | -1.576% |  | 17140 |  | -0.5016% |  | 16957 |  | -1.068% | 73.9% |  |  |  |  | 17:05 PM to 23:00 PM | 115 | 0 | 84.03% | 100% | [7 empty] | 1st Half: Sunny, 2nd Half: Sunny
4th March | 7.0335 | 0 | 6.4452 | 22219.5298 | 19316.5557 | 18276.2203 | -5.386% | -17.75% | 19040.329 | 18026.8 | -5.323% | -1.365% | 18628.2323 | 17965 | -3.56% | -0.3428% | 18425.1846 | 17778 | -3.512% | -1.041% | 73.9% | 85.84% | -17.78% | -20.5% | -647.1846 | ------ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.8477 | 1.1978 | 44.4021 | 1st Half: Sunny, 2nd Half: Sunny
5th March | 7.4955 | 0 | 6.4452 | 23679.034 | 20565.7608 | 19561.0233 | -4.885% | -17.39% | 20271.6704 | 19310.6 | -4.741% | -1.28% | 19832.9234 | 19212 | -3.131% | -0.5106% | 19616.7446 | 19000 | -3.144% | -1.103% | 73.9% | 86.14% | -15.9% | -20.29% | -616.7446 | ------ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.8051 | 2.2268 | 44.5551 | 1st Half: Sunny, 2nd Half: Sunny
6th March | 7.4195 | 0.081067 | 6.4452 | 23182.8447 | 20354.0121 | 19168.5005 | -5.824% | -17.32% | 20062.9497 | 19068.7 | -4.956% | -0.5206% | 19628.7202 | 18975 | -3.33% | -0.4914% | 19414.7671 | 18766 | -3.342% | -1.101% | 73.9% | 86.11% | -17.45% | -19.43% | -648.7671 | 16:48 - 17:00 | 0 | 12 | 100% | 98.33% | 206.344 | 203.3933 | 199 | 196.8309 | 29.1232 | 1.9209 | 45.0704 | 1st Half: Sunny, 2nd Half: Sunny
7th March | 7.5822 | 0 | 6.4452 | 23952.8227 | 20817.7713 | 19792.8807 | -4.923% | -17.37% | 20520.0772 | 19538.5 | -4.783% | -1.285% | 20075.9538 | 19423 | -3.252% | -0.5911% | 19857.1259 | 19221 | -3.204% | -1.04% | 73.9% | 86.06% | -16.16% | -20.28% | -636.1259 | ------ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.9533 | 2.138 | 44.3003 | 1st Half: Sunny, 2nd Half: Sunny
8th March | 7.4442 | 0 | 6.4452 | 23516.8669 | 20463 | 19258 | -5.889% | -18.11% | 20170 | 19146 | -5.077% | -0.5816% | 19733.8705 | 19048.35 | -3.474% | -0.51% | 19518.7713 | 18842 | -3.467% | -1.083% | 73.9% | 86.02% | -17.91% | -20.28% | -676.7713 | ------ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.9842 | 1.4764 | 44.5984 | 1st Half: Sunny, 2nd Half: Sunny
9th March | 7.5498 | 1.2334 | 6.4452 | 19954.0866 | 20703.3875 | 16352.1303 | -21.02% | -18.05% | 20407.3291 | 16158.2 | -20.82% | -1.186% | 19965.646 | 16068 | -19.52% | -0.5582% | 19748.0204 | 15883 | -19.57% | -1.151% | 73.9% | 71.6% | -80.93% | -20.95% | -3865.0204 | 07:03 AM to 10:03 AM | 0 | 0 | 100% | 100% | 3499.5254 | 3449.4821 | 3374.9733 | 3338.1861 | 31.5016 | 1.5115 | 44.9799 | 1st Half: Sunny 2nd Half: Sunny
10th March | 7.2042 | 0 | 6.4452 | 22758.6829 | 19760.5421 | 18847.2098 | -4.622% | -17.19% | 19477.9663 | 18623.9 | -4.385% | -1.185% | 19056.3977 | 18543.65 | -2.691% | -0.4309% | 18848.683 | 18333 | -2.736% | -1.136% | 73.9% | 86.47% | -14.43% | -19.94% | -515.683 | ---- | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 31.7658 | 1.6286 | 44.5473 | 1st Half: Sunny 2nd Half: Sunny
11th March | 7.1778 | 0 | 6.4452 | 22675.4933 | 19701.072 | 18732.5947 | -4.916% | -17.39% | 19419.3466 | 18592.7 | -4.257% | -0.7468% | 18996.5798 | 18516 | -2.53% | -0.4125% | 18789.5171 | 18308 | -2.563% | -1.123% | 73.9% | 86.79% | -14.27% | -19.67% | -481.5171 | ---- | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 32.2889 | 1.6667 | 44.9218 | 1st Half: Sunny 2nd Half: little cloudy
12th March | 7.269 | 0 | 6.4452 | 22963.4979 | 19961.4019 | 19274.5385 | -3.441% | -16.06% | 19675.9538 | 18915.5 | -3.865% | -1.863% | 19250.1001 | 18840.35 | -2.129% | -0.3973% | 19040.274 | 18627 | -2.171% | -1.132% | 73.9% | 87.19% | -11.6% | -19.46% | -413.274 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.9919 | 1.8813 | 44.8905 | 1st Half: partially cloudy 2nd Half: partially cloudy
13th March | 7.1318 | 0 | 6.4452 | 22530.1747 | 19589.4462 | 18806.9373 | -3.995% | -16.53% | 19309.3171 | 18357.7 | -4.928% | -2.389% | 18891.3987 | 18288.65 | -3.191% | -0.3761% | 18685.4824 | 18077 | -3.256% | -1.157% | 73.9% | 86.36% | -15.37% | -20.45% | -608.4824 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 31.5747 | 1.9482 | 45.2748 | 1st Half: partially cloudy 2nd Half: partially cloudy
14th March | 6.1648 | 0 | 6.4452 | 19475.325 | 16951.3372 | 16704.3087 | -1.457% | -14.23% | 16708.9331 | 16557 | -0.9093% | -0.8819% | 16347.2957 | 16489 | 0.8668% | -0.4107% | 16169.1102 | 16309 | 0.8652% | -1.092% | 73.9% | 90.06% | -0.6346% | -16.61% | 139.8898 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.5594 | 2.8086 | 45.0536 | 1st Half: little cloudy 2nd Half: little cloudy
15th March | 6.986 | 1.3297 | 6.4452 | 17868.6594 | 19192.6537 | 14916.1557 | -22.28% | -16.52% | 18918.1988 | 15176.9 | -19.78% | 1.748% | 18508.7455 | 15110 | -18.36% | -0.4408% | 18307.0001 | 15110 | -17.46% | 0% | 73.9% | 73.74% | -77.88% | -15.22% | -3197.0001 | 14:27 PM to 16:01 PM | 0 | 94 | 100% | 86.94% | 3228.1456 | 3181.9831 | 3113.2523 | 3079.3179 | 29.8955 | 2.4018 | 45.4321 | 1st Half: sunny 2nd Half: partially cloudy
16th March | 7.1877 | 0 | 6.4452 | 22706.5578 | 19750.4208 | 18941.4833 | -4.096% | -16.58% | 19467.9898 | 18822.5 | -3.316% | -0.6282% | 19046.6371 | 18744 | -1.589% | -0.4171% | 18839.0288 | 18519 | -1.699% | -1.2% | 73.9% | 87.5% | -10.7% | -18.83% | -320.0288 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.0273 | 2.3745 | 44.414 | 1st Half: sunny 2nd Half: partially cloudy
17th March | 6.5093 | 0.4973 | 6.4452 | 18992.6145 | 17905.1577 | 13202.0803 | -26.27% | -30.49% | 17649.114 | 15484.2 | -12.27% | 17.29% | 17267.1279 | 15493 | -10.27% | 0.05683% | 17078.9162 | 15350 | -10.12% | -0.923% | 73.9% | 80.03% | -58.93% | -14.07% | -1728.9162 | 11:08 AM to 11:11 AM, 12:16 PM to 12:48 PM, 04:17 PM to 04:19 PM | 0 | 37 | 100% | 94.86% | 1628.5418 | 1605.2536 | 1570.5801 | 1553.4608 | 28.6814 | 1.6258 | 44.2168 | 1st Half: little cloudy 2nd Half: partially cloudy | increase loss reason :- every inverter 7 time data missing
18th March | 5.515 | 0 | 6.4452 | 17422.4365 | 15185.6648 | 14972.1255 | -1.406% | -14.06% | 14968.5098 | 14909.4 | -0.3949% | -0.4189% | 14644.541 | 14849 | 1.396% | -0.4051% | 14484.9155 | 14650 | 1.14% | -1.34% | 73.9% | 90.28% | 0.7348% | -16.23% | 165.0845 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.7531 | 2.6837 | 44.6074 | 1st Half: partially cloudy, 2nd Half: partially cloudy
19th March | 5.2922 | 0 | 6.4452 | 16718.4837 | 14592.4051 | 14459.4623 | -0.911% | -13.51% | 14383.7337 | 14210.4 | -1.205% | -1.722% | 14072.4214 | 14127.35 | 0.3903% | -0.5844% | 13919.0321 | 14000 | 0.5817% | -0.9014% | 73.9% | 88.37% | -1.144% | -16.72% | 80.9679 | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 21.3585 | 2.8814 | 39.963 | 1st Half : partially cloudy 2nd Half : fully cloudy
20th March | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 0 | 6.4452 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 19601.6347 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 19258.6 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | -1.75% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 19144 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | -0.5951% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 18900 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | -1.275% | 73.9% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | ____ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 1st Half: sunny 2nd Half: partially sunny | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace
21st March | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 0 | 6.4452 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 16134.5913 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 16137.9 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 0.02051% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 16078 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | -0.3712% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 15895 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | -1.138% | 73.9% | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | _______ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace | 1st Half: sunny 2nd Half: partially sunny | WMS not working from 20th march 2026, 08:40 am, Logger damaged, need to replace
22nd March | 6.5962 | 0.98683 | 6.4452 | 17720.4449 | 18029.3926 | 14589.0357 | -19.08% | -17.67% | 17771.5723 | 14483.5 | -18.5% | -0.7234% | 17386.9358 | 14416 | -17.09% | -0.466% | 17197.4182 | 14250 | -17.14% | -1.151% | 73.9% | 73.77% | -71.81% | -20.01% | -2947.4182 | 15:04 pm to 17:40 pm | 0 | 156 | 100% | 78.33% | 2676.1217 | 2637.8531 | 2580.8755 | 2552.7439 | 27.9863 | 1.5784 | 45.8462 | 1st Half: sunny 2nd Half: partially cloudy | increase due to single phase switchyard braker jumper connection
23rd March | 7.098 | 1.7027 | 6.4452 | 17044.2922 | 19190.4946 | 14044.5985 | -26.81% | -17.6% | 18916.0706 | 13666.5 | -27.75% | -2.692% | 18506.6633 | 13590 | -26.57% | -0.5598% | 18304.9407 | 13434 | -26.61% | -1.148% | 73.9% | 65.33% | -107.7% | -22% | -4870.9407 | 07:45 AM TO 11:01 | 0 | 196 | 100% | 72.78% | 4681.7969 | 4614.8472 | 4515.1665 | 4465.9512 | 28.8933 | 1.5084 | 48.6879 | 1st Half* : sunny *2nd Half* : partially cloudy
24th March | 6.8825 | 0.10457 | 6.4452 | 21412.1692 | 18695 | 16949 | -9.339% | -20.84% | 18427 | 16232 | -11.91% | -4.23% | 18028.3948 | 16163.65 | -10.34% | -0.4211% | 17831.8853 | 15989 | -10.33% | -1.081% | 73.9% | 79.92% | -41.93% | -26.58% | -1842.8853 | 11:16 to 11:21 17:30 to 17:40 | 0 | 15 | 100% | 97.92% | 326.6249 | 321.9542 | 315 | 311.5665 | 29.951 | 1.2041 | 47.8036 | 1st Half: Partially cloudy 2nd Half: partially cloudy | GSS Side main meter reading is wrong in SCADA so that we have used manual meter reading.
25th March | 6.0882 | 0 | 6.4452 | 19233.1273 | 16540 | 16222 | -1.923% | -15.66% | 16303 | 15692 | -3.748% | -3.267% | 15950.2105 | 15637 | -1.964% | -0.3505% | 15776.3532 | 15500 | -1.752% | -0.8761% | 73.9% | 87.69% | -9.386% | -20.15% | -276.3532 | _______ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 30.9047 | 1.9438 | 48.1419 | 1st Half: sunny 2nd Half: fully cloudy
26th March | 6.7798 | 0 | 6.4452 | 21418.1715 | 18541 | 17966 | -3.101% | -16.12% | 18276 | 17939 | -1.844% | -0.1503% | 17880.2424 | 17852.35 | -0.156% | -0.483% | 17685.3477 | 17650 | -0.1999% | -1.133% | 73.9% | 89.15% | -5.301% | -17.88% | -35.3477 | _______ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.6745 | 2.3053 | 46.6122 | 1st Half: sunny 2nd Half: partially cloudy
27th March | 7.3457 | 0.18033 | 6.4452 | 22636.0045 | 20060 | 18659 | -6.984% | -17.57% | 19773 | 18374 | -7.075% | -1.527% | 19344.8642 | 18303.65 | -5.382% | -0.3829% | 19134.0052 | 18100 | -5.404% | -1.113% | 73.9% | 84.38% | -24.85% | -20.59% | -1034.0052 | 9:29 AM to 9:45 AM | 0 | 16 | 100% | 97.78% | 600.3678 | 591.7825 | 579 | 572.6889 | 29.8936 | 2.4932 | 46.6048 | 1st Half: sunny 2nd Half: little cloudy
28th March | 7.3313 | 0 | 6.4452 | 23160.4151 | 18553 | 17307 | -6.716% | -25.27% | 18287 | 18134 | -0.8367% | 4.778% | 19272.629 | 18021 | -6.494% | -0.6231% | 19062.5574 | 17850 | -6.361% | -0.9489% | 73.9% | 83.61% | -20.41% | -22.07% | -1212.5574 | 16:20 pm to 17:28 pm | 0 | 68 | 100% | 90.56% | 1008.9082 | 994.4808 | 973 | 962.3943 | 30.1896 | 3.137 | 47.3396 | 1st Half: sunny 2nd Half: little cloudy | Inv. 3, 5 & 7 was offline on trackSo from 14:40 to 19:00, that's why Inv. input energy data is very less here
29th March | 7.1747 | 0 | 6.4452 | 22665.4895 | 19568 | 19074 | -2.525% | -15.85% | 19288 | 18843 | -2.307% | -1.211% | 18870.4973 | 18742 | -0.6809% | -0.536% | 18664.8088 | 18550 | -0.6151% | -1.024% | 73.9% | 88.94% | -6.128% | -18.62% | -114.8088 | _______ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.9578 | 3.8524 | 47.7881 | 1st Half: sunny 2nd Half: little cloudy
30th March | 5.8463 | 0.080283 | 6.4452 | 18215.5286 | 15917 | 15567 | -2.199% | -14.54% | 15689 | 15083 | -3.863% | -3.109% | 15349.8111 | 15012 | -2.201% | -0.4707% | 15182.4982 | 14850 | -2.19% | -1.079% | 73.9% | 87.25% | -10.45% | -19.2% | -332.4982 | 08:25 - 08:44 | 0 | 19 | 100% | 97.36% | 195.975 | 193.1725 | 189 | 186.9399 | 29.3934 | 2.9193 | 47.4099 | 1st Half: partially sunny 2nd Half: mostly cloudy
31st March | 6.3082 | 0 | 6.4452 | 19928.1293 | 17055 | 16869 | -1.091% | -15.35% | 16811 | 16571 | -1.428% | -1.767% | 16446.8763 | 16492 | 0.2744% | -0.4767% | 16267.6053 | 16330.1635 | 0.3846% | -0.9813% | 73.9% | 88.92% | -1.859% | -18.58% | 62.5582 | _______ | 0 | 0 | 100% | 100% | 0 | 0 | 0 | 0 | 29.3934 | 2.9193 | 47.4099 | 1st Half: partially sunny 2nd Half: partially cloudy
Sum: | 184.9945 | 6.1963 | 199.8 | 564841.4463 | 505055.4763 | 536536.3115 | -2.0561 | -4.719 | 497831.0613 | 533132.8 | -1.8343 | -0.15324 | 488435.1711 | 530699 | -1.4649 | -0.14089 | 483111.2277 | 525081.1635 | -1.454 | -0.32646 |  | 84.26% | -6.8092 | -5.231 | -26835.0642 |  | 115 | 594 | 99.4296 | 97.0536 | 17856.3762 | 17601.03 | 17220.8478 | 17033.1405
Average | 6.8516 | 0.22652 | 6.4452 | [17 empty] | 0.739 | 0.8375 | [12 empty] | 29.8104 | 2.0103 | 45.2616