## Sheet2
Months | Actual POA / Irradiance (kWh/m²) | Inverter Generation (kWh) | MFM Energy (kWh) | Main Meter / JMR Energy (kWh) | Specific Yield (kWh/kWp) | CUF (%) | PR (%) | PVsyst PR (%) | Inverter → MFM Loss (%) | MFM → Main Meter Line Loss (%) | Total (Inverter → Main Meter Loss) (%) | Daytime Plant Availability (%) | Daytime Grid Availability (%) | % Generation (Actual / Simulated) | % of Energy available at main meter Actual | Module Temp (°C) | Ambient Temp (°C) | Remarks
2025-01-01 | 167.71 | 393.382 | 404.42 | 398.409 | 4.0169 | 16.74% | 75.2% | 86.1% | 2.81% Profit | 1.49% Loss | 1.28% Profit | 94.1% | 96.73% | 91.29% | 101.3% | 27.3 | 22.32 | YoY performance improved significantly with higher PR and availability, leading to increased generation despite similar irradiance.
2026-01-01 | 169.98 | 456.472 | 454.5 | 449.674 | 4.6611 | 19.42% | 83.74% | 86.1% | 0.43% Loss | 1.06% Loss | 1.49% Loss | 98.96% | 98.47% | 103% | 98.51% | 34.21 | 18.12 | "Multiple grid breakdown observed due to 132 kV Siwana side LD messages and line changeovers. Interruptions also recorded due to DF/DT fault (220 kV Balotra line impact). Several trippings from Kerli Nadi GSS (33 kV incomer trips, fuse failures, rural feeder faults). Solar VCB tripping observed due to earth fault (2 instances). Extended outage due to Hinglaj feeder jumper burn & replacement work. Scheduled shutdowns carried out for VCB yearly maintenance, auxiliary transformer maintenance, and module isolation for VOC checking. One inverter (Inv-9) tripped due to T203 module issue (temporarily bypassed). Inv-2 remained off for one full day, contributing to generation loss. Majority of downtime attributed to grid and feeder-side disturbances, internal plant faults minimal."
2025-02-01 | 163.06 | 436.662 | 441.98 | 435.424 | 4.9366 | 18.58% | 84.53% | 76.2% | 1.22% Profit | 1.48% Loss | 0.28% Loss | 98.75% | 97.72% | 110.1% | 99.72% | 27.17 | 32.93 | Multiple grid breakdown observed due to 132 kV Siwana side LD messages, Change over in bus & brunt changeover, mokalsr feedar fault & earthing work in g.s.s . One time plant shutdown taken for testing MCCB spreader by L & T engineer. Multiple time plant shutdown due to over voltage, B & Y phase fuse burnout & OC fault.Majority of downtime attributed to grid and feeder-side disturbances, internal plant faults minimal.
2026-02-01 | 177.17 | 443.41 | 441.032 | 436.69 | 5.0128 | 18.87% | 78.02% | 76.2% | 0.54% Loss | 0.98% Loss | 1.52% Loss | 97.47% | 96.6% | 110.4% | 98.48% | 22.27 | 41.57 | "Multiple grid breakdown observed due to 132 kV Siwana side LD messages and line changeovers. Interruptions also recorded due to DF/DT fault (220 kV Balotra Line Impact) .One time shutdown taken for Epoxy bushing of IDT X'mer replacement and testing of X'mer And Transformer yearly maintenance. Majority of downtime this month due to DF/DT fault (220 kV balotra) nd IDT t/f epoxy busing replacement , testing and yearly maintenance ."
2025-03-01 | 218.94 | 567.172 | 572.67 | 564.659 | 5.7915 | 24.13% | 81.64% | 73.9% | 0.97% Profit | 1.40% Loss | 0.44% Loss | 94.63% | 98.63% | 1.21% | 99.56% | 33.19 | 30.23 | During March 2025, plant performance was moderate with noticeable deviation from expected generation. Generation was impacted due to lower grid availability (~94.31%) and higher downtime (~1270 minutes). Significant downtime losses (~64.141 MWh) were observed, indicating major grid dependency issues. Overall, performance was affected primarily due to grid unavailability and environmental factors. Remarks: I think there may be some calibration issue with module temp. in march 2025 bevause the ambient temp. and module temp. cannot be same. And here both are approx same.
2026-03-01 | 184.994 | 533.23 | 531.317 | 524.92 | 5.4449 | 22.69% | 89.82% | 73.9% | 0.36% Loss | 1.20% Loss | 1.56% Loss | 98.68% | 95.91% | 1.13% | 98.44% | 28.81 | 45.26 | "Compared to March 2025, plant performance in March 2026 showed improvement in terms of better grid availability and significantly reduced downtime losses, indicating improved operational stability. However, despite these improvements, overall generation remained lower than March 2025 primarily due to lower irradiance (POA) and higher ambient and module temperatures, which adversely affected plant efficiency and performance. Overall, operational parameters improved, but environmental factors limited the generation performance."